## Changes & Additions to GC Text
#VALUE! | September GCRP Grid Code Version 14.2 Modification Proposal: ESPS Phase 2
Section/Clause | Description
PC.A9 | New section - "ESPS Requirements All information for ESPS connection applications shall include details of the Transmission System Connection Point. This shall include details listed in PC.A2.1, PC.A2.2 for the Connection Point. The minimum technical, design and operational criteria to be met by ESPSs are specified in the Connection Conditions and the PPM1 section."
PC.A9.1 | New clause "Energy Storage Power Stations (ESPS) Provide manufacturer details on electrical characteristics and operating performance with particular reference to Flicker and Harmonic performance. For each Energy Storge Unit, state: Units Total Installed Energy Storage Quantity MWh Usable Energy Storage Quantity1 MWh Maximum Charging Capacity MW Minimum Charging Capacity2 MW Storage Cycle Efficiency % _________________________ 1 Usable Energy Storage Quantity should consider the maximum exported energy at the metering point, i.e. is net of any normal losses within the ESU installation, and should only consider the normally usable fraction of the energy storage modules 2 Can be 0 MW
PC.A9.2 | New clause - "Energy Storage Unit (ESU) parameters Provide electrical parameters relative to the performance of the ESU. This may include but is not limited to parameters of electrical generator, power electronic converters, electrical control and/or protection systems. Laplace diagrams and associated parameters shall be provided to the TSO where appropriate."
PC.A9.3 | New clause - "Energy Storage Unit (ESU) transformer Provide details of the transformer that connects the ESU with the internal ESPS network. This may include but is not limited to the rating of ESU transformer (MVA or kVA), the ESU transformer voltage ratio (kV) or the ESU transformer impedance (%)."
PC.A9.4 | New clause - "Reactive Compensation Provide details of any additional reactive compensation devices and control systems employed by the ESPS. This shall include Mvar capability, the number of stages in the device and the Mvar capability switched in each stage and any control or protection systems that influence the performance of the ESPS at the Connection Point. Laplace diagrams and associated parameters shall be provided to the TSO where appropriate."
PC.A9.5 | New clause - "ESPS control and protection systems Provide details of any control or protection systems that affect the performance of the ESPS at the Connection Point. This shall include any systems or modes of operation that activate during System Voltage or Frequency excursions including Low Voltage Ride Through (FRT), High Voltage Ride Through, Low Frequency Response and High Frequency Response. The transition between ESPS control modes shall also be specified. Laplace diagrams and associated parameters shall be provided to the TSO where appropriate."
PC.A9.6 | New clause - "Grid Connected Transformer of ESPS Provide details of the transformer that connects the ESPS site with the Distribution/Transmission System (equivalent to the Generator Transformer of a conventional Power Station). This shall include but is not limited to rating of grid transformer (MVA or kVA), transformer Voltage ratio (kV), transformer impedance (%), transformer tap changing control and no-load losses."
PC.A9.7 | New clause - "Internal network of ESPS Provide details of the ESPS’s Collector Network and lay out (by means of a single-line diagram or other description of connections). This shall include but is not limited to a breakdown of how the individual ESUs are connected together as well as how they are connected back to the ESPS substation. Please specify different cable or overhead line types and the individual length of each section of circuit. Type1 Type2 Type3 Extend Table as appropriate Total length (m) Conductor cross section area per core (mm) Conductor type (Al, Cu, etc) Type of insulation Charging capacitance (µF/km) Charging current (Ampere/km) Positive sequence resistance (R1 Ohm/km) Positive sequence reactance (X1 Ohm/km)"
PC.A9.8 | New clause - "Flicker and harmonics Provide details of harmonic or flicker contribution from the ESPS that may affect the performance of the ESPS at the Connection Point. This may include harmonic current injections and phase angles associated with the ESPS. Details of any additional AC filter devices shall also be provided by the ESPS to the TSO."
PC.A9.9 | New clause - "Short Circuit Contribution Provide details of the single-phase to ground, phase-phase and three-phase to ground short circuit contribution from the ESPS at the Connection Point. The ESPS shall provide the TSO with the single-phase and three-phase short circuit contribution for rated conditions, i.e. maximum output from the ESPS with all ESUs and any additional devices in the ESPS contributing to the short circuit current. The ESPS shall also provide the single-phase to ground, phase-phase and three-phase to ground short circuit contribution from an individual ESU. Signature plots of the short circuit contribution from an individual ESU shall also be supplied by the ESPS."
OC.5.3 | The text "and (d) Energy Storage Power Stations when acting as Demand." has been added.
OC.5.5.8 | New clause - "Energy Storage Power Stations that cannot switch to Generation during a low Frequency event shall be capable of automatic low Frequency Demand Disconnection where the steady state System Frequency falls below 49.5 Hz for a sustained period of more than 1 minute."
OC.5.5.9 | New clause - "Such Energy Storage Power Stations shall be made subject to automatic low Frequency Demand Disconnection at the TSO’s direction, only when the Energy Storage Power Station is acting as Demand."
OC.5.5.10 | New clause - "The specific performance requirements of the automatic low Frequency Demand Disconnection scheme for such Energy Storage Power Stations shall be specified and agreed with the TSO."
OC.5.5.11 | New clause - "The automatic low Frequency Demand Disconnection scheme shall allow for operation from a nominal AC input to be specified by the TSO, and shall meet the following functional capabilities: (i) Frequency range: where the steady state System Frequency falls below 49.5 Hz for a sustained period of more than 1 minute; (ii) Operating time: no more than 150 ms after triggering the Frequency setpoint; (iii) Voltage lock-out: blocking of the functional capability shall be possible when the Voltage is within a range of 30 to 90 % of reference 1 p.u. Voltage; and (iv) Provide the direction of Active Power flow at the point of Disconnection."
SDC1.1.2 i. | The text "Energy Storage Power Station Demand" has been removed.
SDC1.1.2 vii. | The text "Energy Storage Power Station Demand" has been removed.
SDC1.3 | The text "Energy Storage Generators with regard to their Energy Storage Power Station Demand;" has been removed.
SDC1.4.1.1 (a) | The text "Energy Storage Plant Demand" has been removed.
SDC1.4.3.3.A | The text "Energy Storage Power Station Demand" has been removed.
SDC1.4.4.1 a) (i) | The text "Energy Storage Power Station Demand" has been removed.
SDC1.4.4.5 (a) | The text "Energy Storage Power Station Demand" has been removed.
SDC1.4.4.6 (a) | The text "Energy Storage Generator" has been added.
SDC1.4.6 b) | The text "Energy Storage Power Station Demand" has been removed.
SDC1.4.7.1 | The text "Energy Storage Power Station Demand" has been removed.
SDC1.4.7.2 | The text "Energy Storage Power Station Demand" has been removed.
SDC1.4.7.4 | The text "Energy Storage Power Station Demand" has been removed.
SDC1.4.7.6 | The text "Energy Storage Power Station Demand" has been removed.
SDC1.4.7.7 (a) | The text "Demand" has been removed from the phrase "Energy Storage Power Station Demand" where relevant. The full phrase "Energy Storage Power Station Demand" has been removed where relevant. The text ", Pumped Storage Plant Demand or Energy Storage Power Station Demand" has been removed. The text "With the exception of an Energy Storage Power Station," and "and Energy Storage Power Station," has been added.
SDC1.4.7.8 | The text "Energy Storage Power Station Demand" has been removed.
SDC1.4.7.9 (c) | The text "Energy Storage Power Station Demand" has been removed.
SDC1.4.7.11 | The text "Energy Storage Power Station Demand" has been removed.
SDC1 - APPENDIX A | Technical Parameters table updated for ESPS.
SDC2.1.2 (b) | The text "Energy Storage Generators with regard to their Energy Storage Power Station Demand;" has been removed.
SDC2.3 | The text "Energy Storage Generators with regard to their Energy Storage Power Station Demand;" has been removed.
SDC2.4.1.1 | The text "Energy Storage Power Station Demand" has been removed.
SDC2.4.1.2 (c) | The text "Energy Storage Power Station Demand" has been removed.
SDC2.4.1.3 | The text "Energy Storage Power Station Demand" has been removed.
SDC2.4.2.1 | The text "Energy Storage Power Station Demand" has been removed.
SDC2.4.2.2 | The text "the Energy Storage Generator for the Dispatch of its Energy Storage Power Station Demand" and "Energy Storage Power Station Demand" has been removed.
SDC2.4.2.4 | The text "Energy Storage Power Station Demand" has been removed.
SDC2.4.2.4 (e) | The text" where appropriate Demand Side Units and/or Energy Storage Power Stations in relation to Energy Storage Power Station Demand and/or Pumped Storage Plants in relation to Pumped Storage Plant Demand and" has been removed. The text "and, in the case of Pumped Storage Plant Demand and Energy Storage Power Station, the relevant effective time." has been added.
SDC2.4.2.4 (k) | The text "Energy Storage Power Station: mode changes for ESPS, where contracted, in relation to Energy Storage Power Station Demand;" has been removed.
SDC2.4.2.5 (a) | The text "and/or Energy Storage Power Station in relation to Energy Storage Power Station Demand" has been removed.
SDC2.4.2.9 (a) | The text "and/or Energy Storage Power Station Demand MW Output " has been removed.
SDC2.4.3 | The text "or Energy Storage Power Station Demand" has been removed.
PPM1.3.1 | The text "(c) Grid Connected Energy Storage Power Station Demand" has been removed.
PPM1.3.2 | The text "and Energy Storage Power Station Demand" and "For the avoidance of doubt, within PPM1, references to Controllable PPM and PPM also include Energy Storage Power Station Demand." has been removed.

## Changes & Additions to GC Defs
#VALUE! | September GCRP Grid Code Version 14.2 Modification Proposal: ESPS Phase 2
Description | New definition/modified existing definition/ removal of definition | Definition Wording
Availability | Modified existing definition | At any given time the measure of Active Power a Generation Unit(s), excluding Energy Storage Power Station(s), is capable of delivering to the Connection Point and the term “Availabilities” shall be construed accordingly. This can be calculated as a gross figure. At any given time the measure of Active Power an Energy Storage Power Station is capable of: • importing from the Connection Point; and • exporting to the Connection Point. The term “Availabilities” for an Energy Storage Power Station shall be constructed accordingly. In terms of a Demand Side Unit, the Demand Side Unit MW Capacity as the measure at any given time of the capability of the Demand Side Unit to reduce Demand. At any given time the measure of Active Power an Interconnector is capable of importing to or exporting from the Connection Point and the term “Availabilities” shall be constructed accordingly. This can be calculated as a gross figure.
Central Dispatch | Modified existing definition | The process of Scheduling and issuing Dispatch Instructions directly to a Control Facility by the TSO pursuant to the Grid Code. All Dispatchable PPMs including Energy Storage Power Stations, Interconnectors, Pumped Storage Plant Demand, Energy Storage Power Stations Demand, Demand Side Units, and Aggregated Generating Units are subject to Central Dispatch. In relation to all other Generation Units, thresholds apply as follows: • all other Generation Units with a Registered Capacity of 10 MW or more are subject to Central Dispatch; • all other Generation Units with a Registered Capacity of 5 MW or more and less than 10 MW are not subject to Central Dispatch unless required by the TSO; however, such Generation Units can elect to be subject to Central Dispatch; • all other Generation Units with a Registered Capacity of less than 5 MW are not subject to Central Dispatch unless required by the TSO; • any Power Station, which has an aggregate Registered Capacity of 10 MW or more, consisting of more than one Generation Unit that is not otherwise subject to Central Dispatch, is subject to Central Dispatch as an Aggregated Generating Unit; • all Generation Units with a Registered Capacity of less than 10 MW can elect whether to comply with SDC1.4.4.5 relating to the submission of Commercial Offer Data.
Centrally Dispatched Generating Unit (CDGU) | Modified existing definition | A Generating Unit within a Power Station subject to Central Dispatch, which comprises, unless specified otherwise in relation to a particular use of the term, a Thermal Plant including a CCGT Installation, a Dispatchable PPM including Energy Storage Power Stations, Hydro Unit and Pumped Storage Plant in respect of its Pumped Storage Generation.
Charging Capacity | Removal of definition | The maximum amount of Energy consumed by Energy Storage Power Station when acting as Demand.
Energy Storage Power Station (ESPS) Demand | Removal of definition | An Energy Storage Power Station in its operation of consuming Energy.
Maximum Charge Capacity | Removal of definition | The maximum amount of Energy that can be produced from the storage of an Energy Storage Generator for a Trading Day.
Maximum Storage Capacity Quantity | Modified existing definition | The maximum amount of Energy (MWh) that can be produced from the reservoir of a Pumped Storage Generator or Energy Storage Power Station for a Trading Day.
Minimum Charge Capacity | Removal of definition | The minimum amount of Energy that must be produced from the storage of an Energy Storage Generator for a Trading Day.
Minimum Storage Capacity Quantity | Modified existing definition | The minimum amount of Energy (MWh) that must be produced from the reservoir of a Pumped Storage Generator or Energy Storage Power Station for a Trading Day.
Ramp Down rate | Modified existing definition | The maximum rate of decrease in a Generating Unit’s Output after the End Of Start-up Period. The Ramp Down Rate applies over the output range from its Registered Capacity to Minimum Generation or from its Maximum Export Capacity to Maximum Import Capacity in the case of an Energy Storage Power Station. The rate of change is not dependent upon the initial Warmth of the plant but may depend on the MW Output. There may be circumstances where more than one parameter applies and this is indicated by adding a number at the end of the parameter.
Ramp Up Rate | Modified existing definition | The maximum rate of increase in a Generating Unit’s Output after the End Of Start-up Period. This rate of increase continues until the Generating Unit reaches the level of output instructed by the control room operator of its Registered Capacity or from its Maximum Import Capacity to Maximum Export Capacity in the case of an Energy Storage Power Station. The rate of increase is not dependent upon the initial Warmth of the plant but may depend on the MW Output. There may be circumstances where more than one parameter applies and this is indicated by adding a number at the end of the parameter.
Ramp-down Capability | Modified existing definition | The rate of decrease in a Generation Unit' Output after the End Of Start-up Period. Ramp-down Capabilities apply over the output range from its Registered Capacity to Minimum Ggeneration or from its Maximum Export Capability to Maximum Import Capability in the case of an Energy Storage Power Station. The rate of change is not dependent upon the initial warmth of the plant but may depend on the MW Output.
Ramp-up Capability | Modified existing definition | The rate of increase in a Generation Unit' Output after the End Of Start-up Period. This rate of increase continues until the Generation Unit reaches the level of output instructed by the control room operator or its Registered Capacity or from its Maximum Import Capacity to Maximum Export Capacity in the case of an Energy Storage Power Station. Following the End Of Start-up Period, the rate of increase is not dependent upon the initial warmth of the plant but may depend on the MW Output.
Registered Minimum Output | New definition | As defined in the TSC.
Storage Cycle Efficiency | New definition | For a Pumped Storage Unit, a percentage value calculated from the level of Generation provided by the release of defined quantity of water from the upper reservoir to the lower reservoir through the Generating Unit’s turbine(s) divided by the level of Demand required to pump the same defined quantity of water from the lower reservoir to the upper reservoir.
Target Charge Level Percentage | Removal of definition | As defined in the TSC.
Target Charge Levels | Removal of definition | Part of the Commercial Offer Data for an Energy Storage Power Station Generator and means the target level of the storage for the end of the Trading Day.