## Cover Sheet
Signal List XXXXX DSU XXMW V0.1
Disclaimer:
This Signal List contains information (and/or attachments) which may be privileged or confidential. All content is intended solely for the use of the individual or entity to whom it is addressed. If you are not the intended recipient please be aware that any disclosure, copying, distribution or use of the contents of this message is prohibited. If you suspect that you have received this Signal List in error please notify EirGrid immediately. Further information can be found at: http://www.eirgrid.com/aboutus/legal/

## Version Control
XXXXX DSU Signal List Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by
Note on D3: Administrator: All signal lists circulated to EMS and ESBT for Review before issuance.

## Signal Req. & Process Notes
TSO Signal Requirements
Connection Type | Demand Side Unit
EirGrid RTU requirement
TSO RTU Installed
EirGrid Controls | Not Applied
Demand Side Unit Signals to EirGrid (CC.12.2) | (l) Demand Side Unit MW Response from Generation;
(m) Demand Side Unit MW Response from avoided Demand consumption;
(n) Remaining Demand Side Unit MW Capacity;
(o) Demand Side Unit MW Response from each Demand load with a Demand Side Unit MW Capacity of greater than or equal to 5 MW;
(p) MW Output from Generation Units with a Capacity greater than or equal to 5 MW;
(q) Mvar Output from Generation Units with a Capacity greater than or equal to 5 MW at Individual Demand Sites with a Maximum Export Capacity specified in the Connection Agreement or DSO Connection Agreement as applicable, as required by the TSO;
(r) MW Output from Generation Units on Individual Demand Sites with a combined Capacity of greater than or equal to 5 MW, as required by the TSO; and
(s) Demand Side Unit MW Response from each Individual Demand Site that comprises the Demand Side Unit, as required by the TSO.
DSU Specification of aggregation (CC.12.6) | (a) signals from Demand Side Unit Operators shall be relayed to the TSO Telecommunication Interface Cabinet within 15 seconds of change of demand reduction or Generation Unit Output and with an error of no greater than 0.5 MW or 1% of the Demand Side Unit MW Capacity, whichever is greater; and
(b) a single failure of an item of the Demand Side Unit Operator’s equipment will not result in:
(i) loss of control of more than one Individual Demand Site;
(ii) loss of Demand Side Unit MW Response of more than one Individual Demand Site; or
(iii) the Demand Side Unit MW Response from Generation or Demand Side Unit MW Response from avoided Demand consumption signals being incorrect by more than the Demand Side Unit MW Capacity of the Individual Demand Site with the highest Demand Side Unit MW Capacity comprising the Demand Side Unit.
Additional Notes
General Process Notes: |  | Reference Documents:
A. Each Cert number 0, 1, 2, 3, 4, 5, 6, 7 from the process flow map corresponds to the subsequent Tab within the .xcl file which needs to be sent to generator_testing@eirgrid.com by the responsible party (DSU, ESBT or EMS). B. The DSU submits the Application form. Any changes in the Application Form will result in a new Signal List being issued which will affect the Operational Date. The Signal list is issued as a minor version and is reviewed by EirGrid and sent to DSU for feedback. Once all feedback has been addressed the Signal List is released as a major version to complete works onsite. This shall be completed not less than 6 weeks prior to Operational Date. C. The RTU / ETIE shall be installed on site not less than 4 weeks prior to Operational Date. D. The DSU submits the DSU Wiring Completion Cert and requests a date for pre-grid code check as required by EirGrid. This shall be carried out in accordance with ESBT timelines listed on Tab 0) Inst. Info & Contact Details. E. The Pre Grid Code Check is carried out by DSU / ESBT / EMS EirGrid. The DSU may provide simulated signals to the TSO RTU which will be verified by EMS. Any issues identified must be addressed prior to Operational Certificate. F. Test procedures must be submitted to EirGrid in Advance of Grid Code Compliance Testing (GCCT). These procedures must be agreed by no less than 10 days in advance of testing. G. DSU must liaise with EirGrid to carry out Grid Code Compliance Testing. H. Test Procedures are agreed with generator_testing@eirgrid.com in advance of the test request. I. Grid Code Compliance Testing of the individual demand site is carried out with an EirGrid Witness on site. J. Test profiles 1and test requests shall be sent to generator_testing@eirgird.com 10 business days in advance of the proposed test date. K. Test profiles and test requests must be sent to control@eirgrid.com for approval at least 5 days in advance of test. L. Generator_testing@eirgrid.com shall be copied on all correspondence in relation to the Grid Code Test. M. Signed test procedures and test data files shall be sent to generator_testing@eirgrid.com 1 business day after the test. N. Test reports shall be sent to generator_testing@eirgrid.com 10 business days after the test or as otherwise agreed. O. 10 business days shall be allowed for comments or feedback on the Grid Code Test Report. P. Should there be no further issues after GCCT has been successfully carried out, an Operational Certificate will be issued. Q. Note that this is the general process notes and exceptions may apply depending on circumstance. ALL queries for clarity shall be referred to generator_testing@eirgrid.com.
|  | Attached 1) Signal Lists | Functional Specification Alert System Control Specification for Units subject to Central Dispatch
|  | Attached 6) Grid Code Tests | Grid Code Testing Requirements
|  | Grid Code | http://www.eirgrid.com/operations/gridcode/
|  | Distribution Code: | http://www.esb.ie/esbnetworks/en/about-us/our_networks/distribution_code.jsp
|  | Available Active Power Standard | http://www.eirgrid.com/media/Quality%20Standard%20for%20Windfarm%20Active%20Power.pdf
Abbreviations
|  |  | TSO | Transmission System Operator - EirGrid
|  |  | EMS | Energy Management System - EirGrid
|  |  | DSO | Distribution System Operator - ESBN
|  |  | NCC | National Control Centre, EirGrid
|  |  | ESBTS | ESB Telecoms Services
|  |  | RTU | Remote Terminal Unit
|  |  | ETIE | EirGrid Terminal Interface Enclosure
|  |  | GCCT | Grid Code Compliance Testing
|  |  | DCC | Distribution Control Centre
|  |  | SDCC | South Distribution Control Centre, ESBN
|  |  | NDCC | North Distribution Control Centre, ESBN

## 0) Operational Data
Individual Demand Site Name/Number |  | DSU | Individual demand site no. 1 | Individual demand site no. 2 | Individual demand site no. X | Individual demand site no. X | Individual demand site no. X | Individual demand site no. X | Total
MPRN | [8 empty] | N/A
Bulk Supply Point or Connection Point | [8 empty] | N/A
Special Operating Limits or Network Limitations | [8 empty] | N/A
Irish Grid Co-ordinates | Eastings | [7 empty] | N/A
| Northing | [7 empty] | N/A
Maximum Import Capacity (MIC) | (MW) | [7 empty] | 0
Maximum Export Capacity (MEC) | (MW) | [7 empty] | 0
Individual Demand Site Total Size | (MW) | [7 empty] | 0
Demand Side Unit MW Capacity | (MW) | [7 empty] | 0
Demand Reduction Capability - Avoided Consumption | (MW) | [7 empty] | 0
Demand Reduction Capability - On Site Generation | (MW) | [7 empty] | 0
Notification Time | Time (min) | [7 empty] | N/A
Time to Maximum reduction | Time (min) | [7 empty] | N/A
Ramp up rate | MW/Minute | [7 empty] | N/A
Ramp Down Rate | MW/Minute | [7 empty] | N/A
Minimum Down Time | Time (min) | [7 empty] | N/A
Maximum Up Time | Time (min) | [7 empty] | N/A
G10 Protection | Low Frequency Trip Hz | [7 empty] | N/A
| High Frequency Trip Hz | [7 empty] | N/A
| ROCOF Hz/S | [7 empty] | N/A
Generator Capability | Low Frequency Trip Hz | [7 empty] | N/A
| High Frequency Trip Hz | [7 empty] | N/A
| ROCOF Hz/S | [7 empty] | N/A
Generator MVA | MVA
Generation Capacity of Generator | MW
Fuel Type | [8 empty] | N/A
Standby | kW | [7 empty] | N/A

## 0 ) Inst.Info & Contact Details
XXXXX DSU & Information and Contact Details to be sent by DSU to EirGrid (generator_testing@EirGrid.com)
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
DATE
| HV SUB STATION NAME |  |  |  |  | ESBTS Team |  | Liam Boland
[6 empty] | Nessan Heaslip | Karl O'Keeffe | Noel Cowhey
| EirGrid Contact Person | C&T Team | PHONE: |  | (+353) 1 2370583 | Robert Groarke | Oisín Goulding
| OSP Generic Email: Generator_testing@eirgrid.com |  |  |  |  | Frank Donnelly | Colm MacManus
| EMS Generic Email: ems.services@eirgrid.com |  |  |  |  | Liam Delany | C&T Team
| ESBTS Project Manager | ESBTS Team | PHONE: |  | (+353) 1 7027835
| ESBTS Commissioner | ESBTS Team | PHONE: |  | (+353) 1 7027835
ESBTS Generic Email: esbts.scada.services@esb.ie
| DSU Project Manager |  | PHONE: |  | (+ )
| DSU Contractor |  | PHONE: |  | (+ )
| Work Programme / Schedule (.mpp format) - as per application |  |  | Insert File
| Single Line Diagram(s) - as per application |  |  | Insert file
| Directions including Map to the DSU RTU Location | Insert Map and brief description
| Safety & Site information | DSU to provide details
ESBTS Standard Requirements from IPP (may be customised for particular sites):
1) 90sq mm earth for Telecoms earth bar. 2) 35sq mm bonded from external earth grid to GPS clock antenna mounting bracket and if applicable Satellite antenna mounting bracket. 3) 48V DC Power System consisting of Switched Mode Power Supply (SMPS) with sealed cell battery. 4) If applicable - Fibre termination cabinet with fibre termination unit and fibre to distant station. 5) Satellite link consisting of Satellite transceiver and antenna if applicable. Satellite antenna preferably on a south facing wall with a clear view of the horizon. 6) Install and terminate process control and signal cables in ETI (the wiring schedule is available as a worksheet in the signal list excel file).
| ESB Telecom Services - Indicative Timelines for on site works | 1) 3 weeks notice required by ESBTS to schedule resources. 2) ~1 week to install the RTU cabinet with integrated ETI and GPS clock, GPS clock antenna. 3) ~1 week to pre commission the RTU referenced to frozen signal list with IPP electrical and WTG contractors. 4) ~1 week to install and commission the satellite link including antenna (if applicable). 5) ~2 days to commission the fibre link (if applicable). 6) ~1 week to commission the RTU with IPP electrical and WTG contractors.

## 1) Signal List
XXXXX DSU |  |  |  | XX | MW | V0.1
EirGrid Signals, Command Specification
Signals List |  | Demand Side Unit MW Capacity: XX MW
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Comment
| Double Point Status Indications | (each individual input identified separately for clarity) | [5 empty] | Note: Signals treated as 2-bit binary
| Digital Input Signals from Sub Station to EirGrid | [6 empty] | Functional Specification for Alerts.
A1 | DSU Amber Alert |  | off |  |  | DSU | N/A
A2 | DSU Amber Alert |  | on |  |  | DSU | N/A
A3 | DSU Amber Alert Acknowledge |  | off |  |  | DSU | N/A
A4 | DSU Amber Alert Acknowledge |  | on |  |  | DSU | N/A
A5 | DSU Red Alert |  | off |  |  | DSU | N/A
A6 | DSU Red Alert |  | on |  |  | DSU | N/A
A7 | DSU Red Alert Acknowledge |  | off |  |  | DSU | N/A
A8 | DSU Red Alert Acknowledge |  | on |  |  | DSU | N/A
A9 | DSU Blue Alert |  | off |  |  | DSU | N/A
A10 | DSU Blue Alert |  | on |  |  | DSU | N/A
A11 | DSU Blue Alert Acknowledge |  | off |  |  | DSU | N/A
A12 | DSU Blue Alert Acknowledge |  | on |  |  | DSU | N/A
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Comment
Analogue Input Signals from DSU Control System to EirGrid
C1 | Onsite Generation MVar, AAAAA Generator #1 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
C2 | Onsite Generation MVar, AAAAA Generator #2 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
C3 | Onsite Generation MVar, BBBBB Generator #1 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
C4 | Onsite Generation MVar, BBBBB Generator #2 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
C5 | Onsite Generation MVar, CCCCC Generator #1 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
C6 | Onsite Generation MVar, CCCCC Generator #2 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
C7 | Onsite Generation MVar, CCCCC Generator #3 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
Analogue Input Signals from DSU Control System to EirGrid
D1 | Remaining MW Availability of DSU | 0-10 | mA | 0-XX | MW | DSU | N/A | 120% of Registered Capacity (XX)*1.2 = XXMW)
D2 | Total MW Reduction of DSU achieved from onsite Demand Reduction | 0-10 | mA | #VALUE! | MW | DSU | N/A | 120% of Total demand side unit MW Capacity available from avoided Demand (XX*1.2 = 0MW) - set to XXMW
D3 | Total MW Reduction of DSU achieved from onsite Generation | 0-10 | mA | #VALUE! | MW | DSU | N/A | 120% of Total demand side units MW Capacity from on-site Generation (XX * 1.2 = XXMW)
D4 | Onsite Generation MW, AAAAA Generator #1 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D5 | Onsite Generation MW, AAAAA Generator #2 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D6 | Onsite Generation MW, BBBBB Generator #1 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D7 | Onsite Generation MW, BBBBB Generator #2 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D8 | Onsite Generation MW, CCCCC Generator #1 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D9 | Onsite Generation MW, CCCCC Generator #2 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D10 | Onsite Generation MW, CCCCC Generator #3 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D11 | Demand Reduction from site MW, DDDDDD #1 | 0-10 | mA | 0-12 | MW | DSU | N/A | 120% of Demand Side Unit MW Capacity (9.9MW)
D12 | Demand Reduction from site MW, DDDDDD #2 | 0-10 | mA | 0-12 | MW | DSU | N/A | 120% of Demand Side Unit MW Capacity (9.9MW)
D13 | Demand Reduction from site MW, DDDDDD #3 | 0-10 | mA | 0-12 | MW | DSU | N/A | 120% of Demand Side Unit MW Capacity (9.9MW)
D14 | Demand Reduction from site MW, DDDDDD #4 | 0-10 | mA | 0-12 | MW | DSU | N/A | 120% of Demand Side Unit MW Capacity (9.9MW)
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Comment
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
Digital Output Signals from EirGrid to DSU Control System
F1 | DSU Amber Alert |  | off | pulse | 0.5 seconds | DSU | N/A
F2 | DSU Amber Alert |  | on | pulse | 0.5 seconds | DSU | N/A
F3 | DSU Red Alert |  | off | pulse | 0.5 seconds | DSU | N/A
F4 | DSU Red Alert |  | on | pulse | 0.5 seconds | DSU | N/A
F5 | DSU Blue Alert |  | off | pulse | 0.5 seconds | DSU | N/A
F6 | DSU Blue Alert |  | on | pulse | 0.5 seconds | DSU | N/A
Single Command Outputs
Digital Output Signals from EirGrid to DSU Control System
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Comment
Analogue Output Signals from EirGrid to WTG System
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
Note on E1: Administrator: Insert the Registered Capacity of the WFPS
Note on A5: EirGrid Telecoms Interface Enclosure
Note on H5: No IPP involvement unless otherwise confirmed

## 2) DSU Wiring Completion Cert
XXXXX DSU |  | Type |  | XX | MW | V0.1 |  |  | Wiring Completion Cert
EirGrid Signals, Command Specification | [8 empty] | Continuity Check Complete
DSU Wiring Completion Certificate (to EirGrid ETIE/RTU) to be sent by DSU to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Comment
| Double Point Status Indications | (each individual input identified separately for clarity)
| Digital Input Signals from Sub Station to EirGrid | [6 empty] | Functional Specification for Alerts.
A1 | DSU Amber Alert |  | off |  |  | DSU | N/A
A2 | DSU Amber Alert |  | on |  |  | DSU | N/A
A3 | DSU Amber Alert Acknowledge |  | off |  |  | DSU | N/A
A4 | DSU Amber Alert Acknowledge |  | on |  |  | DSU | N/A
A5 | DSU Red Alert |  | off |  |  | DSU | N/A
A6 | DSU Red Alert |  | on |  |  | DSU | N/A
A7 | DSU Red Alert Acknowledge |  | off |  |  | DSU | N/A
A8 | DSU Red Alert Acknowledge |  | on |  |  | DSU | N/A
A9 | DSU Blue Alert |  | off |  |  | DSU | N/A
A10 | DSU Blue Alert |  | on |  |  | DSU | N/A
A11 | DSU Blue Alert Acknowledge |  | off |  |  | DSU | N/A
A12 | DSU Blue Alert Acknowledge |  | on |  |  | DSU | N/A
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Comment
Analogue Input Signals from DSU Control System to EirGrid
C1 | Onsite Generation MVar, AAAAA Generator #1 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
C2 | Onsite Generation MVar, AAAAA Generator #2 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
C3 | Onsite Generation MVar, BBBBB Generator #1 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
C4 | Onsite Generation MVar, BBBBB Generator #2 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
C5 | Onsite Generation MVar, CCCCC Generator #1 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
C6 | Onsite Generation MVar, CCCCC Generator #2 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
C7 | Onsite Generation MVar, CCCCC Generator #3 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Onsite Generator - Future
Analogue Input Signals from DSU Control System to EirGrid
D1 | Remaining MW Availability of DSU | 0-10 | mA | 0-XX | MW | DSU | N/A | 120% of Registered Capacity (XX)*1.2 = XXMW)
D2 | Total MW Reduction of DSU achieved from onsite Demand Reduction | 0-10 | mA | #VALUE! | MW | DSU | N/A | 120% of Total demand side unit MW Capacity available from avoided Demand (XX*1.2 = 0MW) - set to XXMW
D3 | Total MW Reduction of DSU achieved from onsite Generation | 0-10 | mA | #VALUE! | MW | DSU | N/A | 120% of Total demand side units MW Capacity from on-site Generation (XX * 1.2 = XXMW)
D4 | Onsite Generation MW, AAAAA Generator #1 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D5 | Onsite Generation MW, AAAAA Generator #2 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D6 | Onsite Generation MW, BBBBB Generator #1 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D7 | Onsite Generation MW, BBBBB Generator #2 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D8 | Onsite Generation MW, CCCCC Generator #1 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D9 | Onsite Generation MW, CCCCC Generator #2 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D10 | Onsite Generation MW, CCCCC Generator #3 | 0-10 | mA | 0-6 | MW | DSU | N/A | 120% of Onsite Generation - Future
D11 | Demand Reduction from site MW, DDDDDD #1 | 0-10 | mA | 0-12 | MW | DSU | N/A | 120% of Demand Side Unit MW Capacity (9.9MW)
D12 | Demand Reduction from site MW, DDDDDD #2 | 0-10 | mA | 0-12 | MW | DSU | N/A | 120% of Demand Side Unit MW Capacity (9.9MW)
D13 | Demand Reduction from site MW, DDDDDD #3 | 0-10 | mA | 0-12 | MW | DSU | N/A | 120% of Demand Side Unit MW Capacity (9.9MW)
D14 | Demand Reduction from site MW, DDDDDD #4 | 0-10 | mA | 0-12 | MW | DSU | N/A | 120% of Demand Side Unit MW Capacity (9.9MW)
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Comment
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
Digital Output Signals from EirGrid to DSU Control System
F1 | DSU Amber Alert |  | off | pulse | 0.5 seconds | DSU | N/A
F2 | DSU Amber Alert |  | on | pulse | 0.5 seconds | DSU | N/A
F3 | DSU Red Alert |  | off | pulse | 0.5 seconds | DSU | N/A
F4 | DSU Red Alert |  | on | pulse | 0.5 seconds | DSU | N/A
F5 | DSU Blue Alert |  | off | pulse | 0.5 seconds | DSU | N/A
F6 | DSU Blue Alert |  | on | pulse | 0.5 seconds | DSU | N/A
Single Command Outputs
Digital Output Signals from EirGrid to DSU Control System
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Comment
Analogue Output Signals from EirGrid to WTG System
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet must be clearly marked with labels for identification. |  |  |  | Confirmed  |  |  |  | Comments
All cables for interfacing at station interface cabinet or EirGrid telecoms interface cabinet must be terminated at connection terminals (i.e. strDSUed, crimped and marked at terminal connections). |  |  |  | Confirmed 
All cables for interfacing at station interface cabinet or EirGrid telecoms interface cabinet must use colour coding agreed by all parties i.e. ESBTS & DSU. |  |  |  | Confirmed 
All analogue and digital interface signals must be tested and simulated for compliance with the frozen signal list agreed by all parties. |  |  |  | Confirmed 
ESBTS Satellite Dish bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed 
ESBTS GPS clock antenna bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed 
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 | [6 empty] | DSU Name / Position
DSU Signature
Date
Note on A3: Administrator: To be completed by the IPP and sent to EirGrid to schedule ESBTS site attendance to perform continuity check
Note on A5: EirGrid Telecoms Interface Enclosure

## 3) ESB Telecoms RTU Cert
XXXXX DSU |  |  |  | XX | MW | V0.1 |  | Completion Cert
EirGrid Signals, Command Specification | [7 empty] | Local SCADA Checks/Tests
Pre Energisation Signals Testing Certificate to be sent by ESB Telecoms Services to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | DSU Amber Alert |  | off |  |  | DSU | N/A
A2 | DSU Amber Alert |  | on |  |  | DSU | N/A
A3 | DSU Amber Alert Acknowledge |  | off |  |  | DSU | N/A
A4 | DSU Amber Alert Acknowledge |  | on |  |  | DSU | N/A
A5 | DSU Red Alert |  | off |  |  | DSU | N/A
A6 | DSU Red Alert |  | on |  |  | DSU | N/A
A7 | DSU Red Alert Acknowledge |  | off |  |  | DSU | N/A
A8 | DSU Red Alert Acknowledge |  | on |  |  | DSU | N/A
A9 | DSU Blue Alert |  | off |  |  | DSU | N/A
A10 | DSU Blue Alert |  | on |  |  | DSU | N/A
A11 | DSU Blue Alert Acknowledge |  | off |  |  | DSU | N/A
A12 | DSU Blue Alert Acknowledge |  | on |  |  | DSU | N/A
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from DSU Control System to EirGrid
C1 | Onsite Generation MVar, AAAAA Generator #1 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A
C2 | Onsite Generation MVar, AAAAA Generator #2 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A
C3 | Onsite Generation MVar, BBBBB Generator #1 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A
C4 | Onsite Generation MVar, BBBBB Generator #2 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A
C5 | Onsite Generation MVar, CCCCC Generator #1 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A
C6 | Onsite Generation MVar, CCCCC Generator #2 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A
C7 | Onsite Generation MVar, CCCCC Generator #3 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A
Analogue Input Signals from DSU Control System to EirGrid
D1 | Remaining MW Availability of DSU | 0-10 | mA | 0-XX | MW | DSU | N/A
D2 | Total MW Reduction of DSU achieved from onsite Demand Reduction | 0-10 | mA | #VALUE! | MW | DSU | N/A
D3 | Total MW Reduction of DSU achieved from onsite Generation | 0-10 | mA | #VALUE! | MW | DSU | N/A
D4 | Onsite Generation MW, AAAAA Generator #1 | 0-10 | mA | 0-6 | MW | DSU | N/A
D5 | Onsite Generation MW, AAAAA Generator #2 | 0-10 | mA | 0-6 | MW | DSU | N/A
D6 | Onsite Generation MW, BBBBB Generator #1 | 0-10 | mA | 0-6 | MW | DSU | N/A
D7 | Onsite Generation MW, BBBBB Generator #2 | 0-10 | mA | 0-6 | MW | DSU | N/A
D8 | Onsite Generation MW, CCCCC Generator #1 | 0-10 | mA | 0-6 | MW | DSU | N/A
D9 | Onsite Generation MW, CCCCC Generator #2 | 0-10 | mA | 0-6 | MW | DSU | N/A
D10 | Onsite Generation MW, CCCCC Generator #3 | 0-10 | mA | 0-6 | MW | DSU | N/A
D11 | Demand Reduction from site MW, DDDDDD #1 | 0-10 | mA | 0-12 | MW | DSU | N/A
D12 | Demand Reduction from site MW, DDDDDD #2 | 0-10 | mA | 0-12 | MW | DSU | N/A
D13 | Demand Reduction from site MW, DDDDDD #3 | 0-10 | mA | 0-12 | MW | DSU | N/A
D14 | Demand Reduction from site MW, DDDDDD #4 | 0-10 | mA | 0-12 | MW | DSU | N/A
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
Digital Output Signals from EirGrid to DSU Control System
F1 | DSU Amber Alert |  | off | pulse | 0.5 seconds | DSU | N/A
F2 | DSU Amber Alert |  | on | pulse | 0.5 seconds | DSU | N/A
F3 | DSU Red Alert |  | off | pulse | 0.5 seconds | DSU | N/A
F4 | DSU Red Alert |  | on | pulse | 0.5 seconds | DSU | N/A
F5 | DSU Blue Alert |  | off | pulse | 0.5 seconds | DSU | N/A
F6 | DSU Blue Alert |  | on | pulse | 0.5 seconds | DSU | N/A
Single Command Outputs
Digital Output Signals from EirGrid to DSU Control System
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
Comments
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet are installed and correct. |  |  |  | Confirmed  |  |  | ESBTS Name / Position
ESBTS Signature
Date
| NOTE: Non operable DSU signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  | Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
Note on A5: EirGrid Telecoms Interface Enclosure

## 4) EMS Database Setup Cert
XXXXX DSU |  | XX | MW | V0.1
EirGrid Signals, Command Specification
Energy Management System (EMS) Database setup Certificate
Completion Cert
Continuity Check Complete
Display Work Completed:
EMS Name
EMS Signature
Date
EirGrid Internal Requirement- no DSU requirements. For Information only
Note on A3: Administrator: DCC to be Informed

## 5) Pre Grid Code Check
XXXXX DSU |  |  |  | XX | MW | V0.1 |  | Pre Grid Code Check SignalsTest
EirGrid Signals, Command Specification | [7 empty] | Simulated □/Real □ value tested | mA Range | Value Range | Comment
PreGrid Code Cert to be provided by DSU to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | DSU Amber Alert |  | off |  |  | DSU | N/A | Real □
A2 | DSU Amber Alert |  | on |  |  | DSU | N/A | Real □
A3 | DSU Amber Alert Acknowledge |  | off |  |  | DSU | N/A | Real □
A4 | DSU Amber Alert Acknowledge |  | on |  |  | DSU | N/A | Real □
A5 | DSU Red Alert |  | off |  |  | DSU | N/A | Real □
A6 | DSU Red Alert |  | on |  |  | DSU | N/A | Real □
A7 | DSU Red Alert Acknowledge |  | off |  |  | DSU | N/A | Real □
A8 | DSU Red Alert Acknowledge |  | on |  |  | DSU | N/A | Real □
A9 | DSU Blue Alert |  | off |  |  | DSU | N/A | Real □
A10 | DSU Blue Alert |  | on |  |  | DSU | N/A | Real □
A11 | DSU Blue Alert Acknowledge |  | off |  |  | DSU | N/A | Real □
A12 | DSU Blue Alert Acknowledge |  | on |  |  | DSU | N/A | Real □
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from DSU Control System to EirGrid
C1 | Onsite Generation MVar, AAAAA Generator #1 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Real □
C2 | Onsite Generation MVar, AAAAA Generator #2 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Real □
C3 | Onsite Generation MVar, BBBBB Generator #1 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Real □
C4 | Onsite Generation MVar, BBBBB Generator #2 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Real □
C5 | Onsite Generation MVar, CCCCC Generator #1 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Real □
C6 | Onsite Generation MVar, CCCCC Generator #2 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Real □
C7 | Onsite Generation MVar, CCCCC Generator #3 | -10 to 0 to 10 | mA | -3-0-3 | MVar | DSU | N/A | Real □
Analogue Input Signals from DSU Control System to EirGrid
D1 | Remaining MW Availability of DSU | 0-10 | mA | 0-XX | MW | DSU | N/A | Real □
D2 | Total MW Reduction of DSU achieved from onsite Demand Reduction | 0-10 | mA | #VALUE! | MW | DSU | N/A | Real □
D3 | Total MW Reduction of DSU achieved from onsite Generation | 0-10 | mA | #VALUE! | MW | DSU | N/A | Real □
D4 | Onsite Generation MW, AAAAA Generator #1 | 0-10 | mA | 0-6 | MW | DSU | N/A | Real □
D5 | Onsite Generation MW, AAAAA Generator #2 | 0-10 | mA | 0-6 | MW | DSU | N/A | Real □
D6 | Onsite Generation MW, BBBBB Generator #1 | 0-10 | mA | 0-6 | MW | DSU | N/A | Real □
D7 | Onsite Generation MW, BBBBB Generator #2 | 0-10 | mA | 0-6 | MW | DSU | N/A | Real □
D8 | Onsite Generation MW, CCCCC Generator #1 | 0-10 | mA | 0-6 | MW | DSU | N/A | Real □
D9 | Onsite Generation MW, CCCCC Generator #2 | 0-10 | mA | 0-6 | MW | DSU | N/A | Real □
D10 | Onsite Generation MW, CCCCC Generator #3 | 0-10 | mA | 0-6 | MW | DSU | N/A | Real □
D11 | Demand Reduction from site MW, DDDDDD #1 | 0-10 | mA | 0-12 | MW | DSU | N/A | Real □
D12 | Demand Reduction from site MW, DDDDDD #2 | 0-10 | mA | 0-12 | MW | DSU | N/A | Real □
D13 | Demand Reduction from site MW, DDDDDD #3 | 0-10 | mA | 0-12 | MW | DSU | N/A | Real □
D14 | Demand Reduction from site MW, DDDDDD #4 | 0-10 | mA | 0-12 | MW | DSU | N/A | Real □
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
Digital Output Signals from EirGrid to DSU Control System
F1 | DSU Amber Alert |  | off | pulse | 0.5 seconds | DSU | N/A | Real □
F2 | DSU Amber Alert |  | on | pulse | 0.5 seconds | DSU | N/A | Real □
F3 | DSU Red Alert |  | off | pulse | 0.5 seconds | DSU | N/A | Real □
F4 | DSU Red Alert |  | on | pulse | 0.5 seconds | DSU | N/A | Real □
F5 | DSU Blue Alert |  | off | pulse | 0.5 seconds | DSU | N/A | Real □
F6 | DSU Blue Alert |  | on | pulse | 0.5 seconds | DSU | N/A | Real □
Single Command Outputs
Digital Output Signals from EirGrid to DSU Control System
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
Comments
DSU Name
DSU Signature
EMS Name
EMS Signature
| NOTE: Non operable DSU signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  |  |  |  | ESB Telecoms Name / Position
| Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 |  |  |  |  | ESB Telecoms Signature
Date
Note on A5: EirGrid Telecoms Interface Enclosure

## ETIE Layout
Designation: Indications/Signals |  | ETIE Ref | ETIE ROW 1
POSITIVE 24V or 48V DC DOUBLE POINT INDICATION |  |  | +
DSU Amber Alert | off | A1 | 1
DSU Amber Alert | on | A2 | 2
DSU Amber Alert Acknowledge | off | A3 | 3
DSU Amber Alert Acknowledge | on | A4 | 4
DSU Red Alert | off | A5 | 5
DSU Red Alert | on | A6 | 6
DSU Red Alert Acknowledge | off | A7 | 7
DSU Red Alert Acknowledge | on | A8 | 8
DSU Blue Alert | off | A9 | 9
DSU Blue Alert | on | A10 | 10
DSU Blue Alert Acknowledge | off | A11 | 11
DSU Blue Alert Acknowledge | on | A12 | 12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
POSITIVE 24V or 48V DC SINGLE POINT INDICATION |  |  | +
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
Designation: Measurands |  | ETIE Ref | ETIE ROW 2
Onsite Generation MVar, AAAAA Generator #1 |  | C1 | 1
Onsite Generation MVar, AAAAA Generator #1 |  | C1 | 2
Onsite Generation MVar, AAAAA Generator #2 |  | C2 | 3
Onsite Generation MVar, AAAAA Generator #2 |  | C2 | 4
Onsite Generation MVar, BBBBB Generator #1 |  | C3 | 5
Onsite Generation MVar, BBBBB Generator #1 |  | C3 | 6
Onsite Generation MVar, BBBBB Generator #2 |  | C4 | 7
Onsite Generation MVar, BBBBB Generator #2 |  | C4 | 8
Onsite Generation MVar, CCCCC Generator #1 |  | C5 | 9
Onsite Generation MVar, CCCCC Generator #1 |  | C5 | 10
Onsite Generation MVar, CCCCC Generator #2 |  | C6 | 11
Onsite Generation MVar, CCCCC Generator #2 |  | C6 | 12
Onsite Generation MVar, CCCCC Generator #3 |  | C7 | 13
Onsite Generation MVar, CCCCC Generator #3 |  | C7 | 14
Remaining MW Availability of DSU |  | D1 | 15
Remaining MW Availability of DSU |  | D1 | 16
Total MW Reduction of DSU achieved from onsite Demand Reduction |  | D2 | 17
Total MW Reduction of DSU achieved from onsite Demand Reduction |  | D2 | 18
Total MW Reduction of DSU achieved from onsite Generation |  | D3 | 19
Total MW Reduction of DSU achieved from onsite Generation |  | D3 | 20
Onsite Generation MW, AAAAA Generator #1 |  | D4 | 21
Onsite Generation MW, AAAAA Generator #1 |  | D4 | 22
Onsite Generation MW, AAAAA Generator #2 |  | D5 | 23
Onsite Generation MW, AAAAA Generator #2 |  | D5 | 24
Onsite Generation MW, BBBBB Generator #1 |  | D6 | 25
Onsite Generation MW, BBBBB Generator #1 |  | D6 | 26
Onsite Generation MW, BBBBB Generator #2 |  | D7 | 27
Onsite Generation MW, BBBBB Generator #2 |  | D7 | 28
Onsite Generation MW, CCCCC Generator #1 |  | D8 | 29
Onsite Generation MW, CCCCC Generator #1 |  | D8 | 30
Onsite Generation MW, CCCCC Generator #2 |  | D9 | 31
Onsite Generation MW, CCCCC Generator #2 |  | D9 | 32
Onsite Generation MW, CCCCC Generator #3 |  | D10 | TBC
Onsite Generation MW, CCCCC Generator #3 |  | D10 | TBC
Demand Reduction from site MW, DDDDDD #1 |  | D11 | TBC
Demand Reduction from site MW, DDDDDD #1 |  | D11 | TBC
Demand Reduction from site MW, DDDDDD #2 |  | D12 | TBC
Demand Reduction from site MW, DDDDDD #2 |  | D12 | TBC
Demand Reduction from site MW, DDDDDD #3 |  | D13 | TBC
Demand Reduction from site MW, DDDDDD #3 |  | D13 | TBC
Demand Reduction from site MW, DDDDDD #4 |  | D14 | TBC
Demand Reduction from site MW, DDDDDD #4 |  | D14 | TBC
Analogue Output MW |  |  | +
33
34
35
36
Analogue Output kV |  |  | +
37
38
39
40
Designation: Commands |  | ETIE Ref | ETIE ROW 3
DSU Amber Alert | off | F1 | 1
Command Negative |  |  | 2
DSU Amber Alert | on | F2 | 3
DSU Red Alert | off | F3 | 4
Command Negative |  |  | 5
DSU Red Alert | on | F4 | 6
DSU Blue Alert | off | F5 | 7
Command Negative |  |  | 8
DSU Blue Alert | on | F6 | 9
Command Output |  |  | 10
Command Negative |  |  | 11
Command Output |  |  | 12
Command Output |  |  | 13
Command Negative |  |  | 14
Command Output |  |  | 15
Command Output |  |  | 16
Command Negative |  |  | 17
Command Output |  |  | 18
Command Output |  |  | 19
Command Negative |  |  | 20
Command Output |  |  | 21
Command Output |  |  | 22
Command Negative |  |  | 23
Command Output |  |  | 24
Command Output |  |  | 25
Command Negative |  |  | 26
Command Output |  |  | 27
Command Output |  |  | 28
Command Negative |  |  | 29
Command Output |  |  | 30
Command Output |  |  | 31
Command Negative |  |  | 32
Command Output |  |  | 33
Command Output |  |  | 34
Command Negative |  |  | 35
Command Output |  |  | 36
Command Output |  |  | 37
Command Negative |  |  | 38
Command Output |  |  | 39
Command Output |  |  | 40
Command Negative |  |  | 41
Command Output |  |  | 42
Command Output |  |  | 43
Command Negative |  |  | 44
Command Output |  |  | 45
Command Output |  |  | 46
Command Negative |  |  | 47
Command Output |  |  | 48
Designation: Controls |  | ETIE Ref | ETIE ROW 4
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
Single Controls |  |  | +
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
Note on D2: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4
Note on D76: Administrator: Administrator: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4
Note on D129: Administrator: There is a gap between the off / on commands for command negative
Note on D178: Administrator: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4

## 6) Grid Code Tests
Test Number | Test | Grid Code Ref: | Comments | Status
Grid Code Testing Requirements
1 | DSU Specification of aggregation | CC.12.6 | Demand Side Unit Operators and Generator Aggregators shall provide the TSO the specification of the method of aggregation of SCADA from multiple sites. The minimum specifications shall be agreed with the TSO at application stage and shall address paragraphs CC.12.6 a and b for each of the individual demand sites. | Open
2 | Demonstration of Signals as defined in the EirGrid Signal List including specification of aggregation | CC.12.2, CC.12.6 | These signals must be demonstrated prior to proceeding with any other Gird Code Testing. Details of method of aggregation to be agreed with TSO in advance. | Open
3 | Demonstration of capability to provide Demand Side Unit MW Response from 0MW to the Demand Side Unit MW Capacity | CC.7.4 (a) |  | Open
4 | Demonstration of capability to ramp up and down between defined load points with a rate of not less than 1.67% of Demand Side Unit MW Capacity per minute. The DSU should demonstrate stable operation for some period following ramp up | CC.7.4 (b) |  | Open
5 | Demonstration of capability to ramp up and down between defined load points with a rate of not less than 1.67% of Demand Side Unit MW Capacity per minute. The DSU should demonstrate stable operation for some period following ramp down | CC.7.4 (c) |  | Open
6 | Demonstration of Minimum Down-Time being not greater than 30 minutes | CC.7.4 (d) |  | Open
7 | Demonstration of maximum down-time being not less than 2 hours | CC.7.4 (e) |  | Open
8 | Demonstration of operation of plant on house load at high frequency and low frequency limits of operation for 60 minutes | CC.7.4 (h, i, j, k, l). | As applicable, statement of capability required from OEM. Settings and mode of operation verified for the applicable site. | Open
9 | Demonstration of amber, red and blue alerts | OC.9 | Carried out for initial inspection of Control Room. Inspection of Internal procedures are in place for responding to System Alerts. | Open
10 | Demand Side Unit Control Centre Audit | OC.7 |  | Open
11 | UPS system | OC7.2.5.4.2 | The User should provide sufficient battery backup to power the communications between User and TSO (i.e. control room, RTU etc.) for a minimum of 4 hours of operation. The requirement would be audited during the Grid Code testing by provision of a report on battery load and capacity and during the site survey.
12 | Compliance of Demand Side Units with Dispatch Instructions | OC10.4.5.2 |  | Open
13 | Availability of Demand Side Units | SDC1.4.3.4/5/6 |  | Open
Graph subject to approval of Grid Code Review Panel and CER

## 7) Test request Profiles
DSU Within Day Test Consent Form
Time | MW Response | Available for MW Dispatch | Comment | UNIT NAME
10:00 | As Required | Y |  | REGISTERED CAPACITY
10:10 | As Required | Y |  | TEST DATE
10:20 | As Required | Y |  | TEST DAY | (Automatic Value)
10:30 | As Required | Y |  | LOAD REJECTION TEST (YES / NO)
10:40 | As Required | Y |  | RISK OF TRIP DURING TEST
10:50 | 0 | N |  | PURPOSE OF TEST
11:00 | 2 | N
11:10 | 5 | N
11:20 | 2 | N
11:30 | 0 | N |  | DESCRIPTION OF TEST
11:40 | 2 | N
11:50 | 5 | N
12:00 | 5 | N
12:10 | 5 | N
12:20 | 5 | N |  | CONTACT NAME | MOBILE | ROLE
12:30 | 5 | N
12:40 | 5 | N
12:50 | 5 | N
13:00 | 5 | N
13:10 | 5 | N
13:20 | 5 | N
13:30 | 5 | N
13:40 | 5 | N
13:50 | 5 | N
14:00 | 2 | N
14:10 | 0 | N
14:20 | As Required | Y
14:30 | As Required | Y
14:40 | As Required | Y
14:50 | As Required | Y
15:00 | As Required | Y
15:10 | As Required | Y
15:20 | As Required | Y
15:30 | As Required | Y
15:40 | As Required | Y
15:50 | As Required | Y
16:00 | As Required | Y
16:10 | As Required | Y
16:20 | As Required | Y
16:30 | As Required | Y
16:40 | As Required | Y
16:50 | As Required | Y
17:00 | As Required | Y
17:10 | As Required | Y
17:20 | As Required | Y
17:30 | As Required | Y
17:40 | As Required | Y
17:50 | As Required | Y
Profile Template located at http://www.eirgrid.com/media/DSUTestProfileTemplate.xlsx
Send to generator_testing@eirgrid.com for assessment 10 business days in advance of test.
Send to control@eirgrid.com with generator_testing@eirgrid.com on copy for approval 5 days in advance of test.
Test profiles shall be provided for DSU in aggregate with separate profiles for the individual demand sites.
Note on F6: PLEASE ENTER THE UNIT NAME AND EMS NAME