## Information Note
Info | Summary of Additions/Migrations
This Excel for Publication is intended for informational uses by Industry. - Data freeze date for information included in the Studies: 27/03/2026 The Excel contains the following Tabs: - RES & Battery Generation Table: Contains a complete list of all Wind, Solar, and Battery Generation Assets used in the studies. Prior to the introduction of ECP, connection to the electricity system in Ireland was captured under two broad policy approaches: the group processing approach (GPA, also known as the gate system), used for larger renewables and conventional generators, and the nongroup processing approach (non-GPA), allowing for connection of smaller renewables, low-carbon generators, and experimental technologies. Both the Gate system and non-GPA system have since been replaced by the ECP. * = Battery due to connect without confirmed storage duration. - Generation Table: Summary tables for the Renewable Generation Table tab and Interconnector Capacities. The generation profiles in this study were the same, this will be broken where generation profiles differ across study years. In this tab, "Thermal Technologies" refers to: Gas, Diesel, Biogas, Biomass, Combined Heat & Power (CHP), Landfill Gas (LFG), and Anaerobic Digester (AD) plants. - Network Reinforcements: Contains a table of network reinforcements that are included in the studies. Reinforcements are listed by area, type, project name and study year in which they are first included. - Network Outages: Contains the schedule of network outage months included in the studies. Outages recorded in this tab cover the entire listed month. Outages are recorded with the affected line, the outage month, whether it is a line or transformer affected, and the jurisdiction of the outage. - Modelling Results: Contains the excel format of the Dispatch Down Results in the Area Reports. This is the main body of results data from the Constraint Analysis studies and contains all of the information participants might be familiar with from the previous Area Reports. Results data is displayed in columns covering location as Area, Subgroup, and Node; generation information as the Study Year, Scenario Name, Constraint Methodology, and Generation Type; Installed Capacity, Available Energy, and Generated Energy; and finally, the constraint results, including Surplus, Curtailment, Constraint, and Total Dispatch Down reported in both absolute (GWh) and percentage of available energy (%) units. - Figures and Tables: Contains a pivot table and pivot chart linked to the Model Results. The slicers at the top of this sheet can be used to automatically reproduce any table or chart previously found in the Area Reports and permit filtering by, Area, Subgroup, Node, Constraint Methodology, Generation Type, and Scenario Name. The table and chart in this sheet will automatically update to reflect the selections made. Important Note: Grandfathering and Pro-rata options should not be selected simultaneously. - Contingencies and Lines: Contains a table with the binding hours range for a given pair of lines and contingencies for each scenario included in the study. For each line contingency pair, the annual binding hours are determined and binned into 250 hour ranges to allow for easier comparison. - IC Flows: Contains the Flows used in the Dispatch Down Studies that were obtained for each of the Generation Scenarios and Horizon Years. Forecast flows are from 12 AM January 1st of the forecast year until 12 AM on January 1st of the following year (Total of 1 year). Please note positive figures are importing in all flows, while negative figures are exporting. The interconnector flows are the same for all 3 run types (Surplus, Curtailment, and Constraint). Tabs are colour-coded, blue for information note, yellow for inputs, and green for outputs. Link to EirGrid Website where reports can be found: https://www.eirgrid.ie/industry/customer-information/ecp-constraint-forecast-reports | Changes to the information previously published in the Constraint Forecast Study Summary are as follows: 1. Tables 1, 2, 3, and 4, previously in Section 2 have been migrated to this excel. All information previously shown by those tables can be found in the Generation Table Tab. 2. Appendix B, Contingencies and Line Overloading been migrated to this Excel and can be found in the Contingencies and Lines tab. The below information previously provided in nodal area reports, including maintenance sensitivities, will be provided in Excel format: 1. Table 1-4 Area ‘x’ Generation nodes and subgroups, 2. All Surplus, Curtailment and Constraint tables from Section 1.5 and Section 2 3. All Surplus, Curtailment, and Constraint with sensitivity tables from Section 1.5 and Section 2. (All of the above three items will items can be found in the Modelling results tab, and all tables and figures previously found in the twelve area reports can be generated in the Figures and Tables tab.) Inputs will continue to be published in the assumptions document, and the following, previously found in the Assumptions Document will be available in Excel format: 1. Table 4 – Generation Capacities in Area for Ireland and Northern Ireland has been migrated to the Renewable Generation Table Tab. 2. Network Reinforcements& Network Outages both of which can now be found in the tabs of the same name. Other modelling outputs that will be provided in Excel format include: 1. Hourly Interconnector Flows for each scenario can be found in the Example IC Flows tab.

## RES & Battery Generation Table
ECP-GSS-1 IE Final Wind & Solar Generation Assumptions Generation < 1 MW has not been modelled as part of the ECP-GSS-1 Constraint Analysis. Pipeline Wind and Solar Generation Projects add up to an estimated 342 connected and 406 due to be connected Projects. This is an approximate Sum of Maximum Export Capacity (MEC) of 27 GW. This table represents all Renewable generation included in the ECP-GSS-1 constraints analysis. This data has been collated using the best information available, however, if any significant discrepancies are noted please immediately contact info@eirgrid.com. Maximum Export Capacity (MEC) has been rounded up for reporting purposes, exact MEC figures have been used within the model. Data freeze date: 27/03/2026. * For the sole purpose of the ECP-GSS-1 Constraint Analysis, the priority status assumption is based on whether the unit was connected before the date 04/07/2019 – as referenced in Article 12, EU Regulation 2019/943. ECP-GSS-1 IE Battery Final Assumptions This data has been collated using the best information available. Maximum Export Capacity (MEC) has been rounded up for reporting purposes, exact MEC figures have been used within the model. Data freeze date: 27/03/2026. Pipeline Battery Projects add up to an estimated 76 due to be connected Projects. This is an approximate Sum of Maximum Export Capacity (MEC) of 5632 MW and a sum of Total Battery capacity of 15,307 MWh*. To Note, for the purposes of modelling, the MIC has been set equal to the MEC. * Due to the nature of technology configuration, an estimate may have been applied for Battery Capacity (MWh) due to far out date of connection. Please see below summary of data used."
Name | Area | Node | Generation | System | Connection | Processing | Maximum Export | Controllability | priority / not-priority | Battery Storage Capacity (MWh)
|  |  | Type | Operator | Status | Type | Capacity (MW) | Status (Y/N)
Athea (1)a | E | Athea | wind | TSO | connected | Gate 1 | 34.35 | Y | wind priority | N/A
Ballycadden (1) | H2 | Crory | wind | DSO | connected | Gate 1 | 14.45 | Y | wind priority | N/A
Beenanaspock and Tobertooreen Wind Farm | E | Athea | wind | TSO | connected | Gate 1 | 23.15 | Y | wind not priority | N/A
Clahane (1) | E | Clahane | wind | TSO | connected | Gate 1 | 37.8 | Y | wind priority | N/A
Coomacheo (1) | E | Garrow | wind | TSO | connected | Gate 1 | 41.225 | Y | wind priority | N/A
Corkermore (1) | A | Binbane | wind | DSO | connected | Gate 1 | 9.99 | Y | wind priority | N/A
Cronelea (1) | H2 | Carlow | wind | DSO | connected | Gate 1 | 4.99 | Y | wind priority | N/A
Dunmore (1) | G | Drybridge | wind | DSO | connected | Gate 1 | 1.7 | N | wind uncontrolled | N/A
Glanlee (1) | E | Glanlee | wind | TSO | connected | Gate 1 | 29.8 | Y | wind priority | N/A
Killin Hill (1) | A | Binbane | wind | DSO | connected | Gate 1 | 6 | Y | wind priority | N/A
Killybegs (1) | A | Binbane | wind | DSO | connected | Gate 1 | 2.55 | N | wind uncontrolled | N/A
Knockawarriga (1) | E | Trien | wind | DSO | connected | Gate 1 | 22.5 | Y | wind priority | N/A
Knocknalour (1) | H2 | Crory | wind | DSO | connected | Gate 1 | 5 | Y | wind priority | N/A
Lackan (1) | B | Moy | wind | DSO | connected | Gate 1 | 6 | Y | wind priority | N/A
Loughderryduff (1) | A | Binbane | wind | DSO | connected | Gate 1 | 7.65 | Y | wind priority | N/A
Lurganboy (1) | A | Letterkenny | wind | DSO | connected | Gate 1 | 4.99 | N | wind uncontrolled | N/A
Meenachullalan (1) | A | Binbane | wind | DSO | connected | Gate 1 | 11.9 | Y | wind priority | N/A
Meentycat (2) | A | Meentycat | wind | TSO | connected | Gate 1 | 14 | Y | wind priority | N/A
Moneypoint WF | E | Moneypoint | wind | TSO | connected | Gate 1 | 17.25 | Y | wind priority | N/A
Mount Eagle (2) | E | Tralee | wind | DSO | connected | Gate 1 | 1.7 | N | wind uncontrolled | N/A
Muingnaminnane (1) | E | Reamore | wind | DSO | connected | Gate 1 | 15.3 | Y | wind priority | N/A
Mullananalt (1) | G | Meath Hill | wind | DSO | connected | Gate 1 | 7.5 | Y | wind priority | N/A
Richfield (2) | H2 | Wexford | wind | DSO | connected | Gate 1 | 6.75 | Y | wind priority | N/A
Tournafulla (2) | E | Trien | wind | DSO | connected | Gate 1 | 17.2 | Y | wind priority | N/A
Ballaman formerly (Kennystown) (1) | H2 | Crory | wind | DSO | connected | Gate 2 | 3.6 | N | wind uncontrolled | N/A
Ballybane 2 (Glanta Commons) Wind Farm | F | Ballylickey | wind | DSO | connected | Gate 2 | 8.4 | Y | wind priority | N/A
Ballyduff (1) | H2 | Crory | wind | DSO | connected | Gate 2 | 4 | N | wind uncontrolled | N/A
Ballymartin (1) | H2 | Waterford | wind | DSO | connected | Gate 2 | 6 | Y | wind priority | N/A
Ballynancoran (1) | H2 | Crory | wind | DSO | connected | Gate 2 | 4 | N | wind uncontrolled | N/A
Ballywater (2) | H2 | Ballywater | wind | TSO | connected | Gate 2 | 10.5 | Y | wind priority | N/A
Bawnmore (1) formerly Burren (Cork) | F | Macroom | wind | DSO | connected | Gate 2 | 24 | Y | wind priority | N/A
Beale Hill (3) | E | Trien | wind | DSO | connected | Gate 2 | 1.3 | N | wind uncontrolled | N/A
Beenanaspock and Tobertooreen Wind Farm (battery) | E | Athea | battery | TSO | connected | Gate 2 | 11 | N | battery | 5.5
Boggeragh (1) | E | Boggeragh | wind | TSO | connected | Gate 2 | 57 | Y | wind priority | N/A
Boolinrudda (formerly Loughaun North) | D | Slievecallan | wind | TSO | connected | Gate 2 | 45 | Y | wind priority | N/A
Booltiagh (2) | D | Booltiagh | wind | TSO | connected | Gate 2 | 12 | Y | wind priority | N/A
Bunnyconnellan (1) | B | Glenree | wind | DSO | connected | Gate 2 | 28 | Y | wind not priority | N/A
Caherdowney (1) | E | Garrow | wind | DSO | connected | Gate 2 | 10 | Y | wind priority | N/A
Cappawhite A Wind Farm (Gate 2) | H1 | Cauteen | wind | DSO | connected | Gate 2 | 2.92 | Y | wind priority | N/A
Cappawhite B | H1 | Cauteen | wind | DSO | connected | Gate 2 | 13.18 | Y | wind priority | N/A
Carrons (1) | E | Rathkeale | wind | DSO | connected | Gate 2 | 4.99 | N | wind uncontrolled | N/A
Carrowleagh (1) | B | Glenree | wind | DSO | connected | Gate 2 | 34.15 | Y | wind priority | N/A
Castledockrell (1) | H2 | Castledockrell | wind | TSO | connected | Gate 2 | 20 | Y | wind priority | N/A
Castledockrell (2) | H2 | Castledockrell | wind | TSO | connected | Gate 2 | 2 | Y | wind priority | N/A
Castledockrell (3) | H2 | Castledockrell | wind | TSO | connected | Gate 2 | 3.3 | Y | wind priority | N/A
Castledockrell (4) | H2 | Castledockrell | wind | TSO | connected | Gate 2 | 16.1 | Y | wind priority | N/A
Cloghanaleskirt (1) | E | Cloghboola | wind | DSO | connected | Gate 2 | 12.55 | Y | wind priority | N/A
Cloonlusk (1) | B | Cloon | wind | DSO | connected | Gate 2 | 4.25 | N | wind uncontrolled | N/A
Clydaghroe (1) | E | Garrow | wind | DSO | connected | Gate 2 | 4.99 | N | wind uncontrolled | N/A
Coollegrean (1) | E | Cordal | wind | DSO | connected | Gate 2 | 18.5 | Y | wind priority | N/A
Coomacheo (2) | E | Garrow | wind | TSO | connected | Gate 2 | 18 | Y | wind priority | N/A
Coomagearlahy (2) | E | Coomagearlahy | wind | TSO | connected | Gate 2 | 8.5 | Y | wind priority | N/A
Coomagearlahy (3) | E | Coomagearlahy | wind | TSO | connected | Gate 2 | 30 | Y | wind priority | N/A
Crocane (1) | I | Midleton | wind | DSO | connected | Gate 2 | 1.7 | N | wind uncontrolled | N/A
Cronelea (2) | H2 | Carlow | wind | DSO | connected | Gate 2 | 4.5 | Y | wind priority | N/A
Cronelea Upper (2) | H2 | Carlow | wind | DSO | connected | Gate 2 | 1.7 | N | wind uncontrolled | N/A
Cuillalea (2) | B | Castlebar | wind | DSO | connected | Gate 2 | 1.59 | N | wind uncontrolled | N/A
Curraghgraigue (2) | H1 | Nenagh | wind | DSO | connected | Gate 2 | 2.44 | N | wind uncontrolled | N/A
Derrynadivva Wind Farm (prev. Raheen Bar 2) | B | Castlebar | wind | DSO | connected | Gate 2 | 8.5 | Y | wind priority | N/A
Dromada (1) | E | Dromada | wind | TSO | connected | Gate 2 | 28.5 | Y | wind priority | N/A
Dromdeeveen (2) | E | Glenlara 220kV side | wind | DSO | connected | Gate 2 | 16.5 | Y | wind priority | N/A
Dunmore (2) | G | Drybridge | wind | DSO | connected | Gate 2 | 1.8 | N | wind uncontrolled | N/A
Esk (1) | E | Boggeragh | wind | DSO | connected | Gate 2 | 5.95 | Y | wind not priority | N/A
Flughland (1) | A | Sorne Hill | wind | DSO | connected | Gate 2 | 9.2 | Y | wind priority | N/A
Garracummer (1) | H1 | Cauteen | wind | DSO | connected | Gate 2 | 36.9 | Y | wind priority | N/A
Garranereagh (1) | F | Bandon | wind | DSO | connected | Gate 2 | 8.75 | Y | wind priority | N/A
Garvagh - Glebe (1a) | A | Garvagh | wind | TSO | connected | Gate 2 | 26 | Y | wind priority | N/A
Garvagh - Tullynahaw (1c) | A | Garvagh | wind | TSO | connected | Gate 2 | 22 | Y | wind priority | N/A
Gibbet Hill (1) | H2 | Crory | wind | DSO | connected | Gate 2 | 14.8 | Y | wind priority | N/A
Glackmore Hill (2) | A | Sorne Hill | wind | DSO | connected | Gate 2 | 1.4 | N | wind uncontrolled | N/A
Glanaruddery 1 (formerly Dromadda More Wind Farm) | E | Cloghboola | wind | DSO | connected | Gate 2 | 20 | Y | wind priority | N/A
Glenough (1) | H1 | Cauteen | wind | DSO | connected | Gate 2 | 33 | Y | wind priority | N/A
Gortahile (1) | H2 | Carlow | wind | DSO | connected | Gate 2 | 21 | Y | wind priority | N/A
Grouse Lodge (1) | E | Rathkeale | wind | DSO | connected | Gate 2 | 15 | Y | wind priority | N/A
Holyford (1) | H1 | Cauteen | wind | DSO | connected | Gate 2 | 9 | Y | wind priority | N/A
Kilbranish (1) | H2 | Crane | wind | DSO | connected | Gate 2 | 2.5 | Y | wind priority | N/A
Killaveenoge Windfarm (Derryvacorneen merge with Barrboy Windfarm) | F | Dunmanway | wind | DSO | connected | Gate 2 | 17 | Y | wind priority | N/A
Kingsmountain (2) | B | Cunghill | wind | TSO | connected | Gate 2 | 11.05 | Y | wind priority | N/A
Knockacummer (1) | E | Knockacummer | wind | TSO | connected | Gate 2 | 105 | Y | wind priority | N/A
Knockalassa (formerly Keelderry) | D | Slievecallan | wind | TSO | connected | Gate 2 | 26.875 | Y | wind priority | N/A
Knockaneden (1) | E | Oughtragh | wind | DSO | connected | Gate 2 | 9 | Y | wind priority | N/A
Knockawarriga Extension (Glenduff & Caherlevoy) | E | Trien | wind | DSO | connected | Gate 2 | 6.6 | Y | wind not priority | N/A
Knocknagashel Wind (Cloghboola (1)) | E | Cloghboola | wind | TSO | connected | Gate 2 | 46 | Y | wind priority | N/A
Knocknagoum (1) | E | Reamore | wind | DSO | connected | Gate 2 | 42.55 | Y | wind priority | N/A
Leabeg (1) | C | Dallow | wind | DSO | connected | Gate 2 | 4.25 | N | wind uncontrolled | N/A
Lenanavea (Burren) Wind Farm | B | Castlebar | wind | DSO | connected | Gate 2 | 4.65 | N | wind uncontrolled | N/A
Lisheen (1) | H1 | Lisheen | wind | TSO | connected | Gate 2 | 36 | Y | wind priority | N/A
Lisheen (1a) | H1 | Lisheen | wind | TSO | connected | Gate 2 | 23 | Y | wind priority | N/A
Mace Upper (1) | B | Dalton | wind | DSO | connected | Gate 2 | 2.55 | N | wind uncontrolled | N/A
Martinstown Solar formerly Crowinstown Great wind | G | Navan | solar | DSO | due to connected | Gate 2 | 4.999 | Y | solar not priority | N/A
Mauricetown (Glenduff) Wind Farm | E | Glenlara 220kV side | wind | DSO | connected | Gate 2 | 13.8 | Y | wind not priority | N/A
Meenanilta (3) | A | Letterkenny | wind | DSO | connected | Gate 2 | 3.4 | N | wind uncontrolled | N/A
Meenkeeragh (1) | A | Sorne Hill | wind | DSO | connected | Gate 2 | 4.2 | N | wind uncontrolled | N/A
Mountain Lodge (3) | G | Ratrussan | wind | TSO | connected | Gate 2 | 5.82 | Y | wind priority | N/A
Mulreavy (Mulreavy (1)) | A | Mulreavy | wind | TSO | connected | Gate 2 | 82 | Y | wind priority | N/A
Mulreavy Ext (Croaghnameal (1)) | A | Mulreavy | wind | TSO | connected | Gate 2 | 4.25 | Y | wind priority | N/A
Mulreavy Ext (Meenadreen South (1)) | A | Mulreavy | wind | TSO | connected | Gate 2 | 3.6 | Y | wind priority | N/A
Pluckanes (1) | I | Kilbarry | wind | DSO | connected | Gate 2 | 0.85 | N | wind uncontrolled | N/A
Raheen Barr extension (was Derrynadivva extension) | B | Castlebar | wind | DSO | connected | Gate 2 | 6.8 | Y | wind not priority | N/A
Rahora (1) | H2 | Waterford | wind | DSO | connected | Gate 2 | 4.25 | N | wind uncontrolled | N/A
Reenascreena (1) | F | Dunmanway | wind | DSO | connected | Gate 2 | 4.5 | N | wind uncontrolled | N/A
Roosky (1) | B | Tonroe | wind | DSO | connected | Gate 2 | 3.6 | N | wind uncontrolled | N/A
Scartaglen (1) | E | Cordal | wind | DSO | connected | Gate 2 | 35.45 | Y | wind priority | N/A
Seltanaveeny (1) | A | Arigna | wind | DSO | connected | Gate 2 | 4.6 | N | wind uncontrolled | N/A
Shannagh (1) previously Kilcar | A | Binbane | wind | DSO | connected | Gate 2 | 2.55 | N | wind uncontrolled | N/A
Skrine (1) | C | Lanesboro | wind | DSO | connected | Gate 2 | 4.6 | N | wind uncontrolled | N/A
Slievereagh (1) | H1 | Tipperary | wind | DSO | connected | Gate 2 | 3 | N | wind uncontrolled | N/A
Sorne Hill (2) | A | Sorne Hill | wind | DSO | connected | Gate 2 | 7.4 | Y | wind priority | N/A
Sorne Hill Single Turbine (Enros) | A | Sorne Hill | wind | DSO | connected | Gate 2 | 2.3 | N | wind uncontrolled | N/A
Templederry (1) | H1 | Nenagh | wind | DSO | connected | Gate 2 | 3.9 | N | wind uncontrolled | N/A
Three Trees (1) | A | Sorne Hill | wind | DSO | connected | Gate 2 | 4.25 | N | wind uncontrolled | N/A
Tullynamoyle (1) | A | Corderry | wind | DSO | connected | Gate 2 | 9 | Y | wind priority | N/A
Tullynamoyle 3 (Carrane Hill merged capacity) | A | Corderry | wind | DSO | connected | Gate 2 | 1.598 | N | wind uncontrolled | N/A
WEDcross (1) | E | Knockearagh | wind | DSO | connected | Gate 2 | 4.5 | N | wind uncontrolled | N/A
An Cnoc | H1 | Thurles | wind | DSO | connected | Gate 3 | 11.5 | Y | wind priority | N/A
Ardderoo 2 (Formerly Buffy) | B | Knockranny | wind | TSO | connected | Gate 3 | 64.2 | Y | wind not priority | N/A
Ardderoo Wind Farm | B | Knockranny | wind | TSO | connected | Gate 3 | 27 | Y | wind not priority | N/A
Ballagh (1) | E | Trien | wind | DSO | connected | Gate 3 | 4.6 | N | wind uncontrolled | N/A
Ballinacurry WF | H1 | Thurles | wind | DSO | connected | Gate 3 | 4.6 | N | wind uncontrolled | N/A
Ballybane 2A | F | Ballylickey | wind | DSO | connected | Gate 3 | 17.5 | Y | wind priority | N/A
Ballybane 2A (Glanta Commons) Wind Farm Extension | F | Ballylickey | wind | DSO | connected | Gate 3 | 1.55 | Y | wind priority | N/A
Ballybane 3 (Glanta Commons) Wind Farm | F | Ballylickey | wind | DSO | connected | Gate 3 | 4.45 | Y | wind priority | N/A
Ballybay Wind Farm (Tullaroan) | H1 | Thurles | wind | DSO | connected | Gate 3 | 13.8 | Y | wind priority | N/A
Ballycadden (2) | H2 | Crory | wind | DSO | connected | Gate 3 | 9.762 | Y | wind priority | N/A
Ballycumber (1) | H2 | Arklow | wind | DSO | connected | Gate 3 | 18 | Y | wind priority | N/A
Ballycurreen (1) | K | Dungarvan | wind | DSO | connected | Gate 3 | 4.99 | N | wind uncontrolled | N/A
Ballymartin (2) | H2 | Waterford | wind | DSO | connected | Gate 3 | 8.28 | Y | wind priority | N/A
Barranafaddock (1) | H1 | Barrymore | wind | DSO | connected | Gate 3 | 32.4 | Y | wind priority | N/A
Boggeragh 2 | E | Boggeragh | wind | TSO | connected | Gate 3 | 65.7 | Y | wind priority | N/A
Boolard Wind Farm (Charlevile) | E | Charleville | wind | DSO | connected | Gate 3 | 4.45 | N | wind uncontrolled | N/A
Boolynagleragh (1) | D | Booltiagh | wind | DSO | connected | Gate 3 | 36.98 | Y | wind not priority | N/A
Bruckana (1) | H1 | Lisheen | wind | DSO | connected | Gate 3 | 39.6 | Y | wind priority | N/A
Bunnahowen (1) | B | Bellacorick | wind | DSO | connected | Gate 3 | 2.55 | N | wind uncontrolled | N/A
Cahermurphy (1) | D | Booltiagh | wind | DSO | connected | Gate 3 | 6 | Y | wind not priority | N/A
Cappawhite A | H1 | Cauteen | wind | DSO | connected | Gate 3 | 49.08 | Y | wind priority | N/A
Carrickeeney (1) | B | Sligo | wind | DSO | connected | Gate 3 | 7.65 | Y | wind priority | N/A
Carrigdangan (formerly Barnadivine) | F | Dunmanway | wind | TSO | connected | Gate 3 | 60 | Y | wind not priority | N/A
Carrowleagh (2) | B | Glenree | wind | DSO | connected | Gate 3 | 2.65 | Y | wind not priority | N/A
Carrownawelaun (1) | D | Tullabrack | wind | DSO | connected | Gate 3 | 4.6 | N | wind uncontrolled | N/A
Castlepook (1) | E | Charleville | wind | DSO | connected | Gate 3 | 33.1 | Y | wind priority | N/A
Clahane (2) | E | Clahane | wind | TSO | connected | Gate 3 | 13.8 | Y | wind priority | N/A
Cleanrath (1) | E | Coomataggart | wind | DSO | connected | Gate 3 | 42.64 | Y | wind not priority | N/A
Clogheravaddy Wind Farm (Phase 1) | A | Binbane | wind | DSO | connected | Gate 3 | 9.2 | Y | wind not priority | N/A
Clogheravaddy Wind Farm (Phase 2) | A | Binbane | wind | DSO | connected | Gate 3 | 10.8 | Y | wind not priority | N/A
Collon Wind Power | G | Drybridge | wind | DSO | connected | Gate 3 | 2.3 | N | wind uncontrolled | N/A
Coolberrin Wind Farm (formerly Bragan Wind Farm) | G | Lisdrum | wind | DSO | due to connected | Gate 3 | 33.1 | Y | wind not priority | N/A
Cooly (1) | A | Trillick | wind | DSO | connected | Gate 3 | 4 | N | wind uncontrolled | N/A
Cordal (1+2) | E | Cordal | wind | TSO | connected | Gate 3 | 54 | Y | wind priority | N/A
Corvin Wind Turbine | A | Sorne Hill | wind | DSO | connected | Gate 3 | 2.1 | N | wind uncontrolled | N/A
Corvoderry (was Gortnahurra (1)) | B | Bellacorick | wind | DSO | due to connected | Gate 3 | 33.9 | Y | wind not priority | N/A
Cronalaght (2) | A | Ardnagappary | wind | DSO | connected | Gate 3 | 17.96 | Y | wind not priority | N/A
Cureeny (1) | H1 | Killonan | wind | DSO | due to connected | Gate 3 | 84 | Y | wind not priority | N/A
Curraghderrig (1) | E | Trien | wind | DSO | connected | Gate 3 | 4.5 | N | wind uncontrolled | N/A
Derreenacrinnig West (prev Kilvinane 2 WF) | F | Ballylickey | wind | DSO | due to connected | Gate 3 | 5.82 | Y | wind not priority | N/A
Derrysallagh Wind Farm (Formerly Kilronan 2) | A | Garvagh | wind | DSO | connected | Gate 3 | 34 | Y | wind not priority | N/A
Dooray WF | J | Portlaoise | wind | DSO | due to connected | Gate 3 | 45.001 | Y | wind not priority | N/A
Esk Wind Farm (sub metered Gneeves 2 Merge) | E | Boggeragh | wind | DSO | connected | Gate 3 | 5.4 | Y | wind not priority | N/A
Faughary (1) | B | Sligo | wind | DSO | connected | Gate 3 | 6 | Y | wind priority | N/A
Foyle Windfarm | H1 | Thurles | wind | DSO | connected | Gate 3 | 9.6 | Y | wind priority | N/A
Garracummer (2) | H1 | Cauteen | wind | DSO | connected | Gate 3 | 1 | Y | wind priority | N/A
Glanaruddery 2 (formerly Dromadda More 2) | E | Cloghboola | wind | DSO | connected | Gate 3 | 12 | Y | wind priority | N/A
Glantaunyalkeen Windfarm( Cloghboola (2) Ext) | E | Cloghboola | wind | DSO | connected | Gate 3 | 9.999 | Y | wind priority | N/A
Glencarbry (1) | H1 | Cauteen | wind | DSO | connected | Gate 3 | 33 | Y | wind priority | N/A
Gortnacloghy Wind Farm | E | Trien | wind | DSO | connected | Gate 3 | 4.4 | N | wind uncontrolled | N/A
Grousemount WF | E | Coomataggart | wind | TSO | connected | Gate 3 | 114.2 | Y | wind not priority | N/A
Grove Hill (1) formerly Tullynageer | G | Dundalk | wind | DSO | connected | Gate 3 | 16.1 | Y | wind priority | N/A
Gurteen (1) | H1 | Thurles | wind | DSO | connected | Gate 3 | 2.3 | N | wind uncontrolled | N/A
Kelwin Power Plant - Phase 2 | E | Kilpaddoge | battery | TSO | connected | Gate 3 | 26.6 | N | battery | 13.3
Kilberehert (1) | E | Charleville | wind | DSO | connected | Gate 3 | 4.799 | N | wind uncontrolled | N/A
Kill Hill (1) - phase 1 | H1 | Kill Hill | wind | TSO | connected | Gate 3 | 36 | Y | wind priority | N/A
Killala Battery - Phase 2 | B | Tawnaghmore | battery | DSO | connected | Gate 3 | 10.8 | N | battery | 10.8
Killala Wind Farm (Phase 1) | B | Tawnaghmore | wind | DSO | connected | Gate 3 | 19.2 | Y | wind priority | N/A
Killaveenoge Windfarm (Derryvacorneen merge with Barrboy) | F | Dunmanway | wind | DSO | connected | Gate 3 | 7.8 | Y | wind priority | N/A
Kilmeedy (1) | E | Charleville | wind | DSO | connected | Gate 3 | 4.7 | N | wind uncontrolled | N/A
Kiltumper | D | Booltiagh | wind | DSO | connected | Gate 3 | 4.99 | N | wind uncontrolled | N/A
Knockadosan Solar (formerly Springfarm Wind Farm) | H2 | Arklow | solar | DSO | due to connected | Gate 3 | 6 | Y | solar not priority | N/A
Knockalough (1) | B | Knockranny | wind | TSO | connected | Gate 3 | 33.6 | Y | wind priority | N/A
Knocknagoum (2) formerly Muingnatee (3) | E | Reamore | wind | DSO | connected | Gate 3 | 1.8 | N | wind uncontrolled | N/A
Knocknalour (2) | H2 | Crory | wind | DSO | connected | Gate 3 | 3.95 | N | wind uncontrolled | N/A
Knocknamona Wind Farm (Prev. Crohaun) | K | Woodhouse | wind | TSO | due to connected | Gate 3 | 34 | Y | wind not priority | N/A
Knocknatallig | E | Charleville | wind | DSO | connected | Gate 3 | 18.3 | Y | wind priority | N/A
Leanamore (1) (formerly Tarbert (1)) | E | Kilpaddoge | wind | DSO | connected | Gate 3 | 18 | Y | wind priority | N/A
Leitir Guingaid & Doire Chrith1 & 2 Merge | B | Salthill | wind | DSO | connected | Gate 3 | 40.9 | Y | wind priority | N/A
Lettergull (1) | A | Letterkenny | wind | DSO | due to connected | Gate 3 | 20 | Y | wind not priority | N/A
Lisdowney (1) | H2 | Ballyragget | wind | DSO | connected | Gate 3 | 9.2 | Y | wind priority | N/A
Lissycasey (1) | D | Booltiagh | wind | DSO | connected | Gate 3 | 13.399 | Y | wind not priority | N/A
Lumcloon ESS (Derrycarney) | C | Derrycarney | battery | TSO | connected | Gate 3 | 100 | N | battery | 50
Magheramore and Cloontooa (1) | B | Dalton | wind | DSO | connected | Gate 3 | 40.8 | Y | wind priority | N/A
Meenachullalan (2) | A | Binbane | wind | DSO | due to connected | Gate 3 | 1.9 | Y | wind not priority | N/A
Meenaward | A | Trillick | wind | DSO | connected | Gate 3 | 6.9 | Y | wind priority | N/A
Meenwaun WF | C | Dallow | wind | DSO | connected | Gate 3 | 9.99 | Y | wind priority | N/A
Monaincha Bog Wind Farm | H1 | Ikerrin | wind | DSO | connected | Gate 3 | 35.95 | Y | wind priority | N/A
Mount Lucas (1) | J | Mount Lucas | wind | TSO | connected | Gate 3 | 79.2 | Y | wind priority | N/A
Mulreavy Ext (Meenadreen South (2)) | A | Mulreavy | wind | TSO | connected | Gate 3 | 5.4 | Y | wind priority | N/A
Oriel 1 | G | Oriel 220kV | offshore wind | TSO | due to connected | Gate 3 | 210 | Y | wind not priority | N/A
Oweninny 3 (Previously Oweninny 5) | B | Bellacorick | wind | TSO | due to connected | Gate 3 | 50 | Y | wind not priority | N/A
Oweninny Power (1) | B | Bellacorick | wind | TSO | connected | Gate 3 | 89 | Y | wind not priority | N/A
Oweninny Power (2) | B | Bellacorick | wind | TSO | connected | Gate 3 | 83 | Y | wind not priority | N/A
Raheenleagh (1) | H2 | Arklow | wind | DSO | connected | Gate 3 | 35.2 | Y | wind priority | N/A
Raragh (2) | G | Meath Hill | wind | DSO | connected | Gate 3 | 11.5 | Y | wind not priority | N/A
Rathnacally (1) | E | Charleville | wind | DSO | connected | Gate 3 | 4.45 | N | wind uncontrolled | N/A
Rossaveel Wind | B | Screebe | wind | DSO | connected | Gate 3 | 3 | N | wind uncontrolled | N/A
Scartaglen (2) | E | Cordal | wind | DSO | connected | Gate 3 | 3.8 | Y | wind priority | N/A
Seecon (1) | B | Uggool | wind | TSO | connected | Gate 3 | 105 | Y | wind priority | N/A
Shannonbridge ESS | C | Shannonbridge | battery | TSO | connected | Gate 3 | 100 | N | battery | 50
Sheskin (1) | B | Bellacorick | wind | DSO | connected | Gate 3 | 32.9 | Y | wind not priority | N/A
Sliabh Bawn (1) | C | Sliabh Bawn | wind | TSO | connected | Gate 3 | 58 | Y | wind priority | N/A
Slievereagh Wind Farm (2) | H1 | Tipperary | wind | DSO | connected | Gate 3 | 1.6 | N | wind uncontrolled | N/A
Sorrell Island (prev Glenmore) (1) | D | Booltiagh | wind | DSO | connected | Gate 3 | 24 | Y | wind not priority | N/A
Spaddan (1) | A | Cathaleen's Fall | wind | DSO | connected | Gate 3 | 17.5 | Y | wind priority | N/A
Stack's Mountain | E | Reamore | wind | DSO | due to connected | Gate 3 | 25.3 | Y | wind not priority | N/A
Teevurcher | G | Meath Hill | wind | DSO | connected | Gate 3 | 9 | Y | wind priority | N/A
Tullabrack (1) | D | Tullabrack | wind | DSO | connected | Gate 3 | 13.8 | Y | wind priority | N/A
Tullynamalra (1) | G | Meath Hill | wind | DSO | connected | Gate 3 | 2.638 | N | wind uncontrolled | N/A
Tullynamoyle 2 Wind Farm | A | Corderry | wind | DSO | connected | Gate 3 | 10.225 | Y | wind priority | N/A
Tullynamoyle Wind Farm 3 (Formerly Geevagh 2) | A | Corderry | wind | DSO | connected | Gate 3 | 11.98 | Y | wind priority | N/A
Uggool (1) | B | Uggool | wind | TSO | connected | Gate 3 | 64 | Y | wind priority | N/A
Woodhouse (1) | K | Woodhouse | wind | TSO | connected | Gate 3 | 20 | Y | wind priority | N/A
Altagowlan (1) | A | Corderry | wind | DSO | connected | Pre-Gate | 7.65 | Y | wind priority | N/A
Anarget (1) | A | Cathaleen's Fall | wind | DSO | connected | Pre-Gate | 1.98 | N | wind uncontrolled | N/A
Arklow Bank (1) | H2 | Arklow | offshore wind | DSO | connected | Pre-Gate | 25.2 | Y | wind priority | N/A
Ballincollig Hill (1) | E | Tralee | wind | DSO | connected | Pre-Gate | 15 | Y | wind priority | N/A
Ballinlough (1) | H1 | Nenagh | wind | DSO | connected | Pre-Gate | 2.55 | N | wind uncontrolled | N/A
Ballinveny (1) | H1 | Nenagh | wind | DSO | connected | Pre-Gate | 2.55 | N | wind uncontrolled | N/A
Ballybane (Glanta Commons) Wind Farm | F | Ballylickey | wind | DSO | connected | Pre-Gate | 19.55 | Y | wind priority | N/A
Ballywater (1) | H2 | Ballywater | wind | TSO | connected | Pre-Gate | 31.5 | Y | wind priority | N/A
Beale Hill (1) | E | Trien | wind | DSO | connected | Pre-Gate | 1.65 | N | wind uncontrolled | N/A
Beale Hill (2) | E | Trien | wind | DSO | connected | Pre-Gate | 2.55 | N | wind uncontrolled | N/A
Beallough (1) | K | Butlerstown | wind | DSO | connected | Pre-Gate | 1.7 | N | wind uncontrolled | N/A
Beam Hill (1) | A | Trillick | wind | DSO | connected | Pre-Gate | 14 | Y | wind priority | N/A
Beenageeha (1) | E | Tralee | wind | DSO | connected | Pre-Gate | 3.96 | N | wind uncontrolled | N/A
Bellacorick (1) | B | Bellacorick | wind | DSO | connected | Pre-Gate | 6.45 | Y | wind priority | N/A
Black Banks (1) | A | Corderry | wind | DSO | connected | Pre-Gate | 3.4 | N | wind uncontrolled | N/A
Black Banks (2) | A | Corderry | wind | DSO | connected | Pre-Gate | 6.8 | Y | wind priority | N/A
Booltiagh (1) | D | Booltiagh | wind | TSO | connected | Pre-Gate | 19.45 | Y | wind priority | N/A
Cark (1) | A | Letterkenny | wind | DSO | connected | Pre-Gate | 15 | N | wind uncontrolled | N/A
Carnsore (1) | H2 | Wexford | wind | DSO | connected | Pre-Gate | 11.9 | N | wind uncontrolled | N/A
Carrane Hill (1) | A | Corderry | wind | DSO | connected | Pre-Gate | 3.4 | N | wind uncontrolled | N/A
Carrickallen Wind Farm | G | Shankill | wind | DSO | connected | Pre-Gate | 22 | Y | wind priority | N/A
Carrig (1) | C | Dallow | wind | DSO | connected | Pre-Gate | 2.55 | N | wind uncontrolled | N/A
Carrigcannon (1) | E | Boggeragh | wind | DSO | connected | Pre-Gate | 20 | Y | wind priority | N/A
Coomagearlahy (1) | E | Coomagearlahy | wind | TSO | connected | Pre-Gate | 42.5 | Y | wind priority | N/A
Coomatallin (1) | F | Dunmanway | wind | DSO | connected | Pre-Gate | 5.95 | Y | wind priority | N/A
Coreen (1) | A | Gortawee | wind | DSO | connected | Pre-Gate | 3 | N | wind uncontrolled | N/A
Corrie Mountain (1) | A | Arigna | wind | DSO | connected | Pre-Gate | 4.8 | N | wind uncontrolled | N/A
Crockahenny (1) | A | Trillick | wind | DSO | connected | Pre-Gate | 5 | N | wind uncontrolled | N/A
Cronalaght (1) | A | Ardnagappary | wind | DSO | connected | Pre-Gate | 4.98 | N | wind uncontrolled | N/A
Cronelea Upper (1) | H2 | Carlow | wind | DSO | connected | Pre-Gate | 2.55 | N | wind uncontrolled | N/A
Cuillalea (1) | B | Castlebar | wind | DSO | connected | Pre-Gate | 3.4 | N | wind uncontrolled | N/A
Culliagh (1) | A | Letterkenny | wind | DSO | connected | Pre-Gate | 11.88 | N | wind uncontrolled | N/A
Currabwee (1) | F | Dunmanway | wind | DSO | connected | Pre-Gate | 4.62 | N | wind uncontrolled | N/A
Curraghgraigue (1) | H1 | Nenagh | wind | DSO | connected | Pre-Gate | 2.55 | N | wind uncontrolled | N/A
Dromdeeveen (1) | E | Glenlara 220kV side | wind | DSO | connected | Pre-Gate | 10.5 | Y | wind priority | N/A
Drumlough Hill (1) | A | Trillick | wind | DSO | connected | Pre-Gate | 4.8 | N | wind uncontrolled | N/A
Drumlough Hill (2) | A | Trillick | wind | DSO | connected | Pre-Gate | 9.99 | Y | wind priority | N/A
Gartnaneane (1) | G | Meath Hill | wind | DSO | connected | Pre-Gate | 10.5 | N | wind uncontrolled | N/A
Gartnaneane (2) | G | Meath Hill | wind | DSO | connected | Pre-Gate | 4.5 | N | wind uncontrolled | N/A
Geevagh (1) | A | Corderry | wind | DSO | connected | Pre-Gate | 4.95 | N | wind uncontrolled | N/A
Gneeves (1) | E | Knockearagh | wind | DSO | connected | Pre-Gate | 9.35 | Y | wind priority | N/A
Golagh (1) | A | Golagh | wind | TSO | connected | Pre-Gate | 12 | N | wind uncontrolled | N/A
Golagh (1) (battery) | A | Golagh | battery | TSO | connected | Pre-Gate | 3 | N | battery | 3
Greenoge (1) | H2 | Crane | wind | DSO | connected | Pre-Gate | 4.99 | N | wind uncontrolled | N/A
Inverin (Knock South) (1) | B | Screebe | wind | DSO | connected | Pre-Gate | 2.64 | N | wind uncontrolled | N/A
Kealkil (Curraglass) (1) | F | Ballylickey | wind | DSO | connected | Pre-Gate | 8.5 | N | wind uncontrolled | N/A
Kilronan (1) | A | Arigna | wind | DSO | connected | Pre-Gate | 5 | N | wind uncontrolled | N/A
Kilvinane (1) | F | Bandon | wind | DSO | connected | Pre-Gate | 4.5 | N | wind uncontrolled | N/A
Kingsmountain (1) | B | Cunghill | wind | TSO | connected | Pre-Gate | 23.75 | Y | wind priority | N/A
Knockastanna (1) | D | Ardnacrusha | wind | DSO | connected | Pre-Gate | 7.5 | Y | wind priority | N/A
Lahanaght Hill (1) | F | Dunmanway | wind | DSO | connected | Pre-Gate | 4.25 | N | wind uncontrolled | N/A
Largan Hill (1) | B | Tonroe | wind | DSO | connected | Pre-Gate | 5.94 | N | wind uncontrolled | N/A
Meenadreen (1) | A | Cathaleen's Fall | wind | DSO | connected | Pre-Gate | 3.4 | N | wind uncontrolled | N/A
Meenanilta (1) | A | Letterkenny | wind | DSO | connected | Pre-Gate | 2.55 | N | wind uncontrolled | N/A
Meenanilta (2) | A | Letterkenny | wind | DSO | connected | Pre-Gate | 2.45 | N | wind uncontrolled | N/A
Meentycat (1) | A | Meentycat | wind | TSO | connected | Pre-Gate | 70.96 | Y | wind priority | N/A
Milane Hill (1) | F | Dunmanway | wind | DSO | connected | Pre-Gate | 5.94 | N | wind uncontrolled | N/A
Moanmore (1) | D | Tullabrack | wind | DSO | connected | Pre-Gate | 12.6 | N | wind uncontrolled | N/A
Moneenatieve (1) | A | Corderry | wind | DSO | connected | Pre-Gate | 3.96 | N | wind uncontrolled | N/A
Mount Eagle (1) | E | Tralee | wind | DSO | connected | Pre-Gate | 5.1 | N | wind uncontrolled | N/A
Mountain Lodge (1) | G | Ratrussan | wind | TSO | connected | Pre-Gate | 24.8 | Y | wind priority | N/A
Mountain Lodge (2) | G | Shankill | wind | DSO | connected | Pre-Gate | 3 | N | wind uncontrolled | N/A
Raheen Barr (1) | B | Castlebar | wind | DSO | connected | Pre-Gate | 18.7 | N | wind uncontrolled | N/A
Rathcahill (1) | E | Rathkeale | wind | DSO | connected | Pre-Gate | 12.5 | Y | wind priority | N/A
Ratrussan (1a) | G | Ratrussan | wind | TSO | connected | Pre-Gate | 48 | Y | wind priority | N/A
Richfield (1) | H2 | Wexford | wind | DSO | connected | Pre-Gate | 20.25 | Y | wind priority | N/A
Skehanagh (1) | C | Dallow | wind | DSO | connected | Pre-Gate | 4.25 | N | wind uncontrolled | N/A
Sonnagh Old (1) | C | Somerset | wind | DSO | connected | Pre-Gate | 7.65 | N | wind uncontrolled | N/A
Sorne Hill (1) | A | Sorne Hill | wind | DSO | connected | Pre-Gate | 31.5 | Y | wind priority | N/A
Spion Kop (1) | A | Arigna | wind | DSO | connected | Pre-Gate | 1.2 | N | wind uncontrolled | N/A
Taurbeg (1) | E | Glenlara | wind | DSO | connected | Pre-Gate | 26 | Y | wind priority | N/A
Tournafulla (1) | E | Trien | wind | DSO | connected | Pre-Gate | 7.5 | Y | wind priority | N/A
Tursillagh (1) | E | Tralee | wind | DSO | connected | Pre-Gate | 15 | N | wind uncontrolled | N/A
Tursillagh (2) | E | Tralee | wind | DSO | connected | Pre-Gate | 6.8 | N | wind uncontrolled | N/A
Aghada BESS 02 | I | Aghada | battery | TSO | connected | Pre-Gate 1 | 159 | N | battery | 318
Aghada BESS 01 | I | Aghada | battery | TSO | connected | Post Gate 1 | 19 | N | battery | 38
Ballinknockane Solar Farm | E | Ballinknockane | solar | TSO | due to connected | Non GPA | 50 | Y | solar not priority | N/A
Ballycrissane Solar Farm | C | Somerset | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Ballycullane Solar Park | H2 | Great Island | solar | DSO | connected | Non GPA | 4.99 | Y | solar not priority | N/A
Ballytobin Solar PV | H2 | Kilkenny | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Banemore Solar Farm | E | Clahane | solar | TSO | due to connected | Non GPA | 34 | Y | solar not priority | N/A
Barnderg Solar Farm | B | Cloon | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Beaulieu PV | G | Drybridge | solar | DSO | connected | Non GPA | 3.99 | Y | solar not priority | N/A
Blundelstown | J | Blundelstown | solar | TSO | connected | Non GPA | 60 | Y | solar not priority | N/A
Blusheens Solar (1) | H2 | Wexford | solar | DSO | connected | Non GPA | 7.98 | Y | solar not priority | N/A
Bodenstown Solar Farm | J | Monread | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Bullstown Solar Farm | J | Finglas | solar | DSO | connected | Non GPA | 8.42 | Y | solar not priority | N/A
Carrick Solar | H1 | Ballydine | solar | DSO | due to connected | Non GPA | 5.8 | Y | solar not priority | N/A
Carrickabane Solar Farm | G | Shankill | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Castlekelly Solar PV Farm | H2 | Kilkenny | solar | DSO | connected | Non GPA | 4 | Y | solar not priority | N/A
Coolyduff | I | Kilbarry | solar | DSO | connected | Non GPA | 4.95 | Y | solar not priority | N/A
Courtown Solar Farm (previously Coolnastudd) | H2 | Banoge | solar | DSO | connected | Non GPA | 4 | Y | solar not priority | N/A
Creevy Solar | C | Lanesboro | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Crossfield | E | Mallow | solar | DSO | connected | Non GPA | 4.95 | Y | solar not priority | N/A
Curraghmartin Solar Park | H2 | Waterford | solar | DSO | connected | Non GPA | 3.99 | Y | solar not priority | N/A
DePuy | I | Barnahely | wind | DSO | connected | Non GPA | 2.5 | N | wind uncontrolled | N/A
DePuy Synthes Turbine2 | I | Barnahely | wind | DSO | connected | Non GPA | 0.99 | N | wind uncontrolled | N/A
Dromalour | E | Glenlara | solar | DSO | connected | Non GPA | 4.95 | Y | solar not priority | N/A
Drombeg Solar Park | E | Drombeg | solar | TSO | connected | Non GPA | 50 | Y | solar not priority | N/A
Drumgarriff South | I | Kilbarry | solar | DSO | connected | Non GPA | 4.95 | Y | solar not priority | N/A
Dunmurry Springs PV | J | Newbridge | solar | DSO | connected | Non GPA | 12 | Y | solar not priority | N/A
Farranlahassery Solar | H1 | Cahir | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Featherbed Lane Solar | J | Glasmore | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Gallanstown Solar | J | Gallanstown | solar | TSO | connected | Non GPA | 119 | Y | solar not priority | N/A
Grady Joinery | B | Tonroe | wind | DSO | connected | Non GPA | 2.5 | N | wind uncontrolled | N/A
Grangegeeth Solar | G | Drybridge | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Harristown Solar PV | J | Harristown | solar | TSO | due to connected | Non GPA | 42.3 | Y | solar not priority | N/A
Hilltown PV | G | Baltrasna | solar | DSO | connected | Non GPA | 9.99 | Y | solar not priority | N/A
Hortland PV (from merge Knockanally and Hortland) | J | Dunfirth | solar | DSO | connected | Non GPA | 14 | Y | solar not priority | N/A
Kelwin Power Plant | E | Kilpaddoge | wind | TSO | connected | Non GPA | 37 | Y | wind priority | N/A
Kelwin Power Plant (battery) | E | Kilpaddoge | battery | TSO | connected | Non GPA | 2.6 | N | battery | 5.2
Kerdiffstown PV | J | Monread | solar | DSO | connected | Non GPA | 4 | Y | solar not priority | N/A
Kilkeelan Solar Farm | G | Navan | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Knockglass Solar Farm | F | Macroom | solar | DSO | connected | Non GPA | 4 | Y | solar not priority | N/A
Laghtane Solar Farm | H1 | Ahane | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Leacht Cross Solar | I | Barnahely | solar | DSO | due to connected | Non GPA | 4.95 | Y | solar not priority | N/A
Lehinch Solar Farm | J | Thornsberry | solar | DSO | connected | Non GPA | 4 | Y | solar not priority | N/A
Liffey Autoproduction Project | G | Shankill | wind | DSO | connected | Non GPA | 1.6 | N | wind uncontrolled | N/A
Liffey Autoproduction Project (extension) | G | Shankill | wind | DSO | connected | Non GPA | 1.417 | N | wind uncontrolled | N/A
Lisbrien Solar Farm | H1 | Nenagh | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Lisduff Solar Park (Claremorris) | B | Dalton | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Lisnageeragh Solar Farm | C | Richmond | solar | DSO | connected | Non GPA | 4 | Y | solar not priority | N/A
Liss Solar Farm (prev Lands at Liss) | C | Mullingar | solar | DSO | connected | Non GPA | 4 | Y | solar not priority | N/A
Loughteague | J | Coolnabacky | solar | TSO | due to connected | Non GPA | 55 | Y | solar not priority | N/A
Maine Solar | E | Oughtragh | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Marlinstown Solar Farm (prev Russellstown) | C | Mullingar | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Millvale PV | H2 | Ballybeg | solar | DSO | connected | Non GPA | 8 | Y | solar not priority | N/A
Monatooreen Solar | I | Knockraha | solar | TSO | due to connected | Non GPA | 25.7 | Y | solar not priority | N/A
Muinagh Solar Farm | J | Thornsberry | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Painestown Hill Solar Farm | G | Baltrasna | solar | DSO | connected | Non GPA | 7.14 | Y | solar not priority | N/A
Rathleg Solar Farm | C | Carrick on Shannon | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Rosspile Solar Farm | H2 | Rosspile | solar | TSO | connected | Non GPA | 95 | Y | solar not priority | N/A
Shanagraigue | I | Trabeg | solar | DSO | connected | Non GPA | 4.95 | Y | solar not priority | N/A
Shanderry Solar Farm | J | Portlaoise | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Shannagh Beg Solar Farm | C | Athlone | solar | DSO | due to connected | Non GPA | 4 | Y | solar not priority | N/A
Shantallow Solar | B | Shantallow | solar | TSO | due to connected | Non GPA | 35 | Y | solar not priority | N/A
Taghadoe Solar Farm | J | Griffinrath | solar | DSO | due to connected | Non GPA | 25 | Y | solar not priority | N/A
Threecastles Solar Farm | J | Kilteel | solar | DSO | due to connected | Non GPA | 15 | Y | solar not priority | N/A
Timahoe North solar | J | Timahoe | solar | TSO | connected | Non GPA | 70 | Y | solar not priority | N/A
Tullabeg Solar Park | H2 | Tullabeg | solar | TSO | connected | Non GPA | 50 | Y | solar not priority | N/A
Wind Energy Project (Janssen) | I | Barnahely | wind | DSO | connected | Non GPA | 2 | N | wind uncontrolled | N/A
Woodstock North Solar Farm | J | Athy | solar | DSO | due to connected | Non GPA | 4.99 | Y | solar not priority | N/A
Inchicore BESS | J | Inchicore | battery | DSO | connected | T-4 2022/23 | 30 | N | battery | 60
Poolbeg BESS | J | Poolbeg | battery | TSO | connected | T-4 2022/23 | 75 | N | battery | 150
South Wall BESS | J | Irishtown | battery | TSO | connected | T-4 2022/23 | 30 | N | battery | 60
Cushaling ESPS | J | Cushaling | battery | TSO | connected | T-3 2024/25 | 20 | N | battery | 40
Shannonbridge B ESS | C | Shannonbridge | battery | TSO | connected | T-3 2024/25 | 63.2 | N | battery | 158
Brianstown BESS | C | Richmond | battery | DSO | due to connected | T-4 2026/27 | 5.45 | N | battery | *
Kish (Crag Wicklow) | H2 | Oaklands | battery | TSO | due to connected | T-4 2026/27 | 114 | N | battery | *
Knockraha BESS | I | Knockraha | Battery | TSO | due to connected | T-4 2028/29 | 100 | N | battery | *
Arklow Bank Phase 2 A | H2 | Arklow 220kV | offshore wind | TSO | due to connected | Offshore wind | 400 | Y | wind not priority | N/A
Arklow Bank Phase 2 B | H2 | Arklow 220kV | offshore wind | TSO | due to connected | Offshore wind | 400 | Y | wind not priority | N/A
Bray Bank (Dublin Array) | J | Carrickmines 220kV | offshore wind | TSO | due to connected | Offshore wind | 412 | Y | wind not priority | N/A
Codling Offshore Wind A | J | Poolbeg north 220kV | offshore wind | TSO | due to connected | Offshore wind | 400 | Y | wind not priority | N/A
Codling Offshore Wind B | J | Poolbeg south 220kV | offshore wind | TSO | due to connected | Offshore wind | 450 | Y | wind not priority | N/A
Codling Offshore Wind C | J | Poolbeg south 220kV | offshore wind | TSO | due to connected | Offshore wind | 450 | Y | wind not priority | N/A
Great Island OWF | H2 | Great Island 220kV | offshore wind | TSO | due to connected | Offshore wind | 450 | Y | wind not priority | N/A
Kish Bank (Dublin Array) | J | Carrickmines 220kV | offshore wind | TSO | due to connected | Offshore wind | 412 | Y | wind not priority | N/A
Knockraha | I | Knockraha 220kV | offshore wind | TSO | due to connected | Offshore wind | 450 | Y | wind not priority | N/A
North Irish Sea Array A | J | Belcamp 220kV | offshore wind | TSO | due to connected | Offshore wind | 250 | Y | wind not priority | N/A
North Irish Sea Array B | J | Belcamp 220kV | offshore wind | TSO | due to connected | Offshore wind | 250 | Y | wind not priority | N/A
Oriel offshore new A | G | Oriel 220kV | offshore wind | TSO | due to connected | Offshore wind | 165 | Y | wind not priority | N/A
Avonbeg ESS | H2 | Crane | battery | DSO | connected | ECP-1 | 16 | N | battery | 8
Ballyedock | H2 | Great Island | solar | DSO | due to connected | ECP-1 | 12 | Y | solar not priority | N/A
Ballymacadam (Monraha) Solar PV Farm | H1 | Cahir | solar | DSO | connected | ECP-1 | 21 | Y | solar not priority | N/A
Ballynacrusha | I | Cow Cross | solar | DSO | due to connected | ECP-1 | 4.95 | Y | solar not priority | N/A
Bilboa (1) | H2 | Carlow | wind | DSO | due to connected | ECP-1 | 15 | Y | wind not priority | N/A
Black Lough (1) | B | Glenree | wind | DSO | connected | ECP-1 | 12.5 | Y | wind not priority | N/A
Blackwater Bog Solar 1 | C | Shannonbridge | solar | TSO | due to connected | ECP-1 | 65 | Y | solar not priority | N/A
Callatrim South Solar Farm (prev. Kilcawha) | F | Bandon | solar | DSO | due to connected | ECP-1 | 5.95 | Y | solar not priority | N/A
Carrigdangan Wind Farm - Phase 2 | F | Dunmanway | wind | TSO | due to connected | ECP-1 | 7.95 | Y | wind not priority | N/A
Carrowbeg Battery Storage (Prev MCB) | B | Dalton | battery | DSO | due to connected | ECP-1 | 12 | N | battery | *
Cleggill Solar Park | C | Richmond | solar | DSO | due to connected | ECP-1 | 8 | Y | solar not priority | N/A
Cloghan Wind Farm | C | Derrycarney | wind | TSO | connected | ECP-1 | 34 | Y | wind not priority | N/A
Cloncreen Wind farm | J | Cushaling | wind | TSO | connected | ECP-1 | 75 | Y | wind not priority | N/A
Cloncreen Wind farm (battery) | J | Cushaling | battery | TSO | connected | ECP-1 | 25 | N | battery | 50
Clonfad Solar | J | Clonfad | solar | TSO | due to connected | ECP-1 | 100 | Y | solar not priority | N/A
Cloonascragh Solar | B | Cloon | solar | DSO | due to connected | ECP-1 | 20 | Y | solar not priority | N/A
Clooncon East Single WTG | C | Athlone | wind | DSO | connected | ECP-1 | 0.9 | N | wind uncontrolled | N/A
Cluide Solar | G | Drybridge | solar | DSO | due to connected | ECP-1 | 4 | Y | solar not priority | N/A
Confey Solar Park | J | Griffinrath | solar | DSO | due to connected | ECP-1 | 15.5 | Y | solar not priority | N/A
Croaghonagh 1 Windfarm (Merged with Carrickalangan) | A | Croaghonagh | wind | TSO | connected | ECP-1 | 138.1 | Y | wind not priority | N/A
Crossmore (1) | D | Booltiagh | wind | DSO | connected | ECP-1 | 15 | Y | wind not priority | N/A
Currabeha | F | Bandon | solar | DSO | due to connected | ECP-1 | 4.95 | Y | solar not priority | N/A
Davidstown Solar | H2 | Wexford | solar | DSO | connected | ECP-1 | 4.95 | Y | solar not priority | N/A
Dooleeg More (1) | B | Bellacorick | wind | DSO | due to connected | ECP-1 | 2.5 | Y | wind not priority | N/A
Dromroe Solar | E | Tralee | solar | DSO | due to connected | ECP-1 | 4 | Y | solar not priority | N/A
Drumroe East Solar Farm | K | Dungarvan | solar | DSO | due to connected | ECP-1 | 15 | Y | solar not priority | N/A
ESK Wind Farm Phase 2 | E | Boggeragh | wind | DSO | connected | ECP-1 | 12 | Y | wind not priority | N/A
Firgrove | D | Drumline | solar | DSO | due to connected | ECP-1 | 4 | Y | solar not priority | N/A
Firlough TG371 was Carrowleagh-Kilbride DG741 | B | Firlough | wind | TSO | due to connected | ECP-1 | 48.3 | Y | wind not priority | N/A
Foxhall PV | K | Dungarvan | solar | DSO | due to connected | ECP-1 | 3.99 | Y | solar not priority | N/A
Friarspark (was Glebe Golf Course) | G | Navan | solar | DSO | connected | ECP-1 | 4 | Y | solar not priority | N/A
Gardnershill FGS | J | Stephenstown | battery | DSO | connected | ECP-1 | 8.5 | N | battery | 9.35
Garryndruig | F | Bandon | solar | DSO | due to connected | ECP-1 | 4.95 | Y | solar not priority | N/A
Gaskinstown Solar Farm | G | Deenes | solar | TSO | connected | ECP-1 | 85 | Y | solar not priority | N/A
Gillinstown Solar | G | Garballagh | solar | TSO | connected | ECP-1 | 95 | Y | solar not priority | N/A
Glen Solar | A | Garvagh | solar | TSO | due to connected | ECP-1 | 40 | Y | solar not priority | N/A
Gorey Battery Energy Storage | H2 | Banoge | battery | DSO | connected | ECP-1 | 9 | N | battery | 4.5
Gorey Solar | H2 | Banoge | solar | DSO | connected | ECP-1 | 4 | Y | solar not priority | N/A
Gorman (Graigs) Energy Storage Station | G | Gorman | battery | TSO | connected | ECP-1 | 30 | N | battery | 15
Gorman Energy Storage Station - Extension | G | Gorman | battery | TSO | connected | ECP-1 | 20 | N | battery | 10
Horsepasture Solar Farm (Grian PV) | H1 | Doon | solar | DSO | due to connected | ECP-1 | 8 | Y | solar not priority | N/A
Keiloge Solar (Prev Coolnagapogue Solar Farm Phase 1) | K | Butlerstown | solar | DSO | due to connected | ECP-1 | 3.95 | Y | solar not priority | N/A
Kilcarrig Solar PV Farm | H2 | Carlow | solar | DSO | due to connected | ECP-1 | 4 | Y | solar not priority | N/A
Kilmannock Battery Storage Facility | H2 | Great Island | battery | DSO | due to connected | ECP-1 | 30 | N | battery | *
Knockeenbui (1) | F | Dunmanway | wind | DSO | due to connected | ECP-1 | 13.8 | Y | wind not priority | N/A
Lenalea Wind Farm | A | Lenalea | wind | TSO | connected | ECP-1 | 30.1 | Y | wind not priority | N/A
Lisdrumdoagh Energy Storage Facility | G | Lisdrum | battery | TSO | connected | ECP-1 | 60 | N | battery | 30
Lisheen 3 | H1 | Lisheen | wind | TSO | connected | ECP-1 | 28.8 | Y | wind not priority | N/A
Lurrig Solar Farm | I | Midleton | solar | DSO | connected | ECP-1 | 3.6 | Y | solar not priority | N/A
Macallian Solar | H2 | Crane | solar | DSO | connected | ECP-1 | 9 | Y | solar not priority | N/A
Monroe East solar from merge Ballyfowloo Lawclon | H1 | Cahir | solar | DSO | connected | ECP-1 | 8 | Y | solar not priority | N/A
Mully Graffy Windfarm (Kilgorman) | A | Tievebrack | wind | TSO | due to connected | ECP-1 | 29.9 | Y | wind not priority | N/A
Porterstown Battery Storage Facility | J | Kilteel | battery | TSO | connected | ECP-1 | 30 | N | battery | 30
Rathnaskilloge | K | Rathnaskilloge | solar | TSO | connected | ECP-1 | 95 | Y | solar not priority | N/A
Rhode 37.5MW ESS | J | Derryiron | battery | DSO | due to connected | ECP-1 | 37.5 | N | battery | *
Rooaun Solar | C | Athlone | solar | DSO | due to connected | ECP-1 | 4 | Y | solar not priority | N/A
Roxborough | C | Lanesboro | wind | DSO | due to connected | ECP-1 | 4.95 | Y | wind not priority | N/A
Sorrell Island (Glenmore) WF Ext | D | Booltiagh | wind | DSO | connected | ECP-1 | 8 | Y | wind not priority | N/A
Stamullen Solar Park | G | Drybridge | solar | DSO | due to connected | ECP-1 | 3.99 | Y | solar not priority | N/A
Taghart (1) | G | Meath Hill | wind | DSO | connected | ECP-1 | 23.06 | Y | wind not priority | N/A
Tead More Solar (Meelshane) | I | Midleton | solar | DSO | due to connected | ECP-1 | 3.95 | Y | solar not priority | N/A
Templerainey East Solar Farm (Ballycooleen) | H2 | Arklow | solar | DSO | due to connected | ECP-1 | 4 | Y | solar not priority | N/A
Tullynally Estate | C | Mullingar | solar | DSO | due to connected | ECP-1 | 4 | Y | solar not priority | N/A
Willville Solar Park | G | Dundalk | solar | DSO | due to connected | ECP-1 | 3.99 | Y | solar not priority | N/A
Ardderoo wind extension | B | Knockranny | wind | TSO | due to connected | ECP-2.1 | 18 | Y | wind not priority | N/A
Ballinalard Solar Farm | H1 | Tipperary | solar | DSO | due to connected | ECP-2.1 | 4 | Y | solar not priority | N/A
Ballinrea Solar Park | I | Raffeen | solar | TSO | due to connected | ECP-2.1 | 55 | Y | solar not priority | N/A
Ballylongford Windfarm | E | Drombeg | wind | DSO | due to connected | ECP-2.1 | 25.2 | Y | wind not priority | N/A
Ballymanus Wind Farm | H2 | Arklow | wind | DSO | due to connected | ECP-2.1 | 39.99 | Y | wind not priority | N/A
Bilboa Wind farm Ext | H2 | Carlow | wind | DSO | due to connected | ECP-2.1 | 6 | Y | wind not priority | N/A
Bradán Wind Farm (Killybegs Community Wind Turbine) | A | Binbane | wind | DSO | due to connected | ECP-2.1 | 4.2 | Y | wind not priority | N/A
Claremorris 2 Solar Farm | B | Dalton | solar | DSO | due to connected | ECP-2.1 | 4 | Y | solar not priority | N/A
Clogheravaddy Wind Farm (Phase 3) | A | Binbane | wind | DSO | connected | ECP-2.1 | 3.6 | Y | wind not priority | N/A
Clondardis Solar | C | Shanonagh | solar | TSO | due to connected | ECP-2.1 | 58.6 | Y | solar not priority | N/A
Clonin North solar | J | Derryiron | solar | TSO | due to connected | ECP-2.1 | 47 | Y | solar not priority | N/A
Clooninagh Wind Farm | B | Cloon | wind | DSO | due to connected | ECP-2.1 | 4.5 | Y | wind not priority | N/A
Coole wind | C | Mullingar | wind | TSO | due to connected | ECP-2.1 | 88 | Y | wind not priority | N/A
Coolnagloose Community Solar Farm | H2 | Arklow | solar | DSO | due to connected | ECP-2.1 | 0.85 | N | solar uncontrolled | N/A
Cooltubbrid West Solar | K | Dungarvan | solar | DSO | connected | ECP-2.1 | 4 | Y | solar not priority | N/A
Coppenagh solar | H2 | Carlow | solar | DSO | due to connected | ECP-2.1 | 4.6 | Y | solar not priority | N/A
Coumaclovane Solar Extension | E | Coomagearlahy | solar | TSO | due to connected | ECP-2.1 | 7 | Y | solar not priority | N/A
Crossmore (2) | D | Booltiagh | wind | DSO | connected | ECP-2.1 | 10.2 | Y | wind not priority | N/A
Cushaling wind (loop into Cushaling - Newbridge) | J | Philipstown | wind | TSO | connected | ECP-2.1 | 50 | Y | wind not priority | N/A
Derryadd battery | C | Lanesboro | battery | TSO | due to connected | ECP-2.1 | 16 | N | battery | *
Derryadd wind | C | Lanesboro | wind | TSO | due to connected | ECP-2.1 | 90 | Y | wind not priority | N/A
Dooleeg More Ext. | B | Bellacorick | wind | DSO | due to connected | ECP-2.1 | 1.3 | Y | wind not priority | N/A
Drehid wind | J | Mulgeeth | wind | TSO | connected | ECP-2.1 | 60 | Y | wind not priority | N/A
Dromsallagh Solar | D | Ardnacrusha | solar | DSO | due to connected | ECP-2.1 | 4 | Y | solar not priority | N/A
Drumlins Park wind | G | Lislea | wind | TSO | connected | ECP-2.1 | 48.8 | Y | wind not priority | N/A
Dysart PV | J | Dunfirth | solar | DSO | due to connected | ECP-2.1 | 17.5 | Y | solar not priority | N/A
Erkina solar | H1 | Timoney | solar | TSO | due to connected | ECP-2.1 | 66.56 | Y | solar not priority | N/A
Farran South | H1 | Barrymore | solar | DSO | due to connected | ECP-2.1 | 15 | Y | solar not priority | N/A
Farrangalway Solar PV Farm | F | Bandon | solar | DSO | due to connected | ECP-2.1 | 4.95 | Y | solar not priority | N/A
Firlough Wind Farm | B | Firlough | wind | TSO | due to connected | ECP-2.1 | 27.3 | Y | wind not priority | N/A
Friarspark Solar 2 | G | Navan | solar | DSO | due to connected | ECP-2.1 | 2.1 | Y | solar not priority | N/A
Gortaheera CM2 Windfarm | D | Booltiagh | wind | DSO | due to connected | ECP-2.1 | 3 | Y | wind not priority | N/A
Harlockstown Solar (Gallanstown Solar Extension) | J | Gallanstown | solar | TSO | connected | ECP-2.1 | 31.6 | Y | solar not priority | N/A
Keatingstown Solar Farm | H2 | Kilkenny | solar | DSO | due to connected | ECP-2.1 | 6 | Y | solar not priority | N/A
Kilcannon | K | Dungarvan | solar | DSO | due to connected | ECP-2.1 | 4.95 | Y | solar not priority | N/A
Kilkeelan Phase 2 Solar Farm | G | Navan | solar | DSO | due to connected | ECP-2.1 | 1.35 | Y | solar not priority | N/A
Knocknamork solar | E | Ballyvouskil 220 | solar | TSO | due to connected | ECP-2.1 | 12.5 | Y | solar not priority | N/A
Knocknamork wind | E | Ballyvouskil 220 | wind | TSO | due to connected | ECP-2.1 | 42 | Y | wind not priority | N/A
Knockranny wind | B | Knockranny | wind | TSO | due to connected | ECP-2.1 | 47.3 | Y | wind not priority | N/A
Loan PV | H2 | Ballyragget | solar | DSO | due to connected | ECP-2.1 | 4.99 | Y | solar not priority | N/A
Lysaghtstown Solar | I | Lysaghtstown | solar | TSO | connected | ECP-2.1 | 87 | Y | solar not priority | N/A
Mainscourt | J | Grange | solar | DSO | due to connected | ECP-2.1 | 39.99 | Y | solar not priority | N/A
Middleton solar (Longford) | C | Lanesboro | solar | TSO | due to connected | ECP-2.1 | 56.6 | Y | solar not priority | N/A
Moanvane wind | J | Mount Lucas | wind | TSO | connected | ECP-2.1 | 56.4 | Y | wind not priority | N/A
Muinagh Solar Farm phase 2 | J | Thornsberry | solar | DSO | due to connected | ECP-2.1 | 1.8 | Y | solar not priority | N/A
North Arklow battery | H2 | Arklow | battery | TSO | due to connected | ECP-2.1 | 30 | N | battery | *
North Arklow Solar | H2 | Arklow | solar | TSO | due to connected | ECP-2.1 | 47 | Y | solar not priority | N/A
Parksgrove solar | H2 | Ballyragget | solar | DSO | due to connected | ECP-2.1 | 35 | Y | solar not priority | N/A
Pinewoods wind | H2 | Garrintaggart | wind | TSO | due to connected | ECP-2.1 | 49.5 | Y | wind not priority | N/A
Porterstown BS Facility Ph.2 | J | Kilteel | battery | TSO | due to connected | ECP-2.1 | 60 | N | battery | *
Rathlockstown Solar | J | Gallanstown | solar | TSO | connected | ECP-2.1 | 18.9 | Y | solar not priority | N/A
Templehouse Community Wind Turbine | B | Sligo | wind | DSO | due to connected | ECP-2.1 | 4.08 | Y | wind not priority | N/A
The Dell Solar | H2 | Crory | solar | DSO | due to connected | ECP-2.1 | 20 | Y | solar not priority | N/A
Tracystown Solar | H2 | Wexford | solar | TSO | due to connected | ECP-2.1 | 101.1 | Y | solar not priority | N/A
Tullyhaw Community Wind Turbine | A | Gortawee | wind | DSO | due to connected | ECP-2.1 | 4.2 | Y | wind not priority | N/A
Tullynamoyle Wind Farm 5 | A | Corderry | wind | DSO | due to connected | ECP-2.1 | 16.35 | Y | wind not priority | N/A
WEP Solar Slanemore Mullingar | C | Mullingar | solar | DSO | due to connected | ECP-2.1 | 16.85 | Y | solar not priority | N/A
Willville Extension Solar Park | G | Dundalk | solar | DSO | due to connected | ECP-2.1 | 1 | Y | solar not priority | N/A
Yellow River Wind Farm | J | Derryiron | wind | TSO | connected | ECP-2.1 | 101 | Y | wind not priority | N/A
Ardagh South Energy Storage Facility | G | Meath Hill | battery | TSO | due to connected | ECP-2.2 | 60 | N | battery | *
Ardnadoman Solar Farm | C | Somerset | solar | DSO | due to connected | ECP-2.2 | 4 | Y | solar not priority | N/A
Ballinaclough Solar Farm | H2 | Ballybeg | solar | DSO | due to connected | ECP-2.2 | 8.5 | Y | solar not priority | N/A
Ballyboughlin Solar Farm | J | Thornsberry | solar | DSO | due to connected | ECP-2.2 | 14 | Y | solar not priority | N/A
Ballyduff PV | I | Midleton | solar | DSO | due to connected | ECP-2.2 | 7 | Y | solar not priority | N/A
Ballyenaghty Solar Park | E | Tralee | solar | DSO | due to connected | ECP-2.2 | 9.9 | Y | solar not priority | N/A
Ballymoneen Solar Park | B | Cashla | solar | TSO | due to connected | ECP-2.2 | 100 | Y | solar not priority | N/A
Ballyroe Solar | E | Charleville | solar | TSO | due to connected | ECP-2.2 | 120 | Y | solar not priority | N/A
Ballyvatta Solar Extension | I | Knockraha | solar | TSO | due to connected | ECP-2.2 | 16.3 | Y | solar not priority | N/A
Barnacurragh Solar Park | B | Cloon | solar | TSO | due to connected | ECP-2.2 | 50 | Y | solar not priority | N/A
Barnesmore Windfarm Repowering | A | Golagh | wind | TSO | due to connected | ECP-2.2 | 48 | Y | wind not priority | N/A
Berrings Solar Farm | F | Macroom | solar | DSO | due to connected | ECP-2.2 | 13.8 | Y | solar not priority | N/A
Carriglong Solar Park | K | Butlerstown | solar | DSO | due to connected | ECP-2.2 | 32.7 | Y | solar not priority | N/A
Clashwilliam Solar | H2 | Kilkenny | solar | DSO | due to connected | ECP-2.2 | 44 | Y | solar not priority | N/A
Coldwinters Energy Hub battery | J | Finglas | battery | DSO | due to connected | ECP-2.2 | 15 | N | battery | *
Coolboy Solar Farm | H2 | Arklow | solar | DSO | due to connected | ECP-2.2 | 5.99 | Y | solar not priority | N/A
Coole Wind Farm - Extension | C | Mullingar | wind | TSO | due to connected | ECP-2.2 | 9.5 | Y | wind not priority | N/A
Coppenagh Solar Park Extension | H2 | Carlow | solar | DSO | due to connected | ECP-2.2 | 4.7 | Y | solar not priority | N/A
Darthogue Solar Farm | J | Crakenstown | solar | TSO | due to connected | ECP-2.2 | 47 | Y | solar not priority | N/A
Derrinlough Wind Farm | C | Stonestown | wind | TSO | connected | ECP-2.2 | 105 | Y | wind not priority | N/A
Derrykillew Wind Farm | A | Cathaleen's Fall | wind | DSO | due to connected | ECP-2.2 | 37.5 | Y | wind not priority | N/A
Drumman Solar Farm | G | Shankill | solar | DSO | due to connected | ECP-2.2 | 7 | Y | solar not priority | N/A
East Laois Solar Farm Extension | J | Coolnabacky | solar | TSO | due to connected | ECP-2.2 | 25 | Y | solar not priority | N/A
Erkina Solar Park Extension | H1 | Timoney | solar | TSO | due to connected | ECP-2.2 | 90 | Y | solar not priority | N/A
Farranmacedmond Solar Farm | H2 | Waterford | solar | DSO | due to connected | ECP-2.2 | 6 | Y | solar not priority | N/A
Farranrory Wind Farm | H2 | Ballyragget | wind | DSO | due to connected | ECP-2.2 | 45 | Y | wind not priority | N/A
Fieldstown Solar | J | Finglas | solar | TSO | due to connected | ECP-2.2 | 75 | Y | solar not priority | N/A
Finnis PV | F | Bandon | solar | DSO | connected | ECP-2.2 | 8.5 | Y | solar not priority | N/A
Garballagh2 Solar Farm | G | Garballagh | solar | TSO | due to connected | ECP-2.2 | 48 | Y | solar not priority | N/A
Garr Solar & Storage | J | Derryiron | solar | TSO | due to connected | ECP-2.2 | 85 | Y | solar not priority | N/A
Garr Solar & Storage | J | Derryiron | battery | TSO | due to connected | ECP-2.2 | 50 | N | battery | *
Garreenleen Solar Farm | H2 | Kellis | solar | TSO | due to connected | ECP-2.2 | 81 | Y | solar not priority | N/A
Islanduane Solar Farm | E | Limerick | solar | DSO | due to connected | ECP-2.2 | 4.95 | Y | solar not priority | N/A
Johnstown North PV | H2 | Arklow | solar | DSO | due to connected | ECP-2.2 | 22 | Y | solar not priority | N/A
Kilmannock Battery Storage Facility Phase 2 | H2 | Great Island | battery | TSO | due to connected | ECP-2.2 | 90 | N | battery | *
Leacht Cross Solar Phase 2 | I | Barnahely | solar | DSO | due to connected | ECP-2.2 | 5 | Y | solar not priority | N/A
Leamór Community Wind Turbine | C | Dallow | wind | DSO | due to connected | ECP-2.2 | 4.99 | Y | wind not priority | N/A
Lissane West Solar Farm | D | Ennis | solar | DSO | due to connected | ECP-2.2 | 18.3 | Y | solar not priority | N/A
Magherareagh Solar PV Farm | H1 | Cahir | solar | DSO | due to connected | ECP-2.2 | 3.3 | Y | solar not priority | N/A
Manusmore Solar Park | D | Ennis | solar | TSO | due to connected | ECP-2.2 | 60 | Y | solar not priority | N/A
Milltown Community Solar Farm | B | Cloon | solar | DSO | due to connected | ECP-2.2 | 4.99 | Y | solar not priority | N/A
Monvallet Hybrid Solar & Battery Farm | G | Louth | solar | TSO | due to connected | ECP-2.2 | 50 | Y | solar not priority | N/A
Monvallet Hybrid Solar & Battery Farm (battery) | G | Louth | battery | TSO | due to connected | ECP-2.2 | 134.4 | N | battery | *
Poulbautia Solar Farm | K | Dungarvan | solar | DSO | due to connected | ECP-2.2 | 19 | Y | solar not priority | N/A
Rosspile2 Solar plus Storage Facility | H2 | Rosspile | battery | TSO | due to connected | ECP-2.2 | 100 | N | battery | *
Smithstown | J | Griffinrath | solar | DSO | due to connected | ECP-2.2 | 25.3 | Y | solar not priority | N/A
Thomastown Road Solar | H2 | Kilkenny | solar | DSO | due to connected | ECP-2.2 | 4 | Y | solar not priority | N/A
Timahoe North ph2 battery | J | Timahoe | battery | TSO | due to connected | ECP-2.2 | 20 | N | battery | *
Timahoe North Phase 2 Solar Farm | J | Timahoe | solar | TSO | due to connected | ECP-2.2 | 60 | Y | solar not priority | N/A
Tomsallagh Solar | H2 | Effernoge | solar | TSO | due to connected | ECP-2.2 | 50 | Y | solar not priority | N/A
Altcor Wind Farm | A | Binbane | wind | DSO | due to connected | ECP-2.3 | 9 | Y | wind not priority | N/A
Ballingaddy Solar | D | Ennis | solar | DSO | due to connected | ECP-2.3 | 4.99 | Y | solar not priority | N/A
Ballykenny Solar | C | Richmond | solar | DSO | due to connected | ECP-2.3 | 9 | Y | solar not priority | N/A
Ballymoney PV | H2 | Arklow | solar | DSO | due to connected | ECP-2.3 | 7.6 | Y | solar not priority | N/A
Ballyteige Solar Park | J | Thornsberry | solar | TSO | due to connected | ECP-2.3 | 90 | Y | solar not priority | N/A
Ballyvouskil Battery Storage | E | Ballyvouskil 220 | battery | TSO | due to connected | ECP-2.3 | 70 | N | battery | *
Barnaleen Solar Farm | H1 | Cauteen | solar | TSO | due to connected | ECP-2.3 | 55 | Y | solar not priority | N/A
Barryscourt Solar Farm (Battery) | I | Cow Cross | battery | DSO | due to connected | ECP-2.3 | 2 | N | battery | *
Barryscourt Solar Farm (Solar) | I | Cow Cross | solar | DSO | due to connected | ECP-2.3 | 8 | Y | solar not priority | N/A
Booltiagh Energy Storage | D | Booltiagh | battery | TSO | due to connected | ECP-2.3 | 30 | N | battery | *
Bracklyn Wind Farm (Battery) | J | Bracklyn | battery | TSO | due to connected | ECP-2.3 | 25 | N | battery | *
Bracklyn Wind Farm (Wind) | J | Bracklyn | wind | TSO | due to connected | ECP-2.3 | 64.8 | Y | wind not priority | N/A
Cahershaughnessy Solar | D | Ennis | solar | DSO | due to connected | ECP-2.3 | 8.8 | Y | solar not priority | N/A
Carrigogna Solar | I | Midleton | solar | DSO | due to connected | ECP-2.3 | 10 | Y | solar not priority | N/A
Carrigraigue Solar Extension | E | Boggeragh | solar | TSO | due to connected | ECP-2.3 | 11.5 | Y | solar not priority | N/A
Carrownagowan Wind Farm | D | Ardnacrusha | wind | TSO | due to connected | ECP-2.3 | 91.2 | Y | wind not priority | N/A
Castlebanny Wind Farm | H2 | Kilvinoge | wind | TSO | due to connected | ECP-2.3 | 138.6 | Y | wind not priority | N/A
Chafhill Wind Farm (prev. Glenree) | B | Glenree | wind | DSO | due to connected | ECP-2.3 | 4.95 | Y | wind not priority | N/A
Clonymeath Solar (Battery) | J | Fosterstown | battery | TSO | due to connected | ECP-2.3 | 10 | N | battery | *
Clonymeath Solar (Solar) | J | Fosterstown | solar | TSO | due to connected | ECP-2.3 | 78.8 | Y | solar not priority | N/A
Cuilmore Solar Park | C | Athlone | solar | DSO | due to connected | ECP-2.3 | 40 | Y | solar not priority | N/A
Darthogue Solar Farm Extension | J | Crakenstown | solar | TSO | due to connected | ECP-2.3 | 70 | Y | solar not priority | N/A
Drombeg Solar Park Phase II (Ballydonohoe) | E | Drombeg | solar | TSO | due to connected | ECP-2.3 | 44 | Y | solar not priority | N/A
Drumnahough Wind Farm | A | Lenalea | wind | TSO | due to connected | ECP-2.3 | 72 | Y | wind not priority | N/A
Farran South Solar Phase 2 | H1 | Barrymore | solar | DSO | due to connected | ECP-2.3 | 5.49 | Y | solar not priority | N/A
Fieldstown Solar Farm Ext | J | Finglas | solar | TSO | due to connected | ECP-2.3 | 18.27 | Y | solar not priority | N/A
Gorman Solar Farm | G | Gorman | solar | TSO | due to connected | ECP-2.3 | 46 | Y | solar not priority | N/A
Gortawee Battery Storage Facility | A | Gortawee | battery | TSO | due to connected | ECP-2.3 | 75 | N | battery | *
Gortdrum Solar PV | H1 | Cauteen | solar | DSO | due to connected | ECP-2.3 | 48 | Y | solar not priority | N/A
Grangeford Solar PV | H2 | Kellis | solar | TSO | due to connected | ECP-2.3 | 48 | Y | solar not priority | N/A
Grian PV Ballyboe | H1 | Ballydine | solar | DSO | due to connected | ECP-2.3 | 12 | Y | solar not priority | N/A
Kilcurly Solar | G | Dundalk | solar | DSO | due to connected | ECP-2.3 | 44.9 | Y | solar not priority | N/A
Kilcush Solar Farm | J | Philipstown | solar | TSO | due to connected | ECP-2.3 | 50 | Y | solar not priority | N/A
Kiloran Solar PV Farm | H1 | Lisheen | solar | TSO | due to connected | ECP-2.3 | 76 | Y | solar not priority | N/A
Loughdenee Solar | K | Butlerstown | solar | DSO | due to connected | ECP-2.3 | 9 | Y | solar not priority | N/A
Lysaghtstown Phase 2 | I | Lysaghtstown | solar | TSO | due to connected | ECP-2.3 | 45 | Y | solar not priority | N/A
Midleton Battery Storage Facility | I | Midleton | battery | TSO | due to connected | ECP-2.3 | 80 | N | battery | *
Milltown Solar | G | Balruntagh | solar | TSO | due to connected | ECP-2.3 | 115 | Y | solar not priority | N/A
Monart Spa Ground Mount 3 | H2 | Crane | solar | DSO | due to connected | ECP-2.3 | 1.3 | Y | solar not priority | N/A
Old Court Solar Farm | J | Timahoe | solar | TSO | due to connected | ECP-2.3 | 90 | Y | solar not priority | N/A
Pickardstown PV | K | Butlerstown | solar | DSO | due to connected | ECP-2.3 | 8.8 | Y | solar not priority | N/A
Reask Solar Farm | J | Crakenstown | solar | TSO | due to connected | ECP-2.3 | 55 | Y | solar not priority | N/A
Shrownowen Windfarm | E | Pollagh | wind | TSO | due to connected | ECP-2.3 | 50 | Y | wind not priority | N/A
Stacks Mountain Wind Farm 2 | E | Reamore | wind | DSO | due to connected | ECP-2.3 | 4.5 | Y | wind not priority | N/A
Taduff Solar Park | C | Athlone | solar | TSO | due to connected | ECP-2.3 | 80 | Y | solar not priority | N/A
Tawnaghmore BESS | B | Tawnaghmore | battery | TSO | due to connected | ECP-2.3 | 80 | N | battery | *
Thornsberry Battery Storage Facility | J | Thornsberry | battery | TSO | due to connected | ECP-2.3 | 150 | N | battery | *
Toolestown Solar | J | Maynooth | solar | TSO | due to connected | ECP-2.3 | 50 | Y | solar not priority | N/A
Treascon Solar Farm | J | Bracklone | solar | TSO | due to connected | ECP-2.3 | 60 | Y | solar not priority | N/A
Tullabeg Phase 2 | H2 | Tullabeg | solar | TSO | due to connected | ECP-2.3 | 105 | Y | solar not priority | N/A
Ballina Beverages Energy Centre (battery) | B | Moy | battery | DSO | due to connected | ECP-2.3 (Cat B) | 2 | N | battery | *
College Export AutoProducer (solar) | G | Meath Hill | solar | DSO | due to connected | ECP-2.3 (Cat B) | 0.4 | Y | solar not priority | N/A
Amberhill Community Solar Farm | K | Butlerstown | solar | DSO | due to connected | ECP-2.3 (Cat C) | 4.99 | Y | solar not priority | N/A
Carrowgarve Solar | B | Moy | solar | DSO | due to connected | ECP-2.3 (Cat C) | 4 | Y | solar not priority | N/A
Clonmel Renewable Energy Community A | H1 | Doon | solar | DSO | due to connected | ECP-2.3 (Cat C) | 4.99 | Y | solar not priority | N/A
Cloonbar WF | B | Cloon | wind | DSO | due to connected | ECP-2.3 (Cat C) | 4.99 | Y | wind not priority | N/A
Knockreagh Community Solar | E | Oughtragh | solar | DSO | due to connected | ECP-2.3 (Cat C) | 4.4 | Y | solar not priority | N/A
Lissavilla Polecat Solar | C | Carrick on Shannon | solar | DSO | due to connected | ECP-2.3 (Cat C) | 0.14 | N | solar uncontrolled | N/A
LT SolarFruit | J | Finglas | solar | DSO | due to connected | ECP-2.3 (Cat C) | 2.8 | Y | solar not priority | N/A
Polecat Community PV | C | Carrick on Shannon | solar | DSO | due to connected | ECP-2.3 (Cat C) | 4.99 | Y | solar not priority | N/A
AMS battery | I | Castleview | Battery | DSO | due to connected | ECP-2.4 | 1 | N | battery | *
AMS solar | I | Castleview | solar | DSO | due to connected | ECP-2.4 | 3.49 | Y | solar not priority | N/A
Ardass Solar | C | Carrick on Shannon | solar | DSO | due to connected | ECP-2.4 | 4.99 | Y | solar not priority | N/A
Aught Wind Farm | A | Letterkenny | wind | TSO | due to connected | ECP-2.4 | 57.4 | Y | wind not priority | N/A
Ballycunneen PV | D | Drumline | solar | DSO | due to connected | ECP-2.4 | 12 | Y | solar not priority | N/A
Ballyglasheen West BESS Facility | H1 | Tipperary | Battery | TSO | due to connected | ECP-2.4 | 60 | N | battery | *
Ballyglass Solar Farm | D | Ardnacrusha | solar | TSO | due to connected | ECP-2.4 | 80.019 | Y | solar not priority | N/A
Ballykenny Solar Extension | C | Richmond | solar | DSO | due to connected | ECP-2.4 | 6 | Y | solar not priority | N/A
Ballylongford Solar | E | Pollagh | solar | TSO | due to connected | ECP-2.4 | 128 | Y | solar not priority | N/A
Ballymac Phase 1 and 2 | K | Dungarvan | Battery | TSO | due to connected | ECP-2.4 | 55 | N | battery | *
Ballymac Solar | K | Dungarvan | solar | TSO | due to connected | ECP-2.4 | 5 | Y | solar not priority | N/A
Ballymoneen Phase 2 | B | Cashla | solar | TSO | due to connected | ECP-2.4 | 5 | Y | solar not priority | N/A
Ballymoneen Phase 2 Battery | B | Cashla | Battery | TSO | due to connected | ECP-2.4 | 75 | N | battery | *
Ballyroe Solar Extension | E | Charleville | solar | TSO | due to connected | ECP-2.4 | 45 | Y | solar not priority | N/A
Ballysumaghan BESS & SC | B | Srananagh | Battery | TSO | due to connected | ECP-2.4 | 200 | N | battery | *
Ballyvalode Solar | H1 | Cauteen | solar | TSO | due to connected | ECP-2.4 | 113 | Y | solar not priority | N/A
Barnaleen Solar Phase 2 | H1 | Cauteen | solar | TSO | due to connected | ECP-2.4 | 35 | Y | solar not priority | N/A
Clondardis Solar Extension | C | Shanonagh | solar | TSO | due to connected | ECP-2.4 | 11.4 | Y | solar not priority | N/A
Cloondara Solar Park | C | Richmond | solar | DSO | due to connected | ECP-2.4 | 4 | Y | solar not priority | N/A
Coolcarrigan Solar P2 | J | Timahoe | solar | TSO | due to connected | ECP-2.4 | 120 | Y | solar not priority | N/A
Coolcarrigan Solar P2 Battery | J | Timahoe | Battery | TSO | due to connected | ECP-2.4 | 80 | N | battery | *
Coom Green Energy Park | H1 | Barrymore | wind | TSO | due to connected | ECP-2.4 | 105.6 | Y | wind not priority | N/A
Coom Green Energy Park Battery | H1 | Barrymore | Battery | TSO | due to connected | ECP-2.4 | 50 | N | battery | *
Cronalaght 3 Wind Farm | A | Ardnagappary | wind | DSO | due to connected | ECP-2.4 | 9 | Y | wind not priority | N/A
Culmullin Solar Farm | J | Arodstown | solar | TSO | due to connected | ECP-2.4 | 70 | Y | solar not priority | N/A
Darthogue Solar Farm Ext 2 | J | Gallanstown | solar | TSO | due to connected | ECP-2.4 | 13.5 | Y | solar not priority | N/A
Dernacart Windfarm | J | Bracklone | wind | TSO | due to connected | ECP-2.4 | 57.6 | Y | wind not priority | N/A
Drumgoolan Solar and Battery Farm | G | Louth | solar | TSO | due to connected | ECP-2.4 | 75 | Y | solar not priority | N/A
Drumgoolan Solar and Battery Farm Battery | G | Louth | Battery | TSO | due to connected | ECP-2.4 | 40.5 | N | battery | *
Drummin Solar | D | Ardnacrusha | solar | DSO | due to connected | ECP-2.4 | 35 | Y | solar not priority | N/A
Fieldstown Extension No.2 | J | Finglas | solar | TSO | due to connected | ECP-2.4 | 60 | Y | solar not priority | N/A
Flagford Battery Storage | C | Flagford | Battery | TSO | due to connected | ECP-2.4 | 100 | N | battery | *
Friarstown Solar Farm | H2 | Carlow | solar | TSO | due to connected | ECP-2.4 | 50 | Y | solar not priority | N/A
Friarstown Solar Farm Battery | H2 | Carlow | Battery | TSO | due to connected | ECP-2.4 | 30 | N | battery | *
Garreenleen Solar Farm Phase 2 | H2 | Kellis | solar | TSO | due to connected | ECP-2.4 | 82 | Y | solar not priority | N/A
Golden Forth Solar Park | H2 | Stratford | solar | DSO | due to connected | ECP-2.4 | 0.999 | Y | solar not priority | N/A
JOHNSTOWN SOLAR PARK | H2 | Carlow | solar | DSO | due to connected | ECP-2.4 | 9.99 | Y | solar not priority | N/A
Kilcormac Solar | C | Derrycarney | solar | TSO | due to connected | ECP-2.4 | 125 | Y | solar not priority | N/A
Kilmorna Energy Storage Facility | E | Knockanure | Battery | TSO | due to connected | ECP-2.4 | 170 | N | battery | *
Kilrue Solar | J | Crakenstown | solar | TSO | due to connected | ECP-2.4 | 195 | Y | solar not priority | N/A
Knockroe Wind Farm | H1 | Doon | wind | DSO | due to connected | ECP-2.4 | 33.6 | Y | wind not priority | N/A
Leam Windfarm | C | Carrick on Shannon | wind | DSO | due to connected | ECP-2.4 | 6.9 | Y | wind not priority | N/A
Lyrenacarriga Windfarm and BESS | K | Woodhouse | wind | TSO | due to connected | ECP-2.4 | 85 | Y | wind not priority | N/A
Lyrenacarriga Windfarm and BESS Battery | K | Woodhouse | Battery | TSO | due to connected | ECP-2.4 | 60 | N | battery | *
Maine Solar Extension | E | Oughtragh | solar | DSO | due to connected | ECP-2.4 | 1 | Y | solar not priority | N/A
Mill Farm Solar | G | Ricetown | solar | TSO | due to connected | ECP-2.4 | 63 | Y | solar not priority | N/A
Modelligo Solar Farm | K | Dungarvan | solar | TSO | due to connected | ECP-2.4 | 80 | Y | solar not priority | N/A
Mullagharoy Solar Farm | G | Drybridge | solar | DSO | due to connected | ECP-2.4 | 0.99 | Y | solar not priority | N/A
Reask Phase 2 | J | Crakenstown | solar | TSO | due to connected | ECP-2.4 | 30 | Y | solar not priority | N/A
Sandford Energy Solar Farm Ext. | E | Tralee | solar | DSO | due to connected | ECP-2.4 | 1.5 | Y | solar not priority | N/A
Seven Hills Wind Farm | C | Athlone | wind | TSO | due to connected | ECP-2.4 | 122.4 | Y | wind not priority | N/A
Spion Kop Windfarm Ext. (Ext to DG978) | A | Arigna | wind | DSO | due to connected | ECP-2.4 | 1.5 | Y | wind not priority | N/A
Tarbert BESS | E | Tarbert | Battery | TSO | due to connected | ECP-2.4 | 100 | N | battery | *
Templemichael Solar Plus Storage Facility | H2 | Arklow | solar | TSO | due to connected | ECP-2.4 | 30 | Y | solar not priority | N/A
Templemichael Solar Plus Storage Facility Battery | H2 | Arklow | Battery | TSO | due to connected | ECP-2.4 | 20 | N | battery | *
Tincurry Solar Farm | H2 | Lodgewood | solar | TSO | due to connected | ECP-2.4 | 109 | Y | solar not priority | N/A
Tincurry Solar Farm Battery | H2 | Lodgewood | Battery | TSO | due to connected | ECP-2.4 | 60 | N | battery | *
Tullabeg Phase 3 | H2 | Tullabeg | solar | TSO | due to connected | ECP-2.4 | 30 | Y | solar not priority | N/A
TULLYNAMOYLE WIND FARM 6 | A | Corderry | wind | DSO | due to connected | ECP-2.4 | 20.2 | Y | wind not priority | N/A
White Hill Wind Farm | H2 | Kellymount | wind | TSO | due to connected | ECP-2.4 | 50.4 | Y | wind not priority | N/A
Ardass Solar Ext. | C | Carrick on Shannon | solar | DSO | due to connected | ECP-2.4 (Cat C) | 4.99 | Y | solar not priority | N/A
Brighter Community Solar Farm Kilcummin | E | Knockearagh | solar | DSO | due to connected | ECP-2.4 (Cat C) | 4.99 | Y | solar not priority | N/A
Moy Valley Decarbonising Community CLG | B | Castlebar | solar | DSO | due to connected | ECP-2.4 (Cat C) | 4.99 | Y | solar not priority | N/A
Project GiMAT | J | Fosterstown | solar | DSO | due to connected | ECP-2.4 (Cat C) | 4.99 | Y | solar not priority | N/A
Ballinagree | E | Clashavoon | wind | TSO | due to connected | ECP-2.5 | 112 | Y | wind not priority | N/A
Ballivor | J | Craddanstown | wind | TSO | due to connected | ECP-2.5 | 182 | Y | wind not priority | N/A
Ballyboe ph2 | H1 | Doon | solar | DSO | due to connected | ECP-2.5 | 4 | Y | solar not priority | N/A
Ballydonagh | C | Somerset | solar | TSO | due to connected | ECP-2.5 | 90 | Y | solar not priority | N/A
Ballyduff solar ph2 | I | Midleton | solar | DSO | due to connected | ECP-2.5 | 8 | Y | solar not priority | N/A
Ballymoneen ph3 solar | B | Cashla | solar | TSO | due to connected | ECP-2.5 | 20 | Y | solar not priority | N/A
Ballymoney Solar ph2 | H2 | Arklow | solar | DSO | due to connected | ECP-2.5 | 6.3 | Y | solar not priority | N/A
Ballynahina Solar | I | Kilbarry | solar | DSO | due to connected | ECP-2.5 | 30 | Y | solar not priority | N/A
Ballyteigue Solar ph2 | J | Thornsberry | solar | TSO | due to connected | ECP-2.5 | 90 | Y | solar not priority | N/A
Barretspark Battery | B | Cashla | Battery | TSO | due to connected | ECP-2.5 | 100 | N | Battery | *
Baunogephlure Battery | H2 | Kellis | Battery | TSO | due to connected | ECP-2.5 | 50 | N | battery | *
Baunogephlure Solar | H2 | Kellis | solar | TSO | due to connected | ECP-2.5 | 55 | Y | solar not priority | N/A
Bishopswood Solar | J | Bracklone | solar | TSO | due to connected | ECP-2.5 | 25 | Y | solar not priority | N/A
Borrisbeg | H1 | Borrisbeg | wind | TSO | due to connected | ECP-2.5 | 54 | Y | wind not priority | N/A
Brianstown Bess Phase 2 | C | Richmond | Battery | DSO | due to connected | ECP-2.5 | 9.55 | N | battery | *
Brinny solar non export | F | Bandon | solar | TSO | due to connected | ECP-2.5 | 8.2 | N | solar uncontrolled | N/A
Brownstown Battery | H2 | Kilkenny | Battery | TSO | due to connected | ECP-2.5 | 50 | N | battery | *
Brownstown Solar | H2 | Kilkenny | solar | TSO | due to connected | ECP-2.5 | 50 | Y | solar not priority | N/A
Clonloghan Solar Farm | D | Drumline | solar | DSO | due to connected | ECP-2.5 | 9.99 | Y | solar not priority | N/A
Clonymeath Solar ph2 | J | Curraghdoo | solar | TSO | due to connected | ECP-2.5 | 4 | Y | solar not priority | N/A
Coppenagh Solar ph3 | H2 | Carlow | solar | DSO | due to connected | ECP-2.5 | 20 | Y | solar not priority | N/A
Cregg Solar | C | Cregg | solar | TSO | due to connected | ECP-2.5 | 75 | Y | solar not priority | N/A
Culmullin Solar Farm Ext | J | Arodstown | solar | TSO | due to connected | ECP-2.5 | 120 | Y | solar not priority | N/A
Cush | C | Dallow | wind | TSO | due to connected | ECP-2.5 | 57.6 | Y | wind not priority | N/A
Debsborough Solar Farm | H1 | Nenagh | solar | DSO | due to connected | ECP-2.5 | 42 | Y | solar not priority | N/A
Delamain Solar | J | Dunstown | solar | TSO | due to connected | ECP-2.5 | 210 | Y | solar not priority | N/A
Derrycarney solar | C | Derrycarney | solar | TSO | due to connected | ECP-2.5 | 105 | Y | solar not priority | N/A
Dexcom Roadrunner - Battery CHP Solar | B | Galway | Battery | DSO | due to connected | ECP-2.5 | 6 | N | battery | *
Dexcom Roadrunner - Battery CHP Solar | B | Galway | solar | DSO | due to connected | ECP-2.5 | 1.2 | Y | solar not priority | N/A
Drumlins BESS | G | Lislea | battery | TSO | due to connected | ECP-2.5 | 20 | N | battery | *
Erkina Solar ph2 | H1 | Timoney | solar | TSO | due to connected | ECP-2.5 | 15 | Y | solar not priority | N/A
Esk (3) | E | Boggeragh | solar | DSO | due to connected | ECP-2.5 | 12.7 | Y | solar not priority | N/A
Extension Maothail Solar | C | Carrick on Shannon | solar | DSO | due to connected | ECP-2.5 | 1 | Y | solar not priority | N/A
Fahybeg | D | Ardnacrusha | wind | DSO | due to connected | ECP-2.5 | 40 | Y | wind not priority | N/A
Garravagh Solar ph2 | I | Coolroe | solar | DSO | due to connected | ECP-2.5 | 14 | Y | solar not priority | N/A
Gormagh Battery | J | Thornsberry | Battery | TSO | due to connected | ECP-2.5 | 40 | N | battery | *
Gormagh Solar Farm | J | Thornsberry | solar | TSO | due to connected | ECP-2.5 | 40 | Y | solar not priority | N/A
Grangeford Solar ph2 | H2 | Kellis | solar | TSO | due to connected | ECP-2.5 | 22 | Y | solar not priority | N/A
Hawkinstown Solar | G | Deenes | solar | TSO | due to connected | ECP-2.5 | 85 | Y | solar not priority | N/A
Kellistown Battery | H2 | Kellis | battery | TSO | due to connected | ECP-2.5 | 100 | N | battery | *
Kilbeg Solar | B | Dalton | solar | DSO | due to connected | ECP-2.5 | 12 | Y | solar not priority | N/A
Kilcash Wind Farm | C | Lanesboro | wind | DSO | due to connected | ECP-2.5 | 4.5 | Y | wind not priority | N/A
Kilderry Solar | H2 | Kilkenny | solar | DSO | due to connected | ECP-2.5 | 35 | Y | solar not priority | N/A
Kinnegad solar non export | J | Kinnegad | solar | TSO | due to connected | ECP-2.5 | 12 | N | solar uncontrolled | N/A
Liss Wind Farm | H1 | Thurles | wind | DSO | due to connected | ECP-2.5 | 2.35 | Y | wind not priority | N/A
Lissanore Wind Turbine | C | Richmond | wind | DSO | due to connected | ECP-2.5 | 4.5 | Y | wind not priority | N/A
Lumcloon | C | Derrycarney | solar | TSO | due to connected | ECP-2.5 | 95 | Y | solar not priority | N/A
Manusmore Solar 2 | D | Coolshamroge | solar | TSO | due to connected | ECP-2.5 | 60 | Y | solar not priority | N/A
Meenadreen BESS ECP-2.5 | A | Clogher | Battery | TSO | due to connected | ECP-2.5 | 75 | N | battery | *
Meenawley | A | Binbane | wind | DSO | due to connected | ECP-2.5 | 4.5 | Y | wind not priority | N/A
Milltown ph2 solar | G | Balruntagh | solar | TSO | due to connected | ECP-2.5 | 19 | Y | solar not priority | N/A
Mothel Battery | H1 | Curraghduff | battery | TSO | due to connected | ECP-2.5 | 55 | N | battery | *
Mothel solar | H1 | Curraghduff | solar | TSO | due to connected | ECP-2.5 | 125 | Y | solar not priority | N/A
Moyvilla Solar | B | Cashla | solar | TSO | due to connected | ECP-2.5 | 85 | Y | solar not priority | N/A
Powerscourt BESS | H1 | Doon | battery | TSO | due to connected | ECP-2.5 | 100 | N | battery | *
Rahanisky | I | Kilbarry | solar | DSO | due to connected | ECP-2.5 | 39.9 | Y | solar not priority | N/A
Rath Solar PV (ECP2.4+2.5) | C | Derrycarney | solar | TSO | due to connected | ECP-2.5 | 119.25 | Y | solar not priority | N/A
Rathcoursey Battery | I | Rathcoursey | Battery | TSO | due to connected | ECP-2.5 | 30 | N | battery | *
Rathcoursey Solar | I | Rathcoursey | solar | TSO | due to connected | ECP-2.5 | 110 | Y | solar not priority | N/A
Rathdrinagh Solar | G | Garballagh | solar | TSO | due to connected | ECP-2.5 | 72 | Y | solar not priority | N/A
Rathduff Solar | H1 | Tipperary | solar | DSO | due to connected | ECP-2.5 | 25 | Y | solar not priority | N/A
Sheskin South | B | Bellacorick | wind | TSO | due to connected | ECP-2.5 | 129.6 | Y | wind not priority | N/A
Springmount PV | H1 | Springmount | solar | TSO | due to connected | ECP-2.5 | 65 | Y | solar not priority | N/A
Tomsallagh ph2 | H2 | Effernoge | solar | DSO | due to connected | ECP-2.5 | 1 | Y | solar not priority | N/A
Boliden Tara Mines Solar Farm (non export) | G | Navan | solar | DSO | due to connected | ECP-2.5 (Cat B) | 17 | N | solar uncontrolled | N/A
Carrigaline PV | I | Barnahely | solar | DSO | due to connected | ECP-2.5 (Cat B) | 4 | N | solar uncontrolled | N/A
Ballinakilla Wind Farm | B | Cloon | wind | DSO | due to connected | ECP-2.5 (Cat C) | 4.5 | Y | wind not priority | N/A
Ballinderry Solar | B | Cloon | solar | DSO | due to connected | ECP-2.5 (Cat C) | 4.99 | Y | solar not priority | N/A
Cloonaraher Wind Farm | B | Tonroe | wind | DSO | due to connected | ECP-2.5 (Cat C) | 4.99 | Y | wind not priority | N/A
Derrylough WF | C | Athlone | wind | DSO | due to connected | ECP-2.5 (Cat C) | 4.99 | Y | wind not priority | N/A
Derryveagh solar | C | Athlone | solar | DSO | due to connected | ECP-2.5 (Cat C) | 4.99 | Y | solar not priority | N/A
Dolanstown Solar Farm | J | Griffinrath | solar | DSO | due to connected | ECP-2.5 (Cat C) | 4.9 | Y | solar not priority | N/A
Dundalk Golf club | G | Dundalk | solar | DSO | due to connected | ECP-2.5 (Cat C) | 4.99 | Y | solar not priority | N/A
Blackhall Solar | J | Arodstown | solar | TSO | due to connected | ECP-2.5.1 | 165.6 | Y | solar not priority | N/A
Creemore Battery | J | Woodland | battery | TSO | due to connected | ECP-2.5.1 | 290 | N | battery | *
Glenard (1) | A | Letterkenny | wind | TSO | due to connected | ECP-2.5.1 | 93 | Y | wind not priority | N/A
Gortyrahilly | E | Coomataggart | wind | TSO | due to connected | ECP-2.5.1 | 85.8 | Y | wind not priority | N/A
Inchamore | E | Glanlee | wind | TSO | due to connected | ECP-2.5.1 | 26 | Y | wind not priority | N/A
Kildallan Solar | C | Shanonagh | solar | TSO | due to connected | ECP-2.5.1 | 130 | Y | solar not priority | N/A
Kilrue Solar extension | J | Crakenstown | solar | TSO | due to connected | ECP-2.5.1 | 175 | Y | solar not priority | N/A
Knockanarragh | G | Balruntagh | wind | TSO | due to connected | ECP-2.5.1 | 50.4 | Y | wind not priority | N/A
Oweninney (3) extension | B | Bellacorick | wind | TSO | due to connected | ECP-2.5.1 | 40 | Y | wind not priority | N/A
ShannonB BESS new | C | Shannonbridge | Battery | TSO | due to connected | ECP-2.5.1 | 75 | N | battery | *
Taduff Battery | C | Athlone | Battery | TSO | due to connected | ECP-2.5.1 | 80 | N | battery | *
Agharue wind Farm | H2 | Kilkenny | wind | TSO | due to connected | ECP-GSS1 | 46.2 | Y | wind not priority | N/A
Annagh Wind Farm | E | Charleville | wind | DSO | due to connected | ECP-GSS1 | 37.2 | Y | wind not priority | N/A
Ardgoulbeg Solar | E | Rathkeale | solar | TSO | due to connected | ECP-GSS1 | 54 | Y | solar not priority | N/A
Athclare (prev Croaghaun) Wind Farm | H2 | Castledockrell | wind | DSO | due to connected | ECP-GSS1 | 38.5 | Y | wind not priority | N/A
Ballinla Wind Farm | J2 | Derryiron | wind | TSO | due to connected | ECP-GSS1 | 55 | Y | wind not priority | N/A
Ballinlee Windfarm | E | Charleville | wind | TSO | due to connected | ECP-GSS1 | 76.5 | Y | wind not priority | N/A
Ballinrobe Solar Farm | B | Dalton | solar | DSO | due to connected | ECP-GSS1 | 1 | Y | solar not priority | N/A
Ballybeg Solar Farm | H1 | Barrymore | solar | DSO | due to connected | ECP-GSS1 | 1.96 | Y | Solar not priority | N/A
Ballycar Windfarm | D | Ardnacrusha | wind | TSO | due to connected | ECP-GSS1 | 54 | Y | wind not priority | N/A
Ballycunneen PV and BESS P2 | D | Drumline | solar | DSO | due to connected | ECP-GSS1 | 14 | Y | solar not priority | N/A
Ballykett Windfarm | D | Tullabrack | wind | DSO | due to connected | ECP-GSS1 | 18 | Y | wind not priority | N/A
Ballyloo Solar | H2 | Kellis | solar | TSO | due to connected | ECP-GSS1 | 241 | Y | solar not priority | N/A
Ballymahon PV and BESS | C | Foigha | battery | TSO | due to connected | ECP-GSS1 | 70 | N | battery | *
Ballymahon PV and BESS | C | Foigha | solar | TSO | due to connected | ECP-GSS1 | 70 | Y | solar not priority | N/A
Ballynalacken Wind Farm | H2 | Ballyragget | wind | TSO | due to connected | ECP-GSS1 | 50.4 | Y | wind not priority | N/A
Ballyragget BESS | H2 | Ballyragget | Battery | TSO | due to connected | ECP-GSS1 | 79 | N | battery | *
Ballyroe Solar | E | Charleville | solar | TSO | due to connected | ECP-GSS1 | 7 | Y | solar not priority | N/A
Ballysallagh Solar | I | Knockraha | solar | TSO | due to connected | ECP-GSS1 | 159 | Y | solar not priority | N/A
Barnacurragh Solar 2 | B | Cloon | solar | TSO | due to connected | ECP-GSS1 | 20 | Y | solar not priority | N/A
Bocade Glebe (prev Killeshandra) Solar | A | Gortawee | solar | DSO | due to connected | ECP-GSS1 | 5 | Y | solar not priority | N/A
Boscabell Solar Farm | H1 | Meldrum | solar | TSO | due to connected | ECP-GSS1 | 80 | Y | solar not priority | N/A
Bracklone BESS | J2 | Bracklone | Battery | TSO | due to connected | ECP-GSS1 | 115 | N | battery | *
Cadamstown Solar | J2 | Timahoe | battery | TSO | due to connected | ECP-GSS1 | 211 | N | battery | *
Cadamstown Solar | J2 | Timahoe | solar | TSO | due to connected | ECP-GSS1 | 343 | Y | solar not priority | N/A
Cappakeel Solar Farm | J2 | Bracklone | solar | TSO | due to connected | ECP-GSS1 | 226 | Y | solar not priority | N/A
Castlegarden Solar Farm and Battery | H2 | Kilkenny | battery | TSO | due to connected | ECP-GSS1 | 80 | N | battery | *
Castlegarden Solar Farm and Battery | H2 | Kilkenny | solar | TSO | due to connected | ECP-GSS1 | 56 | Y | solar not priority | N/A
Cloonanny Wind Farm | C | Richmond | wind | DSO | due to connected | ECP-GSS1 | 14 | Y | wind not priority | N/A
Cloonkett Windfarm | E | Prospect | wind | TSO | due to connected | ECP-GSS1 | 63 | Y | wind not priority | N/A
Cooloo Wind Farm | B | Cloon | wind | TSO | due to connected | ECP-GSS1 | 64.8 | Y | wind not priority | N/A
Coolvallanane Beg Solar Farm | F | Brinny | solar | DSO | due to connected | ECP-GSS1 | 11.95 | Y | solar not priority | N/A
Croagh Wind Farm | A | Garvagh | wind | DSO | due to connected | ECP-GSS1 | 48 | Y | wind not priority | N/A
Culmullin Solar Farm Extension | J | Arodstown | solar | TSO | due to connected | ECP-GSS1 | 110 | Y | solar not priority | N/A
Cummeennabuddoge Wind Farm | E | Ballyvouskil 220 | wind | TSO | due to connected | ECP-GSS1 | 122.4 | Y | wind not priority | N/A
Derrynadarragh Windfarm | J2 | Bracklone | wind | TSO | due to connected | ECP-GSS1 | 64.8 | Y | wind not priority | N/A
Drumdowney Solar Farm | H2 | Great Island | solar | TSO | due to connected | ECP-GSS1 | 125 | Y | solar not priority | N/A
Foigha Solar | C | Foigha | solar | TSO | due to connected | ECP-GSS1 | 85 | Y | solar not priority | N/A
Fyanstown Solar | G | Navan | solar | TSO | due to connected | ECP-GSS1 | 100 | Y | solar not priority | N/A
Garrane Windfarm | E | Charleville | wind | TSO | due to connected | ECP-GSS1 | 54 | Y | wind not priority | N/A
Garreenleen Phase 3 Solar Farm & Garreenleen BESS | H2 | Kellis | solar | TSO | due to connected | ECP-GSS1 | 63 | Y | solar not priority | N/A
Glenpatrick Solar Farm | H1 | Doon | solar | DSO | due to connected | ECP-GSS1 | 8 | Y | solar not priority | N/A
Hiskinstown Solar and Battery | J2 | Kinnegad | battery | TSO | due to connected | ECP-GSS1 | 50 | N | battery | *
Hiskinstown Solar and Battery | J2 | Kinnegad | solar | TSO | due to connected | ECP-GSS1 | 75 | Y | solar not priority | N/A
Kilcandra Solar Farm | H2 | Ballybeg | solar | TSO | due to connected | ECP-GSS1 | 134 | Y | solar not priority | N/A
Kilgarvan Wind Farm Repower | E | Glanlee | wind | TSO | due to connected | ECP-GSS1 | 10 | Y | wind not priority | N/A
Killary Solar Farm | G | Gorman | solar | TSO | due to connected | ECP-GSS1 | 70 | Y | solar not priority | N/A
Killough Solar | H1 | Thurles | solar | TSO | due to connected | ECP-GSS1 | 140 | Y | solar not priority | N/A
Kilmorna Solar | E | Knockanure | solar | TSO | due to connected | ECP-GSS1 | 116 | Y | solar not priority | N/A
Kilmullen (prev Bracklone) PV and BESS | J2 | Bracklone | solar | DSO | due to connected | ECP-GSS1 | 10 | Y | solar not priority | N/A
Knockanedan wind Farm | D | Booltiagh | wind | TSO | due to connected | ECP-GSS1 | 48 | Y | wind not priority | N/A
Knockdinnin Solar | J | Richardstown | solar | TSO | due to connected | ECP-GSS1 | 110 | Y | solar not priority | N/A
Knockshanvo Wind Farm | D | Ardnacrusha | wind | TSO | due to connected | ECP-GSS1 | 64.8 | Y | wind not priority | N/A
Laccamore PV and BESS | E | Tralee | battery | TSO | due to connected | ECP-GSS1 | 60 | N | battery | *
Laccamore PV and BESS | E | Tralee | solar | TSO | due to connected | ECP-GSS1 | 100 | Y | solar not priority | N/A
Lackareagh Wind farm | D | Ardnacrusha | wind | TSO | due to connected | ECP-GSS1 | 46.2 | Y | wind not priority | N/A
Lahardan BESS Solar | K | Cullenagh | battery | TSO | due to connected | ECP-GSS1 | 133 | N | battery | *
Lahardan BESS Solar | K | Cullenagh | solar | TSO | due to connected | ECP-GSS1 | 50 | Y | solar not priority | N/A
Lanesboro BESS 2 | C | Lanesboro | Battery | TSO | due to connected | ECP-GSS1 | 100 | N | battery | *
Leamore single turbine | J2 | Dallow | wind | DSO | due to connected | ECP-GSS1 | 4.5 | Y | wind not priority | N/A
Meath Hill BESS | G | Meath Hill | Battery | TSO | due to connected | ECP-GSS1 | 100 | N | battery | *
Moanmore Lower Wind Farm | D | Tullabrack | wind | DSO | due to connected | ECP-GSS1 | 13.5 | Y | wind not priority | N/A
Mogullaun Solar Farm | D | Drumline | solar | TSO | due to connected | ECP-GSS1 | 70.2 | Y | solar not priority | N/A
Mullacash Solar and Battery | J | Dunstown | battery | TSO | due to connected | ECP-GSS1 | 138.4 | N | battery | *
Mullacash Solar and Battery | J | Dunstown | solar | TSO | due to connected | ECP-GSS1 | 231.8 | Y | solar not priority | N/A
Prospect BESS | E | Prospect | Battery | TSO | due to connected | ECP-GSS1 | 200 | N | battery | *
Rathcoon Solar Farm | G | Gorman | solar | TSO | due to connected | ECP-GSS1 | 80 | Y | solar not priority | N/A
Rosehill PV and BESS | H2 | Kilkenny | solar | DSO | due to connected | ECP-GSS1 | 5 | Y | solar not priority | N/A
Rosehill PV and BESS | H2 | Kilkenny | battery | DSO | due to connected | ECP-GSS1 | 5 | N | battery | *
Scart Mountain Wind Farm | K | Woodhouse | wind | TSO | due to connected | ECP-GSS1 | 108 | Y | wind not priority | N/A
Screeb Battery storage | B | Screebe | Battery | TSO | due to connected | ECP-GSS1 | 120 | N | battery | *
Seskin Renewables Wind Farm | H2 | Ballyragget | wind | TSO | due to connected | ECP-GSS1 | 48 | Y | wind not priority | N/A
Seskin Storage | H1 | Cauteen | Battery | TSO | due to connected | ECP-GSS1 | 50 | N | battery | *
Shannonbridge BESS 2 | C | Shannonbridge | Battery | TSO | due to connected | ECP-GSS1 | 100 | N | battery | *
Shelbourne Solar Farm | H2 | Loughtown | battery | TSO | due to connected | ECP-GSS1 | 50 | N | battery | *
Shelbourne Solar Farm | H2 | Loughtown | solar | TSO | due to connected | ECP-GSS1 | 200 | Y | solar not priority | N/A
Shessy PV and BESS | D | Derrybrien | battery | TSO | due to connected | ECP-GSS1 | 40 | N | battery | *
Shessy PV and BESS | D | Derrybrien | solar | TSO | due to connected | ECP-GSS1 | 70 | Y | solar not priority | N/A
Sillouge BESS | G | Navan | Battery | TSO | due to connected | ECP-GSS1 | 150 | N | battery | *
South Galway Solar | B | Cashla | solar | TSO | due to connected | ECP-GSS1 | 101 | Y | solar not priority | N/A
Swordlestown Solar and Battery | J | Dunstown | battery | TSO | due to connected | ECP-GSS1 | 200 | N | battery | *
Swordlestown Solar and Battery | J | Dunstown | solar | TSO | due to connected | ECP-GSS1 | 250 | Y | solar not priority | N/A
Tibbotstown Solar (Lysaghtstown 3) | I | Lysaghtstown | solar | TSO | due to connected | ECP-GSS1 | 74 | Y | solar not priority | N/A
Tullacondra Windfarm | E | Mallow | wind | DSO | due to connected | ECP-GSS1 | 40.5 | Y | wind not priority | N/A
Western Brand South Site | B | Dalton | solar | DSO | due to connected | ECP-GSS1 | 3 | Y | solar not priority | N/A
Whitestown PV | J | Stephenstown | solar | DSO | due to connected | ECP-GSS1 | 9.99 | Y | solar not priority | N/A

## Generation Tables
This tab contains the interconnector limits together with area-wise generation portfolios for all study scenarios. Generation data includes units brought in for this iteration as well as previous iterations. "Thermal Technologies" refers to: Gas, Diesel, Biogas, Biomass, Combined Heat & Power (CHP), Landfill Gas (LFG), and Anaerobic Digester (AD) plants.
Interconnector Capabilities | Export/Import | 2030 | Future Grid
Moyle | Export/Import | 500 | 500
EWIC | Export/Import | 500 | 500
Celtic | Export Import | 700 | 700
Greenlink | Export /Import | 500 | 500
LiriC | Export/Import | - | 700
MARES FG | Export/Import | - | 750
Type | Area | Initial (MW) | 33% ECP (MW) | 33% + 1.3GW offshore | 33% + 2.6GW offshore | 33% + 2.6GW offshore reduced BESS | 66% ECP (MW) | 66% + 4.7GW offshore | 100% ECP (MW)
Battery | A | 3 | 52.5 | 52.5 | 52.5 | 3 | 102.9999 | 102.9999 | 153
Battery | B | 22.8 | 215.19 | 215.19 | 215.19 | 22.8 | 411.4663 | 411.4663 | 605.8
Battery | C | 268.65 | 450.3315 | 450.3315 | 450.3315 | 268.65 | 635.683 | 635.683 | 819.2
Battery | D | - | 23.1 | 23.1 | 23.1 | - | 46.6666 | 46.6666 | 70
Battery | E | 40.2 | 238.2 | 238.2 | 238.2 | 40.2 | 440.1996 | 440.1996 | 640.2
Battery | G | 304.4 | 406.865 | 406.865 | 406.865 | 304.4 | 511.3998 | 511.3998 | 614.9
Battery | H1 | - | 103.95 | 103.95 | 103.95 | - | 209.9998 | 209.9998 | 315
Battery | H2 | 55 | 338.14 | 338.14 | 338.14 | 55 | 626.9994 | 626.9994 | 913
Battery | I | 178 | 248.29 | 248.29 | 248.29 | 178 | 319.9999 | 319.9999 | 391
Battery | J | 366 | 685.572 | 685.572 | 685.572 | 366 | 1011.5994 | 1011.5994 | 1334.4
Battery | J2 | - | 124.08 | 124.08 | 124.08 | - | 250.6664 | 250.6664 | 376
Battery | K | - | 81.84 | 81.84 | 81.84 | - | 165.3332 | 165.3332 | 248
Battery | IE | 1238.05 | 2968.0585 | 2968.0585 | 2968.0585 | 1238.05 | 4733.0132 | 4733.0132 | 6480.5
Battery | NI | 707.224 | 849.3616 | 850.7972 | 850.7972 | 707.224 | 994.3704 | 994.3704 | 1137.944
Battery | Total | 1945.274 | 3817.4201 | 3817.4201 | 3817.4201 | 1945 | 5727 | 5727 | 7618.444
Solar | A | 40 | 41.6667 | 41.6667 | 41.6667 | 41.6667 | 43.3333 | 43.3333 | 45
Solar | B | 24 | 177.3898 | 177.3898 | 177.3898 | 177.3898 | 330.7797 | 330.7797 | 484.17
Solar | C | 92.6 | 498.6663 | 498.6663 | 498.6663 | 498.6663 | 904.7325 | 904.7325 | 1310.8
Solar | D | 22.3 | 165.2995 | 165.2995 | 165.2995 | 165.2995 | 308.299 | 308.299 | 451.299
Solar | E | 177.3 | 396.9798 | 396.9798 | 396.9798 | 396.9798 | 616.6596 | 616.6596 | 836.34
Solar | F | 36.2 | 46.55 | 46.55 | 46.55 | 46.55 | 56.9 | 56.9 | 67.25
Solar | G | 328.099 | 597.6754 | 597.6754 | 597.6754 | 597.6754 | 867.2518 | 867.2518 | 1136.829
Solar | H1 | 201.56 | 497.4064 | 497.4064 | 497.4064 | 497.4064 | 793.2527 | 793.2527 | 1089.1
Solar | H2 | 515 | 1062.9425 | 1062.9425 | 1062.9425 | 1062.9425 | 1610.8849 | 1610.8849 | 2158.829
Solar | I | 176.35 | 362.1298 | 362.1298 | 362.1298 | 362.1298 | 547.9096 | 547.9096 | 733.69
Solar | J | 775.1 | 1933.0488 | 1933.0488 | 1933.0488 | 1933.0488 | 3090.9977 | 3090.9977 | 4248.95
Solar | J2 | - | 25 | 25 | 25 | 25 | 49.9999 | 49.9999 | 75
Solar | K | 111.89 | 186.7199 | 186.7199 | 186.7199 | 186.7199 | 261.5499 | 261.5499 | 336.38
Solar | IE | 2500.399 | 5991.4748 | 5991.4748 | 5991.4748 | 5991.4748 | 9482.5507 | 9482.5507 | 12973.637
Solar | NI | 203.371 | 219.2043 | 219.2043 | 219.2043 | 219.2043 | 235.0376 | 235.0376 | 250.871
Solar | Total | 2703.77 | 6210.6792 | 6210.6792 | 6210.6792 | 6210.6792 | 9717.5883 | 9717.5883 | 13224.508
Onshore Wind | A | 865.693 | 996.4595 | 996.4595 | 996.4595 | 996.4595 | 1127.2261 | 1127.2261 | 1257.993
Onshore Wind | B | 855.07 | 1003.2065 | 1003.2065 | 1003.2065 | 1003.2065 | 1151.343 | 1151.343 | 1299.48
Onshore Wind | C | 240.69 | 376.4665 | 376.4665 | 376.4665 | 376.4665 | 512.2431 | 512.2431 | 648.02
Onshore Wind | D | 263.394 | 388.6272 | 388.6272 | 388.6272 | 388.6272 | 513.8604 | 513.8604 | 639.094
Onshore Wind | E | 1499.503 | 1726.8028 | 1726.8028 | 1726.8028 | 1726.8028 | 1954.1025 | 1954.1025 | 2181.403
Onshore Wind | F | 234.83 | 234.83 | 234.83 | 234.83 | 234.83 | 234.83 | 234.83 | 234.83
Onshore Wind | G | 279.135 | 295.935 | 295.935 | 295.935 | 295.935 | 312.735 | 312.735 | 329.535
Onshore Wind | H1 | 554.22 | 619.4033 | 619.4033 | 619.4033 | 619.4033 | 684.5865 | 684.5865 | 749.77
Onshore Wind | H2 | 350.022 | 510.8852 | 510.8852 | 510.8852 | 510.8852 | 671.7483 | 671.7483 | 832.612
Onshore Wind | I | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04 | 8.04
Onshore Wind | J | 466.601 | 608.0009 | 608.0009 | 608.0009 | 608.0009 | 749.4007 | 749.4007 | 890.801
Onshore Wind | K | 60.69 | 125.0233 | 125.0233 | 125.0233 | 125.0233 | 189.3565 | 189.3565 | 253.69
Onshore Wind | IE | 5677.888 | 6893.6801 | 6893.6801 | 6893.6801 | 6893.6801 | 8109.4722 | 8109.4722 | 9325.268
Onshore Wind | NI | 1656.1095 | 1686.1611 | 1686.1611 | 1686.1611 | 1686.1611 | 1716.2128 | 1716.2128 | 1746.2645
Onshore Wind | Total | 7333.9975 | 8579.8413 | 8579.8413 | 8579.8413 | 8579.8413 | 9825.685 | 9825.685 | 11071.5325
Offshore Wind | E | - | - | - | - | - | - | - | -
Offshore Wind | G | - | - | - | 375 | 375 | - | 375 | -
Offshore Wind | H2 | 25.2 | 25.2 | 25.2 | 425.2 | 425.2 | 25.2 | 1300.4 | 25.2
Offshore Wind | I | - | - | - | - | - | - | 450 | -
Offshore Wind | J | - | - | 1300 | 1800 | 1800 | - | 2624 | -
Ofshore Wind | IE | 25.2 | 25.2 | 1325.2 | 2600.2 | 2600.2 | 25.2 | 4749.4 | 25.2
Offshore Wind | NI | - | - | - | - | - | - | - | -
Offshore Wind | Total | 25.2 | 25.2 | 1325.2 | 2600.2 | 2600.2 | 25.2 | 4749.4 | 25.2
Thermal Technologies | B | 1.5 | 18.6833 | 18.6833 | 18.6833 | 18.6833 | 35.8666 | 35.8666 | 53.05
Thermal Technologies | C | - | 350 | 350 | 350 | 350 | 350 | 350 | 350
Thermal Technologies | E | 9.9 | 19.89 | 19.89 | 19.89 | 19.89 | 19.89 | 19.89 | 19.89
Thermal Technologies | F | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
Thermal Technologies | G | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4
Thermal Technologies | J | 7.5 | 309.8 | 309.8 | 309.8 | 309.8 | 313.1 | 313.1 | 316.4
Thermal Technologies | K | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7
Thermal Technologies | Total | 53 | 732.4733 | 732.4733 | 732.4733 | 732.4733 | 752.9566 | 752.9566 | 773.44

## Network Reinforcements
The content of the following table is an excel format for the information previously contained within Section 2, Table 6 of the Electricity Connection Policy (ECP) Assumptions Document.
Area | Project Type | Project Name | Year | CP Number
A | New | Binbane - Clogher - Cathaleens Fall - 110 kV Clogher tie in | 2035 | CP1318
A | System Reinforcement | Binbane 110 kV Station Busbar Thermal Capacity Need | 2035 | CP1523
A | System Reinforcement | Cathaleen’s Fall Srananagh 110 kV Circuit No 2 DLR | 2035 | CP1509
A | New | Donegal - Srananagh Corridor | 2035 | CP1233
A | Uprate | Drumkeen - Clogher 110 kV circuit 1 | 2035 | CP1327
A | Uprate | Letterkenny - Golagh Tee 110 kV circuit thermal capacity needs | 2035 | CP1447
A | Uprate | Letterkenny station redevelopment | 2035 | CP1023
B | Uprate | Cashla Dalton 110kV Thermal Capacity Increase | 2030 | CP1428
B | Uprate | Cashla-Galway 110 kV cct 2 Uprating | 2030 | CP1275
B | Uprate | Cashla-Galway 110 kV cct 3 Uprating | 2030 | CP1276
B | Uprate | Cashla-Galway 110 kV cot 1 Line uprate | 2030 | CP1191
B | Uprate | Cashla-Salthill 110 kV Thermal Uprate | 2030 | CP1168
B | Uprate | Castlebar Dalton 110kV Thermal Capacity Increase | 2030 | CP1429
B | Uprate | Castlebar-Cloon 110 kV Line Uprate-Refurb | 2030 | CP0848
B | Uprate | Dalton 110 kV Busbar | 2030 | CP0907
B | Upgrade | Flagford - Louth 220 kV Line Refurbishment | 2030 | CP0867
B | Upvoltage | Flagford Sligo Capacity Needs | 2035 | CP0982
B | Uprate | Galway - Salthill Thermal Capacity Need | 2030 | CP1470
B | New | North Connacht (Flagford Tonroe) 110 kV Project | 2030 | CP0816
B | Uprate | Sligo 110 kV Station - Shrananagh 1 & 2 Bay uprates | 2030 | CP1156
B | System Reinforcement | Srananagh 220kV Transformer and Bay Extension | 2035 | CP1543
C | Uprate | Athlone - Lanesboro 110 kV line uprate | 2035 | CP1311
C | Uprate | Lanesboro - Mullingar 110 kV Thermal Uprate | 2030 | CP1000
C | Uprate | Lanesboro – Sliabh Bawn 110 KV Line Uprate | 2035 | CP1078
C | System Reinforcement | Lanesboro 110 kV Station Redevelopment Project | 2030 | CP0919
D | Uprate | Ardnacrusha Drumline 110kV thermal capacity needs | 2035 | CP1450
D | New static device (DLR) | Ardnacrusha Ennis 110kV circuit DLR and related works | 2035 | CP1436
D | Uprate | Drumline 110 kV Station Busbar Thermal Uprate | 2035 | CP1434
D | New static device (DLR) | Drumline Ennis 110kV circuit DLR and related works | 2035 | CP1435
E | New | Cross Shannon 400 kV Cable | 2030 | CP0970
E | System Reinforcement | Kilbarry Knockraha 110 kV Circuit 2 Uprate (Kilbarry Mallow) | 2035 | CP1531
E | Replacement | Prospect Tarbert 220 kV Cable Replacement Project | 2030 | CP0917
E | System Reinforcement | Trien 110 kV Station Works | 2030 | CP0813
F | Uprate | Bandon Dunmanway 110 kV circuit thermal capacity | 2030 | CP1211
F | Uprate | Bandon Raffeen 110 kV circuit thermal capacity | 2030 | CP1212
G | Uprate | Arva - Carrick-on-Shannon 110 kV line uprate | 2030 | CP0841
G | System Reinforcement | Deenes - Drybridge 110 kV Circuit DLR | 2035 | CP1514
G | Uprate | Gorman - Maynooth 220 kV Circuit Capacity Needs | 2035 | CP1454
G | Uprate | Gorman - Platin 110 kV line uprate | 2030 | CP1166
G | Uprate | Lisdrum 110kV Station Busbar Thermal Capacity Need | 2035 | CP1465
G | New static device (DLR) | Lisdrum Louth 110 kV DLR project | 2035 | CP1471
G | New static device (DLR) | Louth - Meath Hill 110 kV DLR | 2035 | CP1473
G | Uprate | Louth - Woodland 220 kV Uprate | 2030 | CP1235
G | Uprate | Meath Hill 110kV Station Busbar Thermal Capacity Need | 2030 | CP1466
G | New | North South 400 kV Interconnector - RoI | 2035 | CP0466
G | New static device (DLR) | Ratrussan - Shankill 110 kV Dynamic Line Rating | 2035 | CP1479
H1 | Uprate | Killonan - Limerick No 1 110 kV Uprate | 2030 | CP1004
H1 | Upgrade | Killonan 220 kV Station Refurbishment - Killonan Station Works | 2030 | CP0624
H1 | Uprate | Limerick - Rathkeale Line Uprate | 2035* | CP1389
H1 | Asset Refurbishment | Lisheen - Thurles 110 kV Protection Upgrade | 2030 | CP1207
H2 | Uprate | Arklow - Ballybeg - Carrickmines 110 kV capacity Needs | 2035 | CP1196
H2 | Asset Refurbishment | Arklow 220 kV Station Redevelopment | 2035 | CP1238
H2 | Uprate | Arklow Lodgewood Line Uprate | 2030 | CP1121
H2 | Uprate | Athy - Carlow 110 kV circuit 1 | 2030 | CP1312
H2 | Uprate | Carlow 110 kV Station Busbar Thermal Capacity Need | 2030 | CP1291
H2 | System Reinforcement | Crane - Wexford 110 kV (DLR) | 2035 | CP1519
H2 | Uprate | Crane - Wexford 110 kV Line uprate | 2030 | CP1172
H2 | Uprate | Great Island - Kellis 220 kV Line Uprate | 2030 | CP0866
H2 | New static device (DLR) | Great Island - Waterford 110 kV (DLR) | 2035 | CP1520
H2 | Uprate | Great Island 220-110 kV transformer upgrades | 2030 | CP1242
H2 | Asset Refurbishment | Kellis- Kilkenny 110kV Circuit Refurbishment | 2035 | CP1574
H2 | Uprate | Lodgewood-Great Island line uprate | 2035 | CP1495
H2 | Replacement | New Ballyvouskill 220-110 kV Transformer | 2030 | CP1247
H2 | New | New Lodgewood 220-110 kV Transformer | 2035 | CP1522
H2 | System Reinforcement | North Wicklow Reinforcement | 2035 | CP1420
I | Uprate | Barrymore Cahir Knockraha 110kV Line Uprate | 2030 | CP1320
I | Uprate | Midleton 110kV Transformer Uprate and Station works DSO | 2030 | CP1449
I | Asset Refurbishment | Whitegate 110 kV Station Refurbishment Project | 2035 | CP1177
J | System Reinforcement | Baltrasna Corduff 110 kV Circuit DLR Project | 2035 | CP1526
J | New static device (DLR) | Baroda - Monread 110 kV circuit 1 (DLR) | 2035 | CP1314
J | New static device (DLR) | Baroda - Newbridge 110 kV circuit 1 (DLR) | 2035 | CP1315
J | Demand Connection | Belcamp Shellybanks 220 kV Cable | 2030 | CP0984
J | Uprate | Blake Maynooth Newbridge Uprate | 2030 | CP1319
J | Uprate | Blundelstown Mullingar 110 kV Line Uprate | 2030 | CP1325
J | System Reinforcement | Bracklone 110 kV Station - DSO | 2030 | CP0644
J | Replacement | Carrickmines - Poolbeg 220 kV Cable Replacement | 2035 | CP1146
J | Uprate | Coolnabacky - Portlaoise 110 kV line uprate | 2030 | CP0835
J | Uprate | Cushaling - Newbridge 110 kV Thermal Uprate | 2030 | CP1002
J | Uprate | Cushaling - Portlaoise 110 kV line uprate | 2035 | CP1003
J | Uprate | Derryiron - Thornsberry 110 kV Line Uprate | 2030 | CP1199
J | New | Dublin Central Bulk Supply Point 220kV Substation | 2035 | CP1273
J | New | Dunstown 400 kV Series Capacitor | 2030 | CP0968
J | Asset Refurbishment | Dunstown T4201 and Woodland T4201 Transformer replacement | 2030 | CP1086
J | Uprate | East Meath - North Dublin Reinforcement | 2030 | CP1021
J | New | Fingal to East Meath Grid Reinforcement | 2035 | CP1214
J | Replacement | Finglas - North Wall Cable Replacement | 2030 | CP1100
J | Asset Refurbishment | Inchicore - 220 kV GIS Station Upgrade | 2030 | CP0692
J | Replacement | Inchicore - Poolbeg 1 220 kV Cable Replacement | 2035 | CP1157
J | Replacement | Inchicore - Poolbeg 2 220 kV Cable Replacement | 2035 | CP1150
J | New | Kildare Meath | 2030 | CP0966
J | Uprate | Kilteel - Maynooth 110 kV | 2030 | CP1384
J | Uprate | Kinnegad 110 kV station, Derryiron 110 kV bay conductor uprate | 2030 | CP1144
J | New | Laois Kilkenny (Coolnabacky) 400 kV Station - New Station & Associated Lines & Station Works | 2030 | CP0585
J | Uprate | Louth 220 kV Station Refurbishment | 2035 | CP0799
J | Uprate | Maynooth - Rinawade 110V line uprate | 2035 | CP1390
J | Uprate | Maynooth - Rinawade 110V line uprate | 2030 | CP1390
J | System Reinforcement | Maynooth - Shannonbridge 220 kV Circuit Capacity Needs | 2030 | CP1477
J | System Reinforcement | Maynooth - Shannonbridge 220 kV Circuit Capacity Needs | 2030 | CP1477
J | Asset Refurbishment | Maynooth - Turlough Hill 220 kV line refurbishment | 2035 | CP0823
J | Uprate | Maynooth 220 kV Station Reconfiguration | 2035 | CP0808
J | New | Moneypoint 400 kV Series Capacitor | 2035 | CP0967
J | New | Mooretown 220 kV Station | 2030 | CP1183
J | Uprate | Newbridge - Portlaoise 110 kV Line uprate | 2030 | CP1170
J | New | Oldstreet-Woodland 400 kV Series Capacitor | 2030 | CP0969
J | Replacement | Poolbeg - North Wall 220 kV Cable Replacement | 2035 | CP1216
J | System Reinforcement | Poolbeg 220 kV Station | 2035 | CP1190
J | Uprate | Rinawade – Dunfirth Tee – Kinnegad 110 kV Circuit Thermal Capacity | 2030 | CP1403
J | System Reinforcement | Woodland 400 kV Station Redevelopment | 2035 | CP1194
Note on D51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A note is needed on what this asterisk refers to.

## Network Outages
The content of the following table is an excel format for the information previously contained within Section 2, Table 7 of the Electricity Connection Policy (ECP) Assumptions Document.
Transmission Unit | Outage Month | Category | Jurisdiction
Arklow T2102 | September | IE | Transformer
Carrickmines T2101 | August | IE | Transformer
Carrickmines T2102 | November | IE | Transformer
Cashla T2101 | September | IE | Transformer
Castlebagot T2101 | April | IE | Transformer
Clashavoon T2102 | March | IE | Transformer
Corduff T2101 | March | IE | Transformer
Cullenagh T2101 | April | IE | Transformer
Dunstown T4201 | May | IE | Transformer
Dunstown T4202 | August | IE | Transformer
Finglas T2101 | June | IE | Transformer
Flagford T2101 | May | IE | Transformer
Inchicore T2101 | July | IE | Transformer
Kilpaddoge T2101 | July | IE | Transformer
Knockanure T2101 | August | IE | Transformer
Knockraha T2101 | June | IE | Transformer
Knockraha T2102 | October | IE | Transformer
Louth T2101 | August | IE | Transformer
Moneypoint T4202 | October | IE | Transformer
Woodland T4201 | July | IE | Transformer
Aghada - Glanagow_220_1 | April | IE | Lines
Aghada - Raffeen_220_1 | June | IE | Lines
Arklow - Carrickmines_220_1 | March | IE | Lines
Arodstown - Gorman_220_1 | April | IE | Lines
Arva - Carrick on Shannon_110_1 | August | IE | Lines
Arva - Shankill_110_1 | July | IE | Lines
Balruntagh - Navan_110_1 | May | IE | Lines
Bracklone - Portlaoise_110_1 | July | IE | Lines
Cahir - Tipperary_110_1 | February | IE | Lines
Carlow - Kellis_110_1 | March | IE | Lines
Carrickmines - Dunstown_220_1 | September | IE | Lines
Carrickmines - Irishtown_220_1 | October | IE | Lines
Carrickmines - Poolbeg_220_1 | May | IE | Lines
Carrigadrohid - Kilbarry_110_1 | November | IE | Lines
Cashla - Cloon_110_1 | March | IE | Lines
Cashla - Flagford_220_1 | November | IE | Lines
Cashla - Prospect_220_1 | April | IE | Lines
Castlebagot - Maynooth 220_1 | October | IE | Lines
Castlebar - Cloon_110_1 | May | IE | Lines
Castlelost - Maynooth a_220_1 | October | IE | Lines
Cathaleens Fall - Clogher_110_1 | August | IE | Lines
Cathaleens Fall - Srananagh_110_1 | October | IE | Lines
Clashavoon - Knockraha_220_1 | August | IE | Lines
Coolnabacky - Moneypoint_380_1 | April | IE | Lines
Corduff - Cruiserath 220 1 | November | IE | Lines
Corduff - Woodland_220_1 | July | IE | Lines
Cullenagh - Great Island_220_1 | May | IE | Lines
Cullenagh - Knockraha_220_1 | September | IE | Lines
Cullenagh - Waterford_110_1 | January | IE | Lines
Derryiron - Kinnegad_110_1 | April | IE | Lines
Dunstown - Kellis_220_1 | August | IE | Lines
Dunstown - Maynooth_b_220_2 | September | IE | Lines
Eastwood - Ikerrin T_110_1 | May | IE | Lines
Flagford - Louth_220_1 | March | IE | Lines
Flagford - Srananagh_220_1 | April | IE | Lines
Galway - Knockranny A1_110_1 | December | IE | Lines
Garballagh - Platin_110_1 | February | IE | Lines
Glanagow - Raffeen_220_1 | July | IE | Lines
Gorman - Louth_220_1 | October | IE | Lines
Gorman - Navan_110_1 | September | IE | Lines
Great Island - Kellis_220_1 | June | IE | Lines
Great Island - Lodgewood_220_1 | July | IE | Lines
Great Island - Waterford_110_1 | September | IE | Lines
Inchicore - Poolbeg_220_1 | May | IE | Lines
Kellystown - Maynooth_220_1 | August | IE | Lines
Killonan - Kilpaddoge_220_1 | August | IE | Lines
Killonan - Knockraha_220_1 | September | IE | Lines
Killonan - Limerick_110_1 | September | IE | Lines
Killonan - Shannonbridge_220_1 | October | IE | Lines
Kilpaddoge - Tarbert_220_1 | March | IE | Lines
Knockraha - Raffeen_220_1 | August | IE | Lines
Louth - Meath Hill_110_1 | September | IE | Lines
Maynooth - Blake-T_110_1 | May | IE | Lines
North Wall - Poolbeg_220_1 | September | IE | Lines
Oldstreet - Woodland_380_1 | June | IE | Lines
Philipstown - Portlaoise_110_1 | December | IE | Lines
Prospect - Tarbert_220_1 | March | IE | Lines
Rabbitpark - Lanesboro_110_1 | April | IE | Lines
Thurles - Eastwood_110_1 | June | IE | Lines

## Modelling Results
This is the main body of results data from the Constraint Analysis studies and contains all of the data previously published in Area Reports.
Area | Subgroup | Node | Year | Generation Scenario | Grandfathering / Pro-rata | Generation Type | Installed (MW) | Available Energy (GWh) | Generation (GWh) | Surplus (GWh) | Curtailment (GWh) | Constraint (GWh) | Total Dispatch Down (GWh) | Surplus (%) | Curtailment (%) | Constraint (%) | Total Dispatch Down (%)
A | A, B North | ardnagappary | 2030 | Initial | Grandfathering | IE wind not priority | 17.96 | 51.9532 | 24.9129 | 6.4633 | 0.93433 | 19.6427 | 27.0403 | 12.44% | 1.798% | 37.81% | 52.05%
I | E,F & I | barnahely | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 3.3167 | 3.8832 | 3.1646 | 0.53806 | 0.072183 | 0.10829 | 0.71853 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | kilpaddoge | 2030 | Initial | Grandfathering | IE wind priority | 55 | 178.0734 | 173.3216 | 0 | 4.7518 | 0 | 4.7518 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | kilpaddoge | 2030 | 33% ECP | Grandfathering | IE wind priority | 55 | 178.0734 | 172.7395 | 0 | 5.3339 | 0 | 5.3339 | 0% | 2.995% | 0% | 2.995%
I | E,F & I | barnahely | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 3.3167 | 3.8832 | 2.8033 | 0.88389 | 0.082546 | 0.11345 | 1.0799 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | kilpaddoge | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 55 | 178.0734 | 171.9247 | 0 | 6.1487 | 0 | 6.1487 | 0% | 3.453% | 0% | 3.453%
E | E,F & I | kilpaddoge | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 55 | 178.0734 | 171.2402 | 0 | 6.8332 | 0 | 6.8332 | 0% | 3.837% | 0% | 3.837%
I | E,F & I | barnahely | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 3.3167 | 3.8832 | 2.8967 | 0.75999 | 0.07342 | 0.15311 | 0.98652 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | kilpaddoge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 55 | 178.0734 | 171.156 | 0 | 6.9174 | 0 | 6.9174 | 0% | 3.885% | 0% | 3.885%
E | E,F & I | kilpaddoge | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 55 | 178.0734 | 172.7395 | 0 | 5.3339 | 0 | 5.3339 | 0% | 2.995% | 0% | 2.995%
I | E,F & I | barnahely | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 3.3167 | 3.8832 | 2.9671 | 0.65283 | 0.073427 | 0.18982 | 0.91608 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | kilpaddoge | 2030 | 100% ECP | Grandfathering | IE wind priority | 55 | 178.0734 | 171.5438 | 0 | 6.5296 | 0 | 6.5296 | 0% | 3.667% | 0% | 3.667%
E | E,F & I | kilpaddoge | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 55 | 178.0734 | 171.5438 | 0 | 6.5296 | 0 | 6.5296 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | barnahely | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 3.3167 | 3.8832 | 3.0589 | 0.53806 | 0.072183 | 0.21404 | 0.82429 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | kilpaddoge | 2035 | 66% ECP | Grandfathering | IE wind priority | 55 | 178.0734 | 176.5538 | 0 | 1.5196 | 0 | 1.5196 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | kilpaddoge | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 55 | 178.0734 | 176.5538 | 0 | 1.5196 | 0 | 1.5196 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | kilpaddoge | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 55 | 178.0734 | 174.9909 | 0 | 3.0825 | 0 | 3.0825 | 0% | 1.731% | 0% | 1.731%
E | E,F & I | kilpaddoge | 2035 | 100% ECP | Grandfathering | IE wind priority | 55 | 178.0734 | 176.3332 | 0 | 1.7402 | 0 | 1.7402 | 0% | 0.9773% | 0% | 0.9773%
H2 | H2 & K | wexford | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 114.03 | 133.5075 | 97.7703 | 30.0654 | 1.2049 | 4.4669 | 35.7372 | 22.52% | 0.9025% | 3.346% | 26.77%
E | E,F & I | knockacummer | 2030 | Initial | Grandfathering | IE wind priority | 105 | 339.9583 | 330.8868 | 0 | 9.0715 | 0 | 9.0715 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | knockacummer | 2030 | 33% ECP | Grandfathering | IE wind priority | 105 | 339.9583 | 329.7755 | 0 | 10.1828 | 0 | 10.1828 | 0% | 2.995% | 0% | 2.995%
H2 | H2 & K | wexford | 2035 | 100% ECP | Grandfathering | IE wind priority | 27 | 76.3756 | 75.6466 | 0 | 0.72902 | 0 | 0.72902 | 0% | 0.9545% | 0% | 0.9545%
E | E,F & I | knockacummer | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 105 | 339.9583 | 328.2198 | 0 | 11.7385 | 0 | 11.7385 | 0% | 3.453% | 0% | 3.453%
E | E,F & I | knockacummer | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 105 | 339.9583 | 326.9131 | 0 | 13.0452 | 0 | 13.0452 | 0% | 3.837% | 0% | 3.837%
H2 | H2 & K | wexford | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 114.03 | 133.5075 | 97.8031 | 29.9552 | 1.1491 | 4.6 | 35.7043 | 22.44% | 0.8607% | 3.445% | 26.74%
I | E,F & I | barnahely | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 9.95 | 11.6496 | 7.4947 | 3.697 | 0.25571 | 0.20214 | 4.1549 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | glenlara 220kv side | 2035 | 100% ECP | Grandfathering | IE wind priority | 53 | 171.598 | 169.921 | 0 | 1.677 | 0 | 1.677 | 0% | 0.9773% | 0% | 0.9773%
E | E,F & I | glenlara 220kv side | 2035 | 100% ECP | Grandfathering | IE wind not priority | 13.8 | 44.6802 | 22.64 | 7.8953 | 0.14901 | 13.9958 | 22.0402 | 17.67% | 0.3335% | 31.32% | 49.33%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 13.8 | 44.6802 | 27.8185 | 9.9858 | 0.77015 | 6.1058 | 16.8618 | 22.35% | 1.724% | 13.67% | 37.74%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 53 | 171.598 | 165.6729 | 0 | 5.9251 | 0 | 5.9251 | 0% | 3.453% | 0% | 3.453%
I | E,F & I | castleview | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 1.1633 | 1.362 | 1.016 | 0.26657 | 0.025752 | 0.053703 | 0.34603 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 13.8 | 44.6802 | 26.1413 | 12.9482 | 0.77581 | 4.8149 | 18.5389 | 28.98% | 1.736% | 10.78% | 41.49%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 53 | 171.598 | 165.0133 | 0 | 6.5847 | 0 | 6.5847 | 0% | 3.837% | 0% | 3.837%
I | E,F & I | castleview | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 1.1633 | 1.362 | 1.0407 | 0.22898 | 0.025755 | 0.06658 | 0.32132 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 13.8 | 44.6802 | 23.6779 | 13.8632 | 0.77076 | 6.3684 | 21.0023 | 31.03% | 1.725% | 14.25% | 47.01%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 53 | 171.598 | 164.9322 | 0 | 6.6658 | 0 | 6.6658 | 0% | 3.885% | 0% | 3.885%
I | E,F & I | castleview | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 1.1633 | 1.362 | 1.0729 | 0.18873 | 0.025318 | 0.075076 | 0.28912 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 13.8 | 44.6802 | 32.2579 | 7.2486 | 0.73391 | 4.4399 | 12.4223 | 16.22% | 1.643% | 9.937% | 27.8%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 53 | 171.598 | 166.4581 | 0 | 5.1399 | 0 | 5.1399 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | glenlara 220kv side | 2030 | 100% ECP | Grandfathering | IE wind not priority | 13.8 | 44.6802 | 27.3912 | 11.92 | 0.75713 | 4.6118 | 17.289 | 26.68% | 1.695% | 10.32% | 38.69%
E | E,F & I | glenlara 220kv side | 2030 | 100% ECP | Grandfathering | IE wind priority | 53 | 171.598 | 165.3058 | 0 | 6.2922 | 0 | 6.2922 | 0% | 3.667% | 0% | 3.667%
E | E,F & I | knockacummer | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 105 | 339.9583 | 326.7524 | 0 | 13.2059 | 0 | 13.2059 | 0% | 3.885% | 0% | 3.885%
I | E,F & I | barnahely | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 9.95 | 11.6496 | 7.9059 | 2.6234 | 0.10514 | 1.0151 | 3.7437 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | glenlara 220kv side | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 53 | 171.598 | 165.3058 | 0 | 6.2922 | 0 | 6.2922 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | barnahely | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 6.6333 | 7.7664 | 5.4036 | 1.7425 | 0.066845 | 0.55338 | 2.3628 | 22.44% | 0.8607% | 7.125% | 30.42%
I | E,F & I | barnahely | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 6.6333 | 7.7664 | 6.1022 | 1.233 | 0.057001 | 0.37413 | 1.6641 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | glenlara 220kv side | 2035 | 66% ECP | Grandfathering | IE wind not priority | 13.8 | 44.6802 | 22.0902 | 7.1337 | 0.13694 | 15.3194 | 22.59 | 15.97% | 0.3065% | 34.29% | 50.56%
E | E,F & I | glenlara 220kv side | 2035 | 66% ECP | Grandfathering | IE wind priority | 53 | 171.598 | 170.1336 | 0 | 1.4644 | 0 | 1.4644 | 0% | 0.8534% | 0% | 0.8534%
I | E,F & I | barnahely | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 6.6333 | 7.7664 | 5.6621 | 1.233 | 0.057001 | 0.81423 | 2.1042 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | glenlara 220kv side | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 13.8 | 44.6802 | 26.8136 | 7.1337 | 0.13694 | 10.596 | 17.8666 | 15.97% | 0.3065% | 23.72% | 39.99%
E | E,F & I | glenlara 220kv side | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 53 | 171.598 | 170.1336 | 0 | 1.4644 | 0 | 1.4644 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | glenlara 220kv side | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 13.8 | 44.6802 | 25.9815 | 13.0679 | 0.26989 | 5.361 | 18.6988 | 29.25% | 0.604% | 12% | 41.85%
E | E,F & I | glenlara 220kv side | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 53 | 171.598 | 168.6276 | 0 | 2.9704 | 0 | 2.9704 | 0% | 1.731% | 0% | 1.731%
I | E,F & I | barnahely | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 9.95 | 11.6496 | 7.5987 | 3.697 | 0.25571 | 0.098114 | 4.0509 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | glenlara 220kv side | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 13.8 | 44.6802 | 28.6714 | 11.92 | 0.75713 | 3.3317 | 16.0088 | 26.68% | 1.695% | 7.457% | 35.83%
E | E,F & I | knockacummer | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 105 | 339.9583 | 329.7755 | 0 | 10.1828 | 0 | 10.1828 | 0% | 2.995% | 0% | 2.995%
H2 | H2 & K | wexford | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 27 | 76.3756 | 74.9711 | 0 | 1.4045 | 0 | 1.4045 | 0% | 1.839% | 0% | 1.839%
E | E,F & I | knockacummer | 2030 | 100% ECP | Grandfathering | IE wind priority | 105 | 339.9583 | 327.4927 | 0 | 12.4656 | 0 | 12.4656 | 0% | 3.667% | 0% | 3.667%
H2 | H2 & K | wexford | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 27 | 76.3756 | 73.9523 | 0 | 2.4233 | 0 | 2.4233 | 0% | 3.173% | 0% | 3.173%
E | E,F & I | knockearagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 9.35 | 30.2725 | 29.2272 | 0 | 1.0453 | 0 | 1.0453 | 0% | 3.453% | 0% | 3.453%
E | E,F & I | knockearagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 1.6633 | 1.9474 | 1.488 | 0.3274 | 0.036824 | 0.095196 | 0.45942 | 16.81% | 1.891% | 4.888% | 23.59%
H2 | H2 & K | wexford | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 114.03 | 133.5075 | 95.567 | 30.3889 | 2.838 | 4.7136 | 37.9404 | 22.76% | 2.126% | 3.531% | 28.42%
E | E,F & I | knockearagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 9.35 | 30.2725 | 29.1108 | 0 | 1.1616 | 0 | 1.1616 | 0% | 3.837% | 0% | 3.837%
E | E,F & I | knockearagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 1.6633 | 1.9474 | 1.4527 | 0.38114 | 0.036821 | 0.076784 | 0.49475 | 19.57% | 1.891% | 3.943% | 25.4%
H2 | H2 & K | wexford | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 27 | 76.3756 | 73.1999 | 0 | 3.1757 | 0 | 3.1757 | 0% | 4.158% | 0% | 4.158%
E | E,F & I | knockearagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 9.35 | 30.2725 | 29.0965 | 0 | 1.176 | 0 | 1.176 | 0% | 3.885% | 0% | 3.885%
E | E,F & I | knockearagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 1.6633 | 1.9474 | 1.4059 | 0.44328 | 0.041397 | 0.056894 | 0.54157 | 22.76% | 2.126% | 2.921% | 27.81%
H2 | H2 & K | wexford | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 114.03 | 133.5075 | 100.1783 | 26.1293 | 2.5243 | 4.6756 | 33.3292 | 19.57% | 1.891% | 3.502% | 24.96%
E | E,F & I | knockearagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 9.35 | 30.2725 | 29.3657 | 0 | 0.90676 | 0 | 0.90676 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | knockearagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 1.6633 | 1.9474 | 1.5871 | 0.26984 | 0.0362 | 0.054309 | 0.36035 | 13.86% | 1.859% | 2.789% | 18.5%
H2 | H2 & K | wexford | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 27 | 76.3756 | 73.2436 | 0 | 3.132 | 0 | 3.132 | 0% | 4.101% | 0% | 4.101%
E | E,F & I | knockearagh | 2030 | 100% ECP | Grandfathering | IE wind priority | 9.35 | 30.2725 | 29.1624 | 0 | 1.11 | 0 | 1.11 | 0% | 3.667% | 0% | 3.667%
E | E,F & I | knockearagh | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 1.6633 | 1.9474 | 1.5341 | 0.26984 | 0.0362 | 0.10734 | 0.41339 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | knockearagh | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 4.99 | 5.8423 | 3.7586 | 1.8541 | 0.12824 | 0.10137 | 2.0837 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | knockearagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 9.35 | 30.2725 | 29.1624 | 0 | 1.11 | 0 | 1.11 | 0% | 3.667% | 0% | 3.667%
E | E,F & I | knockearagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.99 | 5.8423 | 3.8108 | 1.8541 | 0.12824 | 0.049205 | 2.0315 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | wexford | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 27 | 76.3756 | 73.6136 | 0 | 2.762 | 0 | 2.762 | 0% | 3.616% | 0% | 3.616%
H2 | H2 & K | wexford | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 114.03 | 133.5075 | 107.6848 | 18.499 | 2.4817 | 4.842 | 25.8227 | 13.86% | 1.859% | 3.627% | 19.34%
E | E,F & I | knockearagh | 2035 | 66% ECP | Grandfathering | IE wind priority | 9.35 | 30.2725 | 30.0141 | 0 | 0.25834 | 0 | 0.25834 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | knockearagh | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 3.3267 | 3.8949 | 2.8396 | 0.61835 | 0.028586 | 0.40834 | 1.0553 | 15.88% | 0.7339% | 10.48% | 27.09%
H2 | H2 & K | wexford | 2030 | 33% ECP | Grandfathering | IE wind priority | 27 | 76.3756 | 73.9523 | 0 | 2.4233 | 0 | 2.4233 | 0% | 3.173% | 0% | 3.173%
E | E,F & I | knockearagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 9.35 | 30.2725 | 30.0141 | 0 | 0.25834 | 0 | 0.25834 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | knockearagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 3.3267 | 3.8949 | 3.0603 | 0.61835 | 0.028586 | 0.18763 | 0.83457 | 15.88% | 0.7339% | 4.817% | 21.43%
H2 | H2 & K | wexford | 2030 | Initial | Grandfathering | IE Solar not priority | 114.03 | 133.5075 | 111.331 | 11.0418 | 1.7203 | 9.4144 | 22.1765 | 8.271% | 1.289% | 7.052% | 16.61%
E | E,F & I | knockearagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 9.35 | 30.2725 | 29.7485 | 0 | 0.52403 | 0 | 0.52403 | 0% | 1.731% | 0% | 1.731%
E | E,F & I | knockearagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 3.3267 | 3.8949 | 2.7099 | 0.8739 | 0.033523 | 0.27753 | 1.185 | 22.44% | 0.8607% | 7.125% | 30.42%
H2 | H2 & K | wexford | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 114.03 | 133.5075 | 104.9907 | 22.445 | 2.5245 | 3.5473 | 28.5168 | 16.81% | 1.891% | 2.657% | 21.36%
I | E,F & I | castleview | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 1.1633 | 1.362 | 0.98327 | 0.31003 | 0.028953 | 0.039792 | 0.37877 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | knockearagh | 2030 | 33% ECP | Grandfathering | IE wind priority | 9.35 | 30.2725 | 29.3657 | 0 | 0.90676 | 0 | 0.90676 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | knockearagh | 2030 | Initial | Grandfathering | IE wind priority | 9.35 | 30.2725 | 29.4647 | 0 | 0.8078 | 0 | 0.8078 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | knockacummer | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 105 | 339.9583 | 327.4927 | 0 | 12.4656 | 0 | 12.4656 | 0% | 3.667% | 0% | 3.667%
H2 | H2 & K | wexford | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 114.03 | 133.5075 | 109.6571 | 21.1957 | 0.97987 | 1.6748 | 23.8503 | 15.88% | 0.7339% | 1.254% | 17.86%
E | E,F & I | knockacummer | 2035 | 66% ECP | Grandfathering | IE wind priority | 105 | 339.9583 | 337.0572 | 0 | 2.9011 | 0 | 2.9011 | 0% | 0.8534% | 0% | 0.8534%
H2 | H2 & K | wexford | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 27 | 76.3756 | 75.7104 | 0 | 0.66522 | 0 | 0.66522 | 0% | 0.871% | 0% | 0.871%
E | E,F & I | knockacummer | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 105 | 339.9583 | 337.0572 | 0 | 2.9011 | 0 | 2.9011 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | knockacummer | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 105 | 339.9583 | 334.0735 | 0 | 5.8848 | 0 | 5.8848 | 0% | 1.731% | 0% | 1.731%
H2 | H2 & K | wexford | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 114.03 | 133.5075 | 106.1576 | 21.1957 | 0.97987 | 5.1743 | 27.3499 | 15.88% | 0.7339% | 3.876% | 20.49%
E | E,F & I | knockacummer | 2035 | 100% ECP | Grandfathering | IE wind priority | 105 | 339.9583 | 336.636 | 0 | 3.3223 | 0 | 3.3223 | 0% | 0.9773% | 0% | 0.9773%
H2 | H2 & K | wexford | 2035 | 66% ECP | Grandfathering | IE wind priority | 27 | 76.3756 | 75.7104 | 0 | 0.66522 | 0 | 0.66522 | 0% | 0.871% | 0% | 0.871%
E | E,F & I | knockanure | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 38.6666 | 45.2713 | 35.6615 | 6.2729 | 0.84153 | 2.4954 | 9.6098 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | knockanure | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 38.6666 | 45.2713 | 34.5913 | 7.6109 | 0.85603 | 2.213 | 10.6799 | 16.81% | 1.891% | 4.888% | 23.59%
H2 | H2 & K | wexford | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 114.03 | 133.5075 | 111.9085 | 18.499 | 2.4817 | 0.61827 | 21.599 | 13.86% | 1.859% | 0.4631% | 16.18%
E | E,F & I | knockanure | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 38.6666 | 45.2713 | 33.7701 | 8.8602 | 0.85595 | 1.785 | 11.5012 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | knockanure | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 38.6666 | 45.2713 | 36.8944 | 6.2729 | 0.84153 | 1.2625 | 8.3769 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | knockanure | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 116 | 135.814 | 87.375 | 43.1012 | 2.9811 | 2.3566 | 48.4389 | 31.74% | 2.195% | 1.735% | 35.67%
H2 | H2 & K | wexford | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 114.03 | 133.5075 | 88.0784 | 42.3693 | 2.9305 | 0.12933 | 45.4291 | 31.74% | 2.195% | 0.09687% | 34.03%
E | E,F & I | knockanure | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 116 | 135.814 | 88.5877 | 43.1012 | 2.9811 | 1.1438 | 47.2262 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | wexford | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 27 | 76.3756 | 73.4351 | 0 | 2.9405 | 0 | 2.9405 | 0% | 3.85% | 0% | 3.85%
E | E,F & I | knockanure | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 77.3333 | 90.5425 | 66.0109 | 14.3746 | 0.66453 | 9.4925 | 24.5316 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | knockanure | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 77.3333 | 90.5425 | 71.1417 | 14.3746 | 0.66453 | 4.3617 | 19.4008 | 15.88% | 0.7339% | 4.817% | 21.43%
H2 | H2 & K | wexford | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 114.03 | 133.5075 | 86.5148 | 42.3693 | 2.9305 | 1.6929 | 46.9927 | 31.74% | 2.195% | 1.268% | 35.2%
E | E,F & I | knockanure | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 77.3333 | 90.5425 | 62.9966 | 20.3152 | 0.7793 | 6.4515 | 27.546 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | knockanure | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 116 | 135.814 | 92.1689 | 30.5848 | 1.2257 | 11.8346 | 43.6451 | 22.52% | 0.9025% | 8.714% | 32.14%
H2 | H2 & K | wexford | 2030 | 100% ECP | Grandfathering | IE wind priority | 27 | 76.3756 | 73.4351 | 0 | 2.9405 | 0 | 2.9405 | 0% | 3.85% | 0% | 3.85%
E | E,F & I | knockanure | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 38.6666 | 45.2713 | 32.6817 | 10.3046 | 0.96234 | 1.3226 | 12.5895 | 22.76% | 2.126% | 2.921% | 27.81%
H2 | H2 & K | wexford | 2030 | Initial | Grandfathering | IE wind priority | 27 | 76.3756 | 74.2301 | 0 | 2.1455 | 0 | 2.1455 | 0% | 2.809% | 0% | 2.809%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP | Grandfathering | IE wind priority | 53 | 171.598 | 166.4581 | 0 | 5.1399 | 0 | 5.1399 | 0% | 2.995% | 0% | 2.995%
I | E,F & I | castleview | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 1.1633 | 1.362 | 1.11 | 0.18873 | 0.025318 | 0.037984 | 0.25203 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | drombeg | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 25.2 | 81.59 | 48.964 | 13.0267 | 0.25007 | 19.3492 | 32.626 | 15.97% | 0.3065% | 23.72% | 39.99%
I | E,F & I | cow cross | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 10.2833 | 12.0398 | 9.46 | 1.9114 | 0.088366 | 0.58 | 2.5798 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | drombeg | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 79.3333 | 92.8842 | 72.9816 | 14.7463 | 0.68172 | 4.4746 | 19.9026 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | drombeg | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 25.2 | 81.59 | 47.4444 | 23.8631 | 0.49284 | 9.7897 | 34.1456 | 29.25% | 0.604% | 12% | 41.85%
I | E,F & I | cow cross | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 10.2833 | 12.0398 | 8.7778 | 1.9114 | 0.088366 | 1.2623 | 3.2621 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | drombeg | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 79.3333 | 92.8842 | 64.6259 | 20.8406 | 0.79945 | 6.6184 | 28.2584 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | drombeg | 2035 | 100% ECP | Grandfathering | IE wind not priority | 25.2 | 81.59 | 41.3427 | 14.4176 | 0.27211 | 25.5576 | 40.2473 | 17.67% | 0.3335% | 31.32% | 49.33%
E | E,F & I | drombeg | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 94 | 110.0561 | 74.6886 | 24.7842 | 0.99326 | 9.5901 | 35.3676 | 22.52% | 0.9025% | 8.714% | 32.14%
I | E,F & I | cow cross | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 12.95 | 15.162 | 9.8898 | 4.8117 | 0.33281 | 0.1277 | 5.2722 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | garrow | 2030 | Initial | Grandfathering | IE wind priority | 69.225 | 224.1297 | 218.1489 | 0 | 5.9807 | 0 | 5.9807 | 0% | 2.668% | 0% | 2.668%
I | E,F & I | cow cross | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 12.95 | 15.162 | 9.7544 | 4.8117 | 0.33281 | 0.26308 | 5.4076 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | garrow | 2030 | 33% ECP | Grandfathering | IE wind priority | 69.225 | 224.1297 | 217.4163 | 0 | 6.7134 | 0 | 6.7134 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | garrow | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 69.225 | 224.1297 | 216.3906 | 0 | 7.739 | 0 | 7.739 | 0% | 3.453% | 0% | 3.453%
I | E,F & I | cow cross | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 7.6167 | 8.9177 | 7.2676 | 1.2356 | 0.16577 | 0.24869 | 1.6501 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | garrow | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 69.225 | 224.1297 | 215.5291 | 0 | 8.6005 | 0 | 8.6005 | 0% | 3.837% | 0% | 3.837%
E | E,F & I | garrow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 69.225 | 224.1297 | 215.4232 | 0 | 8.7064 | 0 | 8.7064 | 0% | 3.885% | 0% | 3.885%
I | E,F & I | cow cross | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 7.6167 | 8.9177 | 6.4377 | 2.0298 | 0.18956 | 0.26053 | 2.4799 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | garrow | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 69.225 | 224.1297 | 217.4163 | 0 | 6.7134 | 0 | 6.7134 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | garrow | 2030 | 100% ECP | Grandfathering | IE wind priority | 69.225 | 224.1297 | 215.9112 | 0 | 8.2184 | 0 | 8.2184 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | cow cross | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 7.6167 | 8.9177 | 6.6521 | 1.7453 | 0.16861 | 0.35161 | 2.2655 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | garrow | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 69.225 | 224.1297 | 215.9112 | 0 | 8.2184 | 0 | 8.2184 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | cow cross | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 7.6167 | 8.9177 | 6.8139 | 1.4992 | 0.16862 | 0.43592 | 2.1038 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | garrow | 2035 | 66% ECP | Grandfathering | IE wind priority | 69.225 | 224.1297 | 222.217 | 0 | 1.9127 | 0 | 1.9127 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | garrow | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 69.225 | 224.1297 | 222.217 | 0 | 1.9127 | 0 | 1.9127 | 0% | 0.8534% | 0% | 0.8534%
I | E,F & I | cow cross | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 7.6167 | 8.9177 | 7.0247 | 1.2356 | 0.16577 | 0.49154 | 1.893 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | drombeg | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 79.3333 | 92.8842 | 67.7182 | 14.7463 | 0.68172 | 9.738 | 25.1661 | 15.88% | 0.7339% | 10.48% | 27.09%
I | E,F & I | cow cross | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 10.2833 | 12.0398 | 8.3769 | 2.7014 | 0.10363 | 0.85788 | 3.6629 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | drombeg | 2035 | 66% ECP | Grandfathering | IE wind not priority | 25.2 | 81.59 | 40.3387 | 13.0267 | 0.25007 | 27.9745 | 41.2513 | 15.97% | 0.3065% | 34.29% | 50.56%
E | E,F & I | dromada | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 28.5 | 92.2744 | 90.6771 | 0 | 1.5973 | 0 | 1.5973 | 0% | 1.731% | 0% | 1.731%
E | E,F & I | dromada | 2035 | 100% ECP | Grandfathering | IE wind priority | 28.5 | 92.2744 | 91.3726 | 0 | 0.90176 | 0 | 0.90176 | 0% | 0.9773% | 0% | 0.9773%
I | E,F & I | kilbarry | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 79.8 | 93.4306 | 60.9423 | 29.6507 | 2.0508 | 0.78688 | 32.4884 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | drombeg | 2030 | Initial | Grandfathering | IE wind not priority | 25.2 | 81.59 | 41.4031 | 9.7392 | 1.3696 | 29.078 | 40.1869 | 11.94% | 1.679% | 35.64% | 49.25%
I | E,F & I | kilbarry | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 79.8 | 93.4306 | 60.108 | 29.6507 | 2.0508 | 1.6211 | 33.3226 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | drombeg | 2030 | Initial | Grandfathering | IE Solar not priority | 50 | 58.5405 | 44.0885 | 4.8416 | 0.7543 | 8.8561 | 14.452 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | drombeg | 2030 | 33% ECP | Grandfathering | IE wind not priority | 25.2 | 81.59 | 53.3466 | 13.2365 | 1.3402 | 13.6667 | 28.2434 | 16.22% | 1.643% | 16.75% | 34.62%
I | E,F & I | kilbarry | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 33.2 | 38.8709 | 31.6783 | 5.386 | 0.72255 | 1.084 | 7.1926 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | drombeg | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 64.6667 | 75.7124 | 59.6409 | 10.4908 | 1.4074 | 4.1733 | 16.0715 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | drombeg | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 25.2 | 81.59 | 50.799 | 18.235 | 1.4064 | 11.1496 | 30.791 | 22.35% | 1.724% | 13.67% | 37.74%
I | E,F & I | kilbarry | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 33.2 | 38.8709 | 28.0612 | 8.8478 | 0.82629 | 1.1356 | 10.8096 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | drombeg | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 64.6667 | 75.7124 | 57.8511 | 12.7286 | 1.4316 | 3.701 | 17.8613 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | drombeg | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 25.2 | 81.59 | 47.7363 | 23.6446 | 1.4167 | 8.7924 | 33.8537 | 28.98% | 1.736% | 10.78% | 41.49%
E | E,F & I | garrow | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 69.225 | 224.1297 | 220.2499 | 0 | 3.8798 | 0 | 3.8798 | 0% | 1.731% | 0% | 1.731%
I | E,F & I | kilbarry | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 33.2 | 38.8709 | 28.9957 | 7.6076 | 0.73494 | 1.5326 | 9.8751 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | drombeg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 25.2 | 81.59 | 43.2379 | 25.3154 | 1.4075 | 11.6292 | 38.352 | 31.03% | 1.725% | 14.25% | 47.01%
I | E,F & I | kilbarry | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 33.2 | 38.8709 | 29.7009 | 6.5349 | 0.73501 | 1.9001 | 9.17 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | drombeg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 64.6667 | 75.7124 | 54.6574 | 17.2336 | 1.6094 | 2.2119 | 21.0549 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | drombeg | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 25.2 | 81.59 | 58.9057 | 13.2365 | 1.3402 | 8.1076 | 22.6843 | 16.22% | 1.643% | 9.937% | 27.8%
I | E,F & I | kilbarry | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 33.2 | 38.8709 | 30.6197 | 5.386 | 0.72255 | 2.1426 | 8.2511 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | drombeg | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 64.6667 | 75.7124 | 61.7027 | 10.4908 | 1.4074 | 2.1114 | 14.0096 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | drombeg | 2030 | 100% ECP | Grandfathering | IE wind not priority | 25.2 | 81.59 | 50.0188 | 21.767 | 1.3826 | 8.4216 | 31.5712 | 26.68% | 1.695% | 10.32% | 38.69%
I | E,F & I | kilbarry | 2030 | Initial | Grandfathering | IE Solar not priority | 9.9 | 11.591 | 8.7295 | 0.95864 | 0.14935 | 1.7535 | 2.8615 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | drombeg | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 94 | 110.0561 | 70.8039 | 34.9269 | 2.4157 | 1.9096 | 39.2522 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | drombeg | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 25.2 | 81.59 | 52.3565 | 21.767 | 1.3826 | 6.0839 | 29.2335 | 26.68% | 1.695% | 7.457% | 35.83%
E | E,F & I | drombeg | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 94 | 110.0561 | 71.7866 | 34.9269 | 2.4157 | 0.9269 | 38.2695 | 31.74% | 2.195% | 0.8422% | 34.77%
I | E,F & I | cow cross | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 12.95 | 15.162 | 10.2895 | 3.4144 | 0.13684 | 1.3212 | 4.8724 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | drombeg | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 64.6667 | 75.7124 | 56.4776 | 14.818 | 1.4315 | 2.9852 | 19.2347 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | garrow | 2035 | 100% ECP | Grandfathering | IE wind priority | 69.225 | 224.1297 | 221.9393 | 0 | 2.1903 | 0 | 2.1903 | 0% | 0.9773% | 0% | 0.9773%
I | E,F & I | cow cross | 2030 | Initial | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.3648 | 0.47932 | 0.074676 | 0.87675 | 1.4308 | 8.271% | 1.289% | 15.13% | 24.69%
I | E,F & I | coolroe | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 4.6667 | 5.4638 | 4.1748 | 0.91856 | 0.10331 | 0.26708 | 1.289 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | glanlee | 2035 | 100% ECP | Grandfathering | IE wind not priority | 36 | 116.5571 | 59.061 | 20.5965 | 0.38873 | 36.5109 | 57.4961 | 17.67% | 0.3335% | 31.32% | 49.33%
E | E,F & I | glanlee | 2035 | 100% ECP | Grandfathering | IE wind priority | 29.8 | 96.4834 | 95.5405 | 0 | 0.9429 | 0 | 0.9429 | 0% | 0.9773% | 0% | 0.9773%
I | E,F & I | coolroe | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 4.6667 | 5.4638 | 4.304 | 0.75707 | 0.10156 | 0.30116 | 1.1598 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | glenlara | 2030 | Initial | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.3648 | 0.47932 | 0.074676 | 0.87675 | 1.4308 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | glenlara | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.5653 | 0.80304 | 0.10773 | 0.31945 | 1.2302 | 13.86% | 1.859% | 5.512% | 21.23%
I | E,F & I | castleview | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 3.49 | 4.0861 | 2.773 | 0.92018 | 0.036878 | 0.35606 | 1.3131 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | glenlara | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.4283 | 0.97433 | 0.10959 | 0.2833 | 1.3672 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | glenlara | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.3232 | 1.1343 | 0.10958 | 0.22851 | 1.4723 | 19.57% | 1.891% | 3.943% | 25.4%
I | E,F & I | castleview | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 2.3267 | 2.7241 | 1.8953 | 0.61121 | 0.023446 | 0.1941 | 0.82875 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | glenlara | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.1838 | 1.3192 | 0.1232 | 0.16931 | 1.6117 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | glanlee | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 29.8 | 96.4834 | 94.8132 | 0 | 1.6702 | 0 | 1.6702 | 0% | 1.731% | 0% | 1.731%
E | E,F & I | glenlara | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.7231 | 0.80304 | 0.10773 | 0.16162 | 1.0724 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | glenlara | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 3.7285 | 1.8392 | 0.12721 | 0.10056 | 2.067 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | glenlara | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 3.7803 | 1.8392 | 0.12721 | 0.04881 | 2.0153 | 31.74% | 2.195% | 0.8422% | 34.77%
I | E,F & I | castleview | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 2.3267 | 2.7241 | 1.986 | 0.43248 | 0.019993 | 0.28559 | 0.73806 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | glenlara | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.2253 | 0.9201 | 0.042536 | 0.6076 | 1.5702 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | glenlara | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.5537 | 0.9201 | 0.042536 | 0.27919 | 1.2418 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | glenlara | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.0323 | 1.3003 | 0.049882 | 0.41295 | 1.7632 | 22.44% | 0.8607% | 7.125% | 30.42%
I | E,F & I | castleview | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 3.49 | 4.0861 | 2.6653 | 1.2968 | 0.089691 | 0.034414 | 1.4209 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | glenlara | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 3.9331 | 1.3051 | 0.052305 | 0.50501 | 1.8624 | 22.52% | 0.9025% | 8.714% | 32.14%
I | E,F & I | castleview | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 3.49 | 4.0861 | 2.6288 | 1.2968 | 0.089691 | 0.0709 | 1.4573 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | glenlara 220kv side | 2030 | Initial | Grandfathering | IE wind not priority | 13.8 | 44.6802 | 22.6731 | 5.3334 | 0.75004 | 15.9237 | 22.0071 | 11.94% | 1.679% | 35.64% | 49.25%
E | E,F & I | glenlara 220kv side | 2030 | Initial | Grandfathering | IE wind priority | 53 | 171.598 | 167.019 | 0 | 4.579 | 0 | 4.579 | 0% | 2.668% | 0% | 2.668%
I | E,F & I | castleview | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 2.3267 | 2.7241 | 2.1404 | 0.43248 | 0.019993 | 0.13123 | 0.5837 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP | Grandfathering | IE wind not priority | 13.8 | 44.6802 | 29.2136 | 7.2486 | 0.73391 | 7.4841 | 15.4666 | 16.22% | 1.643% | 16.75% | 34.62%
E | E,F & I | glanlee | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 24 | 77.7047 | 45.1851 | 22.7267 | 0.46937 | 9.3235 | 32.5196 | 29.25% | 0.604% | 12% | 41.85%
E | E,F & I | glanlee | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 29.8 | 96.4834 | 95.66 | 0 | 0.82337 | 0 | 0.82337 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | glanlee | 2030 | Initial | Grandfathering | IE wind priority | 29.8 | 96.4834 | 93.9088 | 0 | 2.5746 | 0 | 2.5746 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | glanlee | 2030 | 33% ECP | Grandfathering | IE wind not priority | 12 | 38.8523 | 25.4031 | 6.3031 | 0.63818 | 6.5079 | 13.4492 | 16.22% | 1.643% | 16.75% | 34.62%
E | E,F & I | glanlee | 2030 | 33% ECP | Grandfathering | IE wind priority | 29.8 | 96.4834 | 93.5934 | 0 | 2.89 | 0 | 2.89 | 0% | 2.995% | 0% | 2.995%
I | E,F & I | coolroe | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 14 | 16.3913 | 11.1238 | 3.6913 | 0.14793 | 1.4283 | 5.2675 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | glanlee | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 12 | 38.8523 | 24.19 | 8.6833 | 0.66969 | 5.3094 | 14.6624 | 22.35% | 1.724% | 13.67% | 37.74%
E | E,F & I | glanlee | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 29.8 | 96.4834 | 93.1519 | 0 | 3.3315 | 0 | 3.3315 | 0% | 3.453% | 0% | 3.453%
I | E,F & I | coolroe | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 9.3333 | 10.9275 | 7.603 | 2.4518 | 0.094053 | 0.77863 | 3.3245 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | glanlee | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 12 | 38.8523 | 22.7315 | 11.2593 | 0.67462 | 4.1869 | 16.1208 | 28.98% | 1.736% | 10.78% | 41.49%
E | E,F & I | glanlee | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 29.8 | 96.4834 | 92.7811 | 0 | 3.7024 | 0 | 3.7024 | 0% | 3.837% | 0% | 3.837%
I | E,F & I | coolroe | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 9.3333 | 10.9275 | 8.5861 | 1.7349 | 0.080202 | 0.52642 | 2.3415 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | glanlee | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 12 | 38.8523 | 20.5895 | 12.0549 | 0.67023 | 5.5377 | 18.2629 | 31.03% | 1.725% | 14.25% | 47.01%
E | E,F & I | glanlee | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 29.8 | 96.4834 | 92.7355 | 0 | 3.748 | 0 | 3.748 | 0% | 3.885% | 0% | 3.885%
I | E,F & I | coolroe | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 9.3333 | 10.9275 | 7.9668 | 1.7349 | 0.080202 | 1.1456 | 2.9607 | 15.88% | 0.7339% | 10.48% | 27.09%
I | E,F & I | coolroe | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 4.6667 | 5.4638 | 4.0757 | 1.0693 | 0.1033 | 0.21543 | 1.3881 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | glanlee | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 12 | 38.8523 | 28.0503 | 6.3031 | 0.63818 | 3.8607 | 10.802 | 16.22% | 1.643% | 9.937% | 27.8%
E | E,F & I | glanlee | 2030 | 100% ECP | Grandfathering | IE wind not priority | 36 | 116.5571 | 71.4554 | 31.0957 | 1.9751 | 12.0309 | 45.1017 | 26.68% | 1.695% | 10.32% | 38.69%
E | E,F & I | glanlee | 2030 | 100% ECP | Grandfathering | IE wind priority | 29.8 | 96.4834 | 92.9455 | 0 | 3.5379 | 0 | 3.5379 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | coolroe | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 14 | 16.3913 | 10.6916 | 5.2019 | 0.35979 | 0.13805 | 5.6997 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | glanlee | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 36 | 116.5571 | 74.795 | 31.0957 | 1.9751 | 8.6913 | 41.7621 | 26.68% | 1.695% | 7.457% | 35.83%
E | E,F & I | glanlee | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 29.8 | 96.4834 | 92.9455 | 0 | 3.5379 | 0 | 3.5379 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | coolroe | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 14 | 16.3913 | 10.5453 | 5.2019 | 0.35979 | 0.28441 | 5.8461 | 31.74% | 2.195% | 1.735% | 35.67%
I | E,F & I | coolroe | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.6667 | 5.4638 | 4.4528 | 0.75707 | 0.10156 | 0.15237 | 1.011 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | glanlee | 2035 | 66% ECP | Grandfathering | IE wind not priority | 24 | 77.7047 | 38.4177 | 12.4064 | 0.23816 | 26.6424 | 39.2869 | 15.97% | 0.3065% | 34.29% | 50.56%
E | E,F & I | glanlee | 2035 | 66% ECP | Grandfathering | IE wind priority | 29.8 | 96.4834 | 95.66 | 0 | 0.82337 | 0 | 0.82337 | 0% | 0.8534% | 0% | 0.8534%
I | E,F & I | coolroe | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 4.6667 | 5.4638 | 3.9443 | 1.2437 | 0.11614 | 0.15962 | 1.5194 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | glanlee | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 24 | 77.7047 | 46.6323 | 12.4064 | 0.23816 | 18.4278 | 31.0724 | 15.97% | 0.3065% | 23.72% | 39.99%
E | E,F & I | glanlee | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 29.8 | 96.4834 | 93.5934 | 0 | 2.89 | 0 | 2.89 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | knockearagh | 2035 | 100% ECP | Grandfathering | IE wind priority | 9.35 | 30.2725 | 29.9766 | 0 | 0.29584 | 0 | 0.29584 | 0% | 0.9773% | 0% | 0.9773%
E | E,F & I | knockearagh | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 4.99 | 5.8423 | 3.9649 | 1.3157 | 0.052727 | 0.50909 | 1.8775 | 22.52% | 0.9025% | 8.714% | 32.14%
H2 | H2 & K | lodgewood | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 109 | 127.6183 | 93.4575 | 28.7392 | 1.1518 | 4.2698 | 34.1608 | 22.52% | 0.9025% | 3.346% | 26.77%
E | E,F & I | tralee | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 45.0666 | 52.7645 | 41.5641 | 7.3111 | 0.98082 | 2.9084 | 11.2003 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | tralee | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 15 | 48.5655 | 46.8885 | 0 | 1.6769 | 0 | 1.6769 | 0% | 3.453% | 0% | 3.453%
H2 | H2 & K | lodgewood | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 72.6666 | 85.0788 | 62.3259 | 19.0892 | 0.73227 | 2.9314 | 22.7529 | 22.44% | 0.8607% | 3.445% | 26.74%
E | E,F & I | tralee | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 45.0666 | 52.7645 | 40.3168 | 8.8707 | 0.99772 | 2.5793 | 12.4476 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | tralee | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 15 | 48.5655 | 46.7019 | 0 | 1.8636 | 0 | 1.8636 | 0% | 3.837% | 0% | 3.837%
H2 | H2 & K | lodgewood | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 72.6666 | 85.0788 | 69.8799 | 13.5071 | 0.62443 | 1.0673 | 15.1988 | 15.88% | 0.7339% | 1.254% | 17.86%
E | E,F & I | tralee | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 45.0666 | 52.7645 | 39.3597 | 10.3268 | 0.99763 | 2.0804 | 13.4048 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | tralee | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 15 | 48.5655 | 46.6789 | 0 | 1.8866 | 0 | 1.8866 | 0% | 3.885% | 0% | 3.885%
H2 | H2 & K | lodgewood | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 72.6666 | 85.0788 | 67.6498 | 13.5071 | 0.62443 | 3.2974 | 17.4289 | 15.88% | 0.7339% | 3.876% | 20.49%
E | E,F & I | tralee | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 45.0666 | 52.7645 | 38.0911 | 12.0102 | 1.1216 | 1.5415 | 14.6733 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | tralee | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 15 | 48.5655 | 47.1108 | 0 | 1.4547 | 0 | 1.4547 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | tralee | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 45.0666 | 52.7645 | 43.0011 | 7.3111 | 0.98082 | 1.4715 | 9.7634 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | tralee | 2030 | 100% ECP | Grandfathering | IE wind priority | 15 | 48.5655 | 46.7847 | 0 | 1.7808 | 0 | 1.7808 | 0% | 3.667% | 0% | 3.667%
H2 | H2 & K | lodgewood | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 109 | 127.6183 | 84.1931 | 40.5003 | 2.8012 | 0.12363 | 43.4252 | 31.74% | 2.195% | 0.09687% | 34.03%
E | E,F & I | tralee | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 115.4 | 135.1115 | 86.9231 | 42.8783 | 2.9657 | 2.3444 | 48.1884 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | tralee | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 15 | 48.5655 | 46.7847 | 0 | 1.7808 | 0 | 1.7808 | 0% | 3.667% | 0% | 3.667%
H2 | H2 & K | lodgewood | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 109 | 127.6183 | 82.6985 | 40.5003 | 2.8012 | 1.6182 | 44.9198 | 31.74% | 2.195% | 1.268% | 35.2%
E | E,F & I | tralee | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 115.4 | 135.1115 | 88.1295 | 42.8783 | 2.9657 | 1.1379 | 46.9819 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | lodgewood | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 36.3333 | 42.5394 | 35.6573 | 5.8943 | 0.79075 | 0.197 | 6.8821 | 13.86% | 1.859% | 0.4631% | 16.18%
E | E,F & I | tralee | 2035 | 66% ECP | Grandfathering | IE wind priority | 15 | 48.5655 | 48.151 | 0 | 0.41445 | 0 | 0.41445 | 0% | 0.8534% | 0% | 0.8534%
H2 | H2 & K | lodgewood | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 36.3333 | 42.5394 | 30.4505 | 9.6828 | 0.90427 | 1.5019 | 12.0889 | 22.76% | 2.126% | 3.531% | 28.42%
E | E,F & I | tralee | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 80.2333 | 93.9379 | 68.4863 | 14.9136 | 0.68945 | 9.8485 | 25.4516 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | tralee | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 15 | 48.5655 | 48.151 | 0 | 0.41445 | 0 | 0.41445 | 0% | 0.8534% | 0% | 0.8534%
H2 | H2 & K | lodgewood | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 36.3333 | 42.5394 | 31.9197 | 8.3256 | 0.8043 | 1.4898 | 10.6197 | 19.57% | 1.891% | 3.502% | 24.96%
E | E,F & I | tralee | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 80.2333 | 93.9379 | 73.8095 | 14.9136 | 0.68945 | 4.5253 | 20.1284 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | tralee | 2030 | 33% ECP | Grandfathering | IE wind priority | 15 | 48.5655 | 47.1108 | 0 | 1.4547 | 0 | 1.4547 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | tralee | 2030 | Initial | Grandfathering | IE Solar not priority | 9.9 | 11.591 | 8.7295 | 0.95864 | 0.14935 | 1.7535 | 2.8615 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | tralee | 2030 | Initial | Grandfathering | IE wind priority | 15 | 48.5655 | 47.2695 | 0 | 1.2959 | 0 | 1.2959 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | reamore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 26.8 | 86.7703 | 45.9832 | 26.9227 | 1.4968 | 12.3676 | 40.7871 | 31.03% | 1.725% | 14.25% | 47.01%
H2 | H2 & K | rosspile | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 95 | 111.227 | 88.4414 | 17.6584 | 0.81635 | 4.3108 | 22.7855 | 15.88% | 0.7339% | 3.876% | 20.49%
E | E,F & I | reamore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 57.85 | 187.3008 | 180.025 | 0 | 7.2758 | 0 | 7.2758 | 0% | 3.885% | 0% | 3.885%
E | E,F & I | reamore | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 26.8 | 86.7703 | 62.6458 | 14.077 | 1.4253 | 8.6223 | 24.1246 | 16.22% | 1.643% | 9.937% | 27.8%
E | E,F & I | reamore | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 57.85 | 187.3008 | 181.6906 | 0 | 5.6103 | 0 | 5.6103 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | reamore | 2030 | 100% ECP | Grandfathering | IE wind not priority | 29.8 | 96.4834 | 59.1492 | 25.7404 | 1.635 | 9.9589 | 37.3342 | 26.68% | 1.695% | 10.32% | 38.69%
H2 | H2 & K | rosspile | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 95 | 111.227 | 73.3793 | 35.2984 | 2.4414 | 0.10775 | 37.8476 | 31.74% | 2.195% | 0.09687% | 34.03%
E | E,F & I | reamore | 2030 | 100% ECP | Grandfathering | IE wind priority | 57.85 | 187.3008 | 180.4329 | 0 | 6.868 | 0 | 6.868 | 0% | 3.667% | 0% | 3.667%
E | E,F & I | reamore | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 29.8 | 96.4834 | 61.9136 | 25.7404 | 1.635 | 7.1945 | 34.5698 | 26.68% | 1.695% | 7.457% | 35.83%
H2 | H2 & K | rosspile | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 95 | 111.227 | 72.0767 | 35.2984 | 2.4414 | 1.4104 | 39.1502 | 31.74% | 2.195% | 1.268% | 35.2%
E | E,F & I | reamore | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 57.85 | 187.3008 | 180.4329 | 0 | 6.868 | 0 | 6.868 | 0% | 3.667% | 0% | 3.667%
H2 | H2 & K | rosspile | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 95 | 111.227 | 93.2325 | 15.4118 | 2.0676 | 0.51509 | 17.9944 | 13.86% | 1.859% | 0.4631% | 16.18%
E | E,F & I | tralee | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 15 | 48.5655 | 47.7248 | 0 | 0.84069 | 0 | 0.84069 | 0% | 1.731% | 0% | 1.731%
H2 | H2 & K | rosspile | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 95 | 111.227 | 79.6182 | 25.3174 | 2.3644 | 3.9269 | 31.6087 | 22.76% | 2.126% | 3.531% | 28.42%
E | E,F & I | reamore | 2035 | 66% ECP | Grandfathering | IE wind priority | 57.85 | 187.3008 | 185.7025 | 0 | 1.5984 | 0 | 1.5984 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | reamore | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 28.3 | 91.6268 | 54.9873 | 14.6292 | 0.28083 | 21.7295 | 36.6395 | 15.97% | 0.3065% | 23.72% | 39.99%
H2 | H2 & K | rosspile | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 95 | 111.227 | 83.4599 | 21.7687 | 2.103 | 3.8953 | 27.767 | 19.57% | 1.891% | 3.502% | 24.96%
E | E,F & I | reamore | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 57.85 | 187.3008 | 185.7025 | 0 | 1.5984 | 0 | 1.5984 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | reamore | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 28.3 | 91.6268 | 53.2808 | 26.7986 | 0.55347 | 10.994 | 38.346 | 29.25% | 0.604% | 12% | 41.85%
H2 | H2 & K | rosspile | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 95 | 111.227 | 87.4692 | 18.6993 | 2.1032 | 2.9553 | 23.7577 | 16.81% | 1.891% | 2.657% | 21.36%
E | E,F & I | reamore | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 57.85 | 187.3008 | 184.0586 | 0 | 3.2422 | 0 | 3.2422 | 0% | 1.731% | 0% | 1.731%
E | E,F & I | reamore | 2035 | 100% ECP | Grandfathering | IE wind not priority | 29.8 | 96.4834 | 48.8894 | 17.0493 | 0.32178 | 30.2229 | 47.594 | 17.67% | 0.3335% | 31.32% | 49.33%
H2 | H2 & K | rosspile | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 95 | 111.227 | 89.7137 | 15.4118 | 2.0676 | 4.0339 | 21.5133 | 13.86% | 1.859% | 3.627% | 19.34%
E | E,F & I | reamore | 2035 | 100% ECP | Grandfathering | IE wind priority | 57.85 | 187.3008 | 185.4704 | 0 | 1.8304 | 0 | 1.8304 | 0% | 0.9773% | 0% | 0.9773%
H2 | H2 & K | rosspile | 2030 | Initial | Grandfathering | IE Solar not priority | 95 | 111.227 | 92.7514 | 9.1991 | 1.4332 | 7.8433 | 18.4755 | 8.271% | 1.289% | 7.052% | 16.61%
E | E,F & I | reamore | 2035 | 66% ECP | Grandfathering | IE wind not priority | 28.3 | 91.6268 | 45.3009 | 14.6292 | 0.28083 | 31.4158 | 46.3259 | 15.97% | 0.3065% | 34.29% | 50.56%
H2 | H2 & K | lodgewood | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 36.3333 | 42.5394 | 33.4531 | 7.1516 | 0.80438 | 1.1303 | 9.0863 | 16.81% | 1.891% | 2.657% | 21.36%
E | E,F & I | tralee | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 80.2333 | 93.9379 | 65.359 | 21.077 | 0.80852 | 6.6934 | 28.5789 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | tralee | 2035 | 100% ECP | Grandfathering | IE wind priority | 15 | 48.5655 | 48.0909 | 0 | 0.47461 | 0 | 0.47461 | 0% | 0.9773% | 0% | 0.9773%
E | E,F & I | trien | 2035 | 66% ECP | Grandfathering | IE wind priority | 47.2 | 152.8194 | 151.5152 | 0 | 1.3041 | 0 | 1.3041 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | trien | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 6.6 | 21.3688 | 12.8239 | 3.4118 | 0.065495 | 5.0676 | 8.5449 | 15.97% | 0.3065% | 23.72% | 39.99%
H2 | H2 & K | kilvinoge | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 46.2 | 130.687 | 94.8249 | 29.9558 | 2.414 | 3.4923 | 35.8621 | 22.92% | 1.847% | 2.672% | 27.44%
E | E,F & I | trien | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 47.2 | 152.8194 | 151.5152 | 0 | 1.3041 | 0 | 1.3041 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | trien | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 6.6 | 21.3688 | 12.4259 | 6.2498 | 0.12908 | 2.564 | 8.9429 | 29.25% | 0.604% | 12% | 41.85%
H2 | H2 & K | kilvinoge | 2030 | 33% ECP | Grandfathering | IE wind not priority | 46.2 | 130.687 | 100.5233 | 21.3485 | 2.3408 | 6.4744 | 30.1637 | 16.34% | 1.791% | 4.954% | 23.08%
E | E,F & I | trien | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 47.2 | 152.8194 | 150.174 | 0 | 2.6454 | 0 | 2.6454 | 0% | 1.731% | 0% | 1.731%
E | E,F & I | trien | 2035 | 100% ECP | Grandfathering | IE wind not priority | 6.6 | 21.3688 | 10.8278 | 3.776 | 0.071267 | 6.6937 | 10.541 | 17.67% | 0.3335% | 31.32% | 49.33%
E | E,F & I | trien | 2035 | 100% ECP | Grandfathering | IE wind priority | 47.2 | 152.8194 | 151.3259 | 0 | 1.4934 | 0 | 1.4934 | 0% | 0.9773% | 0% | 0.9773%
F | E,F & I | ballylickey | 2030 | Initial | Grandfathering | IE wind not priority | 5.82 | 18.8354 | 9.6853 | 2.1289 | 0.3084 | 6.7128 | 9.1501 | 11.3% | 1.637% | 35.64% | 48.58%
H2 | H2 & K | kilvinoge | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 46.2 | 130.687 | 81.8112 | 39.5581 | 2.4922 | 6.8255 | 48.8757 | 30.27% | 1.907% | 5.223% | 37.4%
H2 | H2 & K | kilkenny | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 208 | 243.5285 | 178.341 | 54.8417 | 2.1979 | 8.1479 | 65.1875 | 22.52% | 0.9025% | 3.346% | 26.77%
F | E,F & I | ballylickey | 2030 | 33% ECP | Grandfathering | IE wind not priority | 5.82 | 18.8354 | 12.4905 | 2.8812 | 0.30872 | 3.155 | 6.3449 | 15.3% | 1.639% | 16.75% | 33.69%
H2 | H2 & K | kilkenny | 2035 | 100% ECP | Grandfathering | IE wind not priority | 46.2 | 130.6871 | 97.0675 | 23.514 | 0.46793 | 9.6377 | 33.6197 | 17.99% | 0.3581% | 7.375% | 25.73%
F | E,F & I | ballylickey | 2030 | 33% ECP | Grandfathering | IE wind priority | 51.45 | 166.5087 | 161.6042 | 0 | 4.9044 | 0 | 4.9044 | 0% | 2.945% | 0% | 2.945%
F | E,F & I | ballylickey | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 5.82 | 18.8354 | 11.9422 | 4.0002 | 0.31897 | 2.5739 | 6.8931 | 21.24% | 1.693% | 13.67% | 36.6%
H2 | H2 & K | kilkenny | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 142.6665 | 167.0354 | 122.3646 | 37.478 | 1.4377 | 5.7552 | 44.6708 | 22.44% | 0.8607% | 3.445% | 26.74%
F | E,F & I | ballylickey | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 51.45 | 166.5087 | 160.926 | 0 | 5.5827 | 0 | 5.5827 | 0% | 3.353% | 0% | 3.353%
F | E,F & I | ballylickey | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 5.82 | 18.8354 | 11.2658 | 5.2243 | 0.31557 | 2.0298 | 7.5696 | 27.74% | 1.675% | 10.78% | 40.19%
H2 | H2 & K | kilkenny | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 30.8 | 87.1247 | 54.2336 | 27.0083 | 0.58654 | 5.2963 | 32.8911 | 31% | 0.6732% | 6.079% | 37.75%
F | E,F & I | ballylickey | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 51.45 | 166.5087 | 160.3775 | 0 | 6.1312 | 0 | 6.1312 | 0% | 3.682% | 0% | 3.682%
F | E,F & I | ballylickey | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 5.82 | 18.8354 | 10.2539 | 5.5823 | 0.31452 | 2.6846 | 8.5815 | 29.64% | 1.67% | 14.25% | 45.56%
H2 | H2 & K | kilkenny | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 142.6665 | 167.0354 | 137.1955 | 26.5186 | 1.226 | 2.0954 | 29.8399 | 15.88% | 0.7339% | 1.254% | 17.86%
F | E,F & I | ballylickey | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 51.45 | 166.5087 | 160.3111 | 0 | 6.1976 | 0 | 6.1976 | 0% | 3.722% | 0% | 3.722%
F | E,F & I | ballylickey | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 5.82 | 18.8354 | 13.7738 | 2.8812 | 0.30872 | 1.8717 | 5.0615 | 15.3% | 1.639% | 9.937% | 26.87%
H2 | H2 & K | kilkenny | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 30.8 | 87.1247 | 69.1963 | 14.1391 | 0.28635 | 3.5029 | 17.9283 | 16.23% | 0.3287% | 4.021% | 20.58%
F | E,F & I | ballylickey | 2030 | Initial | Grandfathering | IE wind priority | 51.45 | 166.5087 | 162.1983 | 0 | 4.3103 | 0 | 4.3103 | 0% | 2.589% | 0% | 2.589%
E | E,F & I | reamore | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 57.85 | 187.3008 | 180.1136 | 0 | 7.1873 | 0 | 7.1873 | 0% | 3.837% | 0% | 3.837%
E | E,F & I | trien | 2035 | 66% ECP | Grandfathering | IE wind not priority | 6.6 | 21.3688 | 10.5649 | 3.4118 | 0.065495 | 7.3267 | 10.8039 | 15.97% | 0.3065% | 34.29% | 50.56%
H2 | H2 & K | kilvinoge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 46.2 | 130.687 | 77.115 | 42.3721 | 2.5147 | 8.6852 | 53.572 | 32.42% | 1.924% | 6.646% | 40.99%
H2 | H2 & K | lodgewood | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 36.3333 | 42.5394 | 34.3115 | 5.8943 | 0.79075 | 1.5428 | 8.2279 | 13.86% | 1.859% | 3.627% | 19.34%
E | E,F & I | tralee | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 115.4 | 135.1115 | 91.6921 | 30.4266 | 1.2194 | 11.7733 | 43.4193 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | trien | 2030 | Initial | Grandfathering | IE wind not priority | 6.6 | 21.3688 | 10.8437 | 2.5507 | 0.35871 | 7.6157 | 10.5251 | 11.94% | 1.679% | 35.64% | 49.25%
H2 | H2 & K | kilvinoge | 2035 | 100% ECP | Grandfathering | IE wind not priority | 138.6 | 392.0613 | 291.2024 | 70.542 | 1.4038 | 28.9131 | 100.859 | 17.99% | 0.3581% | 7.375% | 25.73%
E | E,F & I | trien | 2030 | Initial | Grandfathering | IE wind priority | 47.2 | 152.8194 | 148.7415 | 0 | 4.0779 | 0 | 4.0779 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | trien | 2030 | 33% ECP | Grandfathering | IE wind not priority | 6.6 | 21.3688 | 13.9717 | 3.4667 | 0.351 | 3.5794 | 7.3971 | 16.22% | 1.643% | 16.75% | 34.62%
H2 | H2 & K | kilvinoge | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 92.3999 | 261.374 | 162.7007 | 81.0248 | 1.7596 | 15.8888 | 98.6733 | 31% | 0.6732% | 6.079% | 37.75%
E | E,F & I | trien | 2030 | 33% ECP | Grandfathering | IE wind priority | 47.2 | 152.8194 | 148.2419 | 0 | 4.5774 | 0 | 4.5774 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | trien | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 6.6 | 21.3688 | 13.3045 | 4.7758 | 0.36833 | 2.9201 | 8.0643 | 22.35% | 1.724% | 13.67% | 37.74%
H2 | H2 & K | kilvinoge | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 92.3999 | 261.374 | 207.589 | 42.4172 | 0.85906 | 10.5087 | 53.785 | 16.23% | 0.3287% | 4.021% | 20.58%
E | E,F & I | trien | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 47.2 | 152.8194 | 147.5426 | 0 | 5.2767 | 0 | 5.2767 | 0% | 3.453% | 0% | 3.453%
E | E,F & I | trien | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 6.6 | 21.3688 | 12.5024 | 6.1926 | 0.37104 | 2.3028 | 8.8664 | 28.98% | 1.736% | 10.78% | 41.49%
E | E,F & I | trien | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 47.2 | 152.8194 | 146.9552 | 0 | 5.8641 | 0 | 5.8641 | 0% | 3.837% | 0% | 3.837%
E | E,F & I | trien | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 6.6 | 21.3688 | 11.3242 | 6.6302 | 0.36863 | 3.0457 | 10.0446 | 31.03% | 1.725% | 14.25% | 47.01%
E | E,F & I | trien | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 47.2 | 152.8194 | 146.883 | 0 | 5.9364 | 0 | 5.9364 | 0% | 3.885% | 0% | 3.885%
E | E,F & I | trien | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 6.6 | 21.3688 | 15.4277 | 3.4667 | 0.351 | 2.1234 | 5.9411 | 16.22% | 1.643% | 9.937% | 27.8%
H2 | H2 & K | kilvinoge | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 138.6 | 392.0613 | 274.8204 | 107.804 | 7.165 | 2.272 | 117.241 | 27.5% | 1.828% | 0.5795% | 29.9%
E | E,F & I | trien | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 47.2 | 152.8194 | 148.2419 | 0 | 4.5774 | 0 | 4.5774 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | trien | 2030 | 100% ECP | Grandfathering | IE wind not priority | 6.6 | 21.3688 | 13.1002 | 5.7009 | 0.36211 | 2.2057 | 8.2687 | 26.68% | 1.695% | 10.32% | 38.69%
H2 | H2 & K | kilvinoge | 2030 | 100% ECP | Grandfathering | IE wind not priority | 138.6 | 392.0613 | 268.4347 | 107.804 | 7.165 | 8.6576 | 123.6267 | 27.5% | 1.828% | 2.208% | 31.53%
E | E,F & I | trien | 2030 | 100% ECP | Grandfathering | IE wind priority | 47.2 | 152.8194 | 147.2158 | 0 | 5.6036 | 0 | 5.6036 | 0% | 3.667% | 0% | 3.667%
E | E,F & I | trien | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 6.6 | 21.3688 | 13.7124 | 5.7009 | 0.36211 | 1.5934 | 7.6564 | 26.68% | 1.695% | 7.457% | 35.83%
H2 | H2 & K | kilvinoge | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 46.2 | 130.687 | 105.7802 | 21.3485 | 2.3408 | 1.2175 | 24.9068 | 16.34% | 1.791% | 0.9316% | 19.06%
E | E,F & I | trien | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 47.2 | 152.8194 | 147.2158 | 0 | 5.6036 | 0 | 5.6036 | 0% | 3.667% | 0% | 3.667%
H2 | H2 & K | kilvinoge | 2035 | 66% ECP | Grandfathering | IE wind not priority | 92.3999 | 261.374 | 202.1 | 42.4172 | 0.85906 | 15.9977 | 59.274 | 16.23% | 0.3287% | 6.121% | 22.68%
H2 | H2 & K | rosspile | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 95 | 111.227 | 91.3569 | 17.6584 | 0.81635 | 1.3953 | 19.8701 | 15.88% | 0.7339% | 1.254% | 17.86%
E | E,F & I | reamore | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 26.8 | 86.7703 | 50.7672 | 25.1458 | 1.5066 | 9.3507 | 36.0031 | 28.98% | 1.736% | 10.78% | 41.49%
E | E,F & I | reamore | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 57.85 | 187.3008 | 180.8335 | 0 | 6.4673 | 0 | 6.4673 | 0% | 3.453% | 0% | 3.453%
E | E,F & I | mallow | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 27 | 87.4178 | 50.8332 | 25.5675 | 0.52805 | 10.4889 | 36.5845 | 29.25% | 0.604% | 12% | 41.85%
H2 | H2 & K | waterford | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 9.99 | 11.6964 | 7.7164 | 3.7119 | 0.25674 | 0.01133 | 3.98 | 31.74% | 2.195% | 0.09687% | 34.03%
E | E,F & I | mallow | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.0323 | 1.3003 | 0.049882 | 0.41295 | 1.7632 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | mallow | 2035 | 100% ECP | Grandfathering | IE wind not priority | 40.5 | 131.1268 | 66.4436 | 23.1711 | 0.43732 | 41.0748 | 64.6832 | 17.67% | 0.3335% | 31.32% | 49.33%
H2 | H2 & K | waterford | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 14.28 | 40.3942 | 38.839 | 0 | 1.5552 | 0 | 1.5552 | 0% | 3.85% | 0% | 3.85%
E | E,F & I | mallow | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 3.9331 | 1.3051 | 0.052305 | 0.50501 | 1.8624 | 22.52% | 0.9025% | 8.714% | 32.14%
H2 | H2 & K | waterford | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 9.99 | 11.6964 | 7.5794 | 3.7119 | 0.25674 | 0.14831 | 4.117 | 31.74% | 2.195% | 1.268% | 35.2%
E | E,F & I | oughtragh | 2030 | Initial | Grandfathering | IE wind priority | 9 | 29.1393 | 28.3617 | 0 | 0.77756 | 0 | 0.77756 | 0% | 2.668% | 0% | 2.668%
H2 | H2 & K | waterford | 2030 | 100% ECP | Grandfathering | IE wind priority | 14.28 | 40.3942 | 38.839 | 0 | 1.5552 | 0 | 1.5552 | 0% | 3.85% | 0% | 3.85%
E | E,F & I | oughtragh | 2030 | Initial | Grandfathering | IE Solar not priority | 4 | 4.6832 | 3.5271 | 0.38733 | 0.060344 | 0.70849 | 1.1562 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | oughtragh | 2030 | 33% ECP | Grandfathering | IE wind priority | 9 | 29.1393 | 28.2665 | 0 | 0.87281 | 0 | 0.87281 | 0% | 2.995% | 0% | 2.995%
H2 | H2 & K | waterford | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 5.99 | 7.0131 | 5.8786 | 0.97175 | 0.13036 | 0.032478 | 1.1346 | 13.86% | 1.859% | 0.4631% | 16.18%
E | E,F & I | mallow | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.5537 | 0.9201 | 0.042536 | 0.27919 | 1.2418 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | oughtragh | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 5.8 | 6.7907 | 5.3492 | 0.94093 | 0.12623 | 0.3743 | 1.4415 | 13.86% | 1.859% | 5.512% | 21.23%
H2 | H2 & K | waterford | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 14.28 | 40.3942 | 39.1126 | 0 | 1.2816 | 0 | 1.2816 | 0% | 3.173% | 0% | 3.173%
E | E,F & I | oughtragh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 5.8 | 6.7907 | 5.1887 | 1.1416 | 0.12841 | 0.33195 | 1.602 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | oughtragh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 9 | 29.1393 | 28.0211 | 0 | 1.1182 | 0 | 1.1182 | 0% | 3.837% | 0% | 3.837%
H2 | H2 & K | waterford | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 5.99 | 7.0131 | 5.0201 | 1.5963 | 0.14908 | 0.2476 | 1.993 | 22.76% | 2.126% | 3.531% | 28.42%
E | E,F & I | oughtragh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 5.8 | 6.7907 | 5.0655 | 1.329 | 0.12839 | 0.26775 | 1.7252 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | oughtragh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 9 | 29.1393 | 28.0074 | 0 | 1.1319 | 0 | 1.1319 | 0% | 3.885% | 0% | 3.885%
H2 | H2 & K | waterford | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 14.28 | 40.3942 | 38.7146 | 0 | 1.6796 | 0 | 1.6796 | 0% | 4.158% | 0% | 4.158%
E | E,F & I | oughtragh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 5.8 | 6.7907 | 4.9023 | 1.5457 | 0.14435 | 0.19839 | 1.8884 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | oughtragh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 9 | 29.1393 | 28.2665 | 0 | 0.87281 | 0 | 0.87281 | 0% | 2.995% | 0% | 2.995%
H2 | H2 & K | waterford | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 5.99 | 7.0131 | 5.2624 | 1.3726 | 0.1326 | 0.24561 | 1.7508 | 19.57% | 1.891% | 3.502% | 24.96%
E | E,F & I | oughtragh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 5.8 | 6.7907 | 5.5342 | 0.94093 | 0.12623 | 0.18937 | 1.2565 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | oughtragh | 2030 | 100% ECP | Grandfathering | IE wind priority | 9 | 29.1393 | 28.0708 | 0 | 1.0685 | 0 | 1.0685 | 0% | 3.667% | 0% | 3.667%
H2 | H2 & K | waterford | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 14.28 | 40.3942 | 38.7377 | 0 | 1.6565 | 0 | 1.6565 | 0% | 4.101% | 0% | 4.101%
E | E,F & I | oughtragh | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 9.4 | 11.0056 | 7.0804 | 3.4927 | 0.24157 | 0.19096 | 3.9252 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | oughtragh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 9 | 29.1393 | 28.1331 | 0 | 1.0062 | 0 | 1.0062 | 0% | 3.453% | 0% | 3.453%
E | E,F & I | oughtragh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 9 | 29.1393 | 28.0708 | 0 | 1.0685 | 0 | 1.0685 | 0% | 3.667% | 0% | 3.667%
E | E,F & I | mallow | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.2253 | 0.9201 | 0.042536 | 0.6076 | 1.5702 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | mallow | 2030 | Initial | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.3648 | 0.47932 | 0.074676 | 0.87675 | 1.4308 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | mallow | 2030 | 33% ECP | Grandfathering | IE wind not priority | 13.5 | 43.7089 | 28.5785 | 7.091 | 0.71795 | 7.3214 | 15.1304 | 16.22% | 1.643% | 16.75% | 34.62%
H2 | H2 & K | waterford | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 9.99 | 11.6964 | 8.5655 | 2.634 | 0.10556 | 0.39134 | 3.1309 | 22.52% | 0.9025% | 3.346% | 26.77%
E | E,F & I | mallow | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.5653 | 0.80304 | 0.10773 | 0.31945 | 1.2302 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | mallow | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 13.5 | 43.7089 | 27.2137 | 9.7688 | 0.75341 | 5.973 | 16.4952 | 22.35% | 1.724% | 13.67% | 37.74%
H2 | H2 & K | waterford | 2035 | 100% ECP | Grandfathering | IE wind priority | 14.28 | 40.3942 | 40.0086 | 0 | 0.38557 | 0 | 0.38557 | 0% | 0.9545% | 0% | 0.9545%
E | E,F & I | mallow | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.4283 | 0.97433 | 0.10959 | 0.2833 | 1.3672 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | mallow | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 13.5 | 43.7089 | 25.573 | 12.6667 | 0.75895 | 4.7102 | 18.1359 | 28.98% | 1.736% | 10.78% | 41.49%
H2 | H2 & K | waterford | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 7.99 | 9.3548 | 6.853 | 2.0989 | 0.080516 | 0.32232 | 2.5018 | 22.44% | 0.8607% | 3.445% | 26.74%
E | E,F & I | mallow | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.3232 | 1.1343 | 0.10958 | 0.22851 | 1.4723 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | mallow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 13.5 | 43.7089 | 23.1632 | 13.5618 | 0.75401 | 6.2299 | 20.5457 | 31.03% | 1.725% | 14.25% | 47.01%
E | E,F & I | mallow | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 27 | 87.4178 | 52.4613 | 13.9572 | 0.26793 | 20.7313 | 34.9564 | 15.97% | 0.3065% | 23.72% | 39.99%
H2 | H2 & K | waterford | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 14.28 | 40.3942 | 39.6514 | 0 | 0.74284 | 0 | 0.74284 | 0% | 1.839% | 0% | 1.839%
E | E,F & I | mallow | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 13.5 | 43.7089 | 31.5566 | 7.091 | 0.71795 | 4.3433 | 12.1523 | 16.22% | 1.643% | 9.937% | 27.8%
H2 | H2 & K | waterford | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 7.99 | 9.3548 | 7.6836 | 1.4852 | 0.068659 | 0.11735 | 1.6712 | 15.88% | 0.7339% | 1.254% | 17.86%
E | E,F & I | mallow | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.7231 | 0.80304 | 0.10773 | 0.16162 | 1.0724 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | mallow | 2030 | 100% ECP | Grandfathering | IE wind not priority | 40.5 | 131.1268 | 80.3873 | 34.9827 | 2.222 | 13.5347 | 50.7394 | 26.68% | 1.695% | 10.32% | 38.69%
H2 | H2 & K | waterford | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 14.28 | 40.3942 | 40.0424 | 0 | 0.35183 | 0 | 0.35183 | 0% | 0.871% | 0% | 0.871%
E | E,F & I | mallow | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 3.7285 | 1.8392 | 0.12721 | 0.10056 | 2.067 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | mallow | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 40.5 | 131.1268 | 84.1444 | 34.9827 | 2.222 | 9.7777 | 46.9824 | 26.68% | 1.695% | 7.457% | 35.83%
H2 | H2 & K | waterford | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 7.99 | 9.3548 | 7.4384 | 1.4852 | 0.068659 | 0.36256 | 1.9164 | 15.88% | 0.7339% | 3.876% | 20.49%
E | E,F & I | mallow | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 3.7803 | 1.8392 | 0.12721 | 0.04881 | 2.0153 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | waterford | 2035 | 66% ECP | Grandfathering | IE wind priority | 14.28 | 40.3942 | 40.0424 | 0 | 0.35183 | 0 | 0.35183 | 0% | 0.871% | 0% | 0.871%
E | E,F & I | mallow | 2035 | 66% ECP | Grandfathering | IE wind not priority | 27 | 87.4178 | 43.2199 | 13.9572 | 0.26793 | 29.9727 | 44.1978 | 15.97% | 0.3065% | 34.29% | 50.56%
E | E,F & I | mallow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.1838 | 1.3192 | 0.1232 | 0.16931 | 1.6117 | 22.76% | 2.126% | 2.921% | 27.81%
H2 | H2 & K | waterford | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 5.99 | 7.0131 | 5.5152 | 1.179 | 0.13261 | 0.18634 | 1.498 | 16.81% | 1.891% | 2.657% | 21.36%
E | E,F & I | pollagh | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 128 | 149.8637 | 96.4138 | 47.56 | 3.2895 | 2.6003 | 53.4499 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | pollagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 50 | 161.8849 | 103.8819 | 43.1885 | 2.7432 | 12.0712 | 58.003 | 26.68% | 1.695% | 7.457% | 35.83%
H2 | H2 & K | tullabeg | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 185 | 216.5999 | 140.3599 | 68.7391 | 4.7544 | 2.7465 | 76.2399 | 31.74% | 2.195% | 1.268% | 35.2%
E | E,F & I | pollagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 128 | 149.8637 | 97.752 | 47.56 | 3.2895 | 1.2622 | 52.1117 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | tullabeg | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 95 | 111.2269 | 93.2325 | 15.4118 | 2.0675 | 0.51509 | 17.9944 | 13.86% | 1.859% | 0.4631% | 16.18%
E | E,F & I | pollagh | 2035 | 66% ECP | Grandfathering | IE wind not priority | 33.3333 | 107.9232 | 53.358 | 17.2311 | 0.33078 | 37.0033 | 54.5652 | 15.97% | 0.3065% | 34.29% | 50.56%
H2 | H2 & K | tullabeg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 95 | 111.2269 | 79.6182 | 25.3174 | 2.3644 | 3.9269 | 31.6087 | 22.76% | 2.126% | 3.531% | 28.42%
E | E,F & I | pollagh | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 85.3332 | 99.909 | 72.8396 | 15.8616 | 0.73328 | 10.4745 | 27.0694 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | pollagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 33.3333 | 107.9232 | 64.7671 | 17.2311 | 0.33078 | 25.5942 | 43.1561 | 15.97% | 0.3065% | 23.72% | 39.99%
H2 | H2 & K | tullabeg | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 95 | 111.2269 | 83.4599 | 21.7687 | 2.103 | 3.8953 | 27.767 | 19.57% | 1.891% | 3.502% | 24.96%
E | E,F & I | pollagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 85.3332 | 99.909 | 78.5012 | 15.8616 | 0.73328 | 4.813 | 21.4078 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | pollagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 33.3333 | 107.9232 | 62.7571 | 31.5649 | 0.65191 | 12.9493 | 45.1661 | 29.25% | 0.604% | 12% | 41.85%
H2 | H2 & K | tullabeg | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 185 | 216.5999 | 142.8966 | 68.7391 | 4.7544 | 0.20982 | 73.7033 | 31.74% | 2.195% | 0.09687% | 34.03%
H2 | H2 & K | tullabeg | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 95 | 111.2269 | 87.4692 | 18.6993 | 2.1032 | 2.9553 | 23.7577 | 16.81% | 1.891% | 2.657% | 21.36%
E | E,F & I | pollagh | 2035 | 100% ECP | Grandfathering | IE wind not priority | 50 | 161.8849 | 82.0292 | 28.6063 | 0.5399 | 50.7096 | 79.8558 | 17.67% | 0.3335% | 31.32% | 49.33%
H2 | H2 & K | tullabeg | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 95 | 111.2269 | 89.7136 | 15.4118 | 2.0675 | 4.0339 | 21.5133 | 13.86% | 1.859% | 3.627% | 19.34%
E | E,F & I | pollagh | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 128 | 149.8637 | 101.7036 | 33.7488 | 1.3525 | 13.0588 | 48.1601 | 22.52% | 0.9025% | 8.714% | 32.14%
H2 | H2 & K | tullabeg | 2030 | Initial | Grandfathering | IE Solar not priority | 50 | 58.5405 | 48.8165 | 4.8416 | 0.7543 | 4.128 | 9.724 | 8.271% | 1.289% | 7.052% | 16.61%
E | E,F & I | reamore | 2030 | Initial | Grandfathering | IE wind not priority | 25.3 | 81.9138 | 41.5674 | 9.7779 | 1.3751 | 29.1934 | 40.3464 | 11.94% | 1.679% | 35.64% | 49.25%
E | E,F & I | reamore | 2030 | Initial | Grandfathering | IE wind priority | 57.85 | 187.3008 | 182.3029 | 0 | 4.998 | 0 | 4.998 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | reamore | 2030 | 33% ECP | Grandfathering | IE wind not priority | 26.8 | 86.7703 | 56.7337 | 14.077 | 1.4253 | 14.5344 | 30.0366 | 16.22% | 1.643% | 16.75% | 34.62%
H2 | H2 & K | rosspile | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 95 | 111.227 | 81.4538 | 25.0479 | 1.0038 | 3.7214 | 29.7731 | 22.52% | 0.9025% | 3.346% | 26.77%
E | E,F & I | reamore | 2030 | 33% ECP | Grandfathering | IE wind priority | 57.85 | 187.3008 | 181.6906 | 0 | 5.6103 | 0 | 5.6103 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | reamore | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 26.8 | 86.7703 | 54.0243 | 19.3928 | 1.4957 | 11.8576 | 32.746 | 22.35% | 1.724% | 13.67% | 37.74%
H2 | H2 & K | rosspile | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 95 | 111.227 | 81.4812 | 24.9561 | 0.95733 | 3.8323 | 29.7458 | 22.44% | 0.8607% | 3.445% | 26.74%
E | E,F & I | pollagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 85.3332 | 99.909 | 69.5135 | 22.4167 | 0.85991 | 7.1189 | 30.3955 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | oughtragh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 9.4 | 11.0056 | 7.1787 | 3.4927 | 0.24157 | 0.09269 | 3.827 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | pollagh | 2030 | 100% ECP | Grandfathering | IE wind not priority | 50 | 161.8849 | 99.2436 | 43.1885 | 2.7432 | 16.7095 | 62.6413 | 26.68% | 1.695% | 10.32% | 38.69%
H2 | H2 & K | waterford | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 14.28 | 40.3942 | 38.9334 | 0 | 1.4608 | 0 | 1.4608 | 0% | 3.616% | 0% | 3.616%
E | E,F & I | oughtragh | 2035 | 66% ECP | Grandfathering | IE wind priority | 9 | 29.1393 | 28.8906 | 0 | 0.24867 | 0 | 0.24867 | 0% | 0.8534% | 0% | 0.8534%
H2 | H2 & K | waterford | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 5.99 | 7.0131 | 5.6567 | 0.97175 | 0.13036 | 0.25435 | 1.3565 | 13.86% | 1.859% | 3.627% | 19.34%
E | E,F & I | oughtragh | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 7.6 | 8.8982 | 6.4873 | 1.4127 | 0.065308 | 0.93289 | 2.4109 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | oughtragh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 9 | 29.1393 | 28.8906 | 0 | 0.24867 | 0 | 0.24867 | 0% | 0.8534% | 0% | 0.8534%
H2 | H2 & K | waterford | 2030 | 33% ECP | Grandfathering | IE wind priority | 14.28 | 40.3942 | 39.1126 | 0 | 1.2816 | 0 | 1.2816 | 0% | 3.173% | 0% | 3.173%
E | E,F & I | oughtragh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 7.6 | 8.8982 | 6.9915 | 1.4127 | 0.065308 | 0.42865 | 1.9066 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | oughtragh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 9 | 29.1393 | 28.6349 | 0 | 0.50441 | 0 | 0.50441 | 0% | 1.731% | 0% | 1.731%
H2 | H2 & K | waterford | 2030 | Initial | Grandfathering | IE Solar not priority | 3.99 | 4.6715 | 3.8956 | 0.38636 | 0.060193 | 0.32942 | 0.77597 | 8.271% | 1.289% | 7.052% | 16.61%
E | E,F & I | oughtragh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 7.6 | 8.8982 | 6.191 | 1.9965 | 0.076586 | 0.63403 | 2.7071 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | oughtragh | 2035 | 100% ECP | Grandfathering | IE wind priority | 9 | 29.1393 | 28.8545 | 0 | 0.28477 | 0 | 0.28477 | 0% | 0.9773% | 0% | 0.9773%
H2 | H2 & K | waterford | 2030 | Initial | Grandfathering | IE wind priority | 14.28 | 40.3942 | 39.2595 | 0 | 1.1347 | 0 | 1.1347 | 0% | 2.809% | 0% | 2.809%
E | E,F & I | oughtragh | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 9.4 | 11.0056 | 7.4689 | 2.4784 | 0.099326 | 0.95901 | 3.5368 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | pollagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 42.6666 | 49.9545 | 40.7111 | 6.9218 | 0.92858 | 1.3931 | 9.2435 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | pollagh | 2030 | 33% ECP | Grandfathering | IE wind not priority | 16.6667 | 53.9616 | 35.2821 | 8.7543 | 0.88636 | 9.0388 | 18.6795 | 16.22% | 1.643% | 16.75% | 34.62%
H2 | H2 & K | tullabeg | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 185 | 216.5999 | 158.6206 | 48.7775 | 1.9548 | 7.247 | 57.9793 | 22.52% | 0.9025% | 3.346% | 26.77%
E | E,F & I | pollagh | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 42.6666 | 49.9545 | 39.3506 | 6.9218 | 0.92858 | 2.7535 | 10.6039 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | pollagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 16.6667 | 53.9616 | 33.5972 | 12.0602 | 0.93013 | 7.3741 | 20.3644 | 22.35% | 1.724% | 13.67% | 37.74%
H2 | H2 & K | tullabeg | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 139.9999 | 163.9133 | 120.0774 | 36.7774 | 1.4108 | 5.6476 | 43.8359 | 22.44% | 0.8607% | 3.445% | 26.74%
E | E,F & I | pollagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 42.6666 | 49.9545 | 38.1698 | 8.3983 | 0.94459 | 2.4419 | 11.7848 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | pollagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 16.6667 | 53.9616 | 31.5716 | 15.6379 | 0.93697 | 5.8151 | 22.39 | 28.98% | 1.736% | 10.78% | 41.49%
H2 | H2 & K | tullabeg | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 139.9999 | 163.9133 | 134.6311 | 26.0229 | 1.203 | 2.0562 | 29.2822 | 15.88% | 0.7339% | 1.254% | 17.86%
E | E,F & I | pollagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 42.6666 | 49.9545 | 37.2636 | 9.7768 | 0.9445 | 1.9696 | 12.6909 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | pollagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 16.6667 | 53.9616 | 28.5965 | 16.7429 | 0.93087 | 7.6913 | 25.3651 | 31.03% | 1.725% | 14.25% | 47.01%
H2 | H2 & K | tullabeg | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 139.9999 | 163.9133 | 130.3346 | 26.0229 | 1.203 | 6.3527 | 33.5787 | 15.88% | 0.7339% | 3.876% | 20.49%
E | E,F & I | pollagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 42.6666 | 49.9545 | 36.0626 | 11.3706 | 1.0619 | 1.4594 | 13.8919 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | pollagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 16.6667 | 53.9616 | 38.9588 | 8.7543 | 0.88636 | 5.3621 | 15.0028 | 16.22% | 1.643% | 9.937% | 27.8%
E | E,F & I | dromada | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 28.5 | 92.2744 | 91.487 | 0 | 0.78745 | 0 | 0.78745 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | dromada | 2035 | 66% ECP | Grandfathering | IE wind priority | 28.5 | 92.2744 | 91.487 | 0 | 0.78745 | 0 | 0.78745 | 0% | 0.8534% | 0% | 0.8534%
I | E,F & I | kilbarry | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 56.5 | 66.1507 | 48.2278 | 10.5021 | 0.48551 | 6.9353 | 17.9229 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | athea | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 34.35 | 111.2149 | 107.8837 | 0 | 3.3312 | 0 | 3.3312 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | athea | 2030 | 100% ECP | Grandfathering | IE wind not priority | 23.15 | 74.9527 | 45.9498 | 19.9963 | 1.2701 | 7.7365 | 29.0029 | 26.68% | 1.695% | 10.32% | 38.69%
J | J City, G South | crakenstown | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 572 | 732.8962 | 564.1022 | 161.1483 | 6.6418 | 1.0038 | 168.7939 | 21.99% | 0.9062% | 0.137% | 23.03%
E | E,F & I | athea | 2030 | 100% ECP | Grandfathering | IE wind priority | 34.35 | 111.2149 | 107.1369 | 0 | 4.078 | 0 | 4.078 | 0% | 3.667% | 0% | 3.667%
E | E,F & I | athea | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 23.15 | 74.9527 | 48.0973 | 19.9963 | 1.2701 | 5.589 | 26.8554 | 26.68% | 1.695% | 7.457% | 35.83%
J | J City, G South | crakenstown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 381.333 | 488.597 | 376.9713 | 107.3479 | 4.1744 | 0.10331 | 111.6256 | 21.97% | 0.8544% | 0.02114% | 22.85%
E | E,F & I | athea | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 34.35 | 111.2149 | 107.1369 | 0 | 4.078 | 0 | 4.078 | 0% | 3.667% | 0% | 3.667%
J | J City, G South | crakenstown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 381.333 | 488.597 | 410.1242 | 74.8436 | 3.5227 | 0.10638 | 78.4727 | 15.32% | 0.721% | 0.02177% | 16.06%
E | E,F & I | athea | 2035 | 66% ECP | Grandfathering | IE wind not priority | 23.15 | 74.9527 | 37.0571 | 11.967 | 0.22973 | 25.6988 | 37.8956 | 15.97% | 0.3065% | 34.29% | 50.56%
J | J City, G South | crakenstown | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 381.333 | 488.597 | 409.5165 | 74.8436 | 3.5227 | 0.7141 | 79.0805 | 15.32% | 0.721% | 0.1462% | 16.19%
E | E,F & I | athea | 2035 | 66% ECP | Grandfathering | IE wind priority | 34.35 | 111.2149 | 110.2659 | 0 | 0.94908 | 0 | 0.94908 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | athea | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 23.15 | 74.9527 | 44.9808 | 11.967 | 0.22973 | 17.7752 | 29.9719 | 15.97% | 0.3065% | 23.72% | 39.99%
E | E,F & I | athea | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 34.35 | 111.2149 | 110.2659 | 0 | 0.94908 | 0 | 0.94908 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | athea | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 23.15 | 74.9527 | 43.5848 | 21.9218 | 0.45275 | 8.9933 | 31.3679 | 29.25% | 0.604% | 12% | 41.85%
J | J City, G South | crakenstown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 572 | 732.8962 | 451.3981 | 231.2829 | 16.1471 | 34.0681 | 281.4981 | 31.56% | 2.203% | 4.648% | 38.41%
E | E,F & I | athea | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 34.35 | 111.2149 | 109.2898 | 0 | 1.9252 | 0 | 1.9252 | 0% | 1.731% | 0% | 1.731%
E | E,F & I | athea | 2035 | 100% ECP | Grandfathering | IE wind not priority | 23.15 | 74.9527 | 37.9795 | 13.2447 | 0.24998 | 23.4785 | 36.9732 | 17.67% | 0.3335% | 31.32% | 49.33%
J | J City, G South | crakenstown | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 572 | 732.8962 | 456.1884 | 231.2829 | 16.1471 | 29.2778 | 276.7078 | 31.56% | 2.203% | 3.995% | 37.76%
E | E,F & I | athea | 2035 | 100% ECP | Grandfathering | IE wind priority | 34.35 | 111.2149 | 110.1281 | 0 | 1.0869 | 0 | 1.0869 | 0% | 0.9773% | 0% | 0.9773%
J | J City, G South | crakenstown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 190.6665 | 244.2985 | 205.2823 | 33.1969 | 4.5242 | 1.2952 | 39.0162 | 13.59% | 1.852% | 0.5302% | 15.97%
E | E,F & I | ballyvouskil 220 | 2030 | Initial | Grandfathering | IE wind not priority | 42 | 135.9833 | 69.0052 | 16.232 | 2.2827 | 48.4634 | 66.9781 | 11.94% | 1.679% | 35.64% | 49.25%
J | J City, G South | crakenstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 190.6665 | 244.2985 | 183.3727 | 55.0699 | 5.1161 | 0.73973 | 60.9258 | 22.54% | 2.094% | 0.3028% | 24.94%
E | E,F & I | ballyvouskil 220 | 2030 | Initial | Grandfathering | IE Solar not priority | 12.5 | 14.6351 | 11.0221 | 1.2104 | 0.18857 | 2.214 | 3.613 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP | Grandfathering | IE wind not priority | 82.8 | 268.0813 | 175.2816 | 43.4915 | 4.4034 | 44.9047 | 92.7997 | 16.22% | 1.643% | 16.75% | 34.62%
E | E,F & I | athea | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 23.15 | 74.9527 | 54.1138 | 12.1598 | 1.2312 | 7.448 | 20.8389 | 16.22% | 1.643% | 9.937% | 27.8%
E | E,F & I | athea | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 34.35 | 111.2149 | 106.8947 | 0 | 4.3202 | 0 | 4.3202 | 0% | 3.885% | 0% | 3.885%
J | J City, G South | dunstown | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 230.5998 | 295.4645 | 248.1365 | 40.1496 | 5.4717 | 1.7066 | 47.328 | 13.59% | 1.852% | 0.5776% | 16.02%
J | J City, G South | dunstown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 461.1995 | 590.929 | 455.9244 | 129.8309 | 5.0487 | 0.12494 | 135.0046 | 21.97% | 0.8544% | 0.02114% | 22.85%
E | D and E North | rathkeale | 2035 | 66% ECP | Grandfathering | IE wind priority | 27.5 | 89.0367 | 88.2769 | 0 | 0.75982 | 0 | 0.75982 | 0% | 0.8534% | 0% | 0.8534%
J | J City, G South | dunstown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 461.1995 | 590.929 | 496.0209 | 90.5189 | 4.2605 | 0.12866 | 94.9081 | 15.32% | 0.721% | 0.02177% | 16.06%
E | D and E North | rathkeale | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 36 | 42.1491 | 34.5721 | 6.6916 | 0.30935 | 0.5761 | 7.5771 | 15.88% | 0.7339% | 1.367% | 17.98%
E | D and E North | rathkeale | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 27.5 | 89.0367 | 88.2769 | 0 | 0.75982 | 0 | 0.75982 | 0% | 0.8534% | 0% | 0.8534%
J | J City, G South | dunstown | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 461.1995 | 590.929 | 495.2859 | 90.5189 | 4.2605 | 0.86366 | 95.6431 | 15.32% | 0.721% | 0.1462% | 16.19%
E | D and E North | rathkeale | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 36 | 42.1491 | 35.1477 | 6.6916 | 0.30935 | 0.00043271 | 7.0014 | 15.88% | 0.7339% | 0.001027% | 16.61%
E | D and E North | rathkeale | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 27.5 | 89.0367 | 87.4954 | 0 | 1.5413 | 0 | 1.5413 | 0% | 1.731% | 0% | 1.731%
E | D and E North | rathkeale | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 36 | 42.1491 | 31.9602 | 9.4571 | 0.36278 | 0.36911 | 10.1889 | 22.44% | 0.8607% | 0.8757% | 24.17%
E | D and E North | rathkeale | 2035 | 100% ECP | Grandfathering | IE wind priority | 27.5 | 89.0367 | 88.1666 | 0 | 0.87012 | 0 | 0.87012 | 0% | 0.9773% | 0% | 0.9773%
J | J City, G South | dunstown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 691.8 | 886.3943 | 545.9391 | 279.7229 | 19.529 | 41.2033 | 340.4552 | 31.56% | 2.203% | 4.648% | 38.41%
E | D and E North | rathkeale | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 54 | 63.2237 | 47.5562 | 14.2378 | 0.5706 | 0.85922 | 15.6676 | 22.52% | 0.9025% | 1.359% | 24.78%
J | J City, G South | crakenstown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 190.6665 | 244.2985 | 191.5897 | 47.3418 | 4.5208 | 0.84614 | 52.7088 | 19.38% | 1.851% | 0.3464% | 21.58%
E | E,F & I | athea | 2030 | Initial | Grandfathering | IE wind not priority | 23.15 | 74.9527 | 38.035 | 8.9469 | 1.2582 | 26.7126 | 36.9177 | 11.94% | 1.679% | 35.64% | 49.25%
J | J City, G South | dunstown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 230.5998 | 295.4645 | 248.2767 | 40.1496 | 5.4717 | 1.5664 | 47.1878 | 13.59% | 1.852% | 0.5302% | 15.97%
E | E,F & I | athea | 2030 | Initial | Grandfathering | IE wind priority | 34.35 | 111.2149 | 108.2472 | 0 | 2.9677 | 0 | 2.9677 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | athea | 2030 | 33% ECP | Grandfathering | IE wind not priority | 23.15 | 74.9527 | 49.0069 | 12.1598 | 1.2312 | 12.5549 | 25.9458 | 16.22% | 1.643% | 16.75% | 34.62%
J | J City, G South | dunstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 230.5998 | 295.4645 | 221.7784 | 66.6038 | 6.1876 | 0.89465 | 73.6861 | 22.54% | 2.094% | 0.3028% | 24.94%
E | E,F & I | athea | 2030 | 33% ECP | Grandfathering | IE wind priority | 34.35 | 111.2149 | 107.8837 | 0 | 3.3312 | 0 | 3.3312 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | athea | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 23.15 | 74.9527 | 46.6665 | 16.7516 | 1.292 | 10.2426 | 28.2862 | 22.35% | 1.724% | 13.67% | 37.74%
J | J City, G South | dunstown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 230.5998 | 295.4645 | 231.7163 | 57.2571 | 5.4676 | 1.0234 | 63.7481 | 19.38% | 1.851% | 0.3464% | 21.58%
E | E,F & I | athea | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 34.35 | 111.2149 | 107.3748 | 0 | 3.8402 | 0 | 3.8402 | 0% | 3.453% | 0% | 3.453%
E | E,F & I | athea | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 23.15 | 74.9527 | 43.853 | 21.7211 | 1.3015 | 8.0772 | 31.0997 | 28.98% | 1.736% | 10.78% | 41.49%
J | J City, G South | dunstown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 230.5998 | 295.4645 | 240.4275 | 48.973 | 5.5129 | 0.55107 | 55.037 | 16.57% | 1.866% | 0.1865% | 18.63%
E | E,F & I | athea | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 34.35 | 111.2149 | 106.9473 | 0 | 4.2676 | 0 | 4.2676 | 0% | 3.837% | 0% | 3.837%
E | E,F & I | athea | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 23.15 | 74.9527 | 39.7206 | 23.256 | 1.293 | 10.6832 | 35.2321 | 31.03% | 1.725% | 14.25% | 47.01%
J | J City, G South | dunstown | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 691.8 | 886.3943 | 551.7328 | 279.7229 | 19.529 | 35.4097 | 334.6616 | 31.56% | 2.203% | 3.995% | 37.76%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 12.5 | 14.6351 | 11.5285 | 2.0279 | 0.27205 | 0.80669 | 3.1066 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 82.8 | 268.0813 | 166.9108 | 59.915 | 4.6209 | 36.6345 | 101.1705 | 22.35% | 1.724% | 13.67% | 37.74%
J | J City, G South | crakenstown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 190.6665 | 244.2985 | 198.7923 | 40.4923 | 4.5582 | 0.45564 | 45.5061 | 16.57% | 1.866% | 0.1865% | 18.63%
E | E,F & I | boggeragh | 2030 | Initial | Grandfathering | IE wind not priority | 23.35 | 75.6003 | 38.3636 | 9.0242 | 1.2691 | 26.9433 | 37.2367 | 11.94% | 1.679% | 35.64% | 49.25%
J | J City, G South | arodstown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 310.3997 | 397.7111 | 306.8494 | 87.3797 | 3.3979 | 0.08409 | 90.8617 | 21.97% | 0.8544% | 0.02114% | 22.85%
E | E,F & I | boggeragh | 2030 | Initial | Grandfathering | IE wind priority | 142.7 | 462.0195 | 449.6909 | 0 | 12.3286 | 0 | 12.3286 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | boggeragh | 2030 | 33% ECP | Grandfathering | IE wind not priority | 23.35 | 75.6003 | 49.4303 | 12.2648 | 1.2418 | 12.6634 | 26.17 | 16.22% | 1.643% | 16.75% | 34.62%
J | J City, G South | arodstown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 310.3997 | 397.7111 | 333.8354 | 60.9217 | 2.8674 | 0.086592 | 63.8757 | 15.32% | 0.721% | 0.02177% | 16.06%
E | E,F & I | boggeragh | 2030 | 33% ECP | Grandfathering | IE wind priority | 142.7 | 462.0195 | 448.1806 | 0 | 13.839 | 0 | 13.839 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | boggeragh | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 8.0667 | 9.4445 | 7.4397 | 1.3086 | 0.17556 | 0.52058 | 2.0048 | 13.86% | 1.859% | 5.512% | 21.23%
J | J City, G South | arodstown | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 310.3997 | 397.7111 | 333.3407 | 60.9217 | 2.8674 | 0.58127 | 64.3704 | 15.32% | 0.721% | 0.1462% | 16.19%
E | E,F & I | boggeragh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 23.35 | 75.6003 | 47.0697 | 16.8963 | 1.3031 | 10.3311 | 28.5306 | 22.35% | 1.724% | 13.67% | 37.74%
E | E,F & I | boggeragh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 142.7 | 462.0195 | 446.0664 | 0 | 15.9532 | 0 | 15.9532 | 0% | 3.453% | 0% | 3.453%
E | E,F & I | boggeragh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 8.0667 | 9.4445 | 7.2165 | 1.5878 | 0.17859 | 0.46167 | 2.2281 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | boggeragh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 23.35 | 75.6003 | 44.2318 | 21.9088 | 1.3127 | 8.147 | 31.3684 | 28.98% | 1.736% | 10.78% | 41.49%
J | J City, G South | arodstown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 465.6 | 596.5672 | 367.4317 | 188.2611 | 13.1435 | 27.7309 | 229.1355 | 31.56% | 2.203% | 4.648% | 38.41%
E | E,F & I | boggeragh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 142.7 | 462.0195 | 444.2905 | 0 | 17.7291 | 0 | 17.7291 | 0% | 3.837% | 0% | 3.837%
J | J City, G South | arodstown | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 465.6 | 596.5672 | 371.331 | 188.2611 | 13.1435 | 23.8317 | 225.2362 | 31.56% | 2.203% | 3.995% | 37.76%
E | E,F & I | boggeragh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 23.35 | 75.6003 | 40.0637 | 23.4569 | 1.3042 | 10.7755 | 35.5365 | 31.03% | 1.725% | 14.25% | 47.01%
E | E,F & I | boggeragh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 142.7 | 462.0195 | 444.0721 | 0 | 17.9474 | 0 | 17.9474 | 0% | 3.885% | 0% | 3.885%
J | J City, G South | arodstown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 155.1998 | 198.8555 | 167.0969 | 27.0218 | 3.6826 | 1.0542 | 31.7586 | 13.59% | 1.852% | 0.5302% | 15.97%
E | E,F & I | boggeragh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 8.0667 | 9.4445 | 6.8181 | 2.1498 | 0.20076 | 0.27592 | 2.6264 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | boggeragh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 23.35 | 75.6003 | 54.5813 | 12.2648 | 1.2418 | 7.5124 | 21.019 | 16.22% | 1.643% | 9.937% | 27.8%
J | J City, G South | arodstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 155.1998 | 198.8555 | 149.2628 | 44.8262 | 4.1645 | 0.60213 | 49.5927 | 22.54% | 2.094% | 0.3028% | 24.94%
E | E,F & I | boggeragh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 142.7 | 462.0195 | 448.1806 | 0 | 13.839 | 0 | 13.839 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | boggeragh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 8.0667 | 9.4445 | 7.6969 | 1.3086 | 0.17556 | 0.26338 | 1.7476 | 13.86% | 1.859% | 2.789% | 18.5%
J | J City, G South | arodstown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 155.1998 | 198.8555 | 155.9513 | 38.5356 | 3.6799 | 0.68875 | 42.9042 | 19.38% | 1.851% | 0.3464% | 21.58%
E | E,F & I | boggeragh | 2030 | 100% ECP | Grandfathering | IE wind not priority | 23.35 | 75.6003 | 46.3468 | 20.169 | 1.2811 | 7.8034 | 29.2535 | 26.68% | 1.695% | 10.32% | 38.69%
E | E,F & I | boggeragh | 2030 | 100% ECP | Grandfathering | IE wind priority | 142.7 | 462.0195 | 445.0781 | 0 | 16.9414 | 0 | 16.9414 | 0% | 3.667% | 0% | 3.667%
J | J City, G South | arodstown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 155.1998 | 198.8555 | 161.8142 | 32.9601 | 3.7103 | 0.37089 | 37.0414 | 16.57% | 1.866% | 0.1865% | 18.63%
E | E,F & I | boggeragh | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 24.2 | 28.3336 | 18.2282 | 8.9918 | 0.62193 | 0.49163 | 10.1054 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | boggeragh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 8.0667 | 9.4445 | 7.0451 | 1.8484 | 0.17857 | 0.37238 | 2.3994 | 19.57% | 1.891% | 3.943% | 25.4%
J | J City, G South | arodstown | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 465.6 | 596.5672 | 459.1713 | 131.1725 | 5.4064 | 0.81707 | 137.3959 | 21.99% | 0.9062% | 0.137% | 23.03%
E | E,F & I | ballyvouskil 220 | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 12.5 | 14.6351 | 9.932 | 3.2958 | 0.13208 | 1.2753 | 4.7031 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 12.5 | 14.6351 | 11.1826 | 2.4604 | 0.27674 | 0.7154 | 3.4526 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 82.8 | 268.0813 | 156.8478 | 77.6893 | 4.6549 | 28.8894 | 111.2335 | 28.98% | 1.736% | 10.78% | 41.49%
J | J City, G South | crakenstown | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 190.6665 | 244.2985 | 205.1664 | 33.1969 | 4.5242 | 1.4111 | 39.1321 | 13.59% | 1.852% | 0.5776% | 16.02%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 12.5 | 14.6351 | 10.9171 | 2.8643 | 0.27671 | 0.57704 | 3.7181 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 82.8 | 268.0813 | 142.0675 | 83.179 | 4.6246 | 38.2102 | 126.0138 | 31.03% | 1.725% | 14.25% | 47.01%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 12.5 | 14.6351 | 10.5652 | 3.3312 | 0.3111 | 0.42756 | 4.0699 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 82.8 | 268.0813 | 193.5472 | 43.4915 | 4.4034 | 26.6391 | 74.534 | 16.22% | 1.643% | 9.937% | 27.8%
J | J City, G South | carrickmines 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 412 | 1656.619 | 1135.222 | 474.6549 | 10.0043 | 36.7378 | 521.397 | 28.65% | 0.6039% | 2.218% | 31.47%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 12.5 | 14.6351 | 11.9271 | 2.0279 | 0.27205 | 0.40813 | 2.708 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | ballyvouskil 220 | 2030 | 100% ECP | Grandfathering | IE wind not priority | 164.4 | 532.2776 | 326.313 | 142.0039 | 9.0197 | 54.9409 | 205.9646 | 26.68% | 1.695% | 10.32% | 38.69%
E | E,F & I | ballyvouskil 220 | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 12.5 | 14.6351 | 9.4154 | 4.6445 | 0.32124 | 0.25394 | 5.2197 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | ballyvouskil 220 | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 164.4 | 532.2776 | 341.5638 | 142.0039 | 9.0197 | 39.6902 | 190.7138 | 26.68% | 1.695% | 7.457% | 35.83%
J | J City, G South | belcamp 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 250 | 1047.3798 | 724.1763 | 293.7322 | 6.2442 | 23.2271 | 323.2034 | 28.04% | 0.5962% | 2.218% | 30.86%
E | E,F & I | ballyvouskil 220 | 2035 | 66% ECP | Grandfathering | IE wind not priority | 123.5999 | 400.1792 | 197.8514 | 63.893 | 1.2265 | 137.2083 | 202.3279 | 15.97% | 0.3065% | 34.29% | 50.56%
E | E,F & I | ballyvouskil 220 | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 12.5 | 14.6351 | 10.6699 | 2.3235 | 0.10741 | 1.5344 | 3.9652 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | ballyvouskil 220 | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 123.5999 | 400.1792 | 240.1565 | 63.893 | 1.2265 | 94.9032 | 160.0227 | 15.97% | 0.3065% | 23.72% | 39.99%
J | J City, G South | belcamp 220kv | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 250 | 1047.3798 | 659.6706 | 306.6733 | 18.9531 | 62.0827 | 387.7091 | 29.28% | 1.81% | 5.927% | 37.02%
E | E,F & I | ballyvouskil 220 | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 12.5 | 14.6351 | 11.4992 | 2.3235 | 0.10741 | 0.70502 | 3.1359 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | ballyvouskil 220 | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 123.5999 | 400.1792 | 232.7033 | 117.0425 | 2.4173 | 48.0161 | 167.4759 | 29.25% | 0.604% | 12% | 41.85%
J | J City, G South | belcamp 220kv | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 250 | 1047.3798 | 676.6354 | 284.83 | 18.5752 | 67.3392 | 370.7444 | 27.19% | 1.773% | 6.429% | 35.4%
E | E,F & I | ballyvouskil 220 | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 12.5 | 14.6351 | 10.1826 | 3.2837 | 0.12596 | 1.0428 | 4.4525 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | ballyvouskil 220 | 2035 | 100% ECP | Grandfathering | IE wind not priority | 164.4 | 532.2776 | 269.7119 | 94.0575 | 1.7752 | 166.7331 | 262.5657 | 17.67% | 0.3335% | 31.32% | 49.33%
E | E,F & I | ballyvouskil 220 | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 12.5 | 14.6351 | 9.5461 | 4.6445 | 0.32124 | 0.12326 | 5.089 | 31.74% | 2.195% | 0.8422% | 34.77%
E | D and E North | rathkeale | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 54 | 63.2237 | 41.6518 | 20.0644 | 1.3878 | 0.11977 | 21.5719 | 31.74% | 2.195% | 0.1894% | 34.12%
J | J City, G South | dunstown | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 691.8 | 886.3943 | 682.2481 | 194.8993 | 8.0329 | 1.214 | 204.1462 | 21.99% | 0.9062% | 0.137% | 23.03%
E | D and E North | rathkeale | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 27.5 | 89.0367 | 85.7719 | 0 | 3.2648 | 0 | 3.2648 | 0% | 3.667% | 0% | 3.667%
J | J City, G South | glasmore | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 4 | 5.1251 | 4.0194 | 0.99319 | 0.094842 | 0.017751 | 1.1058 | 19.38% | 1.851% | 0.3464% | 21.58%
E | D and E North | ballinknockane | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 50 | 58.5405 | 47.3731 | 9.8417 | 1.1069 | 0.21872 | 11.1674 | 16.81% | 1.891% | 0.3736% | 19.08%
E | D and E North | ballinknockane | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 50 | 58.5405 | 45.8331 | 11.4572 | 1.1068 | 0.14334 | 12.7074 | 19.57% | 1.891% | 0.2448% | 21.71%
J | J City, G South | glasmore | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 4 | 5.1251 | 4.1705 | 0.84949 | 0.095627 | 0.009559 | 0.95468 | 16.57% | 1.866% | 0.1865% | 18.63%
E | D and E North | ballinknockane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 50 | 58.5405 | 43.9033 | 13.3249 | 1.2444 | 0.067847 | 14.6372 | 22.76% | 2.126% | 0.1159% | 25%
E | D and E North | ballinknockane | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 50 | 58.5405 | 49.328 | 8.1115 | 1.0882 | 0.012847 | 9.2125 | 13.86% | 1.859% | 0.02195% | 15.74%
J | J City, G South | glasmore | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 4 | 5.1251 | 4.3042 | 0.69644 | 0.094913 | 0.029603 | 0.82095 | 13.59% | 1.852% | 0.5776% | 16.02%
E | D and E North | ballinknockane | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 50 | 58.5405 | 38.3639 | 18.5781 | 1.285 | 0.3135 | 20.1766 | 31.74% | 2.195% | 0.5355% | 34.47%
E | D and E North | ballinknockane | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 50 | 58.5405 | 38.5665 | 18.5781 | 1.285 | 0.1109 | 19.974 | 31.74% | 2.195% | 0.1894% | 34.12%
J | J City, G South | glasmore | 2030 | Initial | Grandfathering | IE Solar not priority | 4 | 5.1251 | 4.6505 | 0.40522 | 0.06628 | 0.0031171 | 0.47462 | 7.907% | 1.293% | 0.06082% | 9.261%
E | D and E North | ballinknockane | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 50 | 58.5405 | 48.0168 | 9.2939 | 0.42966 | 0.80014 | 10.5237 | 15.88% | 0.7339% | 1.367% | 17.98%
E | D and E North | ballinknockane | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 50 | 58.5405 | 48.8163 | 9.2939 | 0.42966 | 0.00060098 | 9.7242 | 15.88% | 0.7339% | 0.001027% | 16.61%
E | D and E North | ballinknockane | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 50 | 58.5405 | 49.0182 | 8.1115 | 1.0882 | 0.32264 | 9.5223 | 13.86% | 1.859% | 0.5511% | 16.27%
E | D and E North | ballinknockane | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 50 | 58.5405 | 44.3892 | 13.1348 | 0.50386 | 0.51266 | 14.1513 | 22.44% | 0.8607% | 0.8757% | 24.17%
E | D and E North | ballinknockane | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 50 | 58.5405 | 44.0335 | 13.1831 | 0.52833 | 0.79558 | 14.507 | 22.52% | 0.9025% | 1.359% | 24.78%
J | J City, G South | gallanstown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 172.2 | 220.6376 | 170.2304 | 48.4755 | 1.8851 | 0.046651 | 50.4072 | 21.97% | 0.8544% | 0.02114% | 22.85%
E | D and E North | limerick | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 1.65 | 1.9318 | 1.6176 | 0.26768 | 0.03591 | 0.010647 | 0.31424 | 13.86% | 1.859% | 0.5511% | 16.27%
E | D and E North | limerick | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 1.65 | 1.9318 | 1.5633 | 0.32478 | 0.036529 | 0.0072177 | 0.36852 | 16.81% | 1.891% | 0.3736% | 19.08%
J | J City, G South | gallanstown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 172.2 | 220.6376 | 185.2014 | 33.7974 | 1.5908 | 0.048038 | 35.4362 | 15.32% | 0.721% | 0.02177% | 16.06%
E | D and E North | limerick | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 1.65 | 1.9318 | 1.5125 | 0.37809 | 0.036526 | 0.0047301 | 0.41934 | 19.57% | 1.891% | 0.2448% | 21.71%
E | D and E North | limerick | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 1.65 | 1.9318 | 1.4488 | 0.43972 | 0.041065 | 0.002239 | 0.48303 | 22.76% | 2.126% | 0.1159% | 25%
J | J City, G South | gallanstown | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 172.2 | 220.6376 | 184.9269 | 33.7974 | 1.5908 | 0.32247 | 35.7107 | 15.32% | 0.721% | 0.1462% | 16.19%
E | D and E North | limerick | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 1.65 | 1.9318 | 1.6278 | 0.26768 | 0.03591 | 0.00042395 | 0.30401 | 13.86% | 1.859% | 0.02195% | 15.74%
E | D and E North | limerick | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 3.798 | 1.8392 | 0.12721 | 0.031037 | 1.9975 | 31.74% | 2.195% | 0.5355% | 34.47%
E | D and E North | limerick | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 3.8181 | 1.8392 | 0.12721 | 0.010979 | 1.9774 | 31.74% | 2.195% | 0.1894% | 34.12%
J | J City, G South | gallanstown | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 183 | 234.4755 | 180.4733 | 51.5562 | 2.1249 | 0.32114 | 54.0023 | 21.99% | 0.9062% | 0.137% | 23.03%
J | J City, G South | gallanstown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 183 | 234.4755 | 144.4158 | 73.9944 | 5.1659 | 10.8994 | 90.0597 | 31.56% | 2.203% | 4.648% | 38.41%
E | D and E North | ballinknockane | 2030 | Initial | Grandfathering | IE Solar not priority | 50 | 58.5405 | 52.2481 | 4.8416 | 0.7543 | 0.69646 | 6.2924 | 8.271% | 1.289% | 1.19% | 10.75%
D | D and E North | tullabrack | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 13.8 | 42.8684 | 41.2096 | 0 | 1.6588 | 0 | 1.6588 | 0% | 3.869% | 0% | 3.869%
J | J City, G South | grange | 2030 | Initial | Grandfathering | IE Solar not priority | 39.99 | 51.2387 | 46.4936 | 4.0512 | 0.66263 | 0.031163 | 4.745 | 7.907% | 1.293% | 0.06082% | 9.261%
D | D and E North | tullabrack | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 10.5 | 32.6172 | 21.6009 | 10.2547 | 0.56501 | 0.19658 | 11.0162 | 31.44% | 1.732% | 0.6027% | 33.77%
D | D and E North | tullabrack | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 13.8 | 42.8684 | 41.1889 | 0 | 1.6795 | 0 | 1.6795 | 0% | 3.918% | 0% | 3.918%
D | D and E North | tullabrack | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 10.5 | 32.6172 | 26.5309 | 5.4722 | 0.55073 | 0.063329 | 6.0862 | 16.78% | 1.688% | 0.1942% | 18.66%
D | D and E North | tullabrack | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 13.8 | 42.8684 | 41.547 | 0 | 1.3213 | 0 | 1.3213 | 0% | 3.082% | 0% | 3.082%
J | J City, G South | glasmore | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 4 | 5.1251 | 3.9448 | 1.1269 | 0.046446 | 0.0070195 | 1.1804 | 21.99% | 0.9062% | 0.137% | 23.03%
D | D and E North | tullabrack | 2030 | 100% ECP | Grandfathering | IE wind not priority | 31.5 | 97.8517 | 68.3417 | 27.0778 | 1.6597 | 0.77253 | 29.51 | 27.67% | 1.696% | 0.7895% | 30.16%
D | D and E North | tullabrack | 2030 | 100% ECP | Grandfathering | IE wind priority | 13.8 | 42.8684 | 41.2746 | 0 | 1.5937 | 0 | 1.5937 | 0% | 3.718% | 0% | 3.718%
J | J City, G South | glasmore | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 4 | 5.1251 | 3.9542 | 1.126 | 0.043788 | 0.0010836 | 1.1709 | 21.97% | 0.8544% | 0.02114% | 22.85%
D | D and E North | tullabrack | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 31.5 | 97.8517 | 68.5508 | 27.0778 | 1.6597 | 0.56349 | 29.3009 | 27.67% | 1.696% | 0.5759% | 29.94%
D | D and E North | tullabrack | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 13.8 | 42.8684 | 41.2746 | 0 | 1.5937 | 0 | 1.5937 | 0% | 3.718% | 0% | 3.718%
J | J City, G South | glasmore | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4 | 5.1251 | 4.302 | 0.78507 | 0.036952 | 0.0011159 | 0.82314 | 15.32% | 0.721% | 0.02177% | 16.06%
J | J City, G South | glasmore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 4 | 5.1251 | 3.847 | 1.1553 | 0.10733 | 0.015519 | 1.2782 | 22.54% | 2.094% | 0.3028% | 24.94%
J | J City, G South | glasmore | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 4 | 5.1251 | 4.2956 | 0.78507 | 0.036952 | 0.0074906 | 0.82952 | 15.32% | 0.721% | 0.1462% | 16.19%
D | D and E North | tullabrack | 2035 | 66% ECP | Grandfathering | IE wind not priority | 21 | 65.2344 | 51.3689 | 10.8359 | 0.20965 | 2.82 | 13.8655 | 16.61% | 0.3214% | 4.323% | 21.25%
D | D and E North | tullabrack | 2035 | 66% ECP | Grandfathering | IE wind priority | 13.8 | 42.8684 | 42.4931 | 0 | 0.37522 | 0 | 0.37522 | 0% | 0.8753% | 0% | 0.8753%
D | D and E North | tullabrack | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 21 | 65.2344 | 53.2673 | 10.8359 | 0.20965 | 0.92156 | 11.9671 | 16.61% | 0.3214% | 1.413% | 18.34%
D | D and E North | tullabrack | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 13.8 | 42.8684 | 42.4931 | 0 | 0.37522 | 0 | 0.37522 | 0% | 0.8753% | 0% | 0.8753%
J | J City, G South | glasmore | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4 | 5.1251 | 3.1566 | 1.6174 | 0.11292 | 0.23824 | 1.9685 | 31.56% | 2.203% | 4.648% | 38.41%
D | D and E North | tullabrack | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 21 | 65.2344 | 44.5126 | 19.4101 | 0.38871 | 0.92302 | 20.7218 | 29.75% | 0.5959% | 1.415% | 31.77%
D | D and E North | tullabrack | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 13.8 | 42.8684 | 42.137 | 0 | 0.73131 | 0 | 0.73131 | 0% | 1.706% | 0% | 1.706%
J | J City, G South | glasmore | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 4 | 5.1251 | 3.1901 | 1.6174 | 0.11292 | 0.20474 | 1.935 | 31.56% | 2.203% | 3.995% | 37.76%
D | D and E North | tullabrack | 2035 | 100% ECP | Grandfathering | IE wind not priority | 31.5 | 97.8517 | 73.99 | 18.0265 | 0.33469 | 5.5005 | 23.8617 | 18.42% | 0.342% | 5.621% | 24.39%
D | D and E North | tullabrack | 2035 | 100% ECP | Grandfathering | IE wind priority | 13.8 | 42.8684 | 42.4464 | 0 | 0.42195 | 0 | 0.42195 | 0% | 0.9843% | 0% | 0.9843%
J | J City, G South | glasmore | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4 | 5.1251 | 4.3066 | 0.69644 | 0.094913 | 0.027171 | 0.81852 | 13.59% | 1.852% | 0.5302% | 15.97%
E | E,F & I | boggeragh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 23.35 | 75.6003 | 48.5129 | 20.169 | 1.2811 | 5.6373 | 27.0874 | 26.68% | 1.695% | 7.457% | 35.83%
E | D and E North | limerick | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 3.3 | 3.8637 | 3.1691 | 0.6134 | 0.028357 | 0.052809 | 0.69456 | 15.88% | 0.7339% | 1.367% | 17.98%
J | J City, G South | gallanstown | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 183 | 234.4755 | 145.9484 | 73.9944 | 5.1659 | 9.3668 | 88.5271 | 31.56% | 2.203% | 3.995% | 37.76%
E | D and E North | prospect | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 63 | 203.975 | 144.9264 | 54.4176 | 3.4565 | 1.1746 | 59.0486 | 26.68% | 1.695% | 0.5759% | 28.95%
E | D and E North | prospect | 2035 | 66% ECP | Grandfathering | IE wind not priority | 42 | 135.9832 | 107.9769 | 21.7112 | 0.41679 | 5.8783 | 28.0063 | 15.97% | 0.3065% | 4.323% | 20.6%
J | J City, G South | finglas | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 164.49 | 210.7589 | 129.8085 | 66.51 | 4.6434 | 9.797 | 80.9504 | 31.56% | 2.203% | 4.648% | 38.41%
E | D and E North | prospect | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 42 | 135.9832 | 111.9342 | 21.7112 | 0.41679 | 1.921 | 24.049 | 15.97% | 0.3065% | 1.413% | 17.69%
E | D and E North | prospect | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 42 | 135.9832 | 93.466 | 39.7717 | 0.82141 | 1.9241 | 42.5172 | 29.25% | 0.604% | 1.415% | 31.27%
J | J City, G South | finglas | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 164.49 | 210.7589 | 131.1861 | 66.51 | 4.6434 | 8.4194 | 79.5728 | 31.56% | 2.203% | 3.995% | 37.76%
E | D and E North | prospect | 2035 | 100% ECP | Grandfathering | IE wind not priority | 63 | 203.975 | 155.7848 | 36.0439 | 0.68028 | 11.466 | 48.1902 | 17.67% | 0.3335% | 5.621% | 23.63%
J | J City, G South | finglas | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 110.4433 | 141.5096 | 118.9095 | 19.2292 | 2.6206 | 0.75022 | 22.6001 | 13.59% | 1.852% | 0.5302% | 15.97%
E | D and E North | rathkeale | 2030 | Initial | Grandfathering | IE wind priority | 27.5 | 89.0367 | 86.6608 | 0 | 2.3759 | 0 | 2.3759 | 0% | 2.668% | 0% | 2.668%
E | D and E North | rathkeale | 2030 | 33% ECP | Grandfathering | IE wind priority | 27.5 | 89.0367 | 86.3698 | 0 | 2.6669 | 0 | 2.6669 | 0% | 2.995% | 0% | 2.995%
J | J City, G South | finglas | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 110.4433 | 141.5096 | 106.2184 | 31.8992 | 2.9635 | 0.42848 | 35.2912 | 22.54% | 2.094% | 0.3028% | 24.94%
E | D and E North | prospect | 2030 | 100% ECP | Grandfathering | IE wind not priority | 63 | 203.975 | 144.4906 | 54.4176 | 3.4565 | 1.6104 | 59.4844 | 26.68% | 1.695% | 0.7895% | 29.16%
E | D and E North | rathkeale | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 18 | 21.0746 | 17.6465 | 2.9201 | 0.39175 | 0.11615 | 3.428 | 13.86% | 1.859% | 0.5511% | 16.27%
J | J City, G South | finglas | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 110.4433 | 141.5096 | 110.9781 | 27.4227 | 2.6187 | 0.49013 | 30.5315 | 19.38% | 1.851% | 0.3464% | 21.58%
E | D and E North | rathkeale | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 18 | 21.0746 | 17.0543 | 3.543 | 0.3985 | 0.078738 | 4.0203 | 16.81% | 1.891% | 0.3736% | 19.08%
E | D and E North | rathkeale | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 27.5 | 89.0367 | 85.6201 | 0 | 3.4166 | 0 | 3.4166 | 0% | 3.837% | 0% | 3.837%
J | J City, G South | finglas | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 110.4433 | 141.5096 | 115.1502 | 23.4551 | 2.6404 | 0.26393 | 26.3594 | 16.57% | 1.866% | 0.1865% | 18.63%
E | D and E North | rathkeale | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 18 | 21.0746 | 16.4999 | 4.1246 | 0.39846 | 0.051601 | 4.5747 | 19.57% | 1.891% | 0.2448% | 21.71%
E | D and E North | rathkeale | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 27.5 | 89.0367 | 85.578 | 0 | 3.4587 | 0 | 3.4587 | 0% | 3.885% | 0% | 3.885%
J | J City, G South | finglas | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 110.4433 | 141.5096 | 118.8423 | 19.2292 | 2.6206 | 0.81736 | 22.6672 | 13.59% | 1.852% | 0.5776% | 16.02%
E | D and E North | rathkeale | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 18 | 21.0746 | 15.8052 | 4.797 | 0.44799 | 0.024425 | 5.2694 | 22.76% | 2.126% | 0.1159% | 25%
E | D and E North | rathkeale | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 27.5 | 89.0367 | 86.3698 | 0 | 2.6669 | 0 | 2.6669 | 0% | 2.995% | 0% | 2.995%
J | J City, G South | finglas | 2030 | Initial | Grandfathering | IE Solar not priority | 83.42 | 106.885 | 96.9867 | 8.451 | 1.3823 | 0.065007 | 9.8982 | 7.907% | 1.293% | 0.06082% | 9.261%
E | D and E North | rathkeale | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 18 | 21.0746 | 17.7581 | 2.9201 | 0.39175 | 0.0046249 | 3.3165 | 13.86% | 1.859% | 0.02195% | 15.74%
E | D and E North | rathkeale | 2030 | 100% ECP | Grandfathering | IE wind priority | 27.5 | 89.0367 | 85.7719 | 0 | 3.2648 | 0 | 3.2648 | 0% | 3.667% | 0% | 3.667%
E | D and E North | rathkeale | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 54 | 63.2237 | 41.433 | 20.0644 | 1.3878 | 0.33858 | 21.7907 | 31.74% | 2.195% | 0.5355% | 34.47%
E | D and E North | rathkeale | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 27.5 | 89.0367 | 85.9623 | 0 | 3.0744 | 0 | 3.0744 | 0% | 3.453% | 0% | 3.453%
E | D and E North | limerick | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 3.3 | 3.8637 | 3.2219 | 0.6134 | 0.028357 | 3.9665e-05 | 0.64179 | 15.88% | 0.7339% | 0.001027% | 16.61%
J | J City, G South | finglas | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 137.4666 | 176.1342 | 147.6265 | 26.9804 | 1.2699 | 0.25743 | 28.5077 | 15.32% | 0.721% | 0.1462% | 16.19%
E | D and E North | prospect | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 21 | 67.9916 | 45.3128 | 21.0961 | 1.1729 | 0.40979 | 22.6788 | 31.03% | 1.725% | 0.6027% | 33.36%
E | D and E North | limerick | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 3.3 | 3.8637 | 2.9297 | 0.8669 | 0.033254 | 0.033835 | 0.93399 | 22.44% | 0.8607% | 0.8757% | 24.17%
E | D and E North | limerick | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.3593 | 1.3051 | 0.052305 | 0.078762 | 1.4362 | 22.52% | 0.9025% | 1.359% | 24.78%
J | J City, G South | gallanstown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 161.4 | 206.7997 | 173.7723 | 28.1013 | 3.8297 | 1.0964 | 33.0274 | 13.59% | 1.852% | 0.5302% | 15.97%
E | D and E North | moneypoint | 2030 | Initial | Grandfathering | IE wind priority | 17.25 | 55.8503 | 54.36 | 0 | 1.4903 | 0 | 1.4903 | 0% | 2.668% | 0% | 2.668%
J | J City, G South | gallanstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 161.4 | 206.7997 | 155.2258 | 46.6169 | 4.3308 | 0.62618 | 51.5739 | 22.54% | 2.094% | 0.3028% | 24.94%
E | D and E North | moneypoint | 2030 | 33% ECP | Grandfathering | IE wind priority | 17.25 | 55.8503 | 54.1774 | 0 | 1.6729 | 0 | 1.6729 | 0% | 2.995% | 0% | 2.995%
E | D and E North | moneypoint | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 17.25 | 55.8503 | 53.9218 | 0 | 1.9285 | 0 | 1.9285 | 0% | 3.453% | 0% | 3.453%
J | J City, G South | gallanstown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 161.4 | 206.7997 | 162.1815 | 40.0751 | 3.8269 | 0.71626 | 44.6182 | 19.38% | 1.851% | 0.3464% | 21.58%
E | D and E North | moneypoint | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 17.25 | 55.8503 | 53.7072 | 0 | 2.1431 | 0 | 2.1431 | 0% | 3.837% | 0% | 3.837%
E | D and E North | moneypoint | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 17.25 | 55.8503 | 53.6808 | 0 | 2.1695 | 0 | 2.1695 | 0% | 3.885% | 0% | 3.885%
J | J City, G South | gallanstown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 161.4 | 206.7997 | 168.2786 | 34.2769 | 3.8586 | 0.3857 | 38.5211 | 16.57% | 1.866% | 0.1865% | 18.63%
E | D and E North | moneypoint | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 17.25 | 55.8503 | 54.1774 | 0 | 1.6729 | 0 | 1.6729 | 0% | 2.995% | 0% | 2.995%
E | D and E North | moneypoint | 2030 | 100% ECP | Grandfathering | IE wind priority | 17.25 | 55.8503 | 53.8024 | 0 | 2.0479 | 0 | 2.0479 | 0% | 3.667% | 0% | 3.667%
E | D and E North | prospect | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 21 | 67.9916 | 55.7123 | 11.0304 | 1.1168 | 0.13201 | 12.2793 | 16.22% | 1.643% | 0.1942% | 18.06%
J | J City, G South | gallanstown | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 161.4 | 206.7997 | 173.6742 | 28.1013 | 3.8297 | 1.1945 | 33.1255 | 13.59% | 1.852% | 0.5776% | 16.02%
J | J City, G South | gallanstown | 2030 | Initial | Grandfathering | IE Solar not priority | 150.6 | 192.9618 | 175.0923 | 15.2567 | 2.4954 | 0.11736 | 17.8695 | 7.907% | 1.293% | 0.06082% | 9.261%
E | D and E North | moneypoint | 2035 | 66% ECP | Grandfathering | IE wind priority | 17.25 | 55.8503 | 55.3737 | 0 | 0.47661 | 0 | 0.47661 | 0% | 0.8534% | 0% | 0.8534%
E | D and E North | moneypoint | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 17.25 | 55.8503 | 55.3737 | 0 | 0.47661 | 0 | 0.47661 | 0% | 0.8534% | 0% | 0.8534%
E | D and E North | moneypoint | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 17.25 | 55.8503 | 54.8835 | 0 | 0.96679 | 0 | 0.96679 | 0% | 1.731% | 0% | 1.731%
E | D and E North | moneypoint | 2035 | 100% ECP | Grandfathering | IE wind priority | 17.25 | 55.8503 | 55.3045 | 0 | 0.5458 | 0 | 0.5458 | 0% | 0.9773% | 0% | 0.9773%
J | J City, G South | finglas | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 164.49 | 210.7589 | 162.2188 | 46.3414 | 1.91 | 0.28866 | 48.5401 | 21.99% | 0.9062% | 0.137% | 23.03%
E | D and E North | prospect | 2030 | 33% ECP | Grandfathering | IE wind not priority | 21 | 67.9916 | 55.2931 | 11.0304 | 1.1168 | 0.55123 | 12.6985 | 16.22% | 1.643% | 0.8107% | 18.68%
J | J City, G South | finglas | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 137.4666 | 176.1342 | 135.8943 | 38.6978 | 1.5048 | 0.037241 | 40.2399 | 21.97% | 0.8544% | 0.02114% | 22.85%
E | D and E North | prospect | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 21 | 67.9916 | 51.2965 | 15.1958 | 1.172 | 0.3273 | 16.6951 | 22.35% | 1.724% | 0.4814% | 24.55%
E | D and E North | prospect | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 21 | 67.9916 | 46.9198 | 19.7038 | 1.1806 | 0.18746 | 21.0718 | 28.98% | 1.736% | 0.2757% | 30.99%
J | J City, G South | finglas | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 137.4666 | 176.1342 | 147.8456 | 26.9804 | 1.2699 | 0.038349 | 28.2886 | 15.32% | 0.721% | 0.02177% | 16.06%
E | D and E North | moneypoint | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 17.25 | 55.8503 | 53.8024 | 0 | 2.0479 | 0 | 2.0479 | 0% | 3.667% | 0% | 3.667%
F | E,F & I | ballylickey | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 51.45 | 166.5087 | 161.6042 | 0 | 4.9044 | 0 | 4.9044 | 0% | 2.945% | 0% | 2.945%
H1 | H1 | timoney | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 166.56 | 195.0101 | 134.168 | 30.9599 | 1.4313 | 28.451 | 60.8421 | 15.88% | 0.7339% | 14.59% | 31.2%
E | E,F & I | boggeragh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 24.2 | 28.3336 | 18.4812 | 8.9918 | 0.62193 | 0.23863 | 9.8524 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | coomagearlahy | 2030 | Initial | Grandfathering | IE wind priority | 81 | 262.2536 | 255.2555 | 0 | 6.998 | 0 | 6.998 | 0% | 2.668% | 0% | 2.668%
I | E,F & I | lysaghtstown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 166.3333 | 194.7446 | 135.4971 | 43.6951 | 1.6762 | 13.8763 | 59.2476 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | coomagearlahy | 2030 | Initial | Grandfathering | IE Solar not priority | 7 | 8.1957 | 6.1724 | 0.67783 | 0.1056 | 1.2399 | 2.0233 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | coomagearlahy | 2030 | 33% ECP | Grandfathering | IE wind priority | 81 | 262.2536 | 254.3982 | 0 | 7.8553 | 0 | 7.8553 | 0% | 2.995% | 0% | 2.995%
I | E,F & I | lysaghtstown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 166.3333 | 194.7446 | 153.0161 | 30.9177 | 1.4293 | 9.3815 | 41.7286 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | coomagearlahy | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 7 | 8.1957 | 6.456 | 1.1356 | 0.15235 | 0.45175 | 1.7397 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | coomagearlahy | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 81 | 262.2536 | 253.1982 | 0 | 9.0554 | 0 | 9.0554 | 0% | 3.453% | 0% | 3.453%
I | E,F & I | lysaghtstown | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 166.3333 | 194.7446 | 141.9805 | 30.9177 | 1.4293 | 20.4171 | 52.7642 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | coomagearlahy | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 7 | 8.1957 | 6.2622 | 1.3778 | 0.15497 | 0.40062 | 1.9334 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | coomagearlahy | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 81 | 262.2536 | 252.1901 | 0 | 10.0634 | 0 | 10.0634 | 0% | 3.837% | 0% | 3.837%
E | E,F & I | coomagearlahy | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 7 | 8.1957 | 6.1136 | 1.604 | 0.15496 | 0.32314 | 2.0821 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | coomagearlahy | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 81 | 262.2536 | 252.0662 | 0 | 10.1874 | 0 | 10.1874 | 0% | 3.885% | 0% | 3.885%
I | E,F & I | lysaghtstown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 206 | 241.1869 | 157.3196 | 76.5419 | 5.2941 | 2.0313 | 83.8672 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | coomagearlahy | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 7 | 8.1957 | 5.9165 | 1.8655 | 0.17422 | 0.23943 | 2.2791 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | coomagearlahy | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 81 | 262.2536 | 254.3982 | 0 | 7.8553 | 0 | 7.8553 | 0% | 2.995% | 0% | 2.995%
I | E,F & I | lysaghtstown | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 206 | 241.1869 | 155.166 | 76.5419 | 5.2941 | 4.1849 | 86.0209 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | coomagearlahy | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 7 | 8.1957 | 6.6792 | 1.1356 | 0.15235 | 0.22855 | 1.5165 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | coomagearlahy | 2030 | 100% ECP | Grandfathering | IE wind priority | 81 | 262.2536 | 252.6372 | 0 | 9.6163 | 0 | 9.6163 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | lysaghtstown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 126.6666 | 148.3026 | 120.861 | 20.5491 | 2.7567 | 4.1357 | 27.4415 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | coomagearlahy | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 7 | 8.1957 | 5.2726 | 2.6009 | 0.1799 | 0.14221 | 2.923 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | coomagearlahy | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 81 | 262.2536 | 252.6372 | 0 | 9.6163 | 0 | 9.6163 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | lysaghtstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 126.6666 | 148.3026 | 107.0609 | 33.7565 | 3.1525 | 4.3326 | 41.2416 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | coomagearlahy | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 7 | 8.1957 | 5.3458 | 2.6009 | 0.1799 | 0.069025 | 2.8499 | 31.74% | 2.195% | 0.8422% | 34.77%
I | E,F & I | lysaghtstown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 126.6666 | 148.3026 | 110.6263 | 29.025 | 2.804 | 5.8473 | 37.6763 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | coomagearlahy | 2035 | 66% ECP | Grandfathering | IE wind priority | 81 | 262.2536 | 260.0155 | 0 | 2.238 | 0 | 2.238 | 0% | 0.8534% | 0% | 0.8534%
I | E,F & I | lysaghtstown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 126.6666 | 148.3026 | 113.3165 | 24.9324 | 2.8043 | 7.2494 | 34.986 | 16.81% | 1.891% | 4.888% | 23.59%
I | E,F & I | lysaghtstown | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 206 | 241.1869 | 163.6792 | 54.3144 | 2.1767 | 21.0165 | 77.5077 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | cloghboola | 2035 | 100% ECP | Grandfathering | IE wind priority | 100.549 | 325.5473 | 322.3659 | 0 | 3.1814 | 0 | 3.1814 | 0% | 0.9773% | 0% | 0.9773%
E | E,F & I | cloghboola | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 100.549 | 325.5473 | 319.912 | 0 | 5.6353 | 0 | 5.6353 | 0% | 1.731% | 0% | 1.731%
E | E,F & I | clashavoon | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 37.3333 | 120.8739 | 87.2676 | 19.6097 | 1.9854 | 12.0112 | 33.6063 | 16.22% | 1.643% | 9.937% | 27.8%
E | E,F & I | clashavoon | 2030 | 100% ECP | Grandfathering | IE wind not priority | 112 | 362.6222 | 222.3057 | 96.7423 | 6.1448 | 37.4293 | 140.3165 | 26.68% | 1.695% | 10.32% | 38.69%
E | E,F & I | clashavoon | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 112 | 362.6222 | 232.6955 | 96.7423 | 6.1448 | 27.0396 | 129.9267 | 26.68% | 1.695% | 7.457% | 35.83%
I | E,F & I | midleton | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 32.55 | 38.1099 | 24.858 | 12.0944 | 0.83652 | 0.32097 | 13.2518 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | clashavoon | 2035 | 66% ECP | Grandfathering | IE wind not priority | 74.6666 | 241.7479 | 119.5218 | 38.5977 | 0.74095 | 82.8874 | 122.2261 | 15.97% | 0.3065% | 34.29% | 50.56%
E | E,F & I | clashavoon | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 74.6666 | 241.7479 | 145.0783 | 38.5977 | 0.74095 | 57.3309 | 96.6696 | 15.97% | 0.3065% | 23.72% | 39.99%
I | E,F & I | midleton | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 32.55 | 38.1099 | 24.5177 | 12.0944 | 0.83652 | 0.66126 | 13.5921 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | clashavoon | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 74.6666 | 241.7479 | 140.5759 | 70.7053 | 1.4603 | 29.0065 | 101.172 | 29.25% | 0.604% | 12% | 41.85%
E | E,F & I | clashavoon | 2035 | 100% ECP | Grandfathering | IE wind not priority | 112 | 362.6222 | 183.7453 | 64.0781 | 1.2094 | 113.5894 | 178.8769 | 17.67% | 0.3335% | 31.32% | 49.33%
I | E,F & I | midleton | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 20.55 | 24.0601 | 19.6081 | 3.3338 | 0.44724 | 0.67097 | 4.452 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | cloghboola | 2030 | Initial | Grandfathering | IE wind priority | 100.549 | 325.5473 | 316.8603 | 0 | 8.687 | 0 | 8.687 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | coomagearlahy | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 7 | 8.1957 | 5.9751 | 1.3011 | 0.060152 | 0.85924 | 2.2205 | 15.88% | 0.7339% | 10.48% | 27.09%
I | E,F & I | midleton | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 20.55 | 24.0601 | 17.3692 | 5.4765 | 0.51145 | 0.70291 | 6.6909 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | cloghboola | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 100.549 | 325.5473 | 314.3064 | 0 | 11.2409 | 0 | 11.2409 | 0% | 3.453% | 0% | 3.453%
I | E,F & I | midleton | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 20.55 | 24.0601 | 17.9477 | 4.7089 | 0.45491 | 0.94865 | 6.1125 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | cloghboola | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 100.549 | 325.5473 | 313.0551 | 0 | 12.4922 | 0 | 12.4922 | 0% | 3.837% | 0% | 3.837%
E | E,F & I | cloghboola | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 100.549 | 325.5473 | 312.9012 | 0 | 12.6461 | 0 | 12.6461 | 0% | 3.885% | 0% | 3.885%
I | E,F & I | midleton | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 20.55 | 24.0601 | 18.3841 | 4.0449 | 0.45495 | 1.1761 | 5.676 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | cloghboola | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 100.549 | 325.5473 | 315.7961 | 0 | 9.7512 | 0 | 9.7512 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | cloghboola | 2030 | 100% ECP | Grandfathering | IE wind priority | 100.549 | 325.5473 | 313.6101 | 0 | 11.9372 | 0 | 11.9372 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | midleton | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 20.55 | 24.0601 | 18.9529 | 3.3338 | 0.44724 | 1.3262 | 5.1073 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | cloghboola | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 100.549 | 325.5473 | 313.6101 | 0 | 11.9372 | 0 | 11.9372 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | midleton | 2030 | Initial | Grandfathering | IE Solar not priority | 14.55 | 17.0353 | 12.8297 | 1.4089 | 0.2195 | 2.5771 | 4.2055 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | cloghboola | 2035 | 66% ECP | Grandfathering | IE wind priority | 100.549 | 325.5473 | 322.7692 | 0 | 2.7781 | 0 | 2.7781 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | cloghboola | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 100.549 | 325.5473 | 322.7692 | 0 | 2.7781 | 0 | 2.7781 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | cloghboola | 2030 | 33% ECP | Grandfathering | IE wind priority | 100.549 | 325.5473 | 315.7961 | 0 | 9.7512 | 0 | 9.7512 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | coomagearlahy | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 81 | 262.2536 | 260.0155 | 0 | 2.238 | 0 | 2.238 | 0% | 0.8534% | 0% | 0.8534%
I | E,F & I | lysaghtstown | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 126.6666 | 148.3026 | 116.8223 | 20.5491 | 2.7567 | 8.1745 | 31.4803 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | coomagearlahy | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 7 | 8.1957 | 6.4396 | 1.3011 | 0.060152 | 0.39481 | 1.7561 | 15.88% | 0.7339% | 4.817% | 21.43%
I | E,F & I | knockraha | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 201 | 235.3328 | 151.3998 | 74.6841 | 5.1656 | 4.0833 | 83.933 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | cordal | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 111.75 | 361.8128 | 347.9289 | 0 | 13.8838 | 0 | 13.8838 | 0% | 3.837% | 0% | 3.837%
E | E,F & I | cordal | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 111.75 | 361.8128 | 347.7579 | 0 | 14.0548 | 0 | 14.0548 | 0% | 3.885% | 0% | 3.885%
I | E,F & I | knockraha | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 66.9999 | 78.4442 | 63.9291 | 10.8694 | 1.4582 | 2.1876 | 14.5151 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | cordal | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 111.75 | 361.8128 | 350.9753 | 0 | 10.8374 | 0 | 10.8374 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | cordal | 2030 | 100% ECP | Grandfathering | IE wind priority | 111.75 | 361.8128 | 348.5458 | 0 | 13.267 | 0 | 13.267 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | knockraha | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 66.9999 | 78.4442 | 56.6296 | 17.8554 | 1.6675 | 2.2917 | 21.8146 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | cordal | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 111.75 | 361.8128 | 348.5458 | 0 | 13.267 | 0 | 13.267 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | knockraha | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 66.9999 | 78.4442 | 58.5154 | 15.3527 | 1.4832 | 3.0929 | 19.9287 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | cordal | 2035 | 66% ECP | Grandfathering | IE wind priority | 111.75 | 361.8128 | 358.7252 | 0 | 3.0876 | 0 | 3.0876 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | cordal | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 111.75 | 361.8128 | 358.7252 | 0 | 3.0876 | 0 | 3.0876 | 0% | 0.8534% | 0% | 0.8534%
I | E,F & I | knockraha | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 66.9999 | 78.4442 | 59.9384 | 13.1879 | 1.4833 | 3.8345 | 18.5057 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | cordal | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 111.75 | 361.8128 | 355.5497 | 0 | 6.2631 | 0 | 6.2631 | 0% | 1.731% | 0% | 1.731%
E | E,F & I | cordal | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 111.75 | 361.8128 | 349.3197 | 0 | 12.4931 | 0 | 12.4931 | 0% | 3.453% | 0% | 3.453%
E | E,F & I | cordal | 2035 | 100% ECP | Grandfathering | IE wind priority | 111.75 | 361.8128 | 358.2769 | 0 | 3.5359 | 0 | 3.5359 | 0% | 0.9773% | 0% | 0.9773%
E | E,F & I | dromada | 2030 | Initial | Grandfathering | IE wind priority | 28.5 | 92.2744 | 89.8121 | 0 | 2.4623 | 0 | 2.4623 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | dromada | 2030 | 33% ECP | Grandfathering | IE wind priority | 28.5 | 92.2744 | 89.5105 | 0 | 2.7639 | 0 | 2.7639 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | dromada | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 28.5 | 92.2744 | 89.0882 | 0 | 3.1862 | 0 | 3.1862 | 0% | 3.453% | 0% | 3.453%
I | E,F & I | kilbarry | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 79.8 | 93.4306 | 63.4058 | 21.0402 | 0.84322 | 8.1414 | 30.0248 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | dromada | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 28.5 | 92.2744 | 88.7336 | 0 | 3.5408 | 0 | 3.5408 | 0% | 3.837% | 0% | 3.837%
E | E,F & I | dromada | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 28.5 | 92.2744 | 88.6899 | 0 | 3.5845 | 0 | 3.5845 | 0% | 3.885% | 0% | 3.885%
I | E,F & I | kilbarry | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 56.5 | 66.1507 | 46.0255 | 14.8423 | 0.56936 | 4.7135 | 20.1252 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | dromada | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 28.5 | 92.2744 | 89.5105 | 0 | 2.7639 | 0 | 2.7639 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | dromada | 2030 | 100% ECP | Grandfathering | IE wind priority | 28.5 | 92.2744 | 88.8909 | 0 | 3.3835 | 0 | 3.3835 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | kilbarry | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 56.5 | 66.1507 | 51.9764 | 10.5021 | 0.48551 | 3.1867 | 14.1743 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | dromada | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 28.5 | 92.2744 | 88.8909 | 0 | 3.3835 | 0 | 3.3835 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | knockraha | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 66.9999 | 78.4442 | 61.7928 | 10.8694 | 1.4582 | 4.3239 | 16.6514 | 13.86% | 1.859% | 5.512% | 21.23%
I | E,F & I | midleton | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 26.55 | 31.085 | 22.6628 | 4.9351 | 0.22815 | 3.259 | 8.4222 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | cordal | 2030 | 33% ECP | Grandfathering | IE wind priority | 111.75 | 361.8128 | 350.9753 | 0 | 10.8374 | 0 | 10.8374 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | cordal | 2030 | Initial | Grandfathering | IE wind priority | 111.75 | 361.8128 | 352.1581 | 0 | 9.6547 | 0 | 9.6547 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | coomagearlahy | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 81 | 262.2536 | 257.7138 | 0 | 4.5397 | 0 | 4.5397 | 0% | 1.731% | 0% | 1.731%
I | E,F & I | lysaghtstown | 2030 | Initial | Grandfathering | IE Solar not priority | 87 | 101.8605 | 76.7139 | 8.4244 | 1.3125 | 15.4096 | 25.1465 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | coomagearlahy | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 7 | 8.1957 | 5.7023 | 1.8389 | 0.07054 | 0.58397 | 2.4934 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | coomagearlahy | 2035 | 100% ECP | Grandfathering | IE wind priority | 81 | 262.2536 | 259.6906 | 0 | 2.5629 | 0 | 2.5629 | 0% | 0.9773% | 0% | 0.9773%
E | E,F & I | coomagearlahy | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 7 | 8.1957 | 5.5619 | 1.8456 | 0.073966 | 0.71415 | 2.6338 | 22.52% | 0.9025% | 8.714% | 32.14%
I | E,F & I | knockraha 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 450 | 1912.6962 | 1158.2967 | 513.6734 | 11.2285 | 229.4976 | 754.3995 | 26.86% | 0.587% | 12% | 39.44%
E | E,F & I | coomataggart | 2030 | Initial | Grandfathering | IE wind not priority | 156.84 | 507.8006 | 257.6851 | 60.6151 | 8.5243 | 180.9761 | 250.1155 | 11.94% | 1.679% | 35.64% | 49.25%
E | E,F & I | coomataggart | 2030 | 33% ECP | Grandfathering | IE wind not priority | 185.44 | 600.3987 | 392.5632 | 97.4042 | 9.862 | 100.5693 | 207.8355 | 16.22% | 1.643% | 16.75% | 34.62%
E | E,F & I | coomataggart | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 185.44 | 600.3987 | 373.8158 | 134.1866 | 10.349 | 82.0472 | 226.5829 | 22.35% | 1.724% | 13.67% | 37.74%
I | E,F & I | knockraha | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 201 | 235.3328 | 153.5012 | 74.6841 | 5.1656 | 1.982 | 81.8316 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | coomataggart | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 185.44 | 600.3987 | 351.2785 | 173.994 | 10.4251 | 64.7011 | 249.1202 | 28.98% | 1.736% | 10.78% | 41.49%
I | E,F & I | knockraha | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 201 | 235.3328 | 159.7064 | 52.9961 | 2.1239 | 20.5064 | 75.6264 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | coomataggart | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 185.44 | 600.3987 | 433.4712 | 97.4042 | 9.862 | 59.6613 | 166.9275 | 16.22% | 1.643% | 9.937% | 27.8%
E | E,F & I | coomataggart | 2030 | 100% ECP | Grandfathering | IE wind not priority | 242.64 | 785.5951 | 481.6094 | 209.5853 | 13.3123 | 81.088 | 303.9856 | 26.68% | 1.695% | 10.32% | 38.69%
I | E,F & I | knockraha | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 133.9999 | 156.8884 | 109.1579 | 35.2013 | 1.3503 | 11.1789 | 47.7305 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | coomataggart | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 242.64 | 785.5951 | 504.1182 | 209.5853 | 13.3123 | 58.5793 | 281.4769 | 26.68% | 1.695% | 7.457% | 35.83%
I | E,F & I | knockraha | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 133.9999 | 156.8884 | 123.2714 | 24.9077 | 1.1515 | 7.5579 | 33.617 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | coomataggart | 2035 | 66% ECP | Grandfathering | IE wind not priority | 214.0399 | 692.9967 | 342.6224 | 110.6446 | 2.124 | 237.6058 | 350.3744 | 15.97% | 0.3065% | 34.29% | 50.56%
E | E,F & I | coomataggart | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 214.0399 | 692.9967 | 415.8828 | 110.6446 | 2.124 | 164.3453 | 277.1139 | 15.97% | 0.3065% | 23.72% | 39.99%
I | E,F & I | knockraha | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 133.9999 | 156.8884 | 114.381 | 24.9077 | 1.1515 | 16.4482 | 42.5074 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | coomataggart | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 214.0399 | 692.9967 | 402.9761 | 202.6844 | 4.186 | 83.1502 | 290.0207 | 29.25% | 0.604% | 12% | 41.85%
E | E,F & I | coomataggart | 2035 | 100% ECP | Grandfathering | IE wind not priority | 242.64 | 785.5951 | 398.0711 | 138.8206 | 2.62 | 246.0834 | 387.524 | 17.67% | 0.3335% | 31.32% | 49.33%
E | E,F & I | coomataggart | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 185.44 | 600.3987 | 318.1764 | 186.2889 | 10.3573 | 85.5761 | 282.2223 | 31.03% | 1.725% | 14.25% | 47.01%
E | E,F & I | clashavoon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 37.3333 | 120.8739 | 64.0562 | 37.5042 | 2.0852 | 17.2284 | 56.8178 | 31.03% | 1.725% | 14.25% | 47.01%
E | E,F & I | clashavoon | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 37.3333 | 120.8739 | 70.7204 | 35.029 | 2.0988 | 13.0258 | 50.1536 | 28.98% | 1.736% | 10.78% | 41.49%
I | E,F & I | midleton | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 26.55 | 31.085 | 24.4243 | 4.9351 | 0.22815 | 1.4975 | 6.6607 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | charleville | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 55.8999 | 180.9871 | 112.6849 | 40.4499 | 3.1197 | 24.7327 | 68.3023 | 22.35% | 1.724% | 13.67% | 37.74%
E | E,F & I | charleville | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 51.4 | 166.4177 | 160.6714 | 0 | 5.7463 | 0 | 5.7463 | 0% | 3.453% | 0% | 3.453%
I | E,F & I | trabeg | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.5653 | 0.80304 | 0.10773 | 0.31945 | 1.2302 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | charleville | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 57.3333 | 67.1264 | 51.2906 | 11.2852 | 1.2693 | 3.2813 | 15.8358 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | charleville | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 55.8999 | 180.9871 | 105.8911 | 52.4496 | 3.1426 | 19.5038 | 75.096 | 28.98% | 1.736% | 10.78% | 41.49%
I | E,F & I | trabeg | 2030 | Initial | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.3648 | 0.47932 | 0.074676 | 0.87675 | 1.4308 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | charleville | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 51.4 | 166.4177 | 160.0317 | 0 | 6.3859 | 0 | 6.3859 | 0% | 3.837% | 0% | 3.837%
E | E,F & I | charleville | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 57.3333 | 67.1264 | 50.0729 | 13.1376 | 1.2692 | 2.6467 | 17.0535 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | charleville | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 55.8999 | 180.9871 | 95.9127 | 56.1558 | 3.1222 | 25.7965 | 85.0745 | 31.03% | 1.725% | 14.25% | 47.01%
E | E,F & I | charleville | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 51.4 | 166.4177 | 159.9531 | 0 | 6.4646 | 0 | 6.4646 | 0% | 3.885% | 0% | 3.885%
I | E,F & I | rathcoursey | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 110 | 128.7891 | 87.4015 | 29.0028 | 1.1623 | 11.2224 | 41.3876 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | charleville | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 57.3333 | 67.1264 | 48.4591 | 15.2793 | 1.4269 | 1.9611 | 18.6672 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | charleville | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 55.8999 | 180.9871 | 130.6677 | 29.362 | 2.9729 | 17.9846 | 50.3195 | 16.22% | 1.643% | 9.937% | 27.8%
I | E,F & I | trabeg | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.4283 | 0.97433 | 0.10959 | 0.2833 | 1.3672 | 16.81% | 1.891% | 4.888% | 23.59%
I | E,F & I | rathcoursey | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 73.3333 | 85.8593 | 59.7381 | 19.2644 | 0.73899 | 6.1178 | 26.1212 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | charleville | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 57.3333 | 67.1264 | 54.7055 | 9.3011 | 1.2478 | 1.872 | 12.4209 | 13.86% | 1.859% | 2.789% | 18.5%
I | E,F & I | rathcoursey | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 73.3333 | 85.8593 | 67.462 | 13.6311 | 0.63016 | 4.1361 | 18.3974 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | charleville | 2030 | 100% ECP | Grandfathering | IE wind not priority | 167.7 | 542.962 | 332.8631 | 144.8543 | 9.2008 | 56.0438 | 210.0989 | 26.68% | 1.695% | 10.32% | 38.69%
E | E,F & I | charleville | 2030 | 100% ECP | Grandfathering | IE wind priority | 51.4 | 166.4177 | 160.3155 | 0 | 6.1022 | 0 | 6.1022 | 0% | 3.667% | 0% | 3.667%
I | E,F & I | rathcoursey | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 73.3333 | 85.8593 | 62.5966 | 13.6311 | 0.63016 | 9.0015 | 23.2627 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | charleville | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 172 | 201.3793 | 129.5561 | 63.9087 | 4.4203 | 3.4942 | 71.8232 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | charleville | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 167.7 | 542.962 | 348.42 | 144.8543 | 9.2008 | 40.4869 | 194.542 | 26.68% | 1.695% | 7.457% | 35.83%
E | E,F & I | charleville | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 51.4 | 166.4177 | 160.3155 | 0 | 6.1022 | 0 | 6.1022 | 0% | 3.667% | 0% | 3.667%
E | E,F & I | charleville | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 172 | 201.3793 | 131.3542 | 63.9087 | 4.4203 | 1.696 | 70.0251 | 31.74% | 2.195% | 0.8422% | 34.77%
I | E,F & I | rathcoursey | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 110 | 128.7891 | 84.0056 | 40.8719 | 2.8269 | 1.0847 | 44.7835 | 31.74% | 2.195% | 0.8422% | 34.77%
I | E,F & I | rathcoursey | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 110 | 128.7891 | 82.8556 | 40.8719 | 2.8269 | 2.2347 | 45.9335 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | charleville | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 51.4 | 166.4177 | 161.4329 | 0 | 4.9847 | 0 | 4.9847 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | charleville | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 57.3333 | 67.1264 | 52.8774 | 9.3011 | 1.2478 | 3.7 | 14.249 | 13.86% | 1.859% | 5.512% | 21.23%
I | E,F & I | trabeg | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.3232 | 1.1343 | 0.10958 | 0.22851 | 1.4723 | 19.57% | 1.891% | 3.943% | 25.4%
I | E,F & I | trabeg | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 3.9331 | 1.3051 | 0.052305 | 0.50501 | 1.8624 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | boggeragh | 2035 | 66% ECP | Grandfathering | IE wind not priority | 23.35 | 75.6003 | 37.3773 | 12.0704 | 0.23171 | 25.9208 | 38.223 | 15.97% | 0.3065% | 34.29% | 50.56%
I | E,F & I | trabeg | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.0323 | 1.3003 | 0.049882 | 0.41295 | 1.7632 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | boggeragh | 2035 | 66% ECP | Grandfathering | IE wind priority | 142.7 | 462.0195 | 458.0768 | 0 | 3.9428 | 0 | 3.9428 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | boggeragh | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 16.1333 | 18.889 | 13.7712 | 2.9988 | 0.13864 | 1.9803 | 5.1178 | 15.88% | 0.7339% | 10.48% | 27.09%
I | E,F & I | trabeg | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.5537 | 0.9201 | 0.042536 | 0.27919 | 1.2418 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | boggeragh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 23.35 | 75.6003 | 45.3694 | 12.0704 | 0.23171 | 17.9287 | 30.2309 | 15.97% | 0.3065% | 23.72% | 39.99%
E | E,F & I | boggeragh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 142.7 | 462.0195 | 458.0768 | 0 | 3.9428 | 0 | 3.9428 | 0% | 0.8534% | 0% | 0.8534%
I | E,F & I | trabeg | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.2253 | 0.9201 | 0.042536 | 0.6076 | 1.5702 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | boggeragh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 16.1333 | 18.889 | 14.8416 | 2.9988 | 0.13864 | 0.90995 | 4.0474 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | charleville | 2030 | 33% ECP | Grandfathering | IE wind priority | 51.4 | 166.4177 | 161.4329 | 0 | 4.9847 | 0 | 4.9847 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | boggeragh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 23.35 | 75.6003 | 43.9614 | 22.1112 | 0.45666 | 9.071 | 31.6389 | 29.25% | 0.604% | 12% | 41.85%
E | E,F & I | boggeragh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 142.7 | 462.0195 | 454.0218 | 0 | 7.9977 | 0 | 7.9977 | 0% | 1.731% | 0% | 1.731%
E | E,F & I | boggeragh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 16.1333 | 18.889 | 13.1424 | 4.2382 | 0.16258 | 1.3459 | 5.7467 | 22.44% | 0.8607% | 7.125% | 30.42%
I | E,F & I | trabeg | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 3.7803 | 1.8392 | 0.12721 | 0.04881 | 2.0153 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | boggeragh | 2035 | 100% ECP | Grandfathering | IE wind not priority | 23.35 | 75.6003 | 38.3076 | 13.3591 | 0.25214 | 23.6814 | 37.2926 | 17.67% | 0.3335% | 31.32% | 49.33%
E | E,F & I | boggeragh | 2035 | 100% ECP | Grandfathering | IE wind priority | 142.7 | 462.0195 | 457.5044 | 0 | 4.5151 | 0 | 4.5151 | 0% | 0.9773% | 0% | 0.9773%
I | E,F & I | trabeg | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 3.7285 | 1.8392 | 0.12721 | 0.10056 | 2.067 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | boggeragh | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 24.2 | 28.3336 | 19.2283 | 6.3806 | 0.25571 | 2.4689 | 9.1053 | 22.52% | 0.9025% | 8.714% | 32.14%
I | E,F & I | trabeg | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.7231 | 0.80304 | 0.10773 | 0.16162 | 1.0724 | 13.86% | 1.859% | 2.789% | 18.5%
I | E,F & I | trabeg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 4.95 | 5.7955 | 4.1838 | 1.3192 | 0.1232 | 0.16931 | 1.6117 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | charleville | 2030 | Initial | Grandfathering | IE wind priority | 51.4 | 166.4177 | 161.977 | 0 | 4.4407 | 0 | 4.4407 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | charleville | 2030 | 33% ECP | Grandfathering | IE wind not priority | 55.8999 | 180.9871 | 118.3362 | 29.362 | 2.9729 | 30.3161 | 62.651 | 16.22% | 1.643% | 16.75% | 34.62%
E | E,F & I | boggeragh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 142.7 | 462.0195 | 445.0781 | 0 | 16.9414 | 0 | 16.9414 | 0% | 3.667% | 0% | 3.667%
E | E,F & I | charleville | 2035 | 66% ECP | Grandfathering | IE wind not priority | 111.7999 | 361.9743 | 178.9626 | 57.7932 | 1.1094 | 124.1091 | 183.0117 | 15.97% | 0.3065% | 34.29% | 50.56%
E | E,F & I | charleville | 2035 | 66% ECP | Grandfathering | IE wind priority | 51.4 | 166.4177 | 164.9975 | 0 | 1.4202 | 0 | 1.4202 | 0% | 0.8534% | 0% | 0.8534%
I | E,F & I | raffeen | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 55 | 64.3945 | 41.4278 | 20.4359 | 1.4135 | 1.1173 | 22.9667 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | clahane | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 51.6 | 167.0652 | 162.0611 | 0 | 5.0041 | 0 | 5.0041 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | clahane | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 34 | 39.8075 | 32.4417 | 5.5158 | 0.73997 | 1.1101 | 7.3659 | 13.86% | 1.859% | 2.789% | 18.5%
I | E,F & I | raffeen | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 55 | 64.3945 | 52.4791 | 8.9226 | 1.197 | 1.7958 | 11.9154 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | clahane | 2030 | 100% ECP | Grandfathering | IE wind priority | 51.6 | 167.0652 | 160.9393 | 0 | 6.126 | 0 | 6.126 | 0% | 3.667% | 0% | 3.667%
E | E,F & I | clahane | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 34 | 39.8075 | 25.6099 | 12.6331 | 0.87378 | 0.69071 | 14.1976 | 31.74% | 2.195% | 1.735% | 35.67%
I | E,F & I | raffeen | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 55 | 64.3945 | 46.487 | 14.6574 | 1.3688 | 1.8813 | 17.9076 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | clahane | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 51.6 | 167.0652 | 160.9393 | 0 | 6.126 | 0 | 6.126 | 0% | 3.667% | 0% | 3.667%
E | E,F & I | clahane | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 34 | 39.8075 | 25.9654 | 12.6331 | 0.87378 | 0.33526 | 13.8422 | 31.74% | 2.195% | 0.8422% | 34.77%
I | E,F & I | raffeen | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 55 | 64.3945 | 48.0351 | 12.6029 | 1.2175 | 2.539 | 16.3594 | 19.57% | 1.891% | 3.943% | 25.4%
I | E,F & I | raffeen | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 55 | 64.3945 | 49.2033 | 10.8259 | 1.2176 | 3.1478 | 15.1913 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | clahane | 2035 | 66% ECP | Grandfathering | IE wind priority | 51.6 | 167.0652 | 165.6395 | 0 | 1.4257 | 0 | 1.4257 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | clahane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 34 | 39.8075 | 28.7374 | 9.061 | 0.8462 | 1.163 | 11.0701 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | clahane | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 34 | 39.8075 | 29.0221 | 6.3199 | 0.29217 | 4.1734 | 10.7855 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | clahane | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 51.6 | 167.0652 | 165.6395 | 0 | 1.4257 | 0 | 1.4257 | 0% | 0.8534% | 0% | 0.8534%
E | E,F & I | clahane | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 34 | 39.8075 | 31.2778 | 6.3199 | 0.29217 | 1.9177 | 8.5297 | 15.88% | 0.7339% | 4.817% | 21.43%
I | E,F & I | raffeen | 2030 | Initial | Grandfathering | IE Solar not priority | 55 | 64.3945 | 48.4973 | 5.3258 | 0.82973 | 9.7417 | 15.8972 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | clahane | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 51.6 | 167.0652 | 164.1733 | 0 | 2.892 | 0 | 2.892 | 0% | 1.731% | 0% | 1.731%
E | E,F & I | clahane | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 34 | 39.8075 | 27.6968 | 8.9317 | 0.34262 | 2.8364 | 12.1107 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | clahane | 2035 | 100% ECP | Grandfathering | IE wind priority | 51.6 | 167.0652 | 165.4326 | 0 | 1.6327 | 0 | 1.6327 | 0% | 0.9773% | 0% | 0.9773%
E | E,F & I | clahane | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 34 | 39.8075 | 27.015 | 8.9645 | 0.35927 | 3.4688 | 12.7925 | 22.52% | 0.9025% | 8.714% | 32.14%
I | E,F & I | midleton | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 32.55 | 38.1099 | 25.8629 | 8.5822 | 0.34394 | 3.3208 | 12.247 | 22.52% | 0.9025% | 8.714% | 32.14%
I | E,F & I | midleton | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 26.55 | 31.085 | 21.6279 | 6.9746 | 0.26755 | 2.2149 | 9.4571 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | clashavoon | 2030 | 33% ECP | Grandfathering | IE wind not priority | 37.3333 | 120.8739 | 79.0319 | 19.6097 | 1.9854 | 20.2469 | 41.842 | 16.22% | 1.643% | 16.75% | 34.62%
E | E,F & I | clashavoon | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 37.3333 | 120.8739 | 75.2576 | 27.0148 | 2.0835 | 16.518 | 45.6163 | 22.35% | 1.724% | 13.67% | 37.74%
I | E,F & I | raffeen | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 55 | 64.3945 | 50.7255 | 8.9226 | 1.197 | 3.5494 | 13.6691 | 13.86% | 1.859% | 5.512% | 21.23%
I | E,F & I | rathcoursey | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 36.6666 | 42.9297 | 34.9861 | 5.9484 | 0.798 | 1.1972 | 7.9436 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | clahane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 51.6 | 167.0652 | 160.5755 | 0 | 6.4897 | 0 | 6.4897 | 0% | 3.885% | 0% | 3.885%
E | E,F & I | clahane | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 34 | 39.8075 | 29.6944 | 7.7909 | 0.75265 | 1.5695 | 10.1131 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | charleville | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 114.6666 | 134.2527 | 97.8783 | 21.314 | 0.98534 | 14.0751 | 36.3745 | 15.88% | 0.7339% | 10.48% | 27.09%
I | E,F & I | rathcoursey | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 36.6666 | 42.9297 | 30.9913 | 9.7716 | 0.91257 | 1.2542 | 11.9384 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | charleville | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 111.7999 | 361.9743 | 217.2288 | 57.7932 | 1.1094 | 85.8428 | 144.7454 | 15.97% | 0.3065% | 23.72% | 39.99%
E | E,F & I | charleville | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 51.4 | 166.4177 | 164.9975 | 0 | 1.4202 | 0 | 1.4202 | 0% | 0.8534% | 0% | 0.8534%
I | E,F & I | rathcoursey | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 36.6666 | 42.9297 | 32.0234 | 8.402 | 0.81168 | 1.6926 | 10.9063 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | charleville | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 114.6666 | 134.2527 | 105.486 | 21.314 | 0.98534 | 6.4674 | 28.7668 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | charleville | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 111.7999 | 361.9743 | 210.4873 | 105.8685 | 2.1865 | 43.432 | 151.487 | 29.25% | 0.604% | 12% | 41.85%
I | E,F & I | rathcoursey | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 36.6666 | 42.9297 | 32.8021 | 7.2173 | 0.81176 | 2.0985 | 10.1275 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | charleville | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 51.4 | 166.4177 | 163.5369 | 0 | 2.8808 | 0 | 2.8808 | 0% | 1.731% | 0% | 1.731%
E | E,F & I | charleville | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 114.6666 | 134.2527 | 93.4087 | 30.1225 | 1.1555 | 9.566 | 40.844 | 22.44% | 0.8607% | 7.125% | 30.42%
I | E,F & I | rathcoursey | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 36.6666 | 42.9297 | 33.817 | 5.9484 | 0.798 | 2.3663 | 9.1127 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | charleville | 2035 | 100% ECP | Grandfathering | IE wind not priority | 167.7 | 542.962 | 275.1258 | 95.9455 | 1.8108 | 170.0799 | 267.8362 | 17.67% | 0.3335% | 31.32% | 49.33%
E | E,F & I | charleville | 2035 | 100% ECP | Grandfathering | IE wind priority | 51.4 | 166.4177 | 164.7913 | 0 | 1.6263 | 0 | 1.6263 | 0% | 0.9773% | 0% | 0.9773%
I | E,F & I | raffeen | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 55 | 64.3945 | 42.0028 | 20.4359 | 1.4135 | 0.54234 | 22.3917 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | charleville | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 172 | 201.3793 | 136.6642 | 45.3499 | 1.8175 | 17.5478 | 64.7151 | 22.52% | 0.9025% | 8.714% | 32.14%
I | E,F & I | raffeen | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 55 | 64.3945 | 43.7008 | 14.5014 | 0.58116 | 5.6112 | 20.6938 | 22.52% | 0.9025% | 8.714% | 32.14%
I | E,F & I | raffeen | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 55 | 64.3945 | 44.8037 | 14.4483 | 0.55424 | 4.5884 | 19.5909 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | clahane | 2030 | Initial | Grandfathering | IE wind priority | 51.6 | 167.0652 | 162.6072 | 0 | 4.458 | 0 | 4.458 | 0% | 2.668% | 0% | 2.668%
E | E,F & I | clahane | 2030 | Initial | Grandfathering | IE Solar not priority | 34 | 39.8075 | 29.9802 | 3.2923 | 0.51292 | 6.0222 | 9.8274 | 8.271% | 1.289% | 15.13% | 24.69%
I | E,F & I | raffeen | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 55 | 64.3945 | 50.5965 | 10.2233 | 0.47262 | 3.1021 | 13.798 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | clahane | 2030 | 33% ECP | Grandfathering | IE wind priority | 51.6 | 167.0652 | 162.0611 | 0 | 5.0041 | 0 | 5.0041 | 0% | 2.995% | 0% | 2.995%
E | E,F & I | clahane | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 34 | 39.8075 | 31.3576 | 5.5158 | 0.73997 | 2.1942 | 8.45 | 13.86% | 1.859% | 5.512% | 21.23%
I | E,F & I | raffeen | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 55 | 64.3945 | 46.9475 | 10.2233 | 0.47262 | 6.7512 | 17.4471 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | clahane | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 51.6 | 167.0652 | 161.2966 | 0 | 5.7686 | 0 | 5.7686 | 0% | 3.453% | 0% | 3.453%
E | E,F & I | clahane | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 34 | 39.8075 | 30.4166 | 6.6924 | 0.75272 | 1.9459 | 9.391 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | clahane | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 51.6 | 167.0652 | 160.6544 | 0 | 6.4108 | 0 | 6.4108 | 0% | 3.837% | 0% | 3.837%
F | E,F & I | ballylickey | 2030 | 100% ECP | Grandfathering | IE wind not priority | 5.82 | 18.8354 | 11.752 | 4.8205 | 0.3187 | 1.9442 | 7.0834 | 25.59% | 1.692% | 10.32% | 37.61%
H2 | H2 & K | kilkenny | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 142.6665 | 167.0354 | 132.8171 | 26.5186 | 1.226 | 6.4737 | 34.2183 | 15.88% | 0.7339% | 3.876% | 20.49%
F | E,F & I | ballylickey | 2030 | 100% ECP | Grandfathering | IE wind priority | 51.45 | 166.5087 | 160.5223 | 0 | 5.9863 | 0 | 5.9863 | 0% | 3.595% | 0% | 3.595%
H1 | H1 | cahir | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 34.1 | 39.9246 | 31.5093 | 5.532 | 0.74214 | 2.1412 | 8.4153 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | cahir | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 36.3 | 42.5004 | 24.2302 | 13.4877 | 0.93289 | 3.8496 | 18.2702 | 31.74% | 2.195% | 9.058% | 42.99%
H2 | H2 & K | ballywater | 2030 | 33% ECP | Grandfathering | IE wind priority | 42 | 118.8065 | 115.037 | 0 | 3.7695 | 0 | 3.7695 | 0% | 3.173% | 0% | 3.173%
H1 | H1 | cahir | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 36.3 | 42.5004 | 24.4862 | 13.4877 | 0.93289 | 3.5936 | 18.0142 | 31.74% | 2.195% | 8.456% | 42.39%
H2 | H2 & K | ballywater | 2030 | Initial | Grandfathering | IE wind priority | 42 | 118.8065 | 115.469 | 0 | 3.3375 | 0 | 3.3375 | 0% | 2.809% | 0% | 2.809%
H1 | H1 | cahir | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 35.2 | 41.2125 | 28.3544 | 6.5429 | 0.30248 | 6.0127 | 12.8581 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | cahir | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 35.2 | 41.2125 | 29.7254 | 6.5429 | 0.30248 | 4.6417 | 11.4871 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | cahir | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 35.2 | 41.2125 | 27.2735 | 9.2469 | 0.35471 | 4.3373 | 13.939 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | cahir | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 36.3 | 42.5004 | 25.9388 | 9.5709 | 0.38357 | 6.6071 | 16.5616 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | cauteen | 2030 | Initial | Grandfathering | IE wind priority | 178.08 | 559.7403 | 542.7823 | 0 | 16.958 | 0 | 16.958 | 0% | 3.03% | 0% | 3.03%
H1 | H1 | cauteen | 2030 | 33% ECP | Grandfathering | IE wind priority | 178.08 | 559.7403 | 540.6153 | 0 | 19.1249 | 0 | 19.1249 | 0% | 3.417% | 0% | 3.417%
H1 | H1 | cauteen | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 83.6666 | 97.9577 | 76.0544 | 13.5732 | 1.8209 | 6.5092 | 21.9033 | 13.86% | 1.859% | 6.645% | 22.36%
H2 | H2 & K | ballyragget | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 39.99 | 46.8207 | 34.2878 | 10.5438 | 0.42256 | 1.5665 | 12.5329 | 22.52% | 0.9025% | 3.346% | 26.77%
H1 | H1 | cauteen | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 178.08 | 559.7403 | 538.2655 | 0 | 21.4747 | 0 | 21.4747 | 0% | 3.837% | 0% | 3.837%
H1 | H1 | cauteen | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 83.6666 | 97.9577 | 73.3428 | 16.4685 | 1.8523 | 6.2941 | 24.6149 | 16.81% | 1.891% | 6.425% | 25.13%
H2 | H2 & K | ballyragget | 2035 | 100% ECP | Grandfathering | IE wind priority | 9.2 | 26.0243 | 25.7759 | 0 | 0.24841 | 0 | 0.24841 | 0% | 0.9545% | 0% | 0.9545%
H1 | H1 | cauteen | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 178.08 | 559.7403 | 536.0855 | 0 | 23.6548 | 0 | 23.6548 | 0% | 4.226% | 0% | 4.226%
H1 | H1 | cauteen | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 83.6666 | 97.9577 | 71.0901 | 19.1717 | 1.8521 | 5.8437 | 26.8676 | 19.57% | 1.891% | 5.966% | 27.43%
H2 | H2 & K | ballyragget | 2035 | 100% ECP | Grandfathering | IE wind not priority | 143.4 | 405.6392 | 301.2873 | 72.9851 | 1.4524 | 29.9144 | 104.3519 | 17.99% | 0.3581% | 7.375% | 25.73%
H1 | H1 | cauteen | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 178.08 | 559.7403 | 535.896 | 0 | 23.8443 | 0 | 23.8443 | 0% | 4.26% | 0% | 4.26%
H1 | H1 | cauteen | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 83.6666 | 97.9577 | 67.6034 | 22.297 | 2.0823 | 5.9749 | 30.3543 | 22.76% | 2.126% | 6.1% | 30.99%
H2 | H2 & K | ballyragget | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 39.99 | 46.8207 | 34.2993 | 10.5052 | 0.40298 | 1.6132 | 12.5214 | 22.44% | 0.8607% | 3.445% | 26.74%
H1 | H1 | cauteen | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 178.08 | 559.7403 | 540.6153 | 0 | 19.1249 | 0 | 19.1249 | 0% | 3.417% | 0% | 3.417%
H1 | H1 | cauteen | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 83.6666 | 97.9577 | 77.3101 | 13.5732 | 1.8209 | 5.2535 | 20.6476 | 13.86% | 1.859% | 5.363% | 21.08%
H2 | H2 & K | ballywater | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 42 | 118.8065 | 114.51 | 0 | 4.2965 | 0 | 4.2965 | 0% | 3.616% | 0% | 3.616%
H1 | H1 | cahir | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 34.1 | 39.9246 | 27.5531 | 9.0876 | 0.84869 | 2.4352 | 12.3715 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | cahir | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 34.1 | 39.9246 | 28.9742 | 7.8138 | 0.75486 | 2.3817 | 10.9504 | 19.57% | 1.891% | 5.966% | 27.43%
H2 | H2 & K | ballywater | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 42 | 118.8065 | 113.9344 | 0 | 4.872 | 0 | 4.872 | 0% | 4.101% | 0% | 4.101%
H1 | H1 | barrymore | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 22.45 | 26.2847 | 16.042 | 5.9192 | 0.23722 | 4.0862 | 10.2426 | 22.52% | 0.9025% | 15.55% | 38.97%
H2 | H2 & K | ballywater | 2035 | 100% ECP | Grandfathering | IE wind priority | 42 | 118.8065 | 117.6724 | 0 | 1.134 | 0 | 1.134 | 0% | 0.9545% | 0% | 0.9545%
H2 | H2 & K | ballywater | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 42 | 118.8065 | 116.6217 | 0 | 2.1848 | 0 | 2.1848 | 0% | 1.839% | 0% | 1.839%
H1 | H1 | borrisbeg | 2030 | 33% ECP | Grandfathering | IE wind not priority | 18 | 56.5775 | 34.5497 | 10.441 | 1.0563 | 10.5305 | 22.0278 | 18.45% | 1.867% | 18.61% | 38.93%
H1 | H1 | borrisbeg | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 18 | 56.5775 | 30.732 | 14.2985 | 1.0636 | 10.4834 | 25.8455 | 25.27% | 1.88% | 18.53% | 45.68%
H2 | H2 & K | ballywater | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 42 | 118.8065 | 117.7717 | 0 | 1.0348 | 0 | 1.0348 | 0% | 0.871% | 0% | 0.871%
H1 | H1 | borrisbeg | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 18 | 56.5775 | 25.6601 | 18.363 | 1.0546 | 11.4998 | 30.9174 | 32.46% | 1.864% | 20.33% | 54.65%
H1 | H1 | borrisbeg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 18 | 56.5775 | 21.9319 | 19.5913 | 1.0487 | 14.0056 | 34.6455 | 34.63% | 1.854% | 24.75% | 61.24%
H2 | H2 & K | ballywater | 2035 | 66% ECP | Grandfathering | IE wind priority | 42 | 118.8065 | 117.7717 | 0 | 1.0348 | 0 | 1.0348 | 0% | 0.871% | 0% | 0.871%
H1 | H1 | borrisbeg | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 18 | 56.5775 | 37.6663 | 10.441 | 1.0563 | 7.4139 | 18.9111 | 18.45% | 1.867% | 13.1% | 33.43%
H2 | H2 & K | ballyragget | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 9.2 | 26.0243 | 25.5457 | 0 | 0.47858 | 0 | 0.47858 | 0% | 1.839% | 0% | 1.839%
H1 | H1 | borrisbeg | 2030 | 100% ECP | Grandfathering | IE wind not priority | 54 | 169.7326 | 88.0027 | 50.593 | 3.1268 | 28.0102 | 81.7299 | 29.81% | 1.842% | 16.5% | 48.15%
H1 | H1 | borrisbeg | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 54 | 169.7326 | 90.611 | 50.593 | 3.1268 | 25.4018 | 79.1216 | 29.81% | 1.842% | 14.97% | 46.62%
H2 | H2 & K | ballywater | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 42 | 118.8065 | 114.2324 | 0 | 4.5741 | 0 | 4.5741 | 0% | 3.85% | 0% | 3.85%
H1 | H1 | borrisbeg | 2035 | 66% ECP | Grandfathering | IE wind not priority | 36 | 113.1549 | 56.5473 | 20.5458 | 0.39085 | 35.671 | 56.6076 | 18.16% | 0.3454% | 31.52% | 50.03%
H1 | H1 | borrisbeg | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 36 | 113.1549 | 61.2959 | 20.5458 | 0.39085 | 30.9224 | 51.8591 | 18.16% | 0.3454% | 27.33% | 45.83%
H2 | H2 & K | ballywater | 2030 | 100% ECP | Grandfathering | IE wind priority | 42 | 118.8065 | 114.2324 | 0 | 4.5741 | 0 | 4.5741 | 0% | 3.85% | 0% | 3.85%
H1 | H1 | borrisbeg | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 36 | 113.1549 | 52.6544 | 36.9617 | 0.72735 | 22.8115 | 60.5005 | 32.66% | 0.6428% | 20.16% | 53.47%
H1 | H1 | borrisbeg | 2035 | 100% ECP | Grandfathering | IE wind not priority | 54 | 169.7326 | 82.7643 | 33.8359 | 0.62901 | 52.5034 | 86.9682 | 19.93% | 0.3706% | 30.93% | 51.24%
H2 | H2 & K | ballywater | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 42 | 118.8065 | 115.037 | 0 | 3.7695 | 0 | 3.7695 | 0% | 3.173% | 0% | 3.173%
H1 | H1 | cahir | 2030 | Initial | Grandfathering | IE Solar not priority | 33 | 38.6367 | 33.4534 | 3.1955 | 0.49784 | 1.49 | 5.1833 | 8.271% | 1.289% | 3.857% | 13.42%
H2 | H2 & K | ballywater | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 42 | 118.8065 | 113.8664 | 0 | 4.94 | 0 | 4.94 | 0% | 4.158% | 0% | 4.158%
H1 | H1 | cahir | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 34.1 | 39.9246 | 30.9975 | 5.532 | 0.74214 | 2.653 | 8.9271 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | cahir | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 34.1 | 39.9246 | 29.8923 | 6.7121 | 0.75493 | 2.5653 | 10.0323 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | cauteen | 2030 | 100% ECP | Grandfathering | IE wind priority | 178.08 | 559.7403 | 537.0379 | 0 | 22.7024 | 0 | 22.7024 | 0% | 4.056% | 0% | 4.056%
H1 | H1 | cauteen | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 251 | 293.8733 | 167.5424 | 93.2622 | 6.4505 | 26.6181 | 126.3309 | 31.74% | 2.195% | 9.058% | 42.99%
H2 | H2 & K | ballyragget | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 110.5999 | 312.8568 | 194.7479 | 96.9843 | 2.1062 | 19.0184 | 118.109 | 31% | 0.6732% | 6.079% | 37.75%
H1 | H1 | curraghduff | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 83.3333 | 97.5674 | 70.3726 | 15.4898 | 0.71609 | 10.9889 | 27.1949 | 15.88% | 0.7339% | 11.26% | 27.87%
H2 | H2 & K | ballyragget | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 143.4 | 405.6392 | 284.3379 | 111.5375 | 7.4132 | 2.3506 | 121.3013 | 27.5% | 1.828% | 0.5795% | 29.9%
H1 | H1 | curraghduff | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 83.3333 | 97.5674 | 64.568 | 21.8913 | 0.83976 | 10.2683 | 32.9994 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | curraghduff | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 125 | 146.3512 | 89.321 | 32.9578 | 1.3208 | 22.7517 | 57.0303 | 22.52% | 0.9025% | 15.55% | 38.97%
H2 | H2 & K | ballyragget | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 39.99 | 46.8207 | 30.3405 | 14.8588 | 1.0277 | 0.59369 | 16.4802 | 31.74% | 2.195% | 1.268% | 35.2%
H1 | H1 | doon | 2030 | Initial | Grandfathering | IE Solar not priority | 8 | 9.3665 | 8.1099 | 0.77466 | 0.12069 | 0.36122 | 1.2566 | 8.271% | 1.289% | 3.857% | 13.42%
H2 | H2 & K | ballyragget | 2030 | 100% ECP | Grandfathering | IE wind priority | 9.2 | 26.0243 | 25.0223 | 0 | 1.0019 | 0 | 1.0019 | 0% | 3.85% | 0% | 3.85%
H1 | H1 | doon | 2030 | 33% ECP | Grandfathering | IE wind not priority | 11.2 | 35.2038 | 21.4976 | 6.4966 | 0.65724 | 6.5523 | 13.7062 | 18.45% | 1.867% | 18.61% | 38.93%
H1 | H1 | doon | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 13.6633 | 15.9972 | 12.4202 | 2.2166 | 0.29736 | 1.063 | 3.577 | 13.86% | 1.859% | 6.645% | 22.36%
H2 | H2 & K | ballyragget | 2030 | 100% ECP | Grandfathering | IE wind not priority | 143.4 | 405.6392 | 277.7311 | 111.5375 | 7.4132 | 8.9575 | 127.9081 | 27.5% | 1.828% | 2.208% | 31.53%
H1 | H1 | doon | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 11.2 | 35.2038 | 19.1221 | 8.8968 | 0.6618 | 6.523 | 16.0816 | 25.27% | 1.88% | 18.53% | 45.68%
H1 | H1 | doon | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 13.6633 | 15.9972 | 11.9774 | 2.6894 | 0.30249 | 1.0279 | 4.0198 | 16.81% | 1.891% | 6.425% | 25.13%
H2 | H2 & K | ballyragget | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 39.99 | 46.8207 | 39.246 | 6.4876 | 0.87033 | 0.21683 | 7.5747 | 13.86% | 1.859% | 0.4631% | 16.18%
H1 | H1 | curraghduff | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 83.3333 | 97.5674 | 67.1269 | 15.4898 | 0.71609 | 14.2346 | 30.4405 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | doon | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 11.2 | 35.2038 | 15.9663 | 11.4258 | 0.65621 | 7.1554 | 19.2375 | 32.46% | 1.864% | 20.33% | 54.65%
H2 | H2 & K | ballyragget | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 9.2 | 26.0243 | 25.1986 | 0 | 0.8257 | 0 | 0.8257 | 0% | 3.173% | 0% | 3.173%
H1 | H1 | doon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 11.2 | 35.2038 | 13.6465 | 12.1901 | 0.65251 | 8.7146 | 21.5572 | 34.63% | 1.854% | 24.75% | 61.24%
H1 | H1 | doon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 13.6633 | 15.9972 | 11.0401 | 3.6413 | 0.34006 | 0.97575 | 4.9571 | 22.76% | 2.126% | 6.1% | 30.99%
H2 | H2 & K | ballyragget | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 77.8 | 220.0747 | 178.1322 | 35.9505 | 3.9419 | 2.0502 | 41.9426 | 16.34% | 1.791% | 0.9316% | 19.06%
H1 | H1 | doon | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 11.2 | 35.2038 | 23.4368 | 6.4966 | 0.65724 | 4.6131 | 11.7669 | 18.45% | 1.867% | 13.1% | 33.43%
H1 | H1 | doon | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 13.6633 | 15.9972 | 12.6253 | 2.2166 | 0.29736 | 0.85793 | 3.3719 | 13.86% | 1.859% | 5.363% | 21.08%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 39.99 | 46.8207 | 33.5151 | 10.6573 | 0.99528 | 1.653 | 13.3056 | 22.76% | 2.126% | 3.531% | 28.42%
H1 | H1 | doon | 2030 | 100% ECP | Grandfathering | IE wind not priority | 33.6 | 105.6114 | 54.7572 | 31.4801 | 1.9456 | 17.4285 | 50.8542 | 29.81% | 1.842% | 16.5% | 48.15%
H1 | H1 | doon | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 24.99 | 29.2585 | 16.6808 | 9.2853 | 0.64223 | 2.6501 | 12.5777 | 31.74% | 2.195% | 9.058% | 42.99%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 9.2 | 26.0243 | 24.9422 | 0 | 1.0821 | 0 | 1.0821 | 0% | 4.158% | 0% | 4.158%
H1 | H1 | doon | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 33.6 | 105.6114 | 56.3802 | 31.4801 | 1.9456 | 15.8056 | 49.2312 | 29.81% | 1.842% | 14.97% | 46.62%
H1 | H1 | doon | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 24.99 | 29.2585 | 16.857 | 9.2853 | 0.64223 | 2.474 | 12.4015 | 31.74% | 2.195% | 8.456% | 42.39%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 77.8 | 220.0747 | 129.8604 | 71.3539 | 4.2348 | 14.6257 | 90.2143 | 32.42% | 1.924% | 6.646% | 40.99%
H1 | H1 | doon | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 13.6633 | 15.9972 | 11.6095 | 3.1309 | 0.30246 | 0.95432 | 4.3877 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | barrymore | 2035 | 100% ECP | Grandfathering | IE wind priority | 32.4 | 101.8395 | 100.7381 | 0 | 1.1014 | 0 | 1.1014 | 0% | 1.082% | 0% | 1.082%
H2 | H2 & K | ballyragget | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 9.2 | 26.0243 | 25.0223 | 0 | 1.0019 | 0 | 1.0019 | 0% | 3.85% | 0% | 3.85%
H1 | H1 | curraghduff | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 125 | 146.3512 | 84.3187 | 46.4453 | 3.2124 | 12.3748 | 62.0325 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | cauteen | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 178.08 | 559.7403 | 537.0379 | 0 | 22.7024 | 0 | 22.7024 | 0% | 4.056% | 0% | 4.056%
H1 | H1 | cauteen | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 251 | 293.8733 | 169.312 | 93.2622 | 6.4505 | 24.8485 | 124.5613 | 31.74% | 2.195% | 8.456% | 42.39%
H2 | H2 & K | ballyragget | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 39.99 | 46.8207 | 38.4564 | 7.4333 | 0.34364 | 0.58734 | 8.3642 | 15.88% | 0.7339% | 1.254% | 17.86%
H2 | H2 & K | ballyragget | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 9.2 | 26.0243 | 25.7976 | 0 | 0.22667 | 0 | 0.22667 | 0% | 0.871% | 0% | 0.871%
H1 | H1 | cauteen | 2035 | 66% ECP | Grandfathering | IE wind priority | 178.08 | 559.7403 | 554.3237 | 0 | 5.4165 | 0 | 5.4165 | 0% | 0.9677% | 0% | 0.9677%
H1 | H1 | cauteen | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 167.3332 | 195.9153 | 134.7908 | 31.1036 | 1.4379 | 28.583 | 61.1245 | 15.88% | 0.7339% | 14.59% | 31.2%
H2 | H2 & K | ballyragget | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 110.5999 | 312.8568 | 248.4778 | 50.7722 | 1.0283 | 12.5786 | 64.3791 | 16.23% | 0.3287% | 4.021% | 20.58%
H1 | H1 | cauteen | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 178.08 | 559.7403 | 554.3237 | 0 | 5.4165 | 0 | 5.4165 | 0% | 0.9677% | 0% | 0.9677%
H1 | H1 | cauteen | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 167.3332 | 195.9153 | 141.3081 | 31.1036 | 1.4379 | 22.0658 | 54.6073 | 15.88% | 0.7339% | 11.26% | 27.87%
H2 | H2 & K | ballyragget | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 39.99 | 46.8207 | 37.2292 | 7.4333 | 0.34364 | 1.8146 | 9.5915 | 15.88% | 0.7339% | 3.876% | 20.49%
H1 | H1 | cauteen | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 178.08 | 559.7403 | 549.1914 | 0 | 10.5489 | 0 | 10.5489 | 0% | 1.885% | 0% | 1.885%
H1 | H1 | cauteen | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 167.3332 | 195.9153 | 129.6525 | 43.9578 | 1.6862 | 20.6188 | 66.2628 | 22.44% | 0.8607% | 10.52% | 33.82%
H2 | H2 & K | ballyragget | 2035 | 66% ECP | Grandfathering | IE wind priority | 9.2 | 26.0243 | 25.7976 | 0 | 0.22667 | 0 | 0.22667 | 0% | 0.871% | 0% | 0.871%
H1 | H1 | cauteen | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 251 | 293.8733 | 179.3565 | 66.1792 | 2.6522 | 45.6854 | 114.5168 | 22.52% | 0.9025% | 15.55% | 38.97%
H2 | H2 & K | ballyragget | 2035 | 66% ECP | Grandfathering | IE wind not priority | 110.5999 | 312.8568 | 241.9076 | 50.7722 | 1.0283 | 19.1488 | 70.9492 | 16.23% | 0.3287% | 6.121% | 22.68%
H1 | H1 | curraghduff | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 41.6666 | 48.7837 | 37.8757 | 6.7596 | 0.90682 | 3.2416 | 10.908 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | curraghduff | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 41.6666 | 48.7837 | 36.5253 | 8.2014 | 0.92245 | 3.1345 | 12.2584 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | curraghduff | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 41.6666 | 48.7837 | 35.4034 | 9.5477 | 0.92236 | 2.9102 | 13.3803 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | curraghduff | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 41.6666 | 48.7837 | 33.667 | 11.1041 | 1.037 | 2.9756 | 15.1167 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | curraghduff | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 41.6666 | 48.7837 | 38.5011 | 6.7596 | 0.90682 | 2.6163 | 10.2826 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | curraghduff | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 125 | 146.3512 | 83.4375 | 46.4453 | 3.2124 | 13.256 | 62.9138 | 31.74% | 2.195% | 9.058% | 42.99%
H2 | H2 & K | ballyragget | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 39.99 | 46.8207 | 30.8888 | 14.8588 | 1.0277 | 0.045356 | 15.9319 | 31.74% | 2.195% | 0.09687% | 34.03%
H1 | H1 | cauteen | 2035 | 100% ECP | Grandfathering | IE wind priority | 178.08 | 559.7403 | 553.6866 | 0 | 6.0537 | 0 | 6.0537 | 0% | 1.082% | 0% | 1.082%
H1 | H1 | barrymore | 2035 | 100% ECP | Grandfathering | IE wind not priority | 105.6 | 331.9214 | 161.8502 | 66.1679 | 1.2301 | 102.6732 | 170.0712 | 19.93% | 0.3706% | 30.93% | 51.24%
H2 | H2 & K | banoge | 2030 | Initial | Grandfathering | IE Solar not priority | 8 | 9.3665 | 7.8106 | 0.77466 | 0.12069 | 0.66049 | 1.5558 | 8.271% | 1.289% | 7.052% | 16.61%
H1 | H1 | barrymore | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 14.9667 | 17.5231 | 11.5964 | 3.9317 | 0.15082 | 1.8442 | 5.9267 | 22.44% | 0.8607% | 10.52% | 33.82%
H2 | H2 & K | carlow | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 21 | 59.4032 | 41.6394 | 16.3339 | 1.0856 | 0.34424 | 17.7638 | 27.5% | 1.828% | 0.5795% | 29.9%
G | J City, G South | gorman | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 130.6665 | 167.4213 | 140.3238 | 25.6457 | 1.2071 | 0.24469 | 27.0975 | 15.32% | 0.721% | 0.1462% | 16.19%
H2 | H2 & K | carlow | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 93.29 | 109.2249 | 70.7793 | 34.6631 | 2.3975 | 1.385 | 38.4455 | 31.74% | 2.195% | 1.268% | 35.2%
G | J City, G South | gorman | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 130.6665 | 167.4213 | 140.5321 | 25.6457 | 1.2071 | 0.036452 | 26.8893 | 15.32% | 0.721% | 0.02177% | 16.06%
G | J City, G South | gorman | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 130.6665 | 167.4213 | 129.172 | 36.7835 | 1.4304 | 0.035399 | 38.2493 | 21.97% | 0.8544% | 0.02114% | 22.85%
H2 | H2 & K | carlow | 2030 | 100% ECP | Grandfathering | IE wind priority | 30.49 | 86.2478 | 82.9273 | 0 | 3.3206 | 0 | 3.3206 | 0% | 3.85% | 0% | 3.85%
G | J City, G South | gorman | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 196 | 251.1323 | 193.2938 | 55.2186 | 2.2759 | 0.34396 | 57.8385 | 21.99% | 0.9062% | 0.137% | 23.03%
H2 | H2 & K | carlow | 2030 | 100% ECP | Grandfathering | IE wind not priority | 21 | 59.4032 | 40.6719 | 16.3339 | 1.0856 | 1.3118 | 18.7313 | 27.5% | 1.828% | 2.208% | 31.53%
H1 | H1 | ahane | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 1.3333 | 1.5611 | 1.212 | 0.21631 | 0.029018 | 0.10373 | 0.34906 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | ahane | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 1.3333 | 1.5611 | 1.1688 | 0.26245 | 0.029518 | 0.10031 | 0.39227 | 16.81% | 1.891% | 6.425% | 25.13%
H2 | H2 & K | carlow | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 31.0966 | 36.4083 | 30.5181 | 5.0448 | 0.67678 | 0.16861 | 5.8902 | 13.86% | 1.859% | 0.4631% | 16.18%
H1 | H1 | ahane | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 1.3333 | 1.5611 | 1.1329 | 0.30553 | 0.029516 | 0.093127 | 0.42817 | 19.57% | 1.891% | 5.966% | 27.43%
G | J City, G South | gorman | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 196 | 251.1323 | 154.6749 | 79.2508 | 5.5329 | 11.6737 | 96.4574 | 31.56% | 2.203% | 4.648% | 38.41%
H1 | H1 | ahane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 1.3333 | 1.5611 | 1.0773 | 0.35533 | 0.033184 | 0.095218 | 0.48373 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | ahane | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 1.3333 | 1.5611 | 1.232 | 0.21631 | 0.029018 | 0.083721 | 0.32904 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | ahane | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 4 | 4.6832 | 2.67 | 1.4862 | 0.1028 | 0.42419 | 2.0132 | 31.74% | 2.195% | 9.058% | 42.99%
H2 | H2 & K | carlow | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 7 | 19.8011 | 16.0273 | 3.2346 | 0.35467 | 0.18447 | 3.7738 | 16.34% | 1.791% | 0.9316% | 19.06%
H1 | H1 | ahane | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4 | 4.6832 | 2.6982 | 1.4862 | 0.1028 | 0.39599 | 1.985 | 31.74% | 2.195% | 8.456% | 42.39%
H2 | H2 & K | carlow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 31.0966 | 36.4083 | 26.0617 | 8.2872 | 0.77394 | 1.2854 | 10.3466 | 22.76% | 2.126% | 3.531% | 28.42%
H1 | H1 | ahane | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 2.6667 | 3.1222 | 2.1481 | 0.49567 | 0.022915 | 0.45551 | 0.9741 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | ahane | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 2.6667 | 3.1222 | 2.2519 | 0.49567 | 0.022915 | 0.35165 | 0.87024 | 15.88% | 0.7339% | 11.26% | 27.87%
H2 | H2 & K | carlow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 30.49 | 86.2478 | 82.6616 | 0 | 3.5862 | 0 | 3.5862 | 0% | 4.158% | 0% | 4.158%
H1 | H1 | ahane | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 2.6667 | 3.1222 | 2.0662 | 0.70052 | 0.026872 | 0.32859 | 1.056 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | ahane | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 4 | 4.6832 | 2.8583 | 1.0546 | 0.042266 | 0.72805 | 1.825 | 22.52% | 0.9025% | 15.55% | 38.97%
H2 | H2 & K | carlow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 7 | 19.8011 | 11.6841 | 6.42 | 0.38102 | 1.3159 | 8.117 | 32.42% | 1.924% | 6.646% | 40.99%
H1 | H1 | ballydine | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 5.9333 | 6.9468 | 5.3935 | 0.96256 | 0.12913 | 0.46161 | 1.5533 | 13.86% | 1.859% | 6.645% | 22.36%
H2 | H2 & K | carlow | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 30.49 | 86.2478 | 83.5113 | 0 | 2.7365 | 0 | 2.7365 | 0% | 3.173% | 0% | 3.173%
H2 | H2 & K | carlow | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 31.0966 | 36.4083 | 27.3192 | 7.1256 | 0.68838 | 1.2751 | 9.0891 | 19.57% | 1.891% | 3.502% | 24.96%
G | J City, G South | gorman | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 196 | 251.1323 | 156.3163 | 79.2508 | 5.5329 | 10.0322 | 94.8159 | 31.56% | 2.203% | 3.995% | 37.76%
G | J City, G South | gorman | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 65.3333 | 83.7107 | 70.3415 | 11.3752 | 1.5502 | 0.44379 | 13.3692 | 13.59% | 1.852% | 0.5302% | 15.97%
G | J City, G South | drybridge | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 16.97 | 21.7434 | 16.7357 | 4.7809 | 0.19705 | 0.02978 | 5.0077 | 21.99% | 0.9062% | 0.137% | 23.03%
H2 | H2 & K | carlow | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 62.1933 | 72.8165 | 59.8083 | 11.5604 | 0.53443 | 0.91344 | 13.0082 | 15.88% | 0.7339% | 1.254% | 17.86%
G | J City, G South | garballagh | 2030 | Initial | Grandfathering | IE Solar not priority | 143 | 183.224 | 166.2563 | 14.4868 | 2.3695 | 0.11144 | 16.9677 | 7.907% | 1.293% | 0.06082% | 9.261%
H2 | H2 & K | carlow | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 30.49 | 86.2478 | 85.4966 | 0 | 0.7512 | 0 | 0.7512 | 0% | 0.871% | 0% | 0.871%
G | J City, G South | garballagh | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 167 | 213.9749 | 179.7001 | 29.0763 | 3.9626 | 1.2359 | 34.2748 | 13.59% | 1.852% | 0.5776% | 16.02%
G | J City, G South | garballagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 167 | 213.9749 | 174.1172 | 35.4661 | 3.9924 | 0.39909 | 39.8577 | 16.57% | 1.866% | 0.1865% | 18.63%
H2 | H2 & K | carlow | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 14 | 39.6021 | 31.4529 | 6.4269 | 0.13016 | 1.5922 | 8.1492 | 16.23% | 0.3287% | 4.021% | 20.58%
G | J City, G South | garballagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 167 | 213.9749 | 167.8086 | 41.4655 | 3.9597 | 0.74111 | 46.1663 | 19.38% | 1.851% | 0.3464% | 21.58%
G | J City, G South | garballagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 167 | 213.9749 | 160.6115 | 48.2344 | 4.4811 | 0.64791 | 53.3634 | 22.54% | 2.094% | 0.3028% | 24.94%
H2 | H2 & K | carlow | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 62.1933 | 72.8165 | 57.8996 | 11.5604 | 0.53443 | 2.8221 | 14.9169 | 15.88% | 0.7339% | 3.876% | 20.49%
G | J City, G South | garballagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 167 | 213.9749 | 179.8016 | 29.0763 | 3.9626 | 1.1344 | 34.1733 | 13.59% | 1.852% | 0.5302% | 15.97%
G | J City, G South | garballagh | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 215 | 275.4767 | 171.4694 | 86.9333 | 6.0693 | 11.0048 | 104.0073 | 31.56% | 2.203% | 3.995% | 37.76%
H2 | H2 & K | carlow | 2035 | 66% ECP | Grandfathering | IE wind priority | 30.49 | 86.2478 | 85.4966 | 0 | 0.7512 | 0 | 0.7512 | 0% | 0.871% | 0% | 0.871%
H2 | H2 & K | carlow | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 30.49 | 86.2478 | 82.9273 | 0 | 3.3206 | 0 | 3.3206 | 0% | 3.85% | 0% | 3.85%
G | J City, G South | garballagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 215 | 275.4767 | 169.6689 | 86.9333 | 6.0693 | 12.8053 | 105.8078 | 31.56% | 2.203% | 4.648% | 38.41%
H2 | H2 & K | carlow | 2035 | 66% ECP | Grandfathering | IE wind not priority | 14 | 39.6021 | 30.6212 | 6.4269 | 0.13016 | 2.4239 | 8.9809 | 16.23% | 0.3287% | 6.121% | 22.68%
G | J City, G South | garballagh | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 191 | 244.7258 | 205.1164 | 37.4873 | 1.7644 | 0.35768 | 39.6094 | 15.32% | 0.721% | 0.1462% | 16.19%
G | J City, G South | garballagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 191 | 244.7258 | 205.4208 | 37.4873 | 1.7644 | 0.053283 | 39.305 | 15.32% | 0.721% | 0.02177% | 16.06%
G | J City, G South | garballagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 191 | 244.7258 | 188.8153 | 53.7678 | 2.0909 | 0.051744 | 55.9104 | 21.97% | 0.8544% | 0.02114% | 22.85%
G | J City, G South | garballagh | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 215 | 275.4767 | 212.0314 | 60.5715 | 2.4965 | 0.3773 | 63.4453 | 21.99% | 0.9062% | 0.137% | 23.03%
G | J City, G South | gorman | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 65.3333 | 83.7107 | 70.3018 | 11.3752 | 1.5502 | 0.48351 | 13.4089 | 13.59% | 1.852% | 0.5776% | 16.02%
G | J City, G South | gorman | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 65.3333 | 83.7107 | 68.1177 | 13.875 | 1.5619 | 0.15613 | 15.593 | 16.57% | 1.866% | 0.1865% | 18.63%
G | J City, G South | gorman | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 65.3333 | 83.7107 | 65.6496 | 16.222 | 1.5491 | 0.28994 | 18.0611 | 19.38% | 1.851% | 0.3464% | 21.58%
H2 | H2 & K | carlow | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 93.29 | 109.2249 | 72.0585 | 34.6631 | 2.3975 | 0.10581 | 37.1664 | 31.74% | 2.195% | 0.09687% | 34.03%
G | J City, G South | gorman | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 65.3333 | 83.7107 | 62.834 | 18.8701 | 1.7531 | 0.25347 | 20.8767 | 22.54% | 2.094% | 0.3028% | 24.94%
H1 | H1 | ballydine | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 5.9333 | 6.9468 | 5.2012 | 1.1679 | 0.13136 | 0.44636 | 1.7456 | 16.81% | 1.891% | 6.425% | 25.13%
H2 | H2 & K | carlow | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 30.49 | 86.2478 | 82.711 | 0 | 3.5369 | 0 | 3.5369 | 0% | 4.101% | 0% | 4.101%
H1 | H1 | barrymore | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 35.2 | 110.6404 | 73.6586 | 20.4179 | 2.0656 | 14.4983 | 36.9818 | 18.45% | 1.867% | 13.1% | 33.43%
H2 | H2 & K | banoge | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 8 | 9.3665 | 7.6932 | 1.487 | 0.068745 | 0.1175 | 1.6733 | 15.88% | 0.7339% | 1.254% | 17.86%
H1 | H1 | barrymore | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 32.4 | 101.8395 | 98.3599 | 0 | 3.4796 | 0 | 3.4796 | 0% | 3.417% | 0% | 3.417%
H1 | H1 | barrymore | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 7.4833 | 8.7616 | 6.9148 | 1.214 | 0.16286 | 0.46988 | 1.8468 | 13.86% | 1.859% | 5.363% | 21.08%
H2 | H2 & K | banoge | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 8 | 9.3665 | 7.4477 | 1.487 | 0.068745 | 0.36301 | 1.9188 | 15.88% | 0.7339% | 3.876% | 20.49%
H1 | H1 | barrymore | 2030 | 100% ECP | Grandfathering | IE wind not priority | 105.6 | 331.9214 | 172.0941 | 98.9373 | 6.1146 | 54.7754 | 159.8274 | 29.81% | 1.842% | 16.5% | 48.15%
H1 | H1 | barrymore | 2030 | 100% ECP | Grandfathering | IE wind priority | 32.4 | 101.8395 | 97.7091 | 0 | 4.1305 | 0 | 4.1305 | 0% | 4.056% | 0% | 4.056%
H1 | H1 | barrymore | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 22.45 | 26.2847 | 14.9854 | 8.3416 | 0.57695 | 2.3808 | 11.2993 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | barrymore | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 105.6 | 331.9214 | 177.1948 | 98.9373 | 6.1146 | 49.6747 | 154.7267 | 29.81% | 1.842% | 14.97% | 46.62%
H2 | H2 & K | banoge | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 8 | 9.3665 | 6.1793 | 2.9725 | 0.2056 | 0.0090734 | 3.1872 | 31.74% | 2.195% | 0.09687% | 34.03%
H1 | H1 | barrymore | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 32.4 | 101.8395 | 97.7091 | 0 | 4.1305 | 0 | 4.1305 | 0% | 4.056% | 0% | 4.056%
H1 | H1 | barrymore | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 22.45 | 26.2847 | 15.1436 | 8.3416 | 0.57695 | 2.2225 | 11.141 | 31.74% | 2.195% | 8.456% | 42.39%
H2 | H2 & K | banoge | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 8 | 9.3665 | 6.0696 | 2.9725 | 0.2056 | 0.11877 | 3.2969 | 31.74% | 2.195% | 1.268% | 35.2%
H1 | H1 | barrymore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 7.4833 | 8.7616 | 6.0466 | 1.9943 | 0.18625 | 0.53441 | 2.715 | 22.76% | 2.126% | 6.1% | 30.99%
H2 | H2 & K | banoge | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 8 | 9.3665 | 7.8512 | 1.2978 | 0.17411 | 0.043376 | 1.5153 | 13.86% | 1.859% | 0.4631% | 16.18%
H1 | H1 | barrymore | 2035 | 66% ECP | Grandfathering | IE wind not priority | 70.3999 | 221.2807 | 110.5815 | 40.1784 | 0.76432 | 69.7565 | 110.6993 | 18.16% | 0.3454% | 31.52% | 50.03%
H2 | H2 & K | banoge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 8 | 9.3665 | 6.7047 | 2.132 | 0.19911 | 0.33069 | 2.6618 | 22.76% | 2.126% | 3.531% | 28.42%
H1 | H1 | barrymore | 2035 | 66% ECP | Grandfathering | IE wind priority | 32.4 | 101.8395 | 100.854 | 0 | 0.98549 | 0 | 0.98549 | 0% | 0.9677% | 0% | 0.9677%
H1 | H1 | barrymore | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 14.9667 | 17.5231 | 12.056 | 2.782 | 0.12861 | 2.5565 | 5.4671 | 15.88% | 0.7339% | 14.59% | 31.2%
H2 | H2 & K | banoge | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 8 | 9.3665 | 7.0282 | 1.8332 | 0.17709 | 0.32803 | 2.3383 | 19.57% | 1.891% | 3.502% | 24.96%
H1 | H1 | barrymore | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 70.3999 | 221.2807 | 119.8674 | 40.1784 | 0.76432 | 60.4705 | 101.4133 | 18.16% | 0.3454% | 27.33% | 45.83%
H1 | H1 | barrymore | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 32.4 | 101.8395 | 100.854 | 0 | 0.98549 | 0 | 0.98549 | 0% | 0.9677% | 0% | 0.9677%
H2 | H2 & K | banoge | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 8 | 9.3665 | 7.3658 | 1.5747 | 0.17711 | 0.24886 | 2.0007 | 16.81% | 1.891% | 2.657% | 21.36%
H1 | H1 | barrymore | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 14.9667 | 17.5231 | 12.6389 | 2.782 | 0.12861 | 1.9736 | 4.8842 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | barrymore | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 70.3999 | 221.2807 | 102.9686 | 72.2807 | 1.4224 | 44.6091 | 118.3121 | 32.66% | 0.6428% | 20.16% | 53.47%
H2 | H2 & K | banoge | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 8 | 9.3665 | 7.5548 | 1.2978 | 0.17411 | 0.3397 | 1.8116 | 13.86% | 1.859% | 3.627% | 19.34%
H1 | H1 | barrymore | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 32.4 | 101.8395 | 99.9203 | 0 | 1.9193 | 0 | 1.9193 | 0% | 1.885% | 0% | 1.885%
H1 | H1 | ballydine | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 5.9333 | 6.9468 | 5.0414 | 1.3596 | 0.13134 | 0.41442 | 1.9053 | 19.57% | 1.891% | 5.966% | 27.43%
H2 | H2 & K | banoge | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 8 | 9.3665 | 6.8616 | 2.1016 | 0.080617 | 0.32272 | 2.5049 | 22.44% | 0.8607% | 3.445% | 26.74%
H1 | H1 | barrymore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 35.2 | 110.6404 | 42.8891 | 38.3118 | 2.0507 | 27.3887 | 67.7513 | 34.63% | 1.854% | 24.75% | 61.24%
H1 | H1 | ballydine | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 5.9333 | 6.9468 | 4.7942 | 1.5812 | 0.14767 | 0.42372 | 2.1526 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | ballydine | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 5.9333 | 6.9468 | 5.4826 | 0.96256 | 0.12913 | 0.37256 | 1.4642 | 13.86% | 1.859% | 5.363% | 21.08%
H2 | H2 & K | carlow | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 7 | 19.8011 | 12.3956 | 5.9936 | 0.3776 | 1.0342 | 7.4054 | 30.27% | 1.907% | 5.223% | 37.4%
H1 | H1 | ballydine | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 11.8815 | 6.6138 | 0.45745 | 1.8877 | 8.9589 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | ballydine | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 12.007 | 6.6138 | 0.45745 | 1.7622 | 8.8334 | 31.74% | 2.195% | 8.456% | 42.39%
H2 | H2 & K | carlow | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 31.0966 | 36.4083 | 28.6316 | 6.1209 | 0.68844 | 0.96736 | 7.7767 | 16.81% | 1.891% | 2.657% | 21.36%
H1 | H1 | ballydine | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 11.8667 | 13.8936 | 9.5589 | 2.2058 | 0.10197 | 2.027 | 4.3347 | 15.88% | 0.7339% | 14.59% | 31.2%
H2 | H2 & K | carlow | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 30.49 | 86.2478 | 83.1288 | 0 | 3.119 | 0 | 3.119 | 0% | 3.616% | 0% | 3.616%
H1 | H1 | ballydine | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 11.8667 | 13.8936 | 10.0211 | 2.2058 | 0.10197 | 1.5648 | 3.8725 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | ballydine | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 11.8667 | 13.8936 | 9.1945 | 3.1173 | 0.11958 | 1.4622 | 4.6991 | 22.44% | 0.8607% | 10.52% | 33.82%
H2 | H2 & K | carlow | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 7 | 19.8011 | 14.3674 | 4.5388 | 0.36576 | 0.52913 | 5.4336 | 22.92% | 1.847% | 2.672% | 27.44%
H1 | H1 | ballydine | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 12.7193 | 4.6932 | 0.18809 | 3.2398 | 8.1211 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | barrymore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 32.4 | 101.8395 | 97.5013 | 0 | 4.3382 | 0 | 4.3382 | 0% | 4.26% | 0% | 4.26%
H2 | H2 & K | carlow | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 31.0966 | 36.4083 | 29.3663 | 5.0448 | 0.67678 | 1.3204 | 7.042 | 13.86% | 1.859% | 3.627% | 19.34%
H1 | H1 | barrymore | 2030 | 33% ECP | Grandfathering | IE wind not priority | 35.2 | 110.6404 | 67.5638 | 20.4179 | 2.0656 | 20.5931 | 43.0765 | 18.45% | 1.867% | 18.61% | 38.93%
H2 | H2 & K | carlow | 2030 | 33% ECP | Grandfathering | IE wind priority | 30.49 | 86.2478 | 83.5113 | 0 | 2.7365 | 0 | 2.7365 | 0% | 3.173% | 0% | 3.173%
H1 | H1 | barrymore | 2030 | 33% ECP | Grandfathering | IE wind priority | 32.4 | 101.8395 | 98.3599 | 0 | 3.4796 | 0 | 3.4796 | 0% | 3.417% | 0% | 3.417%
H1 | H1 | barrymore | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 7.4833 | 8.7616 | 6.8025 | 1.214 | 0.16286 | 0.5822 | 1.9591 | 13.86% | 1.859% | 6.645% | 22.36%
H2 | H2 & K | carlow | 2030 | 33% ECP | Grandfathering | IE wind not priority | 7 | 19.8011 | 15.2308 | 3.2346 | 0.35467 | 0.98098 | 4.5703 | 16.34% | 1.791% | 4.954% | 23.08%
H1 | H1 | barrymore | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 35.2 | 110.6404 | 60.0981 | 27.9615 | 2.08 | 20.5008 | 50.5423 | 25.27% | 1.88% | 18.53% | 45.68%
H1 | H1 | barrymore | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 32.4 | 101.8395 | 97.9324 | 0 | 3.9071 | 0 | 3.9071 | 0% | 3.837% | 0% | 3.837%
H2 | H2 & K | carlow | 2030 | Initial | Grandfathering | IE wind priority | 30.49 | 86.2478 | 83.825 | 0 | 2.4228 | 0 | 2.4228 | 0% | 2.809% | 0% | 2.809%
H1 | H1 | barrymore | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 7.4833 | 8.7616 | 6.5599 | 1.473 | 0.16567 | 0.56296 | 2.2016 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | barrymore | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 35.2 | 110.6404 | 50.1797 | 35.9098 | 2.0624 | 22.4885 | 60.4606 | 32.46% | 1.864% | 20.33% | 54.65%
H1 | H1 | barrymore | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 32.4 | 101.8395 | 97.5358 | 0 | 4.3038 | 0 | 4.3038 | 0% | 4.226% | 0% | 4.226%
H1 | H1 | barrymore | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 7.4833 | 8.7616 | 6.3585 | 1.7148 | 0.16566 | 0.52268 | 2.4031 | 19.57% | 1.891% | 5.966% | 27.43%
H2 | H2 & K | banoge | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 8 | 9.3665 | 6.8593 | 2.1093 | 0.084533 | 0.31338 | 2.5072 | 22.52% | 0.9025% | 3.346% | 26.77%
H1 | H1 | barrymore | 2030 | Initial | Grandfathering | IE wind priority | 32.4 | 101.8395 | 98.7542 | 0 | 3.0853 | 0 | 3.0853 | 0% | 3.03% | 0% | 3.03%
G | J City, G South | drybridge | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 16.64 | 21.3206 | 16.4497 | 4.6843 | 0.18216 | 0.0045079 | 4.8709 | 21.97% | 0.8544% | 0.02114% | 22.85%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 39.99 | 46.8207 | 35.1322 | 9.1635 | 0.88525 | 1.6397 | 11.6885 | 19.57% | 1.891% | 3.502% | 24.96%
H1 | H1 | doon | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 19.3267 | 22.6278 | 15.5681 | 3.5924 | 0.16608 | 3.3013 | 7.0598 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | nenagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 30.6666 | 35.9048 | 25.8971 | 5.7003 | 0.26352 | 4.0439 | 10.0077 | 15.88% | 0.7339% | 11.26% | 27.87%
H2 | H2 & K | arklow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 80.9633 | 94.7927 | 67.8543 | 21.5766 | 2.015 | 3.3467 | 26.9384 | 22.76% | 2.126% | 3.531% | 28.42%
H1 | H1 | nenagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 30.6666 | 35.9048 | 23.761 | 8.056 | 0.30903 | 3.7787 | 12.1438 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | nenagh | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 46 | 53.8573 | 32.8701 | 12.1285 | 0.48606 | 8.3726 | 20.9871 | 22.52% | 0.9025% | 15.55% | 38.97%
H2 | H2 & K | arklow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 53.2 | 150.4882 | 144.2308 | 0 | 6.2574 | 0 | 6.2574 | 0% | 4.158% | 0% | 4.158%
H1 | H1 | springmount | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 21.6666 | 25.3675 | 19.6954 | 3.515 | 0.47155 | 1.6856 | 5.6722 | 13.86% | 1.859% | 6.645% | 22.36%
H2 | H2 & K | arklow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 13.33 | 37.7069 | 22.2499 | 12.2255 | 0.72557 | 2.5059 | 15.457 | 32.42% | 1.924% | 6.646% | 40.99%
H1 | H1 | springmount | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 21.6666 | 25.3675 | 18.9931 | 4.2647 | 0.47967 | 1.63 | 6.3744 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | springmount | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 21.6666 | 25.3675 | 18.4098 | 4.9648 | 0.47963 | 1.5133 | 6.9577 | 19.57% | 1.891% | 5.966% | 27.43%
H2 | H2 & K | arklow | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 80.9633 | 94.7927 | 71.1283 | 18.5523 | 1.7923 | 3.3198 | 23.6643 | 19.57% | 1.891% | 3.502% | 24.96%
H1 | H1 | springmount | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 21.6666 | 25.3675 | 17.5069 | 5.7741 | 0.53924 | 1.5473 | 7.8607 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | springmount | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 21.6666 | 25.3675 | 20.0205 | 3.515 | 0.47155 | 1.3605 | 5.347 | 13.86% | 1.859% | 5.363% | 21.08%
H2 | H2 & K | arklow | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 53.2 | 150.4882 | 144.3169 | 0 | 6.1713 | 0 | 6.1713 | 0% | 4.101% | 0% | 4.101%
H1 | H1 | springmount | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 65 | 76.1026 | 43.3875 | 24.1516 | 1.6705 | 6.8931 | 32.7152 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | springmount | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 65 | 76.1026 | 43.8457 | 24.1516 | 1.6705 | 6.4349 | 32.2569 | 31.74% | 2.195% | 8.456% | 42.39%
H2 | H2 & K | arklow | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 13.33 | 37.7069 | 23.6048 | 11.4136 | 0.71906 | 1.9693 | 14.102 | 30.27% | 1.907% | 5.223% | 37.4%
H1 | H1 | springmount | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 43.3333 | 50.735 | 34.906 | 8.0547 | 0.37237 | 7.402 | 15.8291 | 15.88% | 0.7339% | 14.59% | 31.2%
H2 | H2 & K | arklow | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 80.9633 | 94.7927 | 74.5452 | 15.9364 | 1.7924 | 2.5186 | 20.2474 | 16.81% | 1.891% | 2.657% | 21.36%
H1 | H1 | springmount | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 43.3333 | 50.735 | 36.5937 | 8.0547 | 0.37237 | 5.7142 | 14.1413 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | springmount | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 43.3333 | 50.735 | 33.5754 | 11.3835 | 0.43667 | 5.3395 | 17.1597 | 22.44% | 0.8607% | 10.52% | 33.82%
H2 | H2 & K | arklow | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 53.2 | 150.4882 | 145.046 | 0 | 5.4422 | 0 | 5.4422 | 0% | 3.616% | 0% | 3.616%
H1 | H1 | springmount | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 65 | 76.1026 | 46.4469 | 17.138 | 0.68683 | 11.8309 | 29.6557 | 22.52% | 0.9025% | 15.55% | 38.97%
H2 | H2 & K | arklow | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 13.33 | 37.7069 | 27.3597 | 8.6431 | 0.69651 | 1.0076 | 10.3472 | 22.92% | 1.847% | 2.672% | 27.44%
H1 | H1 | thurles | 2030 | Initial | Grandfathering | IE wind priority | 34.9 | 109.6975 | 106.3741 | 0 | 3.3234 | 0 | 3.3234 | 0% | 3.03% | 0% | 3.03%
H1 | H1 | thurles | 2030 | 33% ECP | Grandfathering | IE wind not priority | 0.78333 | 2.4622 | 1.5036 | 0.45438 | 0.045968 | 0.45827 | 0.95862 | 18.45% | 1.867% | 18.61% | 38.93%
H2 | H2 & K | arklow | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 80.9633 | 94.7927 | 76.4581 | 13.1346 | 1.7621 | 3.4379 | 18.3346 | 13.86% | 1.859% | 3.627% | 19.34%
H1 | H1 | nenagh | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 30.6666 | 35.9048 | 24.7027 | 5.7003 | 0.26352 | 5.2383 | 11.2021 | 15.88% | 0.7339% | 14.59% | 31.2%
H2 | H2 & K | arklow | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 13.33 | 37.7069 | 30.5206 | 6.1596 | 0.67539 | 0.35128 | 7.1863 | 16.34% | 1.791% | 0.9316% | 19.06%
H1 | H1 | nenagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 46 | 53.8573 | 31.0293 | 17.0919 | 1.1822 | 4.5539 | 22.828 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | lisheen | 2035 | 66% ECP | Grandfathering | IE wind priority | 98.6 | 309.9191 | 306.92 | 0 | 2.9991 | 0 | 2.9991 | 0% | 0.9677% | 0% | 0.9677%
H1 | H1 | lisheen | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 50.6666 | 59.321 | 40.8132 | 9.4178 | 0.43538 | 8.6546 | 18.5078 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | lisheen | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 28.8 | 90.524 | 49.0367 | 16.4367 | 0.31268 | 24.738 | 41.4873 | 18.16% | 0.3454% | 27.33% | 45.83%
H1 | H1 | lisheen | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 98.6 | 309.9191 | 306.92 | 0 | 2.9991 | 0 | 2.9991 | 0% | 0.9677% | 0% | 0.9677%
H1 | H1 | lisheen | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 50.6666 | 59.321 | 42.7865 | 9.4178 | 0.43538 | 6.6813 | 16.5345 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | lisheen | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 28.8 | 90.524 | 42.1236 | 29.5694 | 0.58188 | 18.2492 | 48.4005 | 32.66% | 0.6428% | 20.16% | 53.47%
H2 | H2 & K | arklow | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 128.89 | 150.9057 | 99.5564 | 47.8907 | 3.3124 | 0.14618 | 51.3493 | 31.74% | 2.195% | 0.09687% | 34.03%
H1 | H1 | lisheen | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 98.6 | 309.9191 | 304.0783 | 0 | 5.8407 | 0 | 5.8407 | 0% | 1.885% | 0% | 1.885%
H1 | H1 | lisheen | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 50.6666 | 59.321 | 39.2573 | 13.3099 | 0.51057 | 6.2431 | 20.0636 | 22.44% | 0.8607% | 10.52% | 33.82%
H2 | H2 & K | arklow | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 53.2 | 150.4882 | 144.6944 | 0 | 5.7938 | 0 | 5.7938 | 0% | 3.85% | 0% | 3.85%
H1 | H1 | lisheen | 2035 | 100% ECP | Grandfathering | IE wind not priority | 28.8 | 90.524 | 44.141 | 18.0458 | 0.33547 | 28.0018 | 46.3831 | 19.93% | 0.3706% | 30.93% | 51.24%
H1 | H1 | lisheen | 2035 | 100% ECP | Grandfathering | IE wind priority | 98.6 | 309.9191 | 306.5672 | 0 | 3.3518 | 0 | 3.3518 | 0% | 1.082% | 0% | 1.082%
H1 | H1 | thurles | 2030 | 33% ECP | Grandfathering | IE wind priority | 34.9 | 109.6975 | 105.9494 | 0 | 3.7481 | 0 | 3.7481 | 0% | 3.417% | 0% | 3.417%
H2 | H2 & K | arklow | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 39.99 | 113.1207 | 79.2934 | 31.1045 | 2.0673 | 0.65552 | 33.8273 | 27.5% | 1.828% | 0.5795% | 29.9%
H2 | H2 & K | arklow | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 128.89 | 150.9057 | 97.7891 | 47.8907 | 3.3124 | 1.9135 | 53.1166 | 31.74% | 2.195% | 1.268% | 35.2%
H2 | H2 & K | arklow | 2030 | 100% ECP | Grandfathering | IE wind priority | 53.2 | 150.4882 | 144.6944 | 0 | 5.7938 | 0 | 5.7938 | 0% | 3.85% | 0% | 3.85%
H1 | H1 | nenagh | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 15.3333 | 17.9524 | 13.9383 | 2.4875 | 0.33371 | 1.1929 | 4.0141 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | nenagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 15.3333 | 17.9524 | 13.4413 | 3.0181 | 0.33946 | 1.1535 | 4.5111 | 16.81% | 1.891% | 6.425% | 25.13%
H2 | H2 & K | arklow | 2030 | 100% ECP | Grandfathering | IE wind not priority | 39.99 | 113.1207 | 77.451 | 31.1045 | 2.0673 | 2.498 | 35.6698 | 27.5% | 1.828% | 2.208% | 31.53%
H1 | H1 | nenagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 15.3333 | 17.9524 | 13.0285 | 3.5135 | 0.33943 | 1.071 | 4.9239 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | nenagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 15.3333 | 17.9524 | 12.3895 | 4.0863 | 0.38162 | 1.095 | 5.5629 | 22.76% | 2.126% | 6.1% | 30.99%
H2 | H2 & K | arklow | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 80.9633 | 94.7927 | 79.457 | 13.1346 | 1.7621 | 0.43898 | 15.3357 | 13.86% | 1.859% | 0.4631% | 16.18%
H1 | H1 | nenagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 15.3333 | 17.9524 | 14.1684 | 2.4875 | 0.33371 | 0.96279 | 3.784 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | nenagh | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 46 | 53.8573 | 30.705 | 17.0919 | 1.1822 | 4.8782 | 23.1523 | 31.74% | 2.195% | 9.058% | 42.99%
H2 | H2 & K | arklow | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 53.2 | 150.4882 | 145.7135 | 0 | 4.7747 | 0 | 4.7747 | 0% | 3.173% | 0% | 3.173%
H1 | H1 | lisheen | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 76 | 88.9816 | 54.3071 | 20.0383 | 0.80306 | 13.833 | 34.6744 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | thurles | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 46.6666 | 54.6377 | 42.4208 | 7.5707 | 1.0156 | 3.6306 | 12.217 | 13.86% | 1.859% | 6.645% | 22.36%
H2 | H2 & K | arklow | 2030 | 33% ECP | Grandfathering | IE wind priority | 53.2 | 150.4882 | 145.7135 | 0 | 4.7747 | 0 | 4.7747 | 0% | 3.173% | 0% | 3.173%
H1 | H1 | thurles | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 0.78333 | 2.4622 | 1.3374 | 0.62225 | 0.046287 | 0.45622 | 1.1248 | 25.27% | 1.88% | 18.53% | 45.68%
H1 | H1 | tipperary | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 12.3333 | 14.44 | 11.3963 | 2.0008 | 0.26842 | 0.77442 | 3.0437 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | thurles | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 1.5667 | 4.9243 | 2.6675 | 0.89412 | 0.017009 | 1.3457 | 2.2568 | 18.16% | 0.3454% | 27.33% | 45.83%
H1 | H1 | thurles | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 34.9 | 109.6975 | 108.636 | 0 | 1.0615 | 0 | 1.0615 | 0% | 0.9677% | 0% | 0.9677%
H1 | H1 | tipperary | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 12.3333 | 14.44 | 9.9654 | 3.2868 | 0.30695 | 0.88077 | 4.4745 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | thurles | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 93.3332 | 109.2755 | 78.8173 | 17.3486 | 0.80202 | 12.3076 | 30.4582 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | thurles | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 1.5667 | 4.9243 | 2.2914 | 1.6085 | 0.031653 | 0.99272 | 2.6329 | 32.66% | 0.6428% | 20.16% | 53.47%
H1 | H1 | tipperary | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 12.3333 | 14.44 | 10.4794 | 2.8261 | 0.27302 | 0.86143 | 3.9606 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | thurles | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 34.9 | 109.6975 | 107.6302 | 0 | 2.0674 | 0 | 2.0674 | 0% | 1.885% | 0% | 1.885%
H1 | H1 | thurles | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 93.3332 | 109.2755 | 72.3161 | 24.5183 | 0.94053 | 11.5005 | 36.9593 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | tipperary | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 12.3333 | 14.44 | 10.8115 | 2.4276 | 0.27305 | 0.92782 | 3.6285 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | thurles | 2035 | 100% ECP | Grandfathering | IE wind not priority | 2.35 | 7.3865 | 3.6018 | 1.4725 | 0.027374 | 2.2849 | 3.7847 | 19.93% | 0.3706% | 30.93% | 51.24%
H1 | H1 | thurles | 2035 | 100% ECP | Grandfathering | IE wind priority | 34.9 | 109.6975 | 108.5111 | 0 | 1.1864 | 0 | 1.1864 | 0% | 1.082% | 0% | 1.082%
H1 | H1 | tipperary | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 12.3333 | 14.44 | 11.2112 | 2.0008 | 0.26842 | 0.95952 | 3.2288 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | thurles | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 140 | 163.9134 | 100.0395 | 36.9127 | 1.4793 | 25.4819 | 63.8739 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | thurles | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 93.3332 | 109.2755 | 75.1821 | 17.3486 | 0.80202 | 15.9427 | 34.0934 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | timoney | 2030 | Initial | Grandfathering | IE Solar not priority | 156.56 | 183.302 | 158.711 | 15.1601 | 2.3619 | 7.0691 | 24.591 | 8.271% | 1.289% | 3.857% | 13.42%
H1 | H1 | timoney | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 161.56 | 189.1561 | 146.8609 | 26.2098 | 3.5161 | 12.5692 | 42.2952 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | timoney | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 171.56 | 200.8642 | 122.5912 | 45.2339 | 1.8128 | 31.2262 | 78.2729 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | timoney | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 161.56 | 189.1561 | 141.6247 | 31.8006 | 3.5768 | 12.154 | 47.5313 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | timoney | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 161.56 | 189.1561 | 137.2748 | 37.0206 | 3.5764 | 11.2842 | 51.8812 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | timoney | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 166.56 | 195.0101 | 129.0534 | 43.7547 | 1.6784 | 20.5235 | 65.9567 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | timoney | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 161.56 | 189.1561 | 130.542 | 43.0556 | 4.0209 | 11.5376 | 58.6141 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | timoney | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 161.56 | 189.1561 | 149.2857 | 26.2098 | 3.5161 | 10.1444 | 39.8704 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | timoney | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 166.56 | 195.0101 | 140.6552 | 30.9599 | 1.4313 | 21.9638 | 54.3549 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | timoney | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 171.56 | 200.8642 | 114.5163 | 63.7453 | 4.409 | 18.1936 | 86.3479 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | timoney | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 171.56 | 200.8642 | 115.7258 | 63.7453 | 4.409 | 16.9841 | 85.1384 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | tipperary | 2030 | Initial | Grandfathering | IE Solar not priority | 4 | 4.6832 | 4.055 | 0.38733 | 0.060344 | 0.18061 | 0.62828 | 8.271% | 1.289% | 3.857% | 13.42%
H1 | H1 | thurles | 2035 | 66% ECP | Grandfathering | IE wind priority | 34.9 | 109.6975 | 108.636 | 0 | 1.0615 | 0 | 1.0615 | 0% | 0.9677% | 0% | 0.9677%
H1 | H1 | thurles | 2035 | 66% ECP | Grandfathering | IE wind not priority | 1.5667 | 4.9243 | 2.4609 | 0.89412 | 0.017009 | 1.5523 | 2.4635 | 18.16% | 0.3454% | 31.52% | 50.03%
H1 | H1 | thurles | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 34.9 | 109.6975 | 105.4889 | 0 | 4.2086 | 0 | 4.2086 | 0% | 3.837% | 0% | 3.837%
H2 | H2 & K | arklow | 2030 | 33% ECP | Grandfathering | IE wind not priority | 13.33 | 37.7069 | 29.0038 | 6.1596 | 0.67539 | 1.8681 | 8.7031 | 16.34% | 1.791% | 4.954% | 23.08%
H1 | H1 | thurles | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 46.6666 | 54.6377 | 40.9083 | 9.1856 | 1.0331 | 3.5107 | 13.7294 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | thurles | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 0.78333 | 2.4622 | 1.1167 | 0.79913 | 0.045896 | 0.50045 | 1.3455 | 32.46% | 1.864% | 20.33% | 54.65%
H2 | H2 & K | arklow | 2030 | Initial | Grandfathering | IE Solar not priority | 57 | 66.7362 | 55.6509 | 5.5195 | 0.8599 | 4.706 | 11.0853 | 8.271% | 1.289% | 7.052% | 16.61%
H1 | H1 | thurles | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 34.9 | 109.6975 | 105.0617 | 0 | 4.6358 | 0 | 4.6358 | 0% | 4.226% | 0% | 4.226%
H1 | H1 | thurles | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 46.6666 | 54.6377 | 39.6519 | 10.6934 | 1.033 | 3.2594 | 14.9859 | 19.57% | 1.891% | 5.966% | 27.43%
H2 | H2 & K | arklow | 2030 | Initial | Grandfathering | IE wind priority | 53.2 | 150.4882 | 146.2607 | 0 | 4.2275 | 0 | 4.2275 | 0% | 2.809% | 0% | 2.809%
H1 | H1 | thurles | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 0.78333 | 2.4622 | 0.95444 | 0.85258 | 0.045637 | 0.6095 | 1.5077 | 34.63% | 1.854% | 24.75% | 61.24%
H1 | H1 | thurles | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 34.9 | 109.6975 | 105.0245 | 0 | 4.673 | 0 | 4.673 | 0% | 4.26% | 0% | 4.26%
H1 | H1 | thurles | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 46.6666 | 54.6377 | 37.7071 | 12.4366 | 1.1614 | 3.3326 | 16.9307 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | thurles | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 0.78333 | 2.4622 | 1.6392 | 0.45438 | 0.045968 | 0.32264 | 0.82298 | 18.45% | 1.867% | 13.1% | 33.43%
H1 | H1 | tipperary | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 29 | 33.9535 | 20.7225 | 7.6462 | 0.30643 | 5.2784 | 13.231 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | tipperary | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 29 | 33.9535 | 19.3575 | 10.7753 | 0.74528 | 3.0754 | 14.596 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | thurles | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 34.9 | 109.6975 | 105.9494 | 0 | 3.7481 | 0 | 3.7481 | 0% | 3.417% | 0% | 3.417%
H1 | H1 | tipperary | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 20.6667 | 24.1967 | 16.0129 | 5.429 | 0.20826 | 2.5465 | 8.1839 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | thurles | 2030 | 100% ECP | Grandfathering | IE wind not priority | 2.35 | 7.3865 | 3.8297 | 2.2017 | 0.13607 | 1.219 | 3.5568 | 29.81% | 1.842% | 16.5% | 48.15%
H1 | H1 | thurles | 2030 | 100% ECP | Grandfathering | IE wind priority | 34.9 | 109.6975 | 105.2483 | 0 | 4.4492 | 0 | 4.4492 | 0% | 4.056% | 0% | 4.056%
H1 | H1 | tipperary | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 20.6667 | 24.1967 | 17.4524 | 3.8415 | 0.17759 | 2.7253 | 6.7443 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | thurles | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 140 | 163.9134 | 93.45 | 52.0187 | 3.5979 | 14.8468 | 70.4634 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | thurles | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 2.35 | 7.3865 | 3.9433 | 2.2017 | 0.13607 | 1.1055 | 3.4433 | 29.81% | 1.842% | 14.97% | 46.62%
H1 | H1 | tipperary | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 20.6667 | 24.1967 | 16.6475 | 3.8415 | 0.17759 | 3.5302 | 7.5492 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | thurles | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 34.9 | 109.6975 | 105.2483 | 0 | 4.4492 | 0 | 4.4492 | 0% | 4.056% | 0% | 4.056%
H1 | H1 | thurles | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 140 | 163.9134 | 94.437 | 52.0187 | 3.5979 | 13.8597 | 69.4764 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | tipperary | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 29 | 33.9535 | 19.5619 | 10.7753 | 0.74528 | 2.8709 | 14.3915 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | thurles | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 46.6666 | 54.6377 | 43.1212 | 7.5707 | 1.0156 | 2.9302 | 11.5166 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | lisheen | 2035 | 66% ECP | Grandfathering | IE wind not priority | 28.8 | 90.524 | 45.2379 | 16.4367 | 0.31268 | 28.5368 | 45.2861 | 18.16% | 0.3454% | 31.52% | 50.03%
H2 | H2 & K | arklow | 2035 | 66% ECP | Grandfathering | IE wind not priority | 26.66 | 75.4137 | 58.3115 | 12.2386 | 0.24786 | 4.6158 | 17.1022 | 16.23% | 0.3287% | 6.121% | 22.68%
H1 | H1 | kill hill | 2030 | Initial | Grandfathering | IE wind priority | 36 | 113.155 | 109.7269 | 0 | 3.4282 | 0 | 3.4282 | 0% | 3.03% | 0% | 3.03%
H1 | H1 | kill hill | 2030 | 33% ECP | Grandfathering | IE wind priority | 36 | 113.155 | 109.2888 | 0 | 3.8662 | 0 | 3.8662 | 0% | 3.417% | 0% | 3.417%
H2 | H2 & K | ballybeg | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 150.5 | 192.8337 | 142.2343 | 42.4 | 1.7475 | 6.4518 | 50.5994 | 21.99% | 0.9062% | 3.346% | 26.24%
H1 | H1 | kill hill | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 26.6666 | 31.2216 | 24.2404 | 4.3261 | 0.58036 | 2.0746 | 6.9811 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | kill hill | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 36 | 113.155 | 108.8138 | 0 | 4.3413 | 0 | 4.3413 | 0% | 3.837% | 0% | 3.837%
H2 | H2 & K | ballybeg | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 102.9999 | 131.9724 | 97.3026 | 28.9952 | 1.1275 | 4.5471 | 34.6698 | 21.97% | 0.8544% | 3.445% | 26.27%
H1 | H1 | kill hill | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 26.6666 | 31.2216 | 23.3762 | 5.2489 | 0.59037 | 2.0061 | 7.8454 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | kill hill | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 36 | 113.155 | 108.3731 | 0 | 4.782 | 0 | 4.782 | 0% | 4.226% | 0% | 4.226%
H2 | H2 & K | ballybeg | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 102.9999 | 131.9724 | 109.1498 | 20.2156 | 0.9515 | 1.6555 | 22.8227 | 15.32% | 0.721% | 1.254% | 17.29%
H1 | H1 | kill hill | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 26.6666 | 31.2216 | 22.6582 | 6.1105 | 0.59031 | 1.8625 | 8.5634 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | kill hill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 36 | 113.155 | 108.3348 | 0 | 4.8203 | 0 | 4.8203 | 0% | 4.26% | 0% | 4.26%
H2 | H2 & K | ballybeg | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 102.9999 | 131.9724 | 105.6905 | 20.2156 | 0.9515 | 5.1148 | 26.2819 | 15.32% | 0.721% | 3.876% | 19.91%
H1 | H1 | kill hill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 26.6666 | 31.2216 | 21.5469 | 7.1066 | 0.66368 | 1.9044 | 9.6747 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | kill hill | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 36 | 113.155 | 109.2888 | 0 | 3.8662 | 0 | 3.8662 | 0% | 3.417% | 0% | 3.417%
H1 | H1 | kill hill | 2030 | 100% ECP | Grandfathering | IE wind priority | 36 | 113.155 | 108.5656 | 0 | 4.5894 | 0 | 4.5894 | 0% | 4.056% | 0% | 4.056%
H2 | H2 & K | ballybeg | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 150.5 | 192.8337 | 127.5451 | 60.8533 | 4.2485 | 0.1868 | 65.2886 | 31.56% | 2.203% | 0.09687% | 33.86%
H1 | H1 | kill hill | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 80 | 93.6648 | 53.4 | 29.725 | 2.056 | 8.4839 | 40.2648 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | kill hill | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 36 | 113.155 | 108.5656 | 0 | 4.5894 | 0 | 4.5894 | 0% | 4.056% | 0% | 4.056%
H2 | H2 & K | ballybeg | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 150.5 | 192.8337 | 125.2868 | 60.8533 | 4.2485 | 2.4451 | 67.5469 | 31.56% | 2.203% | 1.268% | 35.03%
H1 | H1 | kill hill | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 80 | 93.6648 | 53.964 | 29.725 | 2.056 | 7.9199 | 39.7008 | 31.74% | 2.195% | 8.456% | 42.39%
H2 | H2 & K | ballybeg | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 55.5 | 71.1114 | 59.8021 | 9.6631 | 1.3169 | 0.32932 | 11.3093 | 13.59% | 1.852% | 0.4631% | 15.9%
H1 | H1 | kill hill | 2035 | 66% ECP | Grandfathering | IE wind priority | 36 | 113.155 | 112.06 | 0 | 1.095 | 0 | 1.095 | 0% | 0.9677% | 0% | 0.9677%
H2 | H2 & K | ballybeg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 55.5 | 71.1114 | 51.0815 | 16.03 | 1.4892 | 2.5106 | 20.0298 | 22.54% | 2.094% | 3.531% | 28.17%
H1 | H1 | kill hill | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 53.3333 | 62.4431 | 42.9612 | 9.9135 | 0.4583 | 9.1101 | 19.4819 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | kill hill | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 36 | 113.155 | 112.06 | 0 | 1.095 | 0 | 1.095 | 0% | 0.9677% | 0% | 0.9677%
H2 | H2 & K | ballybeg | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 55.5 | 71.1114 | 53.5246 | 13.7805 | 1.3159 | 2.4904 | 17.5868 | 19.38% | 1.851% | 3.502% | 24.73%
H1 | H1 | kill hill | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 26.6666 | 31.2216 | 24.6407 | 4.3261 | 0.58036 | 1.6744 | 6.5809 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | kill hill | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 53.3333 | 62.4431 | 45.0384 | 9.9135 | 0.4583 | 7.0329 | 17.4047 | 15.88% | 0.7339% | 11.26% | 27.87%
H2 | H2 & K | ballyragget | 2030 | Initial | Grandfathering | IE wind not priority | 45 | 127.2926 | 75.9018 | 15.1317 | 2.3098 | 33.9493 | 51.3908 | 11.89% | 1.815% | 26.67% | 40.37%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 9.2 | 26.0243 | 24.9571 | 0 | 1.0672 | 0 | 1.0672 | 0% | 4.101% | 0% | 4.101%
H1 | H1 | doon | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 22.4 | 70.4075 | 38.1396 | 12.784 | 0.24319 | 19.2406 | 32.2679 | 18.16% | 0.3454% | 27.33% | 45.83%
H1 | H1 | doon | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 19.3267 | 22.6278 | 16.3208 | 3.5924 | 0.16608 | 2.5486 | 6.307 | 15.88% | 0.7339% | 11.26% | 27.87%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 77.8 | 220.0747 | 137.7688 | 66.6151 | 4.1968 | 11.494 | 82.306 | 30.27% | 1.907% | 5.223% | 37.4%
H1 | H1 | doon | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 22.4 | 70.4075 | 32.7627 | 22.9984 | 0.45258 | 14.1938 | 37.6448 | 32.66% | 0.6428% | 20.16% | 53.47%
H1 | H1 | doon | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 19.3267 | 22.6278 | 14.9746 | 5.077 | 0.19476 | 2.3814 | 7.6532 | 22.44% | 0.8607% | 10.52% | 33.82%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 39.99 | 46.8207 | 36.8199 | 7.8714 | 0.88533 | 1.244 | 10.0008 | 16.81% | 1.891% | 2.657% | 21.36%
H1 | H1 | doon | 2035 | 100% ECP | Grandfathering | IE wind not priority | 33.6 | 105.6114 | 51.4978 | 21.0534 | 0.39138 | 32.6688 | 54.1136 | 19.93% | 0.3706% | 30.93% | 51.24%
H1 | H1 | doon | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 24.99 | 29.2585 | 17.857 | 6.5889 | 0.26406 | 4.5485 | 11.4015 | 22.52% | 0.9025% | 15.55% | 38.97%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 9.2 | 26.0243 | 25.0831 | 0 | 0.94114 | 0 | 0.94114 | 0% | 3.616% | 0% | 3.616%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 77.8 | 220.0747 | 159.6836 | 50.4451 | 4.0651 | 5.8809 | 60.3911 | 22.92% | 1.847% | 2.672% | 27.44%
H1 | H1 | ikerrin | 2030 | Initial | Grandfathering | IE wind priority | 35.95 | 112.9979 | 109.5745 | 0 | 3.4234 | 0 | 3.4234 | 0% | 3.03% | 0% | 3.03%
H1 | H1 | ikerrin | 2035 | 100% ECP | Grandfathering | IE wind priority | 35.95 | 112.9979 | 111.7758 | 0 | 1.2221 | 0 | 1.2221 | 0% | 1.082% | 0% | 1.082%
H1 | H1 | ikerrin | 2030 | 33% ECP | Grandfathering | IE wind priority | 35.95 | 112.9979 | 109.137 | 0 | 3.8609 | 0 | 3.8609 | 0% | 3.417% | 0% | 3.417%
H1 | H1 | ikerrin | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 35.95 | 112.9979 | 108.6627 | 0 | 4.3352 | 0 | 4.3352 | 0% | 3.837% | 0% | 3.837%
H1 | H1 | ikerrin | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 35.95 | 112.9979 | 108.2226 | 0 | 4.7753 | 0 | 4.7753 | 0% | 4.226% | 0% | 4.226%
H2 | H2 & K | ballyragget | 2030 | 33% ECP | Grandfathering | IE wind priority | 9.2 | 26.0243 | 25.1986 | 0 | 0.8257 | 0 | 0.8257 | 0% | 3.173% | 0% | 3.173%
H1 | H1 | ikerrin | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 35.95 | 112.9979 | 108.1843 | 0 | 4.8136 | 0 | 4.8136 | 0% | 4.26% | 0% | 4.26%
H1 | H1 | ikerrin | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 35.95 | 112.9979 | 109.137 | 0 | 3.8609 | 0 | 3.8609 | 0% | 3.417% | 0% | 3.417%
H2 | H2 & K | ballyragget | 2030 | 33% ECP | Grandfathering | IE wind not priority | 77.8 | 220.0747 | 169.2795 | 35.9505 | 3.9419 | 10.9029 | 50.7952 | 16.34% | 1.791% | 4.954% | 23.08%
H1 | H1 | ikerrin | 2030 | 100% ECP | Grandfathering | IE wind priority | 35.95 | 112.9979 | 108.4148 | 0 | 4.583 | 0 | 4.583 | 0% | 4.056% | 0% | 4.056%
H1 | H1 | ikerrin | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 35.95 | 112.9979 | 108.4148 | 0 | 4.583 | 0 | 4.583 | 0% | 4.056% | 0% | 4.056%
H2 | H2 & K | ballyragget | 2030 | Initial | Grandfathering | IE Solar not priority | 39.99 | 46.8207 | 39.0435 | 3.8723 | 0.60329 | 3.3016 | 7.7772 | 8.271% | 1.289% | 7.052% | 16.61%
H1 | H1 | ikerrin | 2035 | 66% ECP | Grandfathering | IE wind priority | 35.95 | 112.9979 | 111.9044 | 0 | 1.0935 | 0 | 1.0935 | 0% | 0.9677% | 0% | 0.9677%
H2 | H2 & K | ballyragget | 2030 | Initial | Grandfathering | IE wind priority | 9.2 | 26.0243 | 25.2932 | 0 | 0.73106 | 0 | 0.73106 | 0% | 2.809% | 0% | 2.809%
H1 | H1 | ikerrin | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 35.95 | 112.9979 | 111.9044 | 0 | 1.0935 | 0 | 1.0935 | 0% | 0.9677% | 0% | 0.9677%
H1 | H1 | ikerrin | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 35.95 | 112.9979 | 110.8683 | 0 | 2.1296 | 0 | 2.1296 | 0% | 1.885% | 0% | 1.885%
H2 | H2 & K | ballyragget | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 39.99 | 46.8207 | 37.7647 | 6.4876 | 0.87033 | 1.6981 | 9.056 | 13.86% | 1.859% | 3.627% | 19.34%
H1 | H1 | doon | 2035 | 66% ECP | Grandfathering | IE wind not priority | 22.4 | 70.4075 | 35.185 | 12.784 | 0.24319 | 22.1953 | 35.2225 | 18.16% | 0.3454% | 31.52% | 50.03%
H1 | H1 | kill hill | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 36 | 113.155 | 111.0225 | 0 | 2.1325 | 0 | 2.1325 | 0% | 1.885% | 0% | 1.885%
H1 | H1 | kill hill | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 53.3333 | 62.4431 | 41.3235 | 14.0104 | 0.53745 | 6.5717 | 21.1196 | 22.44% | 0.8607% | 10.52% | 33.82%
H2 | H2 & K | arklow | 2035 | 100% ECP | Grandfathering | IE wind priority | 53.2 | 150.4882 | 149.0518 | 0 | 1.4364 | 0 | 1.4364 | 0% | 0.9545% | 0% | 0.9545%
H1 | H1 | lisheen | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 28.8 | 90.524 | 49.1712 | 22.8776 | 1.7018 | 16.7734 | 41.3528 | 25.27% | 1.88% | 18.53% | 45.68%
H1 | H1 | lisheen | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 98.6 | 309.9191 | 298.0289 | 0 | 11.8902 | 0 | 11.8902 | 0% | 3.837% | 0% | 3.837%
H2 | H2 & K | arklow | 2035 | 100% ECP | Grandfathering | IE wind not priority | 39.99 | 113.1207 | 84.0201 | 20.3534 | 0.40504 | 8.3422 | 29.1006 | 17.99% | 0.3581% | 7.375% | 25.73%
H1 | H1 | lisheen | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 25.3333 | 29.6605 | 22.2074 | 4.9865 | 0.56085 | 1.9058 | 7.4531 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | lisheen | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 28.8 | 90.524 | 41.0562 | 29.3808 | 1.6874 | 18.3997 | 49.4678 | 32.46% | 1.864% | 20.33% | 54.65%
H2 | H2 & K | arklow | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 104.9266 | 122.8491 | 89.9952 | 27.5638 | 1.0574 | 4.2328 | 32.8539 | 22.44% | 0.8607% | 3.445% | 26.74%
H1 | H1 | lisheen | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 98.6 | 309.9191 | 296.8218 | 0 | 13.0973 | 0 | 13.0973 | 0% | 4.226% | 0% | 4.226%
H1 | H1 | lisheen | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 25.3333 | 29.6605 | 21.5253 | 5.805 | 0.5608 | 1.7694 | 8.1352 | 19.57% | 1.891% | 5.966% | 27.43%
H2 | H2 & K | arklow | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 53.2 | 150.4882 | 147.7208 | 0 | 2.7674 | 0 | 2.7674 | 0% | 1.839% | 0% | 1.839%
H1 | H1 | lisheen | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 28.8 | 90.524 | 35.0911 | 31.3461 | 1.6779 | 22.409 | 55.4329 | 34.63% | 1.854% | 24.75% | 61.24%
H1 | H1 | lisheen | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 98.6 | 309.9191 | 296.7169 | 0 | 13.2022 | 0 | 13.2022 | 0% | 4.26% | 0% | 4.26%
H2 | H2 & K | arklow | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 26.66 | 75.4137 | 46.9437 | 23.3779 | 0.5077 | 4.5844 | 28.47 | 31% | 0.6732% | 6.079% | 37.75%
H1 | H1 | lisheen | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 25.3333 | 29.6605 | 20.4695 | 6.7513 | 0.6305 | 1.8091 | 9.1909 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | lisheen | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 25.3333 | 29.6605 | 23.0284 | 4.1098 | 0.55135 | 1.9709 | 6.6321 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | lisheen | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 28.8 | 90.524 | 60.2662 | 16.7056 | 1.69 | 11.8622 | 30.2578 | 18.45% | 1.867% | 13.1% | 33.43%
H1 | H1 | lisheen | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 98.6 | 309.9191 | 299.3299 | 0 | 10.5892 | 0 | 10.5892 | 0% | 3.417% | 0% | 3.417%
H1 | H1 | lisheen | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 25.3333 | 29.6605 | 23.4086 | 4.1098 | 0.55135 | 1.5907 | 6.2518 | 13.86% | 1.859% | 5.363% | 21.08%
H2 | H2 & K | arklow | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 53.2 | 150.4882 | 149.1775 | 0 | 1.3107 | 0 | 1.3107 | 0% | 0.871% | 0% | 0.871%
H1 | H1 | lisheen | 2030 | 100% ECP | Grandfathering | IE wind not priority | 28.8 | 90.524 | 46.9347 | 26.9829 | 1.6676 | 14.9387 | 43.5893 | 29.81% | 1.842% | 16.5% | 48.15%
H1 | H1 | lisheen | 2030 | 100% ECP | Grandfathering | IE wind priority | 98.6 | 309.9191 | 297.3492 | 0 | 12.5699 | 0 | 12.5699 | 0% | 4.056% | 0% | 4.056%
H2 | H2 & K | arklow | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 26.66 | 75.4137 | 59.8953 | 12.2386 | 0.24786 | 3.0321 | 15.5185 | 16.23% | 0.3287% | 4.021% | 20.58%
H1 | H1 | lisheen | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 76 | 88.9816 | 50.73 | 28.2387 | 1.9532 | 8.0597 | 38.2516 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | lisheen | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 28.8 | 90.524 | 48.3259 | 26.9829 | 1.6676 | 13.5476 | 42.1982 | 29.81% | 1.842% | 14.97% | 46.62%
H2 | H2 & K | arklow | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 104.9266 | 122.8491 | 97.6827 | 19.5036 | 0.90165 | 4.7612 | 25.1664 | 15.88% | 0.7339% | 3.876% | 20.49%
H1 | H1 | lisheen | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 98.6 | 309.9191 | 297.3492 | 0 | 12.5699 | 0 | 12.5699 | 0% | 4.056% | 0% | 4.056%
H1 | H1 | lisheen | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 76 | 88.9816 | 51.2658 | 28.2387 | 1.9532 | 7.5239 | 37.7158 | 31.74% | 2.195% | 8.456% | 42.39%
H2 | H2 & K | arklow | 2035 | 66% ECP | Grandfathering | IE wind priority | 53.2 | 150.4882 | 149.1775 | 0 | 1.3107 | 0 | 1.3107 | 0% | 0.871% | 0% | 0.871%
H2 | H2 & K | arklow | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 104.9266 | 122.8491 | 100.9028 | 19.5036 | 0.90165 | 1.5411 | 21.9463 | 15.88% | 0.7339% | 1.254% | 17.86%
H2 | H2 & K | ballybeg | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 55.5 | 71.1114 | 56.1085 | 11.7866 | 1.3268 | 1.8894 | 15.0029 | 16.57% | 1.866% | 2.657% | 21.1%
H1 | H1 | lisheen | 2030 | 33% ECP | Grandfathering | IE wind priority | 98.6 | 309.9191 | 299.3299 | 0 | 10.5892 | 0 | 10.5892 | 0% | 3.417% | 0% | 3.417%
H1 | H1 | lisheen | 2030 | 33% ECP | Grandfathering | IE wind not priority | 28.8 | 90.524 | 55.2796 | 16.7056 | 1.69 | 16.8489 | 35.2445 | 18.45% | 1.867% | 18.61% | 38.93%
H1 | H1 | kill hill | 2035 | 100% ECP | Grandfathering | IE wind priority | 36 | 113.155 | 111.9312 | 0 | 1.2238 | 0 | 1.2238 | 0% | 1.082% | 0% | 1.082%
H2 | H2 & K | ballybeg | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 55.5 | 71.1114 | 57.5524 | 9.6631 | 1.3169 | 2.579 | 13.559 | 13.59% | 1.852% | 3.627% | 19.07%
H1 | H1 | kill hill | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 80 | 93.6648 | 57.1654 | 21.093 | 0.84533 | 14.5611 | 36.4994 | 22.52% | 0.9025% | 15.55% | 38.97%
H2 | H2 & K | ballybeg | 2030 | Initial | Grandfathering | IE Solar not priority | 8 | 10.2503 | 8.5845 | 0.81045 | 0.13256 | 0.72281 | 1.6658 | 7.907% | 1.293% | 7.052% | 16.25%
H1 | H1 | killonan | 2030 | Initial | Grandfathering | IE wind not priority | 84 | 264.0284 | 150.3834 | 35.8162 | 5.0138 | 72.815 | 113.645 | 13.57% | 1.899% | 27.58% | 43.04%
H1 | H1 | killonan | 2030 | 33% ECP | Grandfathering | IE wind not priority | 84 | 264.0284 | 161.232 | 48.7245 | 4.9293 | 49.1426 | 102.7964 | 18.45% | 1.867% | 18.61% | 38.93%
H1 | H1 | killonan | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 84 | 264.0284 | 143.416 | 66.7264 | 4.9635 | 48.9225 | 120.6124 | 25.27% | 1.88% | 18.53% | 45.68%
H2 | H2 & K | arklow 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 400 | 1608.368 | 1040.0532 | 460.83 | 9.7129 | 97.772 | 568.3148 | 28.65% | 0.6039% | 6.079% | 35.33%
H1 | H1 | killonan | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 84 | 264.0284 | 119.7472 | 85.6939 | 4.9216 | 53.6657 | 144.2812 | 32.46% | 1.864% | 20.33% | 54.65%
H1 | H1 | killonan | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 84 | 264.0284 | 102.349 | 91.426 | 4.8938 | 65.3595 | 161.6794 | 34.63% | 1.854% | 24.75% | 61.24%
H2 | H2 & K | arklow | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 128.89 | 150.9057 | 110.5114 | 33.9834 | 1.3619 | 5.049 | 40.3943 | 22.52% | 0.9025% | 3.346% | 26.77%
H1 | H1 | killonan | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 84 | 264.0284 | 175.7764 | 48.7245 | 4.9293 | 34.5982 | 88.252 | 18.45% | 1.867% | 13.1% | 33.43%
H2 | H2 & K | arklow 220kv | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 400 | 1608.368 | 993.5202 | 478.8116 | 29.1476 | 106.8886 | 614.8478 | 29.77% | 1.812% | 6.646% | 38.23%
H1 | H1 | killonan | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 84 | 264.0284 | 140.9504 | 78.7002 | 4.8639 | 39.514 | 123.078 | 29.81% | 1.842% | 14.97% | 46.62%
H2 | H2 & K | arklow 220kv | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 400 | 1608.368 | 1050.0579 | 445.6441 | 28.6643 | 84.0016 | 558.3101 | 27.71% | 1.782% | 5.223% | 34.71%
H1 | H1 | killonan | 2035 | 66% ECP | Grandfathering | IE wind not priority | 84 | 264.0284 | 131.9439 | 47.9402 | 0.91198 | 83.2323 | 132.0845 | 18.16% | 0.3454% | 31.52% | 50.03%
H1 | H1 | killonan | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 84 | 264.0284 | 143.0238 | 47.9402 | 0.91198 | 72.1524 | 121.0046 | 18.16% | 0.3454% | 27.33% | 45.83%
H1 | H1 | killonan | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 84 | 264.0284 | 122.8604 | 86.244 | 1.6972 | 53.2268 | 141.168 | 32.66% | 0.6428% | 20.16% | 53.47%
H1 | H1 | killonan | 2035 | 100% ECP | Grandfathering | IE wind not priority | 84 | 264.0284 | 128.7445 | 52.6336 | 0.97846 | 81.6719 | 135.2839 | 19.93% | 0.3706% | 30.93% | 51.24%
H1 | H1 | lisheen | 2030 | Initial | Grandfathering | IE wind not priority | 28.8 | 90.524 | 51.56 | 12.2798 | 1.719 | 24.9652 | 38.964 | 13.57% | 1.899% | 27.58% | 43.04%
H1 | H1 | lisheen | 2030 | Initial | Grandfathering | IE wind priority | 98.6 | 309.9191 | 300.5297 | 0 | 9.3893 | 0 | 9.3893 | 0% | 3.03% | 0% | 3.03%
H1 | H1 | killonan | 2030 | 100% ECP | Grandfathering | IE wind not priority | 84 | 264.0284 | 136.893 | 78.7002 | 4.8639 | 43.5714 | 127.1354 | 29.81% | 1.842% | 16.5% | 48.15%
D | D and E North | tullabrack | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 10.5 | 32.6172 | 22.355 | 9.6053 | 0.56697 | 0.089928 | 10.2622 | 29.45% | 1.738% | 0.2757% | 31.46%
H2 | H2 & K | carlow | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 14 | 39.6021 | 24.6516 | 12.2765 | 0.26661 | 2.4074 | 14.9505 | 31% | 0.6732% | 6.079% | 37.75%
G | J City, G South | drybridge | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 16.64 | 21.3206 | 17.8698 | 3.2659 | 0.15372 | 0.031161 | 3.4508 | 15.32% | 0.721% | 0.1462% | 16.19%
H2 | H2 & K | great island | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 125.3232 | 146.7297 | 122.9916 | 20.3311 | 2.7275 | 0.6795 | 23.7381 | 13.86% | 1.859% | 0.4631% | 16.18%
G | G North | balruntagh | 2035 | 66% ECP | Grandfathering | IE wind not priority | 33.6 | 104.971 | 85.356 | 17.7065 | 0.33806 | 1.5705 | 19.615 | 16.87% | 0.3221% | 1.496% | 18.69%
G | G North | balruntagh | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 89.3332 | 114.4615 | 94.3838 | 17.5333 | 0.82525 | 1.7192 | 20.0777 | 15.32% | 0.721% | 1.502% | 17.54%
H2 | H2 & K | great island | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 125.3232 | 146.7297 | 105.0317 | 33.3985 | 3.1191 | 5.1804 | 41.6979 | 22.76% | 2.126% | 3.531% | 28.42%
G | G North | balruntagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 33.6 | 104.971 | 86.5625 | 17.7065 | 0.33806 | 0.3639 | 18.4085 | 16.87% | 0.3221% | 0.3467% | 17.54%
G | G North | balruntagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 89.3332 | 114.4615 | 94.59 | 17.5333 | 0.82525 | 1.5129 | 19.8715 | 15.32% | 0.721% | 1.322% | 17.36%
H2 | H2 & K | great island | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 125.3232 | 146.7297 | 110.0996 | 28.7171 | 2.7743 | 5.1387 | 36.63 | 19.57% | 1.891% | 3.502% | 24.96%
G | G North | balruntagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 33.6 | 104.971 | 72.2067 | 31.9359 | 0.63326 | 0.19512 | 32.7643 | 30.42% | 0.6033% | 0.1859% | 31.21%
G | G North | balruntagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 89.3332 | 114.4615 | 87.1918 | 25.1479 | 0.97793 | 1.1439 | 27.2697 | 21.97% | 0.8544% | 0.9994% | 23.82%
H2 | H2 & K | great island | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 125.3232 | 146.7297 | 115.3887 | 24.6679 | 2.7745 | 3.8986 | 31.341 | 16.81% | 1.891% | 2.657% | 21.36%
G | G North | balruntagh | 2035 | 100% ECP | Grandfathering | IE wind not priority | 50.4 | 157.4567 | 125.3598 | 29.202 | 0.54251 | 2.3524 | 32.0969 | 18.55% | 0.3445% | 1.494% | 20.38%
G | G North | balruntagh | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 134 | 171.6925 | 129.9569 | 37.7515 | 1.556 | 2.428 | 41.7355 | 21.99% | 0.9062% | 1.414% | 24.31%
H2 | H2 & K | great island | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 125.3232 | 146.7297 | 118.3496 | 20.3311 | 2.7275 | 5.3215 | 28.3801 | 13.86% | 1.859% | 3.627% | 19.34%
H2 | H2 & K | great island | 2030 | Initial | Grandfathering | IE Solar not priority | 16.99 | 19.8921 | 16.5879 | 1.6452 | 0.25631 | 1.4027 | 3.3042 | 8.271% | 1.289% | 7.052% | 16.61%
G | G North | dundalk | 2030 | Initial | Grandfathering | IE wind priority | 16.1 | 50.2987 | 48.8288 | 0 | 1.4699 | 0 | 1.4699 | 0% | 2.922% | 0% | 2.922%
G | G North | dundalk | 2030 | Initial | Grandfathering | IE Solar not priority | 3.99 | 5.1123 | 4.5757 | 0.40421 | 0.066114 | 0.066354 | 0.53668 | 7.907% | 1.293% | 1.298% | 10.5%
G | G North | dundalk | 2030 | 33% ECP | Grandfathering | IE wind priority | 16.1 | 50.2987 | 48.6591 | 0 | 1.6395 | 0 | 1.6395 | 0% | 3.26% | 0% | 3.26%
G | G North | dundalk | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 20.9533 | 26.8472 | 22.4286 | 3.6482 | 0.49718 | 0.27323 | 4.4186 | 13.59% | 1.852% | 1.018% | 16.46%
H2 | H2 & K | garrintaggart | 2035 | 100% ECP | Grandfathering | IE wind not priority | 49.5 | 140.0219 | 104.0008 | 25.1936 | 0.50136 | 10.3261 | 36.0211 | 17.99% | 0.3581% | 7.375% | 25.73%
G | G North | dundalk | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 16.1 | 50.2987 | 48.4835 | 0 | 1.8152 | 0 | 1.8152 | 0% | 3.609% | 0% | 3.609%
G | G North | dundalk | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 20.9533 | 26.8472 | 21.7474 | 4.4499 | 0.50093 | 0.14902 | 5.0998 | 16.57% | 1.866% | 0.555% | 19%
H2 | H2 & K | garrintaggart | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 33 | 93.3478 | 58.1074 | 28.9374 | 0.62844 | 5.6746 | 35.2405 | 31% | 0.6732% | 6.079% | 37.75%
G | G North | dundalk | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 16.1 | 50.2987 | 48.3162 | 0 | 1.9824 | 0 | 1.9824 | 0% | 3.941% | 0% | 3.941%
G | G North | dundalk | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 20.9533 | 26.8472 | 20.9242 | 5.2026 | 0.49681 | 0.22359 | 5.923 | 19.38% | 1.851% | 0.8328% | 22.06%
H2 | H2 & K | garrintaggart | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 33 | 93.3478 | 74.1389 | 15.149 | 0.30681 | 3.7531 | 19.2089 | 16.23% | 0.3287% | 4.021% | 20.58%
H2 | H2 & K | great island | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 341.99 | 400.4053 | 259.4686 | 127.0707 | 8.7889 | 5.0772 | 140.9368 | 31.74% | 2.195% | 1.268% | 35.2%
G | G North | balruntagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 134 | 171.6925 | 113.5024 | 54.1817 | 3.7827 | 0.22567 | 58.19 | 31.56% | 2.203% | 0.1314% | 33.89%
G | G North | balruntagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 50.4 | 157.4567 | 110.465 | 43.7654 | 2.7211 | 0.50516 | 46.9917 | 27.8% | 1.728% | 0.3208% | 29.84%
F | E,F & I | macroom | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 24 | 77.6717 | 77.0455 | 0 | 0.62619 | 0 | 0.62619 | 0% | 0.8062% | 0% | 0.8062%
F | E,F & I | macroom | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 16.3749 | 3.3086 | 0.15296 | 1.004 | 4.4655 | 15.88% | 0.7339% | 4.817% | 21.43%
F | E,F & I | macroom | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 24 | 77.6717 | 76.423 | 0 | 1.2487 | 0 | 1.2487 | 0% | 1.608% | 0% | 1.608%
F | E,F & I | macroom | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 14.5001 | 4.676 | 0.17937 | 1.485 | 6.3403 | 22.44% | 0.8607% | 7.125% | 30.42%
H2 | H2 & K | great island 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 450 | 1809.414 | 1170.0598 | 518.4337 | 10.927 | 109.9935 | 639.3542 | 28.65% | 0.6039% | 6.079% | 35.33%
F | E,F & I | macroom | 2035 | 100% ECP | Grandfathering | IE wind priority | 24 | 77.6717 | 76.9617 | 0 | 0.70994 | 0 | 0.70994 | 0% | 0.914% | 0% | 0.914%
F | E,F & I | macroom | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 14.1432 | 4.6932 | 0.18809 | 1.816 | 6.6973 | 22.52% | 0.9025% | 8.714% | 32.14%
G | G North | balruntagh | 2030 | 33% ECP | Grandfathering | IE wind not priority | 16.8 | 52.4855 | 39.8099 | 9.0956 | 0.95047 | 2.6295 | 12.6756 | 17.33% | 1.811% | 5.01% | 24.15%
G | G North | balruntagh | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 44.6666 | 57.2308 | 47.8116 | 7.7769 | 1.0599 | 0.58245 | 9.4192 | 13.59% | 1.852% | 1.018% | 16.46%
G | G North | dundalk | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 16.1 | 50.2987 | 48.2806 | 0 | 2.0181 | 0 | 2.0181 | 0% | 4.012% | 0% | 4.012%
H2 | H2 & K | great island | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 341.99 | 400.4053 | 293.2251 | 90.1698 | 3.6137 | 13.3967 | 107.1802 | 22.52% | 0.9025% | 3.346% | 26.77%
G | G North | balruntagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 44.6666 | 57.2308 | 46.3593 | 9.4859 | 1.0678 | 0.31766 | 10.8714 | 16.57% | 1.866% | 0.555% | 19%
H2 | H2 & K | great island | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 233.6565 | 273.5673 | 200.4063 | 61.3807 | 2.3546 | 9.4258 | 73.161 | 22.44% | 0.8607% | 3.445% | 26.74%
G | G North | balruntagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 16.8 | 52.4855 | 35.0636 | 15.8871 | 0.91607 | 0.61865 | 17.4219 | 30.27% | 1.745% | 1.179% | 33.19%
G | G North | balruntagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 44.6666 | 57.2308 | 44.6045 | 11.0906 | 1.0591 | 0.47663 | 12.6263 | 19.38% | 1.851% | 0.8328% | 22.06%
H2 | H2 & K | great island | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 233.6565 | 273.5673 | 224.6961 | 43.4316 | 2.0078 | 3.4317 | 48.8712 | 15.88% | 0.7339% | 1.254% | 17.86%
G | G North | balruntagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 16.8 | 52.4855 | 33.978 | 16.9372 | 0.91637 | 0.65399 | 18.5075 | 32.27% | 1.746% | 1.246% | 35.26%
G | G North | balruntagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 44.6666 | 57.2308 | 42.7087 | 12.901 | 1.1985 | 0.4225 | 14.522 | 22.54% | 2.094% | 0.7382% | 25.37%
H2 | H2 & K | great island | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 233.6565 | 273.5673 | 217.5253 | 43.4316 | 2.0078 | 10.6025 | 56.042 | 15.88% | 0.7339% | 3.876% | 20.49%
G | G North | balruntagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 16.8 | 52.4855 | 42.2171 | 9.0956 | 0.95047 | 0.22232 | 10.2684 | 17.33% | 1.811% | 0.4236% | 19.56%
G | G North | balruntagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 44.6666 | 57.2308 | 48.3797 | 7.7769 | 1.0599 | 0.01429 | 8.851 | 13.59% | 1.852% | 0.02497% | 15.47%
G | G North | balruntagh | 2030 | 100% ECP | Grandfathering | IE wind not priority | 50.4 | 157.4567 | 104.1984 | 43.7654 | 2.7211 | 6.7718 | 53.2583 | 27.8% | 1.728% | 4.301% | 33.82%
G | G North | balruntagh | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 134 | 171.6925 | 111.2095 | 54.1817 | 3.7827 | 2.5186 | 60.483 | 31.56% | 2.203% | 1.467% | 35.23%
H2 | H2 & K | great island | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 341.99 | 400.4053 | 264.1578 | 127.0707 | 8.7889 | 0.38788 | 136.2475 | 31.74% | 2.195% | 0.09687% | 34.03%
G | G North | balruntagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 16.8 | 52.4855 | 37.6135 | 12.4724 | 0.93571 | 1.464 | 14.872 | 23.76% | 1.783% | 2.789% | 28.34%
G | G North | dundalk | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 20.9533 | 26.8472 | 20.0349 | 6.0519 | 0.56224 | 0.1982 | 6.8123 | 22.54% | 2.094% | 0.7382% | 25.37%
H2 | H2 & K | garrintaggart | 2035 | 66% ECP | Grandfathering | IE wind not priority | 33 | 93.3478 | 72.1786 | 15.149 | 0.30681 | 5.7135 | 21.1693 | 16.23% | 0.3287% | 6.121% | 22.68%
G | G North | dundalk | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 16.1 | 50.2987 | 48.6591 | 0 | 1.6395 | 0 | 1.6395 | 0% | 3.26% | 0% | 3.26%
H2 | H2 & K | effernoge | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 34 | 39.8075 | 32.6961 | 6.3199 | 0.29217 | 0.49936 | 7.1114 | 15.88% | 0.7339% | 1.254% | 17.86%
G | G North | lisdrum | 2030 | 100% ECP | Grandfathering | IE wind not priority | 33.1 | 103.409 | 68.4319 | 28.7427 | 1.7871 | 4.4473 | 34.9772 | 27.8% | 1.728% | 4.301% | 33.82%
G | G North | lisdrum | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 33.1 | 103.409 | 72.5474 | 28.7427 | 1.7871 | 0.33176 | 30.8616 | 27.8% | 1.728% | 0.3208% | 29.84%
H2 | H2 & K | effernoge | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 34 | 39.8075 | 31.6527 | 6.3199 | 0.29217 | 1.5428 | 8.1548 | 15.88% | 0.7339% | 3.876% | 20.49%
G | G North | lisdrum | 2035 | 66% ECP | Grandfathering | IE wind not priority | 33.1 | 103.409 | 84.0859 | 17.4431 | 0.33303 | 1.5471 | 19.3232 | 16.87% | 0.3221% | 1.496% | 18.69%
G | G North | lisdrum | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 33.1 | 103.409 | 85.2745 | 17.4431 | 0.33303 | 0.35849 | 18.1346 | 16.87% | 0.3221% | 0.3467% | 17.54%
G | G North | lisdrum | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 33.1 | 103.409 | 71.1323 | 31.4607 | 0.62384 | 0.19221 | 32.2767 | 30.42% | 0.6033% | 0.1859% | 31.21%
H2 | H2 & K | effernoge | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 51 | 59.7113 | 39.3931 | 18.9497 | 1.3107 | 0.057843 | 20.3182 | 31.74% | 2.195% | 0.09687% | 34.03%
G | G North | lisdrum | 2035 | 100% ECP | Grandfathering | IE wind not priority | 33.1 | 103.409 | 82.3295 | 19.1783 | 0.35629 | 1.5449 | 21.0795 | 18.55% | 0.3445% | 1.494% | 20.38%
H2 | H2 & K | effernoge | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 51 | 59.7113 | 38.6938 | 18.9497 | 1.3107 | 0.75714 | 21.0175 | 31.74% | 2.195% | 1.268% | 35.2%
G | G North | lislea | 2030 | Initial | Grandfathering | IE wind not priority | 48.8 | 152.458 | 121.4492 | 19.5124 | 2.8197 | 8.6767 | 31.0088 | 12.8% | 1.85% | 5.691% | 20.34%
G | G North | lisdrum | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 33.1 | 103.409 | 83.1779 | 17.9205 | 1.8727 | 0.43802 | 20.2312 | 17.33% | 1.811% | 0.4236% | 19.56%
G | G North | lislea | 2030 | 33% ECP | Grandfathering | IE wind not priority | 48.8 | 152.458 | 115.6384 | 26.4205 | 2.7609 | 7.6382 | 36.8196 | 17.33% | 1.811% | 5.01% | 24.15%
G | G North | lislea | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 48.8 | 152.458 | 109.2582 | 36.2293 | 2.718 | 4.2525 | 43.1998 | 23.76% | 1.783% | 2.789% | 28.34%
G | G North | lislea | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 48.8 | 152.458 | 101.8516 | 46.1484 | 2.661 | 1.797 | 50.6064 | 30.27% | 1.745% | 1.179% | 33.19%
H2 | H2 & K | effernoge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 17 | 19.9038 | 14.2475 | 4.5305 | 0.4231 | 0.70271 | 5.6563 | 22.76% | 2.126% | 3.531% | 28.42%
G | G North | lislea | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 48.8 | 152.458 | 98.698 | 49.1985 | 2.6618 | 1.8997 | 53.76 | 32.27% | 1.746% | 1.246% | 35.26%
G | G North | lislea | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 48.8 | 152.458 | 122.6308 | 26.4205 | 2.7609 | 0.64578 | 29.8272 | 17.33% | 1.811% | 0.4236% | 19.56%
H2 | H2 & K | effernoge | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 17 | 19.9038 | 14.9349 | 3.8955 | 0.37632 | 0.69706 | 4.9688 | 19.57% | 1.891% | 3.502% | 24.96%
G | G North | lislea | 2030 | 100% ECP | Grandfathering | IE wind not priority | 48.8 | 152.458 | 100.8905 | 42.376 | 2.6347 | 6.5568 | 51.5675 | 27.8% | 1.728% | 4.301% | 33.82%
G | G North | lislea | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 48.8 | 152.458 | 106.9582 | 42.376 | 2.6347 | 0.48913 | 45.4999 | 27.8% | 1.728% | 0.3208% | 29.84%
H2 | H2 & K | effernoge | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 17 | 19.9038 | 15.6524 | 3.3462 | 0.37636 | 0.52884 | 4.2514 | 16.81% | 1.891% | 2.657% | 21.36%
G | G North | lislea | 2035 | 66% ECP | Grandfathering | IE wind not priority | 48.8 | 152.458 | 123.9695 | 25.7166 | 0.49099 | 2.2809 | 28.4885 | 16.87% | 0.3221% | 1.496% | 18.69%
H2 | H2 & K | effernoge | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 17 | 19.9038 | 16.054 | 2.7579 | 0.36998 | 0.72186 | 3.8497 | 13.86% | 1.859% | 3.627% | 19.34%
G | G North | lislea | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 48.8 | 152.458 | 125.7219 | 25.7166 | 0.49099 | 0.52852 | 26.7362 | 16.87% | 0.3221% | 0.3467% | 17.54%
G | G North | lislea | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 48.8 | 152.458 | 104.8718 | 46.3831 | 0.91974 | 0.28338 | 47.5862 | 30.42% | 0.6033% | 0.1859% | 31.21%
H2 | H2 & K | effernoge | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 17 | 19.9038 | 16.6837 | 2.7579 | 0.36998 | 0.092174 | 3.2201 | 13.86% | 1.859% | 0.4631% | 16.18%
H2 | H2 & K | kellis | 2030 | Initial | Grandfathering | IE Solar not priority | 81 | 94.8356 | 79.0828 | 7.8434 | 1.222 | 6.6874 | 15.7528 | 8.271% | 1.289% | 7.052% | 16.61%
G | G North | lisdrum | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 33.1 | 103.409 | 66.9447 | 33.3703 | 1.8055 | 1.2885 | 36.4643 | 32.27% | 1.746% | 1.246% | 35.26%
G | G North | lisdrum | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 33.1 | 103.409 | 69.0838 | 31.3015 | 1.8049 | 1.2189 | 34.3252 | 30.27% | 1.745% | 1.179% | 33.19%
G | G North | dundalk | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 20.9533 | 26.8472 | 22.6951 | 3.6482 | 0.49718 | 0.0067033 | 4.1521 | 13.59% | 1.852% | 0.02497% | 15.47%
G | G North | dundalk | 2030 | 100% ECP | Grandfathering | IE wind priority | 16.1 | 50.2987 | 48.4074 | 0 | 1.8913 | 0 | 1.8913 | 0% | 3.76% | 0% | 3.76%
G | G North | dundalk | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 54.88 | 70.317 | 45.5461 | 22.1902 | 1.5492 | 1.0315 | 24.7709 | 31.56% | 2.203% | 1.467% | 35.23%
H2 | H2 & K | garrintaggart | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 49.5 | 140.0219 | 98.1501 | 38.5014 | 2.5589 | 0.81141 | 41.8718 | 27.5% | 1.828% | 0.5795% | 29.9%
G | G North | dundalk | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 16.1 | 50.2987 | 48.4074 | 0 | 1.8913 | 0 | 1.8913 | 0% | 3.76% | 0% | 3.76%
G | G North | dundalk | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 54.88 | 70.317 | 46.4852 | 22.1902 | 1.5492 | 0.092425 | 23.8319 | 31.56% | 2.203% | 0.1314% | 33.89%
H2 | H2 & K | garrintaggart | 2030 | 100% ECP | Grandfathering | IE wind not priority | 49.5 | 140.0219 | 95.8695 | 38.5014 | 2.5589 | 3.092 | 44.1524 | 27.5% | 1.828% | 2.208% | 31.53%
H2 | H2 & K | garrintaggart | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 16.5 | 46.6739 | 37.7786 | 7.6245 | 0.836 | 0.43481 | 8.8953 | 16.34% | 1.791% | 0.9316% | 19.06%
G | G North | dundalk | 2035 | 66% ECP | Grandfathering | IE wind priority | 16.1 | 50.2987 | 49.8541 | 0 | 0.44458 | 0 | 0.44458 | 0% | 0.8839% | 0% | 0.8839%
G | G North | dundalk | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 37.9166 | 48.5821 | 40.0603 | 7.4418 | 0.35027 | 0.72969 | 8.5218 | 15.32% | 0.721% | 1.502% | 17.54%
H2 | H2 & K | garrintaggart | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 16.5 | 46.6739 | 27.5411 | 15.1329 | 0.89812 | 3.1018 | 19.1328 | 32.42% | 1.924% | 6.646% | 40.99%
H2 | H2 & K | effernoge | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 34 | 39.8075 | 29.1617 | 8.9317 | 0.34262 | 1.3716 | 10.6458 | 22.44% | 0.8607% | 3.445% | 26.74%
G | G North | dundalk | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 16.1 | 50.2987 | 49.8541 | 0 | 0.44458 | 0 | 0.44458 | 0% | 0.8839% | 0% | 0.8839%
H2 | H2 & K | garrintaggart | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 16.5 | 46.6739 | 29.2183 | 14.1279 | 0.89007 | 2.4377 | 17.4556 | 30.27% | 1.907% | 5.223% | 37.4%
G | G North | dundalk | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 16.1 | 50.2987 | 49.4026 | 0 | 0.89601 | 0 | 0.89601 | 0% | 1.781% | 0% | 1.781%
G | G North | dundalk | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 37.9166 | 48.5821 | 37.0077 | 10.6738 | 0.41507 | 0.48551 | 11.5744 | 21.97% | 0.8544% | 0.9994% | 23.82%
H2 | H2 & K | garrintaggart | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 16.5 | 46.6739 | 33.866 | 10.6985 | 0.86214 | 1.2472 | 12.8079 | 22.92% | 1.847% | 2.672% | 27.44%
G | G North | dundalk | 2035 | 100% ECP | Grandfathering | IE wind priority | 16.1 | 50.2987 | 49.7956 | 0 | 0.50304 | 0 | 0.50304 | 0% | 1% | 0% | 1%
G | G North | dundalk | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 54.88 | 70.317 | 53.2242 | 15.4612 | 0.63725 | 0.99441 | 17.0929 | 21.99% | 0.9062% | 1.414% | 24.31%
H2 | H2 & K | garrintaggart | 2030 | 33% ECP | Grandfathering | IE wind not priority | 16.5 | 46.6739 | 35.9012 | 7.6245 | 0.836 | 2.3123 | 10.7728 | 16.34% | 1.791% | 4.954% | 23.08%
G | G North | lisdrum | 2030 | Initial | Grandfathering | IE wind not priority | 33.1 | 103.409 | 82.3764 | 13.2348 | 1.9126 | 5.8852 | 21.0326 | 12.8% | 1.85% | 5.691% | 20.34%
G | G North | lisdrum | 2030 | 33% ECP | Grandfathering | IE wind not priority | 33.1 | 103.409 | 78.4351 | 17.9205 | 1.8727 | 5.1808 | 24.974 | 17.33% | 1.811% | 5.01% | 24.15%
H2 | H2 & K | effernoge | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 51 | 59.7113 | 43.7278 | 13.4468 | 0.5389 | 1.9978 | 15.9835 | 22.52% | 0.9025% | 3.346% | 26.77%
G | G North | lisdrum | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 33.1 | 103.409 | 74.1075 | 24.5736 | 1.8436 | 2.8844 | 29.3015 | 23.76% | 1.783% | 2.789% | 28.34%
G | G North | dundalk | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 37.9166 | 48.5821 | 40.1478 | 7.4418 | 0.35027 | 0.64215 | 8.4343 | 15.32% | 0.721% | 1.322% | 17.36%
F | E,F & I | macroom | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 15.1939 | 3.3086 | 0.15296 | 2.1849 | 5.6465 | 15.88% | 0.7339% | 10.48% | 27.09%
F | E,F & I | macroom | 2035 | 66% ECP | Grandfathering | IE wind priority | 24 | 77.6717 | 77.0455 | 0 | 0.62619 | 0 | 0.62619 | 0% | 0.8062% | 0% | 0.8062%
H2 | H2 & K | kilkenny | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 77.3333 | 90.5426 | 67.9392 | 17.7205 | 1.7119 | 3.1709 | 22.6033 | 19.57% | 1.891% | 3.502% | 24.96%
F | E,F & I | bandon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 26.0167 | 30.4606 | 21.9898 | 6.9334 | 0.64751 | 0.8899 | 8.4708 | 22.76% | 2.126% | 2.921% | 27.81%
F | E,F & I | bandon | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 8.75 | 28.3178 | 27.4837 | 0 | 0.83409 | 0 | 0.83409 | 0% | 2.945% | 0% | 2.945%
H2 | H2 & K | kilkenny | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 15.4 | 43.5623 | 27.2704 | 13.186 | 0.83073 | 2.2752 | 16.2919 | 30.27% | 1.907% | 5.223% | 37.4%
F | E,F & I | bandon | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 26.0167 | 30.4606 | 24.8242 | 4.2207 | 0.56622 | 0.84946 | 5.6363 | 13.86% | 1.859% | 2.789% | 18.5%
F | E,F & I | bandon | 2030 | 100% ECP | Grandfathering | IE wind priority | 8.75 | 28.3178 | 27.2997 | 0 | 1.0181 | 0 | 1.0181 | 0% | 3.595% | 0% | 3.595%
H2 | H2 & K | kilkenny | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 77.3333 | 90.5426 | 71.2029 | 15.2219 | 1.7121 | 2.4057 | 19.3396 | 16.81% | 1.891% | 2.657% | 21.36%
F | E,F & I | bandon | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 41.25 | 48.2959 | 31.0709 | 15.327 | 1.0601 | 0.838 | 17.2251 | 31.74% | 2.195% | 1.735% | 35.67%
F | E,F & I | bandon | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 8.75 | 28.3178 | 27.2997 | 0 | 1.0181 | 0 | 1.0181 | 0% | 3.595% | 0% | 3.595%
H2 | H2 & K | kilkenny | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 15.4 | 43.5623 | 31.6083 | 9.9853 | 0.80467 | 1.1641 | 11.954 | 22.92% | 1.847% | 2.672% | 27.44%
F | E,F & I | bandon | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 41.25 | 48.2959 | 31.5021 | 15.327 | 1.0601 | 0.40675 | 16.7938 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | kilkenny | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 77.3333 | 90.5426 | 73.03 | 12.5457 | 1.6831 | 3.2837 | 17.5125 | 13.86% | 1.859% | 3.627% | 19.34%
F | E,F & I | bandon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 8.75 | 28.3178 | 27.2638 | 0 | 1.054 | 0 | 1.054 | 0% | 3.722% | 0% | 3.722%
F | E,F & I | bandon | 2035 | 66% ECP | Grandfathering | IE wind priority | 8.75 | 28.3178 | 28.0895 | 0 | 0.2283 | 0 | 0.2283 | 0% | 0.8062% | 0% | 0.8062%
F | E,F & I | bandon | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 33.6333 | 39.3782 | 28.7091 | 6.2517 | 0.28902 | 4.1284 | 10.6691 | 15.88% | 0.7339% | 10.48% | 27.09%
F | E,F & I | bandon | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 8.75 | 28.3178 | 28.0895 | 0 | 0.2283 | 0 | 0.2283 | 0% | 0.8062% | 0% | 0.8062%
H2 | H2 & K | kilkenny | 2030 | Initial | Grandfathering | IE Solar not priority | 12 | 14.0497 | 11.716 | 1.162 | 0.18103 | 0.99073 | 2.3337 | 8.271% | 1.289% | 7.052% | 16.61%
F | E,F & I | bandon | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 33.6333 | 39.3782 | 30.9405 | 6.2517 | 0.28902 | 1.897 | 8.4377 | 15.88% | 0.7339% | 4.817% | 21.43%
F | E,F & I | bandon | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 8.75 | 28.3178 | 27.8625 | 0 | 0.45525 | 0 | 0.45525 | 0% | 1.608% | 0% | 1.608%
F | E,F & I | bandon | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 33.6333 | 39.3782 | 27.3981 | 8.8353 | 0.33893 | 2.8059 | 11.9801 | 22.44% | 0.8607% | 7.125% | 30.42%
F | E,F & I | bandon | 2035 | 100% ECP | Grandfathering | IE wind priority | 8.75 | 28.3178 | 28.059 | 0 | 0.25883 | 0 | 0.25883 | 0% | 0.914% | 0% | 0.914%
H2 | H2 & K | kellymount | 2035 | 100% ECP | Grandfathering | IE wind not priority | 50.4 | 142.5678 | 105.8918 | 25.6517 | 0.51047 | 10.5139 | 36.676 | 17.99% | 0.3581% | 7.375% | 25.73%
F | E,F & I | bandon | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 41.25 | 48.2959 | 32.7756 | 10.8761 | 0.43587 | 4.2084 | 15.5203 | 22.52% | 0.9025% | 8.714% | 32.14%
H2 | H2 & K | kellymount | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 33.6 | 95.0451 | 59.1639 | 29.4636 | 0.63986 | 5.7777 | 35.8812 | 31% | 0.6732% | 6.079% | 37.75%
F | E,F & I | dunmanway | 2030 | Initial | Grandfathering | IE wind not priority | 81.75 | 264.5691 | 136.0436 | 29.9034 | 4.3319 | 94.2904 | 128.5256 | 11.3% | 1.637% | 35.64% | 48.58%
H2 | H2 & K | kilkenny | 2030 | 33% ECP | Grandfathering | IE wind not priority | 15.4 | 43.5623 | 33.5078 | 7.1162 | 0.78027 | 2.1581 | 10.0546 | 16.34% | 1.791% | 4.954% | 23.08%
H2 | H2 & K | kellymount | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 33.6 | 95.0451 | 75.4869 | 15.4245 | 0.31239 | 3.8213 | 19.5582 | 16.23% | 0.3287% | 4.021% | 20.58%
F | E,F & I | bandon | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 26.0167 | 30.4606 | 22.7221 | 5.9616 | 0.57592 | 1.201 | 7.7385 | 19.57% | 1.891% | 3.943% | 25.4%
F | E,F & I | bandon | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 8.75 | 28.3178 | 27.2751 | 0 | 1.0427 | 0 | 1.0427 | 0% | 3.682% | 0% | 3.682%
F | E,F & I | ballylickey | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 5.82 | 18.8354 | 12.2916 | 4.8205 | 0.3187 | 1.4045 | 6.5437 | 25.59% | 1.692% | 7.457% | 34.74%
H2 | H2 & K | kilkenny | 2035 | 66% ECP | Grandfathering | IE wind not priority | 30.8 | 87.1247 | 67.3667 | 14.1391 | 0.28635 | 5.3326 | 19.758 | 16.23% | 0.3287% | 6.121% | 22.68%
F | E,F & I | ballylickey | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 51.45 | 166.5087 | 160.5223 | 0 | 5.9863 | 0 | 5.9863 | 0% | 3.595% | 0% | 3.595%
F | E,F & I | ballylickey | 2035 | 66% ECP | Grandfathering | IE wind not priority | 5.82 | 18.8354 | 9.5761 | 2.7434 | 0.057915 | 6.458 | 9.2593 | 14.56% | 0.3075% | 34.29% | 49.16%
F | E,F & I | ballylickey | 2035 | 66% ECP | Grandfathering | IE wind priority | 51.45 | 166.5087 | 165.1663 | 0 | 1.3424 | 0 | 1.3424 | 0% | 0.8062% | 0% | 0.8062%
F | E,F & I | ballylickey | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 5.82 | 18.8354 | 11.5673 | 2.7434 | 0.057915 | 4.4668 | 7.2681 | 14.56% | 0.3075% | 23.72% | 38.59%
H2 | H2 & K | kilkenny | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 208 | 243.5285 | 160.6621 | 77.285 | 5.3455 | 0.23591 | 82.8664 | 31.74% | 2.195% | 0.09687% | 34.03%
F | E,F & I | ballylickey | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 51.45 | 166.5087 | 165.1663 | 0 | 1.3424 | 0 | 1.3424 | 0% | 0.8062% | 0% | 0.8062%
F | E,F & I | ballylickey | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 5.82 | 18.8354 | 11.2471 | 5.2185 | 0.10975 | 2.26 | 7.5883 | 27.71% | 0.5827% | 12% | 40.29%
H2 | H2 & K | kilkenny | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 46.2 | 130.6871 | 91.6068 | 35.9347 | 2.3883 | 0.75732 | 39.0803 | 27.5% | 1.828% | 0.5795% | 29.9%
H2 | H2 & K | kilkenny | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 15.4 | 43.5623 | 25.705 | 14.124 | 0.83825 | 2.8951 | 17.8573 | 32.42% | 1.924% | 6.646% | 40.99%
F | E,F & I | ballylickey | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 51.45 | 166.5087 | 163.8318 | 0 | 2.6769 | 0 | 2.6769 | 0% | 1.608% | 0% | 1.608%
H2 | H2 & K | kilkenny | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 208 | 243.5285 | 157.8101 | 77.285 | 5.3455 | 3.088 | 85.7184 | 31.74% | 2.195% | 1.268% | 35.2%
F | E,F & I | ballylickey | 2035 | 100% ECP | Grandfathering | IE wind priority | 51.45 | 166.5087 | 164.9867 | 0 | 1.5219 | 0 | 1.5219 | 0% | 0.914% | 0% | 0.914%
H2 | H2 & K | kilkenny | 2030 | 100% ECP | Grandfathering | IE wind not priority | 46.2 | 130.6871 | 89.4782 | 35.9347 | 2.3883 | 2.8859 | 41.2089 | 27.5% | 1.828% | 2.208% | 31.53%
F | E,F & I | bandon | 2030 | Initial | Grandfathering | IE wind priority | 8.75 | 28.3178 | 27.5848 | 0 | 0.73305 | 0 | 0.73305 | 0% | 2.589% | 0% | 2.589%
H2 | H2 & K | kilkenny | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 77.3333 | 90.5426 | 75.8945 | 12.5457 | 1.6831 | 0.4193 | 14.6481 | 13.86% | 1.859% | 0.4631% | 16.18%
F | E,F & I | bandon | 2030 | Initial | Grandfathering | IE Solar not priority | 18.4 | 21.5429 | 16.2246 | 1.7817 | 0.27758 | 3.259 | 5.3183 | 8.271% | 1.289% | 15.13% | 24.69%
F | E,F & I | bandon | 2030 | 33% ECP | Grandfathering | IE wind priority | 8.75 | 28.3178 | 27.4837 | 0 | 0.83409 | 0 | 0.83409 | 0% | 2.945% | 0% | 2.945%
H2 | H2 & K | kilkenny | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 15.4 | 43.5623 | 35.2601 | 7.1162 | 0.78027 | 0.40583 | 8.3023 | 16.34% | 1.791% | 0.9316% | 19.06%
F | E,F & I | bandon | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 26.0167 | 30.4606 | 23.9947 | 4.2207 | 0.56622 | 1.679 | 6.4659 | 13.86% | 1.859% | 5.512% | 21.23%
F | E,F & I | bandon | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 8.75 | 28.3178 | 27.3684 | 0 | 0.94944 | 0 | 0.94944 | 0% | 3.353% | 0% | 3.353%
H2 | H2 & K | kilkenny | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 77.3333 | 90.5426 | 64.812 | 20.6092 | 1.9247 | 3.1967 | 25.7306 | 22.76% | 2.126% | 3.531% | 28.42%
F | E,F & I | bandon | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 26.0167 | 30.4606 | 23.2746 | 5.121 | 0.57598 | 1.489 | 7.1859 | 16.81% | 1.891% | 4.888% | 23.59%
F | E,F & I | ballylickey | 2035 | 100% ECP | Grandfathering | IE wind not priority | 5.82 | 18.8354 | 9.8045 | 3.0675 | 0.063241 | 5.9001 | 9.0308 | 16.29% | 0.3358% | 31.32% | 47.95%
F | E,F & I | dunmanway | 2030 | Initial | Grandfathering | IE wind priority | 30.75 | 99.5168 | 96.9407 | 0 | 2.5761 | 0 | 2.5761 | 0% | 2.589% | 0% | 2.589%
H2 | H2 & K | kellymount | 2035 | 66% ECP | Grandfathering | IE wind not priority | 33.6 | 95.0451 | 73.4909 | 15.4245 | 0.31239 | 5.8173 | 21.5542 | 16.23% | 0.3287% | 6.121% | 22.68%
H2 | H2 & K | kellis | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 421.6663 | 493.6912 | 405.4961 | 78.3786 | 3.6234 | 6.1931 | 88.1951 | 15.88% | 0.7339% | 1.254% | 17.86%
F | E,F & I | macroom | 2030 | Initial | Grandfathering | IE wind priority | 24 | 77.6717 | 75.661 | 0 | 2.0106 | 0 | 2.0106 | 0% | 2.589% | 0% | 2.589%
H2 | H2 & K | kellis | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 421.6663 | 493.6912 | 392.5554 | 78.3786 | 3.6234 | 19.1338 | 101.1358 | 15.88% | 0.7339% | 3.876% | 20.49%
F | E,F & I | macroom | 2030 | Initial | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 15.6955 | 1.7236 | 0.26853 | 3.1528 | 5.1449 | 8.271% | 1.289% | 15.13% | 24.69%
F | E,F & I | macroom | 2030 | 33% ECP | Grandfathering | IE wind priority | 24 | 77.6717 | 75.3839 | 0 | 2.2878 | 0 | 2.2878 | 0% | 2.945% | 0% | 2.945%
F | E,F & I | macroom | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 16.4166 | 2.8877 | 0.38739 | 1.1487 | 4.4238 | 13.86% | 1.859% | 5.512% | 21.23%
F | E,F & I | macroom | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 24 | 77.6717 | 75.0675 | 0 | 2.6042 | 0 | 2.6042 | 0% | 3.353% | 0% | 3.353%
H2 | H2 & K | kellis | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 592 | 693.1195 | 457.269 | 219.965 | 15.214 | 0.67143 | 235.8505 | 31.74% | 2.195% | 0.09687% | 34.03%
F | E,F & I | macroom | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 15.924 | 3.5037 | 0.39407 | 1.0187 | 4.9165 | 16.81% | 1.891% | 4.888% | 23.59%
F | E,F & I | macroom | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 24 | 77.6717 | 74.8117 | 0 | 2.86 | 0 | 2.86 | 0% | 3.682% | 0% | 3.682%
H2 | H2 & K | kellis | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 592 | 693.1195 | 449.1517 | 219.965 | 15.214 | 8.7888 | 243.9678 | 31.74% | 2.195% | 1.268% | 35.2%
F | E,F & I | dunmanway | 2035 | 100% ECP | Grandfathering | IE wind priority | 30.75 | 99.5168 | 98.6072 | 0 | 0.90961 | 0 | 0.90961 | 0% | 0.914% | 0% | 0.914%
F | E,F & I | macroom | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 15.5459 | 4.0788 | 0.39403 | 0.8217 | 5.2945 | 19.57% | 1.891% | 3.943% | 25.4%
H2 | H2 & K | kellis | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 251.3332 | 294.2634 | 246.6571 | 40.7736 | 5.4699 | 1.3627 | 47.6063 | 13.86% | 1.859% | 0.4631% | 16.18%
F | E,F & I | macroom | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 15.0449 | 4.7437 | 0.44301 | 0.60885 | 5.7955 | 22.76% | 2.126% | 2.921% | 27.81%
F | E,F & I | macroom | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 24 | 77.6717 | 75.3839 | 0 | 2.2878 | 0 | 2.2878 | 0% | 2.945% | 0% | 2.945%
H2 | H2 & K | kellis | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 251.3332 | 294.2634 | 210.639 | 66.98 | 6.2552 | 10.3892 | 83.6244 | 22.76% | 2.126% | 3.531% | 28.42%
F | E,F & I | macroom | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 16.9842 | 2.8877 | 0.38739 | 0.58118 | 3.8563 | 13.86% | 1.859% | 2.789% | 18.5%
F | E,F & I | macroom | 2030 | 100% ECP | Grandfathering | IE wind priority | 24 | 77.6717 | 74.8792 | 0 | 2.7925 | 0 | 2.7925 | 0% | 3.595% | 0% | 3.595%
H2 | H2 & K | kellis | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 251.3332 | 294.2634 | 220.8026 | 57.5916 | 5.5637 | 10.3055 | 73.4608 | 19.57% | 1.891% | 3.502% | 24.96%
F | E,F & I | macroom | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 13.4075 | 6.6138 | 0.45745 | 0.36161 | 7.4329 | 31.74% | 2.195% | 1.735% | 35.67%
F | E,F & I | macroom | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 24 | 77.6717 | 74.8792 | 0 | 2.7925 | 0 | 2.7925 | 0% | 3.595% | 0% | 3.595%
H2 | H2 & K | kellis | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 251.3332 | 294.2634 | 231.4096 | 49.4711 | 5.5642 | 7.8185 | 62.8538 | 16.81% | 1.891% | 2.657% | 21.36%
F | E,F & I | macroom | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 17.8 | 20.8404 | 13.5936 | 6.6138 | 0.45745 | 0.17552 | 7.2468 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | kellis | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 251.3332 | 294.2634 | 237.3476 | 40.7736 | 5.4699 | 10.6722 | 56.9158 | 13.86% | 1.859% | 3.627% | 19.34%
F | E,F & I | macroom | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 24 | 77.6717 | 74.7807 | 0 | 2.891 | 0 | 2.891 | 0% | 3.722% | 0% | 3.722%
F | E,F & I | dunmanway | 2030 | 33% ECP | Grandfathering | IE wind not priority | 81.75 | 264.5691 | 175.4464 | 40.4699 | 4.3364 | 44.3164 | 89.1227 | 15.3% | 1.639% | 16.75% | 33.69%
H2 | H2 & K | kellis | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 421.6663 | 493.6912 | 361.6617 | 110.7701 | 4.2492 | 17.0101 | 132.0294 | 22.44% | 0.8607% | 3.445% | 26.74%
F | E,F & I | dunmanway | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 30.75 | 99.5168 | 97.9169 | 0 | 1.5999 | 0 | 1.5999 | 0% | 1.608% | 0% | 1.608%
F | E,F & I | dunmanway | 2030 | 33% ECP | Grandfathering | IE wind priority | 30.75 | 99.5168 | 96.5856 | 0 | 2.9312 | 0 | 2.9312 | 0% | 2.945% | 0% | 2.945%
F | E,F & I | dunmanway | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 81.75 | 264.5691 | 167.7454 | 56.1889 | 4.4803 | 36.1546 | 96.8238 | 21.24% | 1.693% | 13.67% | 36.6%
F | E,F & I | dunmanway | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 30.75 | 99.5168 | 96.1802 | 0 | 3.3366 | 0 | 3.3366 | 0% | 3.353% | 0% | 3.353%
F | E,F & I | dunmanway | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 81.75 | 264.5691 | 158.2437 | 73.3819 | 4.4327 | 28.5109 | 106.3254 | 27.74% | 1.675% | 10.78% | 40.19%
H2 | H2 & K | kellymount | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 50.4 | 142.5678 | 99.9347 | 39.2015 | 2.6055 | 0.82617 | 42.6331 | 27.5% | 1.828% | 0.5795% | 29.9%
F | E,F & I | dunmanway | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 30.75 | 99.5168 | 95.8524 | 0 | 3.6644 | 0 | 3.6644 | 0% | 3.682% | 0% | 3.682%
F | E,F & I | dunmanway | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 81.75 | 264.5691 | 144.0301 | 78.4115 | 4.4179 | 37.7096 | 120.539 | 29.64% | 1.67% | 14.25% | 45.56%
H2 | H2 & K | kellymount | 2030 | 100% ECP | Grandfathering | IE wind not priority | 50.4 | 142.5678 | 97.6126 | 39.2015 | 2.6055 | 3.1482 | 44.9552 | 27.5% | 1.828% | 2.208% | 31.53%
F | E,F & I | dunmanway | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 30.75 | 99.5168 | 95.8127 | 0 | 3.7041 | 0 | 3.7041 | 0% | 3.722% | 0% | 3.722%
F | E,F & I | dunmanway | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 81.75 | 264.5691 | 193.4728 | 40.4699 | 4.3364 | 26.2901 | 71.0964 | 15.3% | 1.639% | 9.937% | 26.87%
H2 | H2 & K | kellymount | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 16.8 | 47.5225 | 38.4655 | 7.7631 | 0.8512 | 0.44272 | 9.057 | 16.34% | 1.791% | 0.9316% | 19.06%
F | E,F & I | dunmanway | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 30.75 | 99.5168 | 96.5856 | 0 | 2.9312 | 0 | 2.9312 | 0% | 2.945% | 0% | 2.945%
F | E,F & I | dunmanway | 2030 | 100% ECP | Grandfathering | IE wind not priority | 81.75 | 264.5691 | 165.0729 | 67.7112 | 4.4766 | 27.3085 | 99.4962 | 25.59% | 1.692% | 10.32% | 37.61%
F | E,F & I | dunmanway | 2035 | 100% ECP | Grandfathering | IE wind not priority | 81.75 | 264.5691 | 137.7185 | 43.0875 | 0.88831 | 82.8748 | 126.8507 | 16.29% | 0.3358% | 31.32% | 47.95%
H2 | H2 & K | kellymount | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 16.8 | 47.5225 | 28.0418 | 15.408 | 0.91445 | 3.1582 | 19.4807 | 32.42% | 1.924% | 6.646% | 40.99%
F | E,F & I | dunmanway | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 81.75 | 264.5691 | 172.6533 | 67.7112 | 4.4766 | 19.7281 | 91.9158 | 25.59% | 1.692% | 7.457% | 34.74%
H2 | H2 & K | kellymount | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 16.8 | 47.5225 | 29.7495 | 14.3848 | 0.90625 | 2.482 | 17.773 | 30.27% | 1.907% | 5.223% | 37.4%
F | E,F & I | dunmanway | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 30.75 | 99.5168 | 95.939 | 0 | 3.5778 | 0 | 3.5778 | 0% | 3.595% | 0% | 3.595%
H2 | H2 & K | kellymount | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 16.8 | 47.5225 | 34.4818 | 10.893 | 0.87782 | 1.2699 | 13.0408 | 22.92% | 1.847% | 2.672% | 27.44%
F | E,F & I | dunmanway | 2035 | 66% ECP | Grandfathering | IE wind not priority | 81.75 | 264.5691 | 134.5092 | 38.5344 | 0.8135 | 90.712 | 130.06 | 14.56% | 0.3075% | 34.29% | 49.16%
H2 | H2 & K | kellymount | 2030 | 33% ECP | Grandfathering | IE wind not priority | 16.8 | 47.5225 | 36.5539 | 7.7631 | 0.8512 | 2.3543 | 10.9686 | 16.34% | 1.791% | 4.954% | 23.08%
F | E,F & I | dunmanway | 2035 | 66% ECP | Grandfathering | IE wind priority | 30.75 | 99.5168 | 98.7145 | 0 | 0.8023 | 0 | 0.8023 | 0% | 0.8062% | 0% | 0.8062%
F | E,F & I | dunmanway | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 81.75 | 264.5691 | 162.4782 | 38.5344 | 0.8135 | 62.743 | 102.091 | 14.56% | 0.3075% | 23.72% | 38.59%
F | E,F & I | dunmanway | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 30.75 | 99.5168 | 98.7145 | 0 | 0.8023 | 0 | 0.8023 | 0% | 0.8062% | 0% | 0.8062%
F | E,F & I | dunmanway | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 81.75 | 264.5691 | 157.9813 | 73.3016 | 1.5416 | 31.7447 | 106.5878 | 27.71% | 0.5827% | 12% | 40.29%
H2 | H2 & K | kellis | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 592 | 693.1195 | 507.5858 | 156.088 | 6.2554 | 23.1903 | 185.5337 | 22.52% | 0.9025% | 3.346% | 26.77%
F | E,F & I | dunmanway | 2030 | 100% ECP | Grandfathering | IE wind priority | 30.75 | 99.5168 | 95.939 | 0 | 3.5778 | 0 | 3.5778 | 0% | 3.595% | 0% | 3.595%
G | J City, G South | drybridge | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 16.64 | 21.3206 | 17.8963 | 3.2659 | 0.15372 | 0.004642 | 3.4243 | 15.32% | 0.721% | 0.02177% | 16.06%
G | G North | lislea | 2035 | 100% ECP | Grandfathering | IE wind not priority | 48.8 | 152.458 | 121.3801 | 28.2749 | 0.52529 | 2.2777 | 31.0779 | 18.55% | 0.3445% | 1.494% | 20.38%
H2 | H2 & K | castledockrell | 2035 | 100% ECP | Grandfathering | IE wind priority | 41.4 | 117.1092 | 115.9914 | 0 | 1.1178 | 0 | 1.1178 | 0% | 0.9545% | 0% | 0.9545%
G | G North | shankill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 3.6667 | 4.698 | 3.5059 | 1.059 | 0.098387 | 0.034683 | 1.1921 | 22.54% | 2.094% | 0.7382% | 25.37%
G | G North | shankill | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 22 | 68.7311 | 66.4907 | 0 | 2.2404 | 0 | 2.2404 | 0% | 3.26% | 0% | 3.26%
H2 | H2 & K | castledockrell | 2035 | 100% ECP | Grandfathering | IE wind not priority | 38.5 | 108.9059 | 80.8895 | 19.595 | 0.38995 | 8.0314 | 28.0164 | 17.99% | 0.3581% | 7.375% | 25.73%
G | G North | shankill | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 3.6667 | 4.698 | 3.9715 | 0.6384 | 0.087003 | 0.001173 | 0.72658 | 13.59% | 1.852% | 0.02497% | 15.47%
G | G North | shankill | 2030 | 100% ECP | Grandfathering | IE wind priority | 22 | 68.7311 | 66.1467 | 0 | 2.5843 | 0 | 2.5843 | 0% | 3.76% | 0% | 3.76%
H2 | H2 & K | castledockrell | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 41.4 | 117.1092 | 114.9556 | 0 | 2.1536 | 0 | 2.1536 | 0% | 1.839% | 0% | 1.839%
G | G North | shankill | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 11 | 14.0942 | 9.1291 | 4.4477 | 0.31052 | 0.20675 | 4.965 | 31.56% | 2.203% | 1.467% | 35.23%
G | G North | shankill | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 22 | 68.7311 | 66.1467 | 0 | 2.5843 | 0 | 2.5843 | 0% | 3.76% | 0% | 3.76%
H2 | H2 & K | castledockrell | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 25.6666 | 72.6039 | 45.1946 | 22.5069 | 0.48878 | 4.4136 | 27.4092 | 31% | 0.6732% | 6.079% | 37.75%
G | G North | shankill | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 11 | 14.0942 | 9.3174 | 4.4477 | 0.31052 | 0.018525 | 4.7768 | 31.56% | 2.203% | 0.1314% | 33.89%
H2 | H2 & K | castledockrell | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 41.4 | 117.1092 | 116.0892 | 0 | 1.02 | 0 | 1.02 | 0% | 0.871% | 0% | 0.871%
G | G North | shankill | 2035 | 66% ECP | Grandfathering | IE wind priority | 22 | 68.7311 | 68.1236 | 0 | 0.60751 | 0 | 0.60751 | 0% | 0.8839% | 0% | 0.8839%
H2 | H2 & K | castledockrell | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 25.6666 | 72.6039 | 57.6636 | 11.7826 | 0.23863 | 2.9191 | 14.9403 | 16.23% | 0.3287% | 4.021% | 20.58%
G | G North | shankill | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 7.3333 | 9.3961 | 7.7479 | 1.4393 | 0.067744 | 0.14113 | 1.6482 | 15.32% | 0.721% | 1.502% | 17.54%
G | G North | shankill | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 22 | 68.7311 | 68.1236 | 0 | 0.60751 | 0 | 0.60751 | 0% | 0.8839% | 0% | 0.8839%
H2 | H2 & K | castledockrell | 2035 | 66% ECP | Grandfathering | IE wind priority | 41.4 | 117.1092 | 116.0892 | 0 | 1.02 | 0 | 1.02 | 0% | 0.871% | 0% | 0.871%
G | G North | shankill | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 7.3333 | 9.3961 | 7.7649 | 1.4393 | 0.067744 | 0.1242 | 1.6312 | 15.32% | 0.721% | 1.322% | 17.36%
G | G North | shankill | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 22 | 68.7311 | 67.5067 | 0 | 1.2244 | 0 | 1.2244 | 0% | 1.781% | 0% | 1.781%
H2 | H2 & K | castledockrell | 2035 | 66% ECP | Grandfathering | IE wind not priority | 25.6666 | 72.6039 | 56.1389 | 11.7826 | 0.23863 | 4.4438 | 16.465 | 16.23% | 0.3287% | 6.121% | 22.68%
G | G North | shankill | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 7.3333 | 9.3961 | 7.1575 | 2.0644 | 0.080278 | 0.0939 | 2.2386 | 21.97% | 0.8544% | 0.9994% | 23.82%
G | G North | shankill | 2035 | 100% ECP | Grandfathering | IE wind priority | 22 | 68.7311 | 68.0437 | 0 | 0.68738 | 0 | 0.68738 | 0% | 1% | 0% | 1%
G | G North | shankill | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 11 | 14.0942 | 10.6681 | 3.099 | 0.12773 | 0.19932 | 3.4261 | 21.99% | 0.9062% | 1.414% | 24.31%
G | G North | shankill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 22 | 68.7311 | 65.9734 | 0 | 2.7576 | 0 | 2.7576 | 0% | 4.012% | 0% | 4.012%
G | G North | shankill | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 3.6667 | 4.698 | 3.6616 | 0.91042 | 0.086938 | 0.039126 | 1.0365 | 19.38% | 1.851% | 0.8328% | 22.06%
G | G North | shankill | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 22 | 68.7311 | 66.0222 | 0 | 2.7089 | 0 | 2.7089 | 0% | 3.941% | 0% | 3.941%
G | G North | ratrussan | 2035 | 100% ECP | Grandfathering | IE wind priority | 78.62 | 245.6199 | 243.1634 | 0 | 2.4564 | 0 | 2.4564 | 0% | 1% | 0% | 1%
H2 | H2 & K | crane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 2.5 | 7.0718 | 6.7778 | 0 | 0.29405 | 0 | 0.29405 | 0% | 4.158% | 0% | 4.158%
G | G North | ricetown | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 21 | 26.907 | 22.4786 | 3.6563 | 0.49829 | 0.27384 | 4.4284 | 13.59% | 1.852% | 1.018% | 16.46%
H2 | H2 & K | crane | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 9.4333 | 11.0446 | 8.2874 | 2.1616 | 0.20882 | 0.3868 | 2.7572 | 19.57% | 1.891% | 3.502% | 24.96%
G | G North | ricetown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 21 | 26.907 | 21.7958 | 4.4598 | 0.50204 | 0.14935 | 5.1112 | 16.57% | 1.866% | 0.555% | 19%
G | G North | ricetown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 21 | 26.907 | 20.9708 | 5.2142 | 0.49792 | 0.22409 | 5.9362 | 19.38% | 1.851% | 0.8328% | 22.06%
H2 | H2 & K | crane | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 2.5 | 7.0718 | 6.7818 | 0 | 0.29 | 0 | 0.29 | 0% | 4.101% | 0% | 4.101%
G | G North | ricetown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 21 | 26.907 | 20.0795 | 6.0654 | 0.56349 | 0.19864 | 6.8275 | 22.54% | 2.094% | 0.7382% | 25.37%
G | G North | ricetown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 21 | 26.907 | 22.7457 | 3.6563 | 0.49829 | 0.0067182 | 4.1613 | 13.59% | 1.852% | 0.02497% | 15.47%
H2 | H2 & K | crane | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 9.4333 | 11.0446 | 8.6855 | 1.8568 | 0.20884 | 0.29345 | 2.3591 | 16.81% | 1.891% | 2.657% | 21.36%
G | G North | ricetown | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 63 | 80.7211 | 52.2851 | 25.4735 | 1.7784 | 1.1841 | 28.436 | 31.56% | 2.203% | 1.467% | 35.23%
G | G North | ricetown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 63 | 80.7211 | 53.3631 | 25.4735 | 1.7784 | 0.1061 | 27.358 | 31.56% | 2.203% | 0.1314% | 33.89%
H2 | H2 & K | crane | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 2.5 | 7.0718 | 6.8161 | 0 | 0.25574 | 0 | 0.25574 | 0% | 3.616% | 0% | 3.616%
G | J City, G South | baltrasna | 2030 | Initial | Grandfathering | IE Solar not priority | 17.13 | 21.9484 | 19.9159 | 1.7354 | 0.28384 | 0.013349 | 2.0326 | 7.907% | 1.293% | 0.06082% | 9.261%
H2 | H2 & K | crane | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 9.4333 | 11.0446 | 8.9084 | 1.5304 | 0.2053 | 0.40056 | 2.1362 | 13.86% | 1.859% | 3.627% | 19.34%
G | G North | ricetown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 42 | 53.814 | 44.4714 | 8.2433 | 0.38799 | 0.7113 | 9.3426 | 15.32% | 0.721% | 1.322% | 17.36%
G | G North | ricetown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 42 | 53.814 | 40.9932 | 11.8233 | 0.45977 | 0.53779 | 12.8208 | 21.97% | 0.8544% | 0.9994% | 23.82%
H2 | H2 & K | crane | 2030 | 33% ECP | Grandfathering | IE wind priority | 2.5 | 7.0718 | 6.8474 | 0 | 0.22438 | 0 | 0.22438 | 0% | 3.173% | 0% | 3.173%
G | G North | ricetown | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 63 | 80.7211 | 61.0992 | 17.7488 | 0.73153 | 1.1415 | 19.6219 | 21.99% | 0.9062% | 1.414% | 24.31%
H2 | H2 & K | crane | 2030 | Initial | Grandfathering | IE Solar not priority | 9 | 10.5373 | 8.787 | 0.87149 | 0.13577 | 0.74305 | 1.7503 | 8.271% | 1.289% | 7.052% | 16.61%
G | G North | shankill | 2030 | Initial | Grandfathering | IE wind priority | 22 | 68.7311 | 66.7226 | 0 | 2.0085 | 0 | 2.0085 | 0% | 2.922% | 0% | 2.922%
G | G North | shankill | 2030 | 33% ECP | Grandfathering | IE wind priority | 22 | 68.7311 | 66.4907 | 0 | 2.2404 | 0 | 2.2404 | 0% | 3.26% | 0% | 3.26%
H2 | H2 & K | crane | 2030 | Initial | Grandfathering | IE wind priority | 2.5 | 7.0718 | 6.8732 | 0 | 0.19866 | 0 | 0.19866 | 0% | 2.809% | 0% | 2.809%
G | G North | shankill | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 3.6667 | 4.698 | 3.9248 | 0.6384 | 0.087003 | 0.047813 | 0.77322 | 13.59% | 1.852% | 1.018% | 16.46%
G | G North | shankill | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 22 | 68.7311 | 66.2507 | 0 | 2.4803 | 0 | 2.4803 | 0% | 3.609% | 0% | 3.609%
G | G North | shankill | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 3.6667 | 4.698 | 3.8056 | 0.7787 | 0.087658 | 0.026076 | 0.89243 | 16.57% | 1.866% | 0.555% | 19%
G | G North | ricetown | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 42 | 53.814 | 44.3745 | 8.2433 | 0.38799 | 0.80828 | 9.4395 | 15.32% | 0.721% | 1.502% | 17.54%
H2 | H2 & K | castledockrell | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 41.4 | 117.1092 | 112.6005 | 0 | 4.5087 | 0 | 4.5087 | 0% | 3.85% | 0% | 3.85%
G | J City, G South | baltrasna | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 17.13 | 21.9484 | 18.4327 | 2.9825 | 0.40646 | 0.12677 | 3.5157 | 13.59% | 1.852% | 0.5776% | 16.02%
G | J City, G South | baltrasna | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 17.13 | 21.9484 | 17.8601 | 3.6379 | 0.40952 | 0.040936 | 4.0884 | 16.57% | 1.866% | 0.1865% | 18.63%
G | J City, G South | deenes | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 85 | 108.9094 | 67.7902 | 34.369 | 2.3995 | 4.3507 | 41.1192 | 31.56% | 2.203% | 3.995% | 37.76%
G | J City, G South | deenes | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 85 | 108.9094 | 67.0784 | 34.369 | 2.3995 | 5.0626 | 41.831 | 31.56% | 2.203% | 4.648% | 38.41%
H2 | H2 & K | castledockrell | 2030 | 33% ECP | Grandfathering | IE wind not priority | 12.8333 | 36.3019 | 27.9231 | 5.9301 | 0.65022 | 1.7985 | 8.3788 | 16.34% | 1.791% | 4.954% | 23.08%
G | J City, G South | deenes | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 85 | 108.9094 | 91.2822 | 16.6828 | 0.78522 | 0.15918 | 17.6272 | 15.32% | 0.721% | 0.1462% | 16.19%
H2 | H2 & K | castledockrell | 2030 | Initial | Grandfathering | IE wind priority | 41.4 | 117.1092 | 113.8194 | 0 | 3.2898 | 0 | 3.2898 | 0% | 2.809% | 0% | 2.809%
G | J City, G South | deenes | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 56.6666 | 72.6062 | 60.8547 | 11.1219 | 0.52348 | 0.10612 | 11.7515 | 15.32% | 0.721% | 0.1462% | 16.19%
G | J City, G South | deenes | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 85 | 108.9094 | 91.4176 | 16.6828 | 0.78522 | 0.023712 | 17.4918 | 15.32% | 0.721% | 0.02177% | 16.06%
G | J City, G South | deenes | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 56.6666 | 72.6062 | 60.945 | 11.1219 | 0.52348 | 0.015808 | 11.6612 | 15.32% | 0.721% | 0.02177% | 16.06%
G | J City, G South | deenes | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 85 | 108.9094 | 84.0278 | 23.9281 | 0.93049 | 0.023027 | 24.8816 | 21.97% | 0.8544% | 0.02114% | 22.85%
G | J City, G South | deenes | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 56.6666 | 72.6062 | 56.0185 | 15.952 | 0.62033 | 0.015352 | 16.5877 | 21.97% | 0.8544% | 0.02114% | 22.85%
G | J City, G South | deenes | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 85 | 108.9094 | 83.8264 | 23.9469 | 0.98699 | 0.14916 | 25.083 | 21.99% | 0.9062% | 0.137% | 23.03%
H2 | H2 & K | castledockrell | 2030 | 33% ECP | Grandfathering | IE wind priority | 41.4 | 117.1092 | 113.3936 | 0 | 3.7157 | 0 | 3.7157 | 0% | 3.173% | 0% | 3.173%
G | J City, G South | drybridge | 2030 | Initial | Grandfathering | IE Solar not priority | 15.98 | 20.475 | 18.5789 | 1.6189 | 0.26479 | 0.012453 | 1.8961 | 7.907% | 1.293% | 0.06082% | 9.261%
H2 | H2 & K | carlow | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 93.29 | 109.2249 | 79.9876 | 24.597 | 0.98576 | 3.6544 | 29.2372 | 22.52% | 0.9025% | 3.346% | 26.77%
G | J City, G South | drybridge | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 16.31 | 20.8978 | 17.5503 | 2.8397 | 0.38701 | 0.12071 | 3.3474 | 13.59% | 1.852% | 0.5776% | 16.02%
G | J City, G South | drybridge | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 16.31 | 20.8978 | 17.0051 | 3.4638 | 0.38992 | 0.038977 | 3.8927 | 16.57% | 1.866% | 0.1865% | 18.63%
H2 | H2 & K | carlow | 2035 | 100% ECP | Grandfathering | IE wind priority | 30.49 | 86.2478 | 85.4246 | 0 | 0.82325 | 0 | 0.82325 | 0% | 0.9545% | 0% | 0.9545%
G | J City, G South | drybridge | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 16.31 | 20.8978 | 16.389 | 4.0497 | 0.38672 | 0.072381 | 4.5088 | 19.38% | 1.851% | 0.3464% | 21.58%
G | J City, G South | drybridge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 16.31 | 20.8978 | 15.6861 | 4.7108 | 0.43764 | 0.063278 | 5.2117 | 22.54% | 2.094% | 0.3028% | 24.94%
H2 | H2 & K | carlow | 2035 | 100% ECP | Grandfathering | IE wind not priority | 21 | 59.4032 | 44.1216 | 10.6882 | 0.2127 | 4.3808 | 15.2817 | 17.99% | 0.3581% | 7.375% | 25.73%
G | J City, G South | drybridge | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 16.31 | 20.8978 | 17.5603 | 2.8397 | 0.38701 | 0.11079 | 3.3375 | 13.59% | 1.852% | 0.5302% | 15.97%
G | J City, G South | drybridge | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 16.97 | 21.7434 | 13.5341 | 6.8617 | 0.47905 | 0.86861 | 8.2093 | 31.56% | 2.203% | 3.995% | 37.76%
H2 | H2 & K | carlow | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 62.1933 | 72.8165 | 53.3429 | 16.3379 | 0.62673 | 2.5089 | 19.4736 | 22.44% | 0.8607% | 3.445% | 26.74%
G | J City, G South | drybridge | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 16.97 | 21.7434 | 13.392 | 6.8617 | 0.47905 | 1.0107 | 8.3514 | 31.56% | 2.203% | 4.648% | 38.41%
H2 | H2 & K | carlow | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 30.49 | 86.2478 | 84.6618 | 0 | 1.5861 | 0 | 1.5861 | 0% | 1.839% | 0% | 1.839%
G | G North | ratrussan | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 78.62 | 245.6199 | 241.2445 | 0 | 4.3754 | 0 | 4.3754 | 0% | 1.781% | 0% | 1.781%
G | J City, G South | deenes | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 28.3333 | 36.3031 | 30.5052 | 4.9331 | 0.6723 | 0.19246 | 5.7979 | 13.59% | 1.852% | 0.5302% | 15.97%
H2 | H2 & K | castledockrell | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 12.8333 | 36.3019 | 26.3403 | 8.3211 | 0.67056 | 0.97008 | 9.9617 | 22.92% | 1.847% | 2.672% | 27.44%
H2 | H2 & K | castledockrell | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 38.5 | 108.9059 | 76.339 | 29.9456 | 1.9903 | 0.6311 | 32.5669 | 27.5% | 1.828% | 0.5795% | 29.9%
G | J City, G South | baltrasna | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 17.13 | 21.9484 | 17.2129 | 4.2533 | 0.40616 | 0.07602 | 4.7355 | 19.38% | 1.851% | 0.3464% | 21.58%
G | J City, G South | baltrasna | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 17.13 | 21.9484 | 16.4747 | 4.9476 | 0.45965 | 0.066459 | 5.4737 | 22.54% | 2.094% | 0.3028% | 24.94%
H2 | H2 & K | castledockrell | 2030 | 100% ECP | Grandfathering | IE wind priority | 41.4 | 117.1092 | 112.6005 | 0 | 4.5087 | 0 | 4.5087 | 0% | 3.85% | 0% | 3.85%
G | J City, G South | baltrasna | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 17.13 | 21.9484 | 18.4431 | 2.9825 | 0.40646 | 0.11636 | 3.5053 | 13.59% | 1.852% | 0.5302% | 15.97%
G | J City, G South | baltrasna | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 17.13 | 21.9484 | 13.6617 | 6.9264 | 0.48357 | 0.8768 | 8.2867 | 31.56% | 2.203% | 3.995% | 37.76%
H2 | H2 & K | castledockrell | 2030 | 100% ECP | Grandfathering | IE wind not priority | 38.5 | 108.9059 | 74.5652 | 29.9456 | 1.9903 | 2.4049 | 34.3407 | 27.5% | 1.828% | 2.208% | 31.53%
G | J City, G South | baltrasna | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 17.13 | 21.9484 | 13.5183 | 6.9264 | 0.48357 | 1.0203 | 8.4302 | 31.56% | 2.203% | 4.648% | 38.41%
H2 | H2 & K | castledockrell | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 41.4 | 117.1092 | 113.3936 | 0 | 3.7157 | 0 | 3.7157 | 0% | 3.173% | 0% | 3.173%
G | J City, G South | baltrasna | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 17.13 | 21.9484 | 18.396 | 3.3621 | 0.15825 | 0.032078 | 3.5524 | 15.32% | 0.721% | 0.1462% | 16.19%
G | J City, G South | baltrasna | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 17.13 | 21.9484 | 18.4233 | 3.3621 | 0.15825 | 0.0047787 | 3.5251 | 15.32% | 0.721% | 0.02177% | 16.06%
H2 | H2 & K | castledockrell | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 12.8333 | 36.3019 | 29.3834 | 5.9301 | 0.65022 | 0.33819 | 6.9185 | 16.34% | 1.791% | 0.9316% | 19.06%
G | J City, G South | baltrasna | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 17.13 | 21.9484 | 16.9341 | 4.8222 | 0.18752 | 0.0046407 | 5.0144 | 21.97% | 0.8544% | 0.02114% | 22.85%
G | J City, G South | deenes | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 85 | 108.9094 | 91.5158 | 14.7993 | 2.0169 | 0.57738 | 17.3936 | 13.59% | 1.852% | 0.5302% | 15.97%
G | J City, G South | baltrasna | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 17.13 | 21.9484 | 16.8935 | 4.826 | 0.19891 | 0.030061 | 5.055 | 21.99% | 0.9062% | 0.137% | 23.03%
G | J City, G South | deenes | 2030 | Initial | Grandfathering | IE Solar not priority | 85 | 108.9094 | 98.8237 | 8.611 | 1.4084 | 0.066239 | 10.0857 | 7.907% | 1.293% | 0.06082% | 9.261%
H2 | H2 & K | castledockrell | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 12.8333 | 36.3019 | 21.4208 | 11.77 | 0.69854 | 2.4125 | 14.8811 | 32.42% | 1.924% | 6.646% | 40.99%
G | J City, G South | deenes | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 85 | 108.9094 | 91.4641 | 14.7993 | 2.0169 | 0.62906 | 17.4453 | 13.59% | 1.852% | 0.5776% | 16.02%
G | J City, G South | deenes | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 28.3333 | 36.3031 | 30.488 | 4.9331 | 0.6723 | 0.20969 | 5.8151 | 13.59% | 1.852% | 0.5776% | 16.02%
H2 | H2 & K | castledockrell | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 41.4 | 117.1092 | 112.3068 | 0 | 4.8024 | 0 | 4.8024 | 0% | 4.101% | 0% | 4.101%
G | J City, G South | deenes | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 85 | 108.9094 | 88.6225 | 18.0516 | 2.0321 | 0.20313 | 20.2868 | 16.57% | 1.866% | 0.1865% | 18.63%
G | J City, G South | deenes | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 28.3333 | 36.3031 | 29.5408 | 6.0172 | 0.67736 | 0.067709 | 6.7623 | 16.57% | 1.866% | 0.1865% | 18.63%
H2 | H2 & K | castledockrell | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 12.8333 | 36.3019 | 22.7253 | 10.9884 | 0.69227 | 1.896 | 13.5766 | 30.27% | 1.907% | 5.223% | 37.4%
G | J City, G South | deenes | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 85 | 108.9094 | 85.4116 | 21.1052 | 2.0154 | 0.37721 | 23.4978 | 19.38% | 1.851% | 0.3464% | 21.58%
G | J City, G South | deenes | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 28.3333 | 36.3031 | 28.4705 | 7.0351 | 0.6718 | 0.12574 | 7.8326 | 19.38% | 1.851% | 0.3464% | 21.58%
H2 | H2 & K | castledockrell | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 41.4 | 117.1092 | 112.8741 | 0 | 4.2351 | 0 | 4.2351 | 0% | 3.616% | 0% | 3.616%
G | J City, G South | deenes | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 85 | 108.9094 | 81.7484 | 24.5504 | 2.2808 | 0.32977 | 27.161 | 22.54% | 2.094% | 0.3028% | 24.94%
G | J City, G South | deenes | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 28.3333 | 36.3031 | 27.2494 | 8.1835 | 0.76026 | 0.10992 | 9.0537 | 22.54% | 2.094% | 0.3028% | 24.94%
H2 | H2 & K | castledockrell | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 41.4 | 117.1092 | 112.2398 | 0 | 4.8694 | 0 | 4.8694 | 0% | 4.158% | 0% | 4.158%
H2 | H2 & K | crane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 9.4333 | 11.0446 | 7.906 | 2.514 | 0.23478 | 0.38994 | 3.1387 | 22.76% | 2.126% | 3.531% | 28.42%
G | G North | ratrussan | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 78.62 | 245.6199 | 243.4489 | 0 | 2.171 | 0 | 2.171 | 0% | 0.8839% | 0% | 0.8839%
G | G North | ratrussan | 2035 | 66% ECP | Grandfathering | IE wind priority | 78.62 | 245.6199 | 243.4489 | 0 | 2.171 | 0 | 2.171 | 0% | 0.8839% | 0% | 0.8839%
G | G North | meath hill | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 16.5 | 51.5483 | 49.5166 | 0 | 2.0317 | 0 | 2.0317 | 0% | 3.941% | 0% | 3.941%
H2 | H2 & K | crory | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 44.012 | 124.4979 | 119.7047 | 0 | 4.7932 | 0 | 4.7932 | 0% | 3.85% | 0% | 3.85%
G | G North | meath hill | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 0.13333 | 0.17084 | 0.13315 | 0.033106 | 0.0031614 | 0.0014228 | 0.03769 | 19.38% | 1.851% | 0.8328% | 22.06%
G | G North | meath hill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 34.56 | 107.9703 | 69.8976 | 34.8422 | 1.8851 | 1.3454 | 38.0727 | 32.27% | 1.746% | 1.246% | 35.26%
H2 | H2 & K | crory | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 20 | 23.4162 | 15.174 | 7.4312 | 0.51399 | 0.29692 | 8.2422 | 31.74% | 2.195% | 1.268% | 35.2%
G | G North | meath hill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 16.5 | 51.5483 | 49.4801 | 0 | 2.0682 | 0 | 2.0682 | 0% | 4.012% | 0% | 4.012%
G | G North | meath hill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 0.13333 | 0.17084 | 0.12749 | 0.03851 | 0.0035777 | 0.0012612 | 0.043349 | 22.54% | 2.094% | 0.7382% | 25.37%
H2 | H2 & K | crory | 2030 | 100% ECP | Grandfathering | IE wind priority | 44.012 | 124.4979 | 119.7047 | 0 | 4.7932 | 0 | 4.7932 | 0% | 3.85% | 0% | 3.85%
G | G North | meath hill | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 34.56 | 107.9703 | 86.8467 | 18.7109 | 1.9553 | 0.45734 | 21.1235 | 17.33% | 1.811% | 0.4236% | 19.56%
G | G North | meath hill | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 16.5 | 51.5483 | 49.868 | 0 | 1.6803 | 0 | 1.6803 | 0% | 3.26% | 0% | 3.26%
H2 | H2 & K | crory | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 20 | 23.4162 | 19.6279 | 3.2446 | 0.43527 | 0.10844 | 3.7883 | 13.86% | 1.859% | 0.4631% | 16.18%
G | G North | meath hill | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 0.13333 | 0.17084 | 0.14442 | 0.023215 | 0.0031638 | 4.2655e-05 | 0.026421 | 13.59% | 1.852% | 0.02497% | 15.47%
G | G North | meath hill | 2030 | 100% ECP | Grandfathering | IE wind not priority | 34.56 | 107.9703 | 71.4503 | 30.0106 | 1.8659 | 4.6435 | 36.52 | 27.8% | 1.728% | 4.301% | 33.82%
H2 | H2 & K | crory | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 44.012 | 124.4979 | 120.5478 | 0 | 3.9501 | 0 | 3.9501 | 0% | 3.173% | 0% | 3.173%
G | G North | meath hill | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 34.56 | 107.9703 | 72.131 | 32.6822 | 1.8845 | 1.2727 | 35.8393 | 30.27% | 1.745% | 1.179% | 33.19%
G | G North | meath hill | 2030 | 100% ECP | Grandfathering | IE wind priority | 16.5 | 51.5483 | 49.6101 | 0 | 1.9383 | 0 | 1.9383 | 0% | 3.76% | 0% | 3.76%
H2 | H2 & K | crory | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 20 | 23.4162 | 16.7617 | 5.33 | 0.49776 | 0.82672 | 6.6545 | 22.76% | 2.126% | 3.531% | 28.42%
G | G North | meath hill | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 34.56 | 107.9703 | 75.7474 | 30.0106 | 1.8659 | 0.3464 | 32.2229 | 27.8% | 1.728% | 0.3208% | 29.84%
G | G North | meath hill | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 16.5 | 51.5483 | 49.6101 | 0 | 1.9383 | 0 | 1.9383 | 0% | 3.76% | 0% | 3.76%
H2 | H2 & K | crory | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 44.012 | 124.4979 | 119.3212 | 0 | 5.1767 | 0 | 5.1767 | 0% | 4.158% | 0% | 4.158%
G | G North | meath hill | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 0.4 | 0.51251 | 0.33881 | 0.16174 | 0.011292 | 0.00067365 | 0.1737 | 31.56% | 2.203% | 0.1314% | 33.89%
H2 | H2 & K | crory | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 20 | 23.4162 | 17.5705 | 4.5829 | 0.44274 | 0.82007 | 5.8457 | 19.57% | 1.891% | 3.502% | 24.96%
H2 | H2 & K | crory | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 44.012 | 124.4979 | 119.3924 | 0 | 5.1054 | 0 | 5.1054 | 0% | 4.101% | 0% | 4.101%
G | G North | meath hill | 2035 | 66% ECP | Grandfathering | IE wind not priority | 34.56 | 107.9703 | 87.7948 | 18.2124 | 0.34772 | 1.6153 | 20.1755 | 16.87% | 0.3221% | 1.496% | 18.69%
G | G North | meath hill | 2035 | 66% ECP | Grandfathering | IE wind priority | 16.5 | 51.5483 | 51.0927 | 0 | 0.45563 | 0 | 0.45563 | 0% | 0.8839% | 0% | 0.8839%
H2 | H2 & K | crory | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 20 | 23.4162 | 18.4146 | 3.9367 | 0.44278 | 0.62216 | 5.0016 | 16.81% | 1.891% | 2.657% | 21.36%
G | G North | meath hill | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 0.26667 | 0.34168 | 0.28174 | 0.052338 | 0.0024634 | 0.0051319 | 0.059934 | 15.32% | 0.721% | 1.502% | 17.54%
G | G North | meath hill | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 0.4 | 0.51251 | 0.33197 | 0.16174 | 0.011292 | 0.0075181 | 0.18055 | 31.56% | 2.203% | 1.467% | 35.23%
G | G North | meath hill | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 34.56 | 107.9703 | 89.0358 | 18.2124 | 0.34772 | 0.3743 | 18.9345 | 16.87% | 0.3221% | 0.3467% | 17.54%
H2 | H2 & K | crory | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 20 | 23.4162 | 15.4483 | 7.4312 | 0.51399 | 0.022684 | 7.9679 | 31.74% | 2.195% | 0.09687% | 34.03%
G | G North | meath hill | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 16.5 | 51.5483 | 49.6881 | 0 | 1.8603 | 0 | 1.8603 | 0% | 3.609% | 0% | 3.609%
G | G North | louth | 2030 | Initial | Grandfathering | IE Solar not priority | 50 | 64.0644 | 57.339 | 5.0653 | 0.8285 | 0.83151 | 6.7253 | 7.907% | 1.293% | 1.298% | 10.5%
G | G North | louth | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 75 | 96.0965 | 80.2807 | 13.0582 | 1.7796 | 0.97799 | 15.8158 | 13.59% | 1.852% | 1.018% | 16.46%
H2 | H2 & K | crory | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 20 | 23.4162 | 17.1482 | 5.2732 | 0.21133 | 0.78346 | 6.268 | 22.52% | 0.9025% | 3.346% | 26.77%
G | G North | louth | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 75 | 96.0965 | 77.8422 | 15.9279 | 1.793 | 0.53338 | 18.2543 | 16.57% | 1.866% | 0.555% | 19%
G | G North | louth | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 75 | 96.0965 | 74.8957 | 18.6222 | 1.7783 | 0.80031 | 21.2008 | 19.38% | 1.851% | 0.8328% | 22.06%
H2 | H2 & K | crory | 2035 | 100% ECP | Grandfathering | IE wind priority | 44.012 | 124.4979 | 123.3095 | 0 | 1.1884 | 0 | 1.1884 | 0% | 0.9545% | 0% | 0.9545%
G | G North | louth | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 75 | 96.0965 | 71.7125 | 21.6621 | 2.0125 | 0.70942 | 24.384 | 22.54% | 2.094% | 0.7382% | 25.37%
G | G North | louth | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 75 | 96.0965 | 81.2347 | 13.0582 | 1.7796 | 0.023994 | 14.8618 | 13.59% | 1.852% | 0.02497% | 15.47%
H2 | H2 & K | crory | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 20 | 23.4162 | 17.1539 | 5.2539 | 0.20154 | 0.80681 | 6.2623 | 22.44% | 0.8607% | 3.445% | 26.74%
G | G North | louth | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 125 | 160.1609 | 103.7402 | 50.5426 | 3.5286 | 2.3494 | 56.4207 | 31.56% | 2.203% | 1.467% | 35.23%
G | G North | louth | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 125 | 160.1609 | 105.8791 | 50.5426 | 3.5286 | 0.21052 | 54.2818 | 31.56% | 2.203% | 0.1314% | 33.89%
H2 | H2 & K | crory | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 44.012 | 124.4979 | 122.2084 | 0 | 2.2895 | 0 | 2.2895 | 0% | 1.839% | 0% | 1.839%
G | G North | louth | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 99.9999 | 128.1286 | 105.6535 | 19.6268 | 0.92379 | 1.9245 | 22.4751 | 15.32% | 0.721% | 1.502% | 17.54%
G | G North | meath hill | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 0.13333 | 0.17084 | 0.13839 | 0.028316 | 0.0031876 | 0.00094823 | 0.032452 | 16.57% | 1.866% | 0.555% | 19%
H2 | H2 & K | crory | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 20 | 23.4162 | 19.233 | 3.7176 | 0.17186 | 0.29374 | 4.1832 | 15.88% | 0.7339% | 1.254% | 17.86%
G | G North | louth | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 99.9999 | 128.1286 | 97.6028 | 28.1507 | 1.0947 | 1.2805 | 30.5258 | 21.97% | 0.8544% | 0.9994% | 23.82%
H2 | H2 & K | crory | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 44.012 | 124.4979 | 123.4135 | 0 | 1.0844 | 0 | 1.0844 | 0% | 0.871% | 0% | 0.871%
G | G North | louth | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 125 | 160.1609 | 121.2285 | 35.216 | 1.4515 | 2.265 | 38.9324 | 21.99% | 0.9062% | 1.414% | 24.31%
H2 | H2 & K | crory | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 20 | 23.4162 | 18.6192 | 3.7176 | 0.17186 | 0.90753 | 4.797 | 15.88% | 0.7339% | 3.876% | 20.49%
G | G North | meath hill | 2030 | Initial | Grandfathering | IE wind not priority | 34.56 | 107.9703 | 86.0099 | 13.8186 | 1.9969 | 6.1448 | 21.9604 | 12.8% | 1.85% | 5.691% | 20.34%
G | G North | meath hill | 2030 | Initial | Grandfathering | IE wind priority | 16.5 | 51.5483 | 50.0419 | 0 | 1.5064 | 0 | 1.5064 | 0% | 2.922% | 0% | 2.922%
H2 | H2 & K | crory | 2035 | 66% ECP | Grandfathering | IE wind priority | 44.012 | 124.4979 | 123.4135 | 0 | 1.0844 | 0 | 1.0844 | 0% | 0.871% | 0% | 0.871%
G | G North | meath hill | 2030 | 33% ECP | Grandfathering | IE wind not priority | 34.56 | 107.9703 | 81.8948 | 18.7109 | 1.9553 | 5.4093 | 26.0755 | 17.33% | 1.811% | 5.01% | 24.15%
G | G North | meath hill | 2030 | 33% ECP | Grandfathering | IE wind priority | 16.5 | 51.5483 | 49.868 | 0 | 1.6803 | 0 | 1.6803 | 0% | 3.26% | 0% | 3.26%
G | G North | meath hill | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 0.13333 | 0.17084 | 0.14272 | 0.023215 | 0.0031638 | 0.0017386 | 0.028117 | 13.59% | 1.852% | 1.018% | 16.46%
G | G North | meath hill | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 34.56 | 107.9703 | 77.3763 | 25.6575 | 1.9249 | 3.0116 | 30.594 | 23.76% | 1.783% | 2.789% | 28.34%
G | G North | louth | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 99.9999 | 128.1286 | 105.8844 | 19.6268 | 0.92379 | 1.6936 | 22.2442 | 15.32% | 0.721% | 1.322% | 17.36%
H2 | H2 & K | crory | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 44.012 | 124.4979 | 119.9955 | 0 | 4.5023 | 0 | 4.5023 | 0% | 3.616% | 0% | 3.616%
G | G North | meath hill | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 0.26667 | 0.34168 | 0.28236 | 0.052338 | 0.0024634 | 0.0045162 | 0.059318 | 15.32% | 0.721% | 1.322% | 17.36%
G | G North | oriel 220kv | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 165 | 691.2706 | 482.8751 | 187.9878 | 12.2596 | 8.1481 | 208.3955 | 27.19% | 1.773% | 1.179% | 30.15%
H2 | H2 & K | crane | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 9.8667 | 11.552 | 9.1855 | 1.834 | 0.084786 | 0.44772 | 2.3665 | 15.88% | 0.7339% | 3.876% | 20.49%
G | G North | oriel 220kv | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 210 | 879.799 | 614.5684 | 239.2572 | 15.6032 | 10.3703 | 265.2306 | 27.19% | 1.773% | 1.179% | 30.15%
G | G North | oriel 220kv | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 165 | 691.2706 | 467.7437 | 202.4044 | 12.509 | 8.6135 | 223.527 | 29.28% | 1.81% | 1.246% | 32.34%
H2 | H2 & K | crane | 2035 | 66% ECP | Grandfathering | IE wind priority | 2.5 | 7.0718 | 7.0102 | 0 | 0.061594 | 0 | 0.061594 | 0% | 0.871% | 0% | 0.871%
G | G North | oriel 220kv | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 210 | 879.799 | 595.3101 | 257.6056 | 15.9206 | 10.9627 | 284.4888 | 29.28% | 1.81% | 1.246% | 32.34%
G | G North | oriel 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 165 | 691.2706 | 492.0013 | 193.8632 | 4.1211 | 1.2849 | 199.2693 | 28.04% | 0.5962% | 0.1859% | 28.83%
G | G North | oriel 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 210 | 879.799 | 626.1835 | 246.735 | 5.2451 | 1.6353 | 253.6155 | 28.04% | 0.5962% | 0.1859% | 28.83%
H2 | H2 & K | crane | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 2.5 | 7.0718 | 7.0102 | 0 | 0.061594 | 0 | 0.061594 | 0% | 0.871% | 0% | 0.871%
H2 | H2 & K | crane | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 10.3 | 12.0593 | 7.9559 | 3.8271 | 0.2647 | 0.011682 | 4.1035 | 31.74% | 2.195% | 0.09687% | 34.03%
G | G North | ratrussan | 2030 | Initial | Grandfathering | IE wind priority | 78.62 | 245.6199 | 238.4422 | 0 | 7.1777 | 0 | 7.1777 | 0% | 2.922% | 0% | 2.922%
H2 | H2 & K | crane | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 2.5 | 7.0718 | 6.7995 | 0 | 0.27227 | 0 | 0.27227 | 0% | 3.85% | 0% | 3.85%
G | G North | ratrussan | 2030 | 33% ECP | Grandfathering | IE wind priority | 78.62 | 245.6199 | 237.6136 | 0 | 8.0062 | 0 | 8.0062 | 0% | 3.26% | 0% | 3.26%
G | G North | ratrussan | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 78.62 | 245.6199 | 236.7561 | 0 | 8.8638 | 0 | 8.8638 | 0% | 3.609% | 0% | 3.609%
H2 | H2 & K | crane | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 10.3 | 12.0593 | 7.8146 | 3.8271 | 0.2647 | 0.15291 | 4.2447 | 31.74% | 2.195% | 1.268% | 35.2%
G | G North | ratrussan | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 78.62 | 245.6199 | 235.9392 | 0 | 9.6807 | 0 | 9.6807 | 0% | 3.941% | 0% | 3.941%
G | G North | ratrussan | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 78.62 | 245.6199 | 235.7651 | 0 | 9.8548 | 0 | 9.8548 | 0% | 4.012% | 0% | 4.012%
H2 | H2 & K | crane | 2030 | 100% ECP | Grandfathering | IE wind priority | 2.5 | 7.0718 | 6.7995 | 0 | 0.27227 | 0 | 0.27227 | 0% | 3.85% | 0% | 3.85%
G | G North | ratrussan | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 78.62 | 245.6199 | 237.6136 | 0 | 8.0062 | 0 | 8.0062 | 0% | 3.26% | 0% | 3.26%
G | G North | ratrussan | 2030 | 100% ECP | Grandfathering | IE wind priority | 78.62 | 245.6199 | 236.3844 | 0 | 9.2355 | 0 | 9.2355 | 0% | 3.76% | 0% | 3.76%
H2 | H2 & K | crane | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 9.4333 | 11.0446 | 9.2578 | 1.5304 | 0.2053 | 0.051148 | 1.7868 | 13.86% | 1.859% | 0.4631% | 16.18%
G | G North | ratrussan | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 78.62 | 245.6199 | 236.3844 | 0 | 9.2355 | 0 | 9.2355 | 0% | 3.76% | 0% | 3.76%
H2 | H2 & K | crane | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 2.5 | 7.0718 | 6.8474 | 0 | 0.22438 | 0 | 0.22438 | 0% | 3.173% | 0% | 3.173%
G | G North | meath hill | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 16.5 | 51.5483 | 51.0927 | 0 | 0.45563 | 0 | 0.45563 | 0% | 0.8839% | 0% | 0.8839%
G | G North | navan | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 116.449 | 149.2046 | 112.9355 | 32.8069 | 1.3522 | 2.11 | 36.2691 | 21.99% | 0.9062% | 1.414% | 24.31%
H2 | H2 & K | crane | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 9.8667 | 11.552 | 9.4883 | 1.834 | 0.084786 | 0.14491 | 2.0637 | 15.88% | 0.7339% | 1.254% | 17.86%
H2 | H2 & K | crory | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 20 | 23.4162 | 18.8871 | 3.2446 | 0.43527 | 0.84924 | 4.5291 | 13.86% | 1.859% | 3.627% | 19.34%
G | G North | meath hill | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 34.56 | 107.9703 | 74.2699 | 32.8484 | 0.65136 | 0.20069 | 33.7004 | 30.42% | 0.6033% | 0.1859% | 31.21%
G | G North | meath hill | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 16.5 | 51.5483 | 50.63 | 0 | 0.91827 | 0 | 0.91827 | 0% | 1.781% | 0% | 1.781%
H2 | H2 & K | crory | 2030 | 33% ECP | Grandfathering | IE wind priority | 44.012 | 124.4979 | 120.5478 | 0 | 3.9501 | 0 | 3.9501 | 0% | 3.173% | 0% | 3.173%
G | G North | meath hill | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 0.26667 | 0.34168 | 0.26027 | 0.075068 | 0.0029192 | 0.0034146 | 0.081402 | 21.97% | 0.8544% | 0.9994% | 23.82%
G | G North | meath hill | 2035 | 100% ECP | Grandfathering | IE wind not priority | 34.56 | 107.9703 | 85.961 | 20.0242 | 0.37201 | 1.6131 | 22.0093 | 18.55% | 0.3445% | 1.494% | 20.38%
H2 | H2 & K | crory | 2030 | Initial | Grandfathering | IE Solar not priority | 20 | 23.4162 | 19.5266 | 1.9366 | 0.30172 | 1.6512 | 3.8896 | 8.271% | 1.289% | 7.052% | 16.61%
G | G North | meath hill | 2035 | 100% ECP | Grandfathering | IE wind priority | 16.5 | 51.5483 | 51.0328 | 0 | 0.51553 | 0 | 0.51553 | 0% | 1% | 0% | 1%
G | G North | meath hill | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 0.4 | 0.51251 | 0.38793 | 0.11269 | 0.0046446 | 0.0072479 | 0.12458 | 21.99% | 0.9062% | 1.414% | 24.31%
H2 | H2 & K | crory | 2030 | Initial | Grandfathering | IE wind priority | 44.012 | 124.4979 | 121.0005 | 0 | 3.4973 | 0 | 3.4973 | 0% | 2.809% | 0% | 2.809%
G | G North | navan | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 81.9656 | 105.0215 | 80.0008 | 23.0739 | 0.89727 | 1.0495 | 25.0207 | 21.97% | 0.8544% | 0.9994% | 23.82%
G | G North | navan | 2030 | Initial | Grandfathering | IE Solar not priority | 12.999 | 16.6554 | 14.907 | 1.3169 | 0.21539 | 0.21618 | 1.7484 | 7.907% | 1.293% | 1.298% | 10.5%
G | G North | navan | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 47.4823 | 60.8385 | 50.8255 | 8.2671 | 1.1267 | 0.61916 | 10.013 | 13.59% | 1.852% | 1.018% | 16.46%
G | G North | navan | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 47.4823 | 60.8385 | 49.2817 | 10.0839 | 1.1352 | 0.33768 | 11.5568 | 16.57% | 1.866% | 0.555% | 19%
H2 | H2 & K | crane | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 10.3 | 12.0593 | 8.8313 | 2.7157 | 0.10884 | 0.40348 | 3.228 | 22.52% | 0.9025% | 3.346% | 26.77%
G | G North | navan | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 47.4823 | 60.8385 | 47.4163 | 11.7897 | 1.1258 | 0.50667 | 13.4222 | 19.38% | 1.851% | 0.8328% | 22.06%
G | G North | navan | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 47.4823 | 60.8385 | 45.401 | 13.7142 | 1.2741 | 0.44913 | 15.4375 | 22.54% | 2.094% | 0.7382% | 25.37%
H2 | H2 & K | crane | 2035 | 100% ECP | Grandfathering | IE wind priority | 2.5 | 7.0718 | 7.0043 | 0 | 0.067502 | 0 | 0.067502 | 0% | 0.9545% | 0% | 0.9545%
G | G North | navan | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 47.4823 | 60.8385 | 51.4295 | 8.2671 | 1.1267 | 0.01519 | 9.409 | 13.59% | 1.852% | 0.02497% | 15.47%
G | G North | navan | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 116.449 | 149.2046 | 96.6436 | 47.0851 | 3.2873 | 2.1887 | 52.561 | 31.56% | 2.203% | 1.467% | 35.23%
H2 | H2 & K | crane | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 9.8667 | 11.552 | 8.4626 | 2.5919 | 0.099428 | 0.39802 | 3.0894 | 22.44% | 0.8607% | 3.445% | 26.74%
G | G North | navan | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 116.449 | 149.2046 | 98.6361 | 47.0851 | 3.2873 | 0.19611 | 50.5685 | 31.56% | 2.203% | 0.1314% | 33.89%
H2 | H2 & K | crane | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 2.5 | 7.0718 | 6.9418 | 0 | 0.13005 | 0 | 0.13005 | 0% | 1.839% | 0% | 1.839%
G | G North | navan | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 81.9656 | 105.0215 | 86.5996 | 16.0873 | 0.75719 | 1.5774 | 18.4219 | 15.32% | 0.721% | 1.502% | 17.54%
G | G North | navan | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 81.9656 | 105.0215 | 86.7889 | 16.0873 | 0.75719 | 1.3881 | 18.2326 | 15.32% | 0.721% | 1.322% | 17.36%
J | J City, G South | grange | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 39.99 | 51.2387 | 43.0312 | 6.9626 | 0.94889 | 0.29595 | 8.2075 | 13.59% | 1.852% | 0.5776% | 16.02%
J | J City, G South | arodstown | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 155.1998 | 198.8555 | 167.0025 | 27.0218 | 3.6826 | 1.1486 | 31.853 | 13.59% | 1.852% | 0.5776% | 16.02%
J | J Country | kilteel | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 15 | 19.2193 | 12.382 | 3.7244 | 0.35566 | 2.7572 | 6.8373 | 19.38% | 1.851% | 14.35% | 35.58%
B | A, B North | glenree | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 48.1 | 146.2938 | 59.7126 | 42.5459 | 2.5465 | 41.4887 | 86.5812 | 29.08% | 1.741% | 28.36% | 59.18%
B | A, B North | glenree | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 34.15 | 103.8656 | 99.8665 | 0 | 3.9991 | 0 | 3.9991 | 0% | 3.85% | 0% | 3.85%
J | J Country | monread | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 8 | 10.2503 | 7.1104 | 1.3929 | 0.18983 | 1.5572 | 3.1399 | 13.59% | 1.852% | 15.19% | 30.63%
J | J Country | monread | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 8 | 10.2503 | 5.5069 | 2.3106 | 0.21466 | 2.2181 | 4.7434 | 22.54% | 2.094% | 21.64% | 46.28%
B | A, B North | glenree | 2035 | 66% ECP | Grandfathering | IE wind not priority | 46.45 | 141.2754 | 84.9398 | 24.6336 | 0.43533 | 31.2667 | 56.3356 | 17.44% | 0.3081% | 22.13% | 39.88%
B | A, B North | glenree | 2035 | 66% ECP | Grandfathering | IE wind priority | 34.15 | 103.8656 | 102.938 | 0 | 0.92759 | 0 | 0.92759 | 0% | 0.8931% | 0% | 0.8931%
J | J Country | monread | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 8 | 10.2503 | 6.6037 | 1.9864 | 0.18968 | 1.4705 | 3.6466 | 19.38% | 1.851% | 14.35% | 35.58%
B | A, B North | glenree | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 46.45 | 141.2754 | 88.3304 | 24.6336 | 0.43533 | 27.8762 | 52.9451 | 17.44% | 0.3081% | 19.73% | 37.48%
B | A, B North | glenree | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 34.15 | 103.8656 | 102.938 | 0 | 0.92759 | 0 | 0.92759 | 0% | 0.8931% | 0% | 0.8931%
J | J Country | monread | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 8 | 10.2503 | 6.7381 | 1.699 | 0.19125 | 1.6219 | 3.5122 | 16.57% | 1.866% | 15.82% | 34.26%
B | A, B North | glenree | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 46.45 | 141.2754 | 77.2939 | 43.3389 | 0.82023 | 19.8224 | 63.9816 | 30.68% | 0.5806% | 14.03% | 45.29%
J | J Country | monread | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 8 | 10.2503 | 4.3177 | 3.2347 | 0.22583 | 2.472 | 5.9326 | 31.56% | 2.203% | 24.12% | 57.88%
B | A, B North | glenree | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 34.15 | 103.8656 | 102.062 | 0 | 1.8035 | 0 | 1.8035 | 0% | 1.736% | 0% | 1.736%
B | A, B North | glenree | 2035 | 100% ECP | Grandfathering | IE wind not priority | 48.1 | 146.2938 | 79.7076 | 28.3079 | 0.49659 | 37.7817 | 66.5862 | 19.35% | 0.3394% | 25.83% | 45.52%
B | A, B North | glenree | 2035 | 100% ECP | Grandfathering | IE wind priority | 34.15 | 103.8656 | 102.7952 | 0 | 1.0704 | 0 | 1.0704 | 0% | 1.031% | 0% | 1.031%
J | J Country | monread | 2030 | Initial | Grandfathering | IE Solar not priority | 8 | 10.2503 | 8.1161 | 0.81045 | 0.13256 | 1.1912 | 2.1342 | 7.907% | 1.293% | 11.62% | 20.82%
B | A, B North | moy | 2030 | Initial | Grandfathering | IE wind priority | 6 | 18.2487 | 17.721 | 0 | 0.52773 | 0 | 0.52773 | 0% | 2.892% | 0% | 2.892%
B | A, B North | moy | 2030 | 33% ECP | Grandfathering | IE wind priority | 6 | 18.2487 | 17.6604 | 0 | 0.58828 | 0 | 0.58828 | 0% | 3.224% | 0% | 3.224%
J | J Country | maynooth | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 50 | 64.0644 | 23.4928 | 14.0864 | 0.58058 | 25.9046 | 40.5715 | 21.99% | 0.9062% | 40.44% | 63.33%
B | A, B North | moy | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 1.3333 | 1.4039 | 1.0609 | 0.18511 | 0.025898 | 0.13197 | 0.34298 | 13.19% | 1.845% | 9.401% | 24.43%
B | A, B North | moy | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 6 | 18.2487 | 17.5872 | 0 | 0.66156 | 0 | 0.66156 | 0% | 3.625% | 0% | 3.625%
J | J Country | maynooth | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 33.3333 | 42.7095 | 20.0076 | 9.3836 | 0.3649 | 12.9535 | 22.7019 | 21.97% | 0.8544% | 30.33% | 53.15%
B | A, B North | moy | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 1.3333 | 1.4039 | 1.0379 | 0.22497 | 0.026329 | 0.11467 | 0.36597 | 16.02% | 1.875% | 8.168% | 26.07%
J | J Country | monread | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 8 | 10.2503 | 6.7952 | 1.3929 | 0.18983 | 1.8724 | 3.4551 | 13.59% | 1.852% | 18.27% | 33.71%
B | A, B North | glenree | 2030 | 100% ECP | Grandfathering | IE wind priority | 34.15 | 103.8656 | 99.8665 | 0 | 3.9991 | 0 | 3.9991 | 0% | 3.85% | 0% | 3.85%
B | A, B North | glenree | 2030 | 100% ECP | Grandfathering | IE wind not priority | 48.1 | 146.2938 | 56.7173 | 42.5459 | 2.5465 | 44.484 | 89.5765 | 29.08% | 1.741% | 30.41% | 61.23%
J | J Country | monread | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 8 | 10.2503 | 4.523 | 3.2347 | 0.22583 | 2.2667 | 5.7273 | 31.56% | 2.203% | 22.11% | 55.87%
B | A, B North | firlough | 2030 | 100% ECP | Grandfathering | IE wind not priority | 75.6 | 229.9338 | 89.1441 | 66.8706 | 4.0024 | 69.9167 | 140.7897 | 29.08% | 1.741% | 30.41% | 61.23%
B | A, B North | firlough | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 75.6 | 229.9338 | 93.8519 | 66.8706 | 4.0024 | 65.2089 | 136.0819 | 29.08% | 1.741% | 28.36% | 59.18%
J | J Country | mount lucas | 2030 | 33% ECP | Grandfathering | IE wind not priority | 56.4 | 173.9366 | 118.3508 | 32.467 | 3.2698 | 19.8489 | 55.5857 | 18.67% | 1.88% | 11.41% | 31.96%
B | A, B North | firlough | 2035 | 66% ECP | Grandfathering | IE wind not priority | 59.5 | 180.9663 | 108.8034 | 31.5543 | 0.55764 | 40.051 | 72.1629 | 17.44% | 0.3081% | 22.13% | 39.88%
J | J Country | mount lucas | 2030 | Initial | Grandfathering | IE wind priority | 79.2 | 244.2514 | 236.7168 | 0 | 7.5346 | 0 | 7.5346 | 0% | 3.085% | 0% | 3.085%
B | A, B North | firlough | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 59.5 | 180.9663 | 113.1465 | 31.5543 | 0.55764 | 35.7079 | 67.8198 | 17.44% | 0.3081% | 19.73% | 37.48%
B | A, B North | firlough | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 59.5 | 180.9663 | 99.0093 | 55.5148 | 1.0507 | 25.3915 | 81.957 | 30.68% | 0.5806% | 14.03% | 45.29%
J | J Country | mount lucas | 2030 | Initial | Grandfathering | IE wind not priority | 56.4 | 173.9366 | 122.1868 | 23.9487 | 3.3821 | 24.4189 | 51.7498 | 13.77% | 1.944% | 14.04% | 29.75%
B | A, B North | firlough | 2035 | 100% ECP | Grandfathering | IE wind not priority | 75.6 | 229.9338 | 125.2785 | 44.4923 | 0.7805 | 59.3825 | 104.6553 | 19.35% | 0.3394% | 25.83% | 45.52%
B | A, B North | glenree | 2030 | Initial | Grandfathering | IE wind not priority | 43.15 | 131.2386 | 62.0508 | 17.221 | 2.3475 | 49.6192 | 69.1878 | 13.12% | 1.789% | 37.81% | 52.72%
B | A, B North | glenree | 2030 | Initial | Grandfathering | IE wind priority | 34.15 | 103.8656 | 100.8619 | 0 | 3.0037 | 0 | 3.0037 | 0% | 2.892% | 0% | 2.892%
J | J Country | monread | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 8 | 10.2503 | 3.7589 | 2.2538 | 0.092893 | 4.1447 | 6.4914 | 21.99% | 0.9062% | 40.44% | 63.33%
B | A, B North | glenree | 2030 | 33% ECP | Grandfathering | IE wind not priority | 44.8 | 136.257 | 65.1462 | 24.4098 | 2.3607 | 44.3403 | 71.1108 | 17.91% | 1.733% | 32.54% | 52.19%
B | A, B North | glenree | 2030 | 33% ECP | Grandfathering | IE wind priority | 34.15 | 103.8656 | 100.5173 | 0 | 3.3483 | 0 | 3.3483 | 0% | 3.224% | 0% | 3.224%
J | J Country | monread | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 8 | 10.2503 | 4.8018 | 2.2521 | 0.087576 | 3.1088 | 5.4485 | 21.97% | 0.8544% | 30.33% | 53.15%
B | A, B North | glenree | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 44.8 | 136.257 | 62.2351 | 33.0824 | 2.3995 | 38.5401 | 74.022 | 24.28% | 1.761% | 28.28% | 54.33%
B | A, B North | glenree | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 34.15 | 103.8656 | 100.1002 | 0 | 3.7654 | 0 | 3.7654 | 0% | 3.625% | 0% | 3.625%
J | J Country | monread | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 8 | 10.2503 | 5.0494 | 1.5701 | 0.073903 | 3.5569 | 5.2009 | 15.32% | 0.721% | 34.7% | 50.74%
B | A, B North | glenree | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 44.8 | 136.257 | 58.3262 | 41.9608 | 2.3579 | 33.6121 | 77.9308 | 30.8% | 1.731% | 24.67% | 57.19%
B | A, B North | glenree | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 34.15 | 103.8656 | 99.765 | 0 | 4.1005 | 0 | 4.1005 | 0% | 3.948% | 0% | 3.948%
J | J Country | monread | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 8 | 10.2503 | 4.7495 | 1.5701 | 0.073903 | 3.8568 | 5.5008 | 15.32% | 0.721% | 37.63% | 53.67%
B | A, B North | glenree | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 44.8 | 136.257 | 54.0169 | 44.6129 | 2.343 | 35.2843 | 82.2401 | 32.74% | 1.72% | 25.9% | 60.36%
B | A, B North | glenree | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 34.15 | 103.8656 | 99.7119 | 0 | 4.1537 | 0 | 4.1537 | 0% | 3.999% | 0% | 3.999%
B | A, B North | glenree | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 44.8 | 136.257 | 70.2443 | 24.4098 | 2.3607 | 39.2422 | 66.0127 | 17.91% | 1.733% | 28.8% | 48.45%
B | A, B North | glenree | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 34.15 | 103.8656 | 100.5173 | 0 | 3.3483 | 0 | 3.3483 | 0% | 3.224% | 0% | 3.224%
B | A, B North | moy | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 6 | 18.2487 | 17.5283 | 0 | 0.72044 | 0 | 0.72044 | 0% | 3.948% | 0% | 3.948%
J | J Country | mount lucas | 2030 | 33% ECP | Grandfathering | IE wind priority | 79.2 | 244.2514 | 235.8509 | 0 | 8.4005 | 0 | 8.4005 | 0% | 3.439% | 0% | 3.439%
J | J Country | maynooth | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 33.3333 | 42.7095 | 21.039 | 6.5423 | 0.30793 | 14.8203 | 21.6705 | 15.32% | 0.721% | 34.7% | 50.74%
B | A, B North | moy | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 6 | 18.2487 | 17.5189 | 0 | 0.72978 | 0 | 0.72978 | 0% | 3.999% | 0% | 3.999%
J | J Country | kinnegad | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 49.9999 | 64.0643 | 30.0114 | 14.0753 | 0.54735 | 19.4302 | 34.0529 | 21.97% | 0.8544% | 30.33% | 53.15%
B | A, B North | sligo | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 1.36 | 4.1364 | 1.8893 | 1.0043 | 0.072842 | 1.17 | 2.2471 | 24.28% | 1.761% | 28.28% | 54.33%
B | A, B North | sligo | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 13.65 | 41.5158 | 40.0108 | 0 | 1.505 | 0 | 1.505 | 0% | 3.625% | 0% | 3.625%
J | J Country | kinnegad | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 49.9999 | 64.0643 | 31.5586 | 9.8134 | 0.46189 | 22.2304 | 32.5057 | 15.32% | 0.721% | 34.7% | 50.74%
B | A, B North | sligo | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 1.36 | 4.1364 | 1.7706 | 1.2738 | 0.07158 | 1.0204 | 2.3658 | 30.8% | 1.731% | 24.67% | 57.19%
B | A, B North | sligo | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 13.65 | 41.5158 | 39.8768 | 0 | 1.639 | 0 | 1.639 | 0% | 3.948% | 0% | 3.948%
J | J Country | kinnegad | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 49.9999 | 64.0643 | 29.6842 | 9.8134 | 0.46189 | 24.1048 | 34.3801 | 15.32% | 0.721% | 37.63% | 53.67%
B | A, B North | sligo | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 1.36 | 4.1364 | 1.6398 | 1.3543 | 0.071125 | 1.0711 | 2.4966 | 32.74% | 1.72% | 25.9% | 60.36%
B | A, B North | sligo | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 13.65 | 41.5158 | 39.8556 | 0 | 1.6603 | 0 | 1.6603 | 0% | 3.999% | 0% | 3.999%
B | A, B North | sligo | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 1.36 | 4.1364 | 2.1324 | 0.74101 | 0.071664 | 1.1913 | 2.004 | 17.91% | 1.733% | 28.8% | 48.45%
B | A, B North | sligo | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 13.65 | 41.5158 | 40.1775 | 0 | 1.3383 | 0 | 1.3383 | 0% | 3.224% | 0% | 3.224%
J | J Country | kinnegad | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 75 | 96.0965 | 42.4031 | 30.3256 | 2.1172 | 21.2507 | 53.6934 | 31.56% | 2.203% | 22.11% | 55.87%
B | A, B North | sligo | 2030 | 33% ECP | Grandfathering | IE wind priority | 13.65 | 41.5158 | 40.1775 | 0 | 1.3383 | 0 | 1.3383 | 0% | 3.224% | 0% | 3.224%
B | A, B North | sligo | 2030 | 100% ECP | Grandfathering | IE wind not priority | 4.08 | 12.4091 | 4.811 | 3.6089 | 0.216 | 3.7733 | 7.5982 | 29.08% | 1.741% | 30.41% | 61.23%
J | J Country | kinnegad | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 75 | 96.0965 | 40.4784 | 30.3256 | 2.1172 | 23.1753 | 55.6181 | 31.56% | 2.203% | 24.12% | 57.88%
B | A, B North | sligo | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 4.08 | 12.4091 | 5.065 | 3.6089 | 0.216 | 3.5192 | 7.3441 | 29.08% | 1.741% | 28.36% | 59.18%
B | A, B North | sligo | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 13.65 | 41.5158 | 39.9174 | 0 | 1.5985 | 0 | 1.5985 | 0% | 3.85% | 0% | 3.85%
J | J Country | kinnegad | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 25 | 32.0321 | 22.22 | 4.3527 | 0.5932 | 4.8662 | 9.8121 | 13.59% | 1.852% | 15.19% | 30.63%
J | J Country | kinnegad | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 25 | 32.0321 | 17.2089 | 7.2207 | 0.67082 | 6.9317 | 14.8232 | 22.54% | 2.094% | 21.64% | 46.28%
B | A, B North | sligo | 2035 | 66% ECP | Grandfathering | IE wind not priority | 2.72 | 8.2727 | 4.9739 | 1.4425 | 0.025492 | 1.8309 | 3.2989 | 17.44% | 0.3081% | 22.13% | 39.88%
B | A, B North | sligo | 2035 | 66% ECP | Grandfathering | IE wind priority | 13.65 | 41.5158 | 41.1451 | 0 | 0.37076 | 0 | 0.37076 | 0% | 0.8931% | 0% | 0.8931%
J | J Country | kinnegad | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 25 | 32.0321 | 20.6367 | 6.2074 | 0.59276 | 4.5953 | 11.3955 | 19.38% | 1.851% | 14.35% | 35.58%
B | A, B North | sligo | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 2.72 | 8.2727 | 5.1724 | 1.4425 | 0.025492 | 1.6324 | 3.1003 | 17.44% | 0.3081% | 19.73% | 37.48%
B | A, B North | sligo | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 13.65 | 41.5158 | 41.1451 | 0 | 0.37076 | 0 | 0.37076 | 0% | 0.8931% | 0% | 0.8931%
J | J Country | kinnegad | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 25 | 32.0321 | 21.0567 | 5.3093 | 0.59767 | 5.0685 | 10.9755 | 16.57% | 1.866% | 15.82% | 34.26%
B | A, B North | sligo | 2030 | 100% ECP | Grandfathering | IE wind priority | 13.65 | 41.5158 | 39.9174 | 0 | 1.5985 | 0 | 1.5985 | 0% | 3.85% | 0% | 3.85%
B | A, B North | sligo | 2030 | 33% ECP | Grandfathering | IE wind not priority | 1.36 | 4.1364 | 1.9777 | 0.74101 | 0.071664 | 1.346 | 2.1587 | 17.91% | 1.733% | 32.54% | 52.19%
J | J Country | kinnegad | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 75 | 96.0965 | 35.2392 | 21.1296 | 0.87087 | 38.8568 | 60.8573 | 21.99% | 0.9062% | 40.44% | 63.33%
B | A, B North | sligo | 2030 | Initial | Grandfathering | IE wind priority | 13.65 | 41.5158 | 40.3152 | 0 | 1.2006 | 0 | 1.2006 | 0% | 2.892% | 0% | 2.892%
J | J Country | maynooth | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 33.3333 | 42.7095 | 19.7895 | 6.5423 | 0.30793 | 16.0699 | 22.9201 | 15.32% | 0.721% | 37.63% | 53.67%
B | A, B North | moy | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 1.3333 | 1.4039 | 0.96146 | 0.30897 | 0.029341 | 0.10413 | 0.44244 | 22.01% | 2.09% | 7.417% | 31.52%
B | A, B North | moy | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 6 | 18.2487 | 17.6604 | 0 | 0.58828 | 0 | 0.58828 | 0% | 3.224% | 0% | 3.224%
B | A, B North | moy | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 1.3333 | 1.4039 | 1.0702 | 0.18511 | 0.025898 | 0.12267 | 0.33368 | 13.19% | 1.845% | 8.738% | 23.77%
B | A, B North | moy | 2030 | 100% ECP | Grandfathering | IE wind priority | 6 | 18.2487 | 17.5461 | 0 | 0.70262 | 0 | 0.70262 | 0% | 3.85% | 0% | 3.85%
J | J Country | maynooth | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 50 | 64.0644 | 28.2687 | 20.217 | 1.4115 | 14.1671 | 35.7956 | 31.56% | 2.203% | 22.11% | 55.87%
B | A, B North | moy | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 4 | 4.2117 | 2.6187 | 1.3161 | 0.092465 | 0.18444 | 1.593 | 31.25% | 2.195% | 4.379% | 37.82%
B | A, B North | moy | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 6 | 18.2487 | 17.5461 | 0 | 0.70262 | 0 | 0.70262 | 0% | 3.85% | 0% | 3.85%
J | J Country | maynooth | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 50 | 64.0644 | 26.9856 | 20.217 | 1.4115 | 15.4502 | 37.0787 | 31.56% | 2.203% | 24.12% | 57.88%
B | A, B North | moy | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4 | 4.2117 | 2.6293 | 1.3161 | 0.092465 | 0.17386 | 1.5824 | 31.25% | 2.195% | 4.128% | 37.57%
J | J Country | maynooth | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 14.8133 | 2.9018 | 0.39547 | 3.2441 | 6.5414 | 13.59% | 1.852% | 15.19% | 30.63%
B | A, B North | moy | 2035 | 66% ECP | Grandfathering | IE wind priority | 6 | 18.2487 | 18.0857 | 0 | 0.16297 | 0 | 0.16297 | 0% | 0.8931% | 0% | 0.8931%
J | J Country | maynooth | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 11.4726 | 4.8138 | 0.44721 | 4.6211 | 9.8821 | 22.54% | 2.094% | 21.64% | 46.28%
B | A, B North | moy | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 2.6667 | 2.8078 | 2.2037 | 0.42591 | 0.020532 | 0.1577 | 0.60414 | 15.17% | 0.7313% | 5.617% | 21.52%
B | A, B North | moy | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 6 | 18.2487 | 18.0857 | 0 | 0.16297 | 0 | 0.16297 | 0% | 0.8931% | 0% | 0.8931%
J | J Country | maynooth | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 13.7578 | 4.1383 | 0.39517 | 3.0635 | 7.597 | 19.38% | 1.851% | 14.35% | 35.58%
B | A, B North | moy | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 2.6667 | 2.8078 | 2.2615 | 0.42591 | 0.020532 | 0.09985 | 0.54629 | 15.17% | 0.7313% | 3.556% | 19.46%
B | A, B North | moy | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 6 | 18.2487 | 17.9318 | 0 | 0.31688 | 0 | 0.31688 | 0% | 1.736% | 0% | 1.736%
J | J Country | maynooth | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 14.0378 | 3.5395 | 0.39845 | 3.379 | 7.317 | 16.57% | 1.866% | 15.82% | 34.26%
B | A, B North | moy | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 2.6667 | 2.8078 | 2.0853 | 0.60566 | 0.024124 | 0.092716 | 0.7225 | 21.57% | 0.8592% | 3.302% | 25.73%
B | A, B North | moy | 2035 | 100% ECP | Grandfathering | IE wind priority | 6 | 18.2487 | 18.0606 | 0 | 0.18807 | 0 | 0.18807 | 0% | 1.031% | 0% | 1.031%
J | J Country | maynooth | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 14.1566 | 2.9018 | 0.39547 | 3.9009 | 7.1982 | 13.59% | 1.852% | 18.27% | 33.71%
B | A, B North | moy | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 4 | 4.2117 | 3.062 | 0.92339 | 0.038692 | 0.18766 | 1.1497 | 21.92% | 0.9187% | 4.456% | 27.3%
B | A, B North | moy | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 1.3333 | 1.4039 | 1.0108 | 0.26321 | 0.026135 | 0.10373 | 0.39307 | 18.75% | 1.862% | 7.389% | 28%
B | A, B North | sligo | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 2.72 | 8.2727 | 4.5261 | 2.5378 | 0.04803 | 1.1608 | 3.7466 | 30.68% | 0.5806% | 14.03% | 45.29%
B | A, B North | firlough | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 43.4 | 131.999 | 68.0492 | 23.647 | 2.2869 | 38.0159 | 63.9498 | 17.91% | 1.733% | 28.8% | 48.45%
J | J Country | mount lucas | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 56.4 | 173.9366 | 115.2278 | 44.3856 | 3.3025 | 11.0207 | 58.7087 | 25.52% | 1.899% | 6.336% | 33.75%
J | J Country | mulgeeth | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 60 | 185.0389 | 103.3362 | 55.4554 | 3.4025 | 22.8449 | 81.7027 | 29.97% | 1.839% | 12.35% | 44.15%
B | A, B North | castlebar | 2035 | 66% ECP | Grandfathering | IE wind not priority | 6.8 | 20.6819 | 12.4347 | 3.6062 | 0.06373 | 4.5773 | 8.2472 | 17.44% | 0.3081% | 22.13% | 39.88%
J | J Country | mulgeeth | 2030 | 100% ECP | Grandfathering | IE wind not priority | 60 | 185.0389 | 98.0024 | 55.4554 | 3.4025 | 28.1787 | 87.0365 | 29.97% | 1.839% | 15.23% | 47.04%
B | A, B North | castlebar | 2035 | 66% ECP | Grandfathering | IE wind priority | 8.5 | 25.8523 | 25.6215 | 0 | 0.23088 | 0 | 0.23088 | 0% | 0.8931% | 0% | 0.8931%
B | A, B North | castlebar | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 3.3267 | 4.2624 | 3.3394 | 0.65292 | 0.030731 | 0.2394 | 0.92305 | 15.32% | 0.721% | 5.617% | 21.66%
J | J Country | mulgeeth | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 60 | 185.0389 | 131.7013 | 34.5394 | 3.4785 | 15.3196 | 53.3376 | 18.67% | 1.88% | 8.279% | 28.83%
B | A, B North | castlebar | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 6.8 | 20.6819 | 12.931 | 3.6062 | 0.06373 | 4.0809 | 7.7508 | 17.44% | 0.3081% | 19.73% | 37.48%
B | A, B North | castlebar | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 8.5 | 25.8523 | 25.6215 | 0 | 0.23088 | 0 | 0.23088 | 0% | 0.8931% | 0% | 0.8931%
J | J Country | mulgeeth | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 60 | 185.0389 | 107.8613 | 64.2196 | 3.4259 | 9.5321 | 77.1776 | 34.71% | 1.851% | 5.151% | 41.71%
B | A, B North | castlebar | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 3.3267 | 4.2624 | 3.4272 | 0.65292 | 0.030731 | 0.15158 | 0.83523 | 15.32% | 0.721% | 3.556% | 19.6%
B | A, B North | castlebar | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 6.8 | 20.6819 | 11.3154 | 6.3446 | 0.12008 | 2.9019 | 9.3665 | 30.68% | 0.5806% | 14.03% | 45.29%
J | J Country | mulgeeth | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 60 | 185.0389 | 114.3786 | 60.1544 | 3.4718 | 7.0342 | 70.6603 | 32.51% | 1.876% | 3.801% | 38.19%
B | A, B North | castlebar | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 8.5 | 25.8523 | 25.4034 | 0 | 0.44891 | 0 | 0.44891 | 0% | 1.736% | 0% | 1.736%
J | J Country | mulgeeth | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 60 | 185.0389 | 122.5828 | 47.2187 | 3.5133 | 11.7241 | 62.4561 | 25.52% | 1.899% | 6.336% | 33.75%
B | A, B North | castlebar | 2035 | 100% ECP | Grandfathering | IE wind not priority | 6.8 | 20.6819 | 11.2684 | 4.002 | 0.070204 | 5.3413 | 9.4134 | 19.35% | 0.3394% | 25.83% | 45.52%
B | A, B North | castlebar | 2035 | 100% ECP | Grandfathering | IE wind priority | 8.5 | 25.8523 | 25.5859 | 0 | 0.26643 | 0 | 0.26643 | 0% | 1.031% | 0% | 1.031%
J | J Country | mulgeeth | 2030 | 33% ECP | Grandfathering | IE wind not priority | 60 | 185.0389 | 125.9052 | 34.5394 | 3.4785 | 21.1158 | 59.1338 | 18.67% | 1.88% | 11.41% | 31.96%
B | A, B North | castlebar | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 4.645 | 1.4058 | 0.057942 | 0.28488 | 1.7486 | 21.99% | 0.9062% | 4.456% | 27.35%
J | J Country | mulgeeth | 2030 | Initial | Grandfathering | IE wind not priority | 60 | 185.0389 | 129.9859 | 25.4774 | 3.598 | 25.9776 | 55.053 | 13.77% | 1.944% | 14.04% | 29.75%
B | A, B North | cunghill | 2030 | Initial | Grandfathering | IE wind priority | 34.8 | 105.8425 | 102.7817 | 0 | 3.0608 | 0 | 3.0608 | 0% | 2.892% | 0% | 2.892%
B | A, B North | cunghill | 2030 | 33% ECP | Grandfathering | IE wind priority | 34.8 | 105.8425 | 102.4305 | 0 | 3.412 | 0 | 3.412 | 0% | 3.224% | 0% | 3.224%
B | A, B North | castlebar | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 3.3267 | 4.2624 | 3.1488 | 0.93648 | 0.036417 | 0.14075 | 1.1136 | 21.97% | 0.8544% | 3.302% | 26.13%
B | A, B North | castlebar | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 3.9712 | 2.0177 | 0.14086 | 0.26393 | 2.4224 | 31.56% | 2.203% | 4.128% | 37.89%
J | J Country | newbridge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 12 | 15.3754 | 8.2603 | 3.4659 | 0.32199 | 3.3272 | 7.1151 | 22.54% | 2.094% | 21.64% | 46.28%
B | A, B North | castlebar | 2030 | 33% ECP | Grandfathering | IE wind priority | 8.5 | 25.8523 | 25.0189 | 0 | 0.8334 | 0 | 0.8334 | 0% | 3.224% | 0% | 3.224%
B | A, B North | castlebar | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 1.6633 | 2.1312 | 1.6018 | 0.2896 | 0.039468 | 0.20035 | 0.52942 | 13.59% | 1.852% | 9.401% | 24.84%
J | J Country | newbridge | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 12 | 15.3754 | 9.9056 | 2.9796 | 0.28453 | 2.2058 | 5.4698 | 19.38% | 1.851% | 14.35% | 35.58%
B | A, B North | castlebar | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 6.8 | 20.6819 | 9.4464 | 5.0214 | 0.36421 | 5.8498 | 11.2355 | 24.28% | 1.761% | 28.28% | 54.33%
B | A, B North | castlebar | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 8.5 | 25.8523 | 24.9151 | 0 | 0.93721 | 0 | 0.93721 | 0% | 3.625% | 0% | 3.625%
J | J Country | newbridge | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 12 | 15.3754 | 10.1072 | 2.5485 | 0.28688 | 2.4329 | 5.2682 | 16.57% | 1.866% | 15.82% | 34.26%
B | A, B North | castlebar | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 1.6633 | 2.1312 | 1.5641 | 0.35325 | 0.039765 | 0.17407 | 0.56708 | 16.57% | 1.866% | 8.168% | 26.61%
B | A, B North | castlebar | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 6.8 | 20.6819 | 8.8531 | 6.3691 | 0.3579 | 5.1018 | 11.8288 | 30.8% | 1.731% | 24.67% | 57.19%
J | J Country | newbridge | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 12 | 15.3754 | 10.1927 | 2.0893 | 0.28474 | 2.8086 | 5.1827 | 13.59% | 1.852% | 18.27% | 33.71%
B | A, B North | castlebar | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 8.5 | 25.8523 | 24.8317 | 0 | 1.0206 | 0 | 1.0206 | 0% | 3.948% | 0% | 3.948%
B | A, B North | castlebar | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 1.6633 | 2.1312 | 1.5213 | 0.413 | 0.039438 | 0.15748 | 0.60991 | 19.38% | 1.851% | 7.389% | 28.62%
J | J Country | newbridge | 2030 | Initial | Grandfathering | IE Solar not priority | 12 | 15.3754 | 12.1742 | 1.2157 | 0.19884 | 1.7867 | 3.2013 | 7.907% | 1.293% | 11.62% | 20.82%
B | A, B North | castlebar | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 6.8 | 20.6819 | 8.199 | 6.7716 | 0.35563 | 5.3557 | 12.4829 | 32.74% | 1.72% | 25.9% | 60.36%
B | A, B North | castlebar | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 8.5 | 25.8523 | 24.8185 | 0 | 1.0339 | 0 | 1.0339 | 0% | 3.999% | 0% | 3.999%
B | A, B North | castlebar | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 1.6633 | 2.1312 | 1.4481 | 0.48042 | 0.044632 | 0.15807 | 0.68312 | 22.54% | 2.094% | 7.417% | 32.05%
B | A, B North | castlebar | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 6.8 | 20.6819 | 10.6621 | 3.7051 | 0.35832 | 5.9564 | 10.0198 | 17.91% | 1.733% | 28.8% | 48.45%
J | J Country | mulgeeth | 2035 | 100% ECP | Grandfathering | IE wind not priority | 60 | 185.0389 | 97.7927 | 37.53 | 0.69714 | 49.019 | 87.2462 | 20.28% | 0.3768% | 26.49% | 47.15%
B | A, B North | castlebar | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 8.5 | 25.8523 | 25.0189 | 0 | 0.8334 | 0 | 0.8334 | 0% | 3.224% | 0% | 3.224%
B | A, B North | castlebar | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 1.6633 | 2.1312 | 1.6159 | 0.2896 | 0.039468 | 0.18623 | 0.5153 | 13.59% | 1.852% | 8.738% | 24.18%
J | J Country | mulgeeth | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 60 | 185.0389 | 106.7175 | 60.9947 | 1.1945 | 16.1323 | 78.3214 | 32.96% | 0.6455% | 8.718% | 42.33%
B | A, B North | castlebar | 2030 | 100% ECP | Grandfathering | IE wind not priority | 6.8 | 20.6819 | 8.0183 | 6.0148 | 0.36001 | 6.2888 | 12.6636 | 29.08% | 1.741% | 30.41% | 61.23%
B | A, B North | castlebar | 2030 | 100% ECP | Grandfathering | IE wind priority | 8.5 | 25.8523 | 24.857 | 0 | 0.99538 | 0 | 0.99538 | 0% | 3.85% | 0% | 3.85%
J | J Country | mulgeeth | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 60 | 185.0389 | 112.9711 | 34.2341 | 0.6491 | 37.1846 | 72.0678 | 18.5% | 0.3508% | 20.1% | 38.95%
B | A, B North | castlebar | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 3.9551 | 2.0177 | 0.14086 | 0.27999 | 2.4385 | 31.56% | 2.203% | 4.379% | 38.14%
B | A, B North | castlebar | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 6.8 | 20.6819 | 8.4417 | 6.0148 | 0.36001 | 5.8654 | 12.2402 | 29.08% | 1.741% | 28.36% | 59.18%
J | J Country | mulgeeth | 2035 | 66% ECP | Grandfathering | IE wind not priority | 60 | 185.0389 | 110.6285 | 34.2341 | 0.6491 | 39.5272 | 74.4104 | 18.5% | 0.3508% | 21.36% | 40.21%
B | A, B North | castlebar | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 8.5 | 25.8523 | 24.857 | 0 | 0.99538 | 0 | 0.99538 | 0% | 3.85% | 0% | 3.85%
B | A, B North | cunghill | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 34.8 | 105.8425 | 102.0055 | 0 | 3.837 | 0 | 3.837 | 0% | 3.625% | 0% | 3.625%
B | A, B North | firlough | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 43.4 | 131.999 | 52.3289 | 43.2187 | 2.2697 | 34.1816 | 79.6701 | 32.74% | 1.72% | 25.9% | 60.36%
B | A, B North | cunghill | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 34.8 | 105.8425 | 101.6639 | 0 | 4.1786 | 0 | 4.1786 | 0% | 3.948% | 0% | 3.948%
B | A, B North | cunghill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 34.8 | 105.8425 | 101.6098 | 0 | 4.2327 | 0 | 4.2327 | 0% | 3.999% | 0% | 3.999%
B | A, B North | dalton | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 24 | 30.7509 | 19.0226 | 9.7042 | 0.6775 | 1.3466 | 11.7283 | 31.56% | 2.203% | 4.379% | 38.14%
J | J Country | mount lucas | 2030 | 100% ECP | Grandfathering | IE wind priority | 79.2 | 244.2514 | 234.3578 | 0 | 9.8935 | 0 | 9.8935 | 0% | 4.051% | 0% | 4.051%
B | A, B North | dalton | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 40.8 | 124.0912 | 119.3134 | 0 | 4.7778 | 0 | 4.7778 | 0% | 3.85% | 0% | 3.85%
B | A, B North | dalton | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 24 | 30.7509 | 19.0998 | 9.7042 | 0.6775 | 1.2694 | 11.6511 | 31.56% | 2.203% | 4.128% | 37.89%
J | J Country | mount lucas | 2030 | 100% ECP | Grandfathering | IE wind not priority | 56.4 | 173.9366 | 92.1222 | 52.1281 | 3.1983 | 26.488 | 81.8143 | 29.97% | 1.839% | 15.23% | 47.04%
J | J Country | mount lucas | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 79.2 | 244.2514 | 235.8509 | 0 | 8.4005 | 0 | 8.4005 | 0% | 3.439% | 0% | 3.439%
B | A, B North | dalton | 2035 | 66% ECP | Grandfathering | IE wind priority | 40.8 | 124.0912 | 122.983 | 0 | 1.1082 | 0 | 1.1082 | 0% | 0.8931% | 0% | 0.8931%
B | A, B North | dalton | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 17.3333 | 22.209 | 17.3995 | 3.402 | 0.16012 | 1.2474 | 4.8095 | 15.32% | 0.721% | 5.617% | 21.66%
J | J Country | mount lucas | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 56.4 | 173.9366 | 123.7993 | 32.467 | 3.2698 | 14.4005 | 50.1373 | 18.67% | 1.88% | 8.279% | 28.83%
B | A, B North | dalton | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 40.8 | 124.0912 | 122.983 | 0 | 1.1082 | 0 | 1.1082 | 0% | 0.8931% | 0% | 0.8931%
B | A, B North | dalton | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 17.3333 | 22.209 | 17.8571 | 3.402 | 0.16012 | 0.78979 | 4.3519 | 15.32% | 0.721% | 3.556% | 19.6%
B | A, B North | dalton | 2030 | 100% ECP | Grandfathering | IE wind priority | 40.8 | 124.0912 | 119.3134 | 0 | 4.7778 | 0 | 4.7778 | 0% | 3.85% | 0% | 3.85%
J | J Country | mount lucas | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 79.2 | 244.2514 | 233.8294 | 0 | 10.422 | 0 | 10.422 | 0% | 4.267% | 0% | 4.267%
B | A, B North | dalton | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 17.3333 | 22.209 | 16.4064 | 4.8795 | 0.18975 | 0.73336 | 5.8026 | 21.97% | 0.8544% | 3.302% | 26.13%
J | J Country | mount lucas | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 56.4 | 173.9366 | 101.3896 | 60.3664 | 3.2203 | 8.9602 | 72.5469 | 34.71% | 1.851% | 5.151% | 41.71%
B | A, B North | dalton | 2035 | 100% ECP | Grandfathering | IE wind priority | 40.8 | 124.0912 | 122.8124 | 0 | 1.2789 | 0 | 1.2789 | 0% | 1.031% | 0% | 1.031%
B | A, B North | dalton | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 24 | 30.7509 | 22.3406 | 6.7615 | 0.27868 | 1.3702 | 8.4103 | 21.99% | 0.9062% | 4.456% | 27.35%
J | J Country | mount lucas | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 79.2 | 244.2514 | 233.8657 | 0 | 10.3857 | 0 | 10.3857 | 0% | 4.252% | 0% | 4.252%
J | J Country | mount lucas | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 56.4 | 173.9366 | 107.5158 | 56.5451 | 3.2635 | 6.6121 | 66.4207 | 32.51% | 1.876% | 3.801% | 38.19%
B | A, B North | firlough | 2030 | Initial | Grandfathering | IE wind not priority | 27.3 | 83.0316 | 39.2581 | 10.8954 | 1.4852 | 31.3929 | 43.7735 | 13.12% | 1.789% | 37.81% | 52.72%
B | A, B North | firlough | 2030 | 33% ECP | Grandfathering | IE wind not priority | 43.4 | 131.999 | 63.1104 | 23.647 | 2.2869 | 42.9547 | 68.8886 | 17.91% | 1.733% | 32.54% | 52.19%
J | J Country | mount lucas | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 79.2 | 244.2514 | 234.7994 | 0 | 9.452 | 0 | 9.452 | 0% | 3.87% | 0% | 3.87%
B | A, B North | firlough | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 43.4 | 131.999 | 60.2902 | 32.0485 | 2.3245 | 37.3357 | 71.7088 | 24.28% | 1.761% | 28.28% | 54.33%
B | A, B North | firlough | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 43.4 | 131.999 | 56.5035 | 40.6495 | 2.2843 | 32.5617 | 75.4955 | 30.8% | 1.731% | 24.67% | 57.19%
B | A, B North | dalton | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 40.8 | 124.0912 | 121.9365 | 0 | 2.1548 | 0 | 2.1548 | 0% | 1.736% | 0% | 1.736%
J | J Country | mount lucas | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 56.4 | 173.9366 | 97.136 | 52.1281 | 3.1983 | 21.4742 | 76.8006 | 29.97% | 1.839% | 12.35% | 44.15%
B | A, B North | dalton | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 10.6667 | 13.6671 | 10.3626 | 1.8572 | 0.2531 | 1.1942 | 3.3045 | 13.59% | 1.852% | 8.738% | 24.18%
B | A, B North | dalton | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 40.8 | 124.0912 | 120.0909 | 0 | 4.0003 | 0 | 4.0003 | 0% | 3.224% | 0% | 3.224%
B | A, B North | cunghill | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 34.8 | 105.8425 | 102.4305 | 0 | 3.412 | 0 | 3.412 | 0% | 3.224% | 0% | 3.224%
J | J Country | mount lucas | 2035 | 100% ECP | Grandfathering | IE wind not priority | 56.4 | 173.9366 | 91.9251 | 35.2782 | 0.65531 | 46.0779 | 82.0114 | 20.28% | 0.3768% | 26.49% | 47.15%
B | A, B North | cunghill | 2030 | 100% ECP | Grandfathering | IE wind priority | 34.8 | 105.8425 | 101.7673 | 0 | 4.0752 | 0 | 4.0752 | 0% | 3.85% | 0% | 3.85%
B | A, B North | cunghill | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 34.8 | 105.8425 | 101.7673 | 0 | 4.0752 | 0 | 4.0752 | 0% | 3.85% | 0% | 3.85%
J | J Country | mount lucas | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 79.2 | 244.2514 | 239.5748 | 0 | 4.6765 | 0 | 4.6765 | 0% | 1.915% | 0% | 1.915%
B | A, B North | cunghill | 2035 | 66% ECP | Grandfathering | IE wind priority | 34.8 | 105.8425 | 104.8973 | 0 | 0.94524 | 0 | 0.94524 | 0% | 0.8931% | 0% | 0.8931%
J | J Country | mount lucas | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 56.4 | 173.9366 | 100.3144 | 57.335 | 1.1228 | 15.1643 | 73.6221 | 32.96% | 0.6455% | 8.718% | 42.33%
B | A, B North | cunghill | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 34.8 | 105.8425 | 104.8973 | 0 | 0.94524 | 0 | 0.94524 | 0% | 0.8931% | 0% | 0.8931%
B | A, B North | cunghill | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 34.8 | 105.8425 | 104.0046 | 0 | 1.8379 | 0 | 1.8379 | 0% | 1.736% | 0% | 1.736%
J | J Country | mount lucas | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 79.2 | 244.2514 | 241.8676 | 0 | 2.3837 | 0 | 2.3837 | 0% | 0.9759% | 0% | 0.9759%
B | A, B North | cunghill | 2035 | 100% ECP | Grandfathering | IE wind priority | 34.8 | 105.8425 | 104.7517 | 0 | 1.0908 | 0 | 1.0908 | 0% | 1.031% | 0% | 1.031%
J | J Country | mount lucas | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 56.4 | 173.9366 | 106.1929 | 32.18 | 0.61016 | 34.9535 | 67.7437 | 18.5% | 0.3508% | 20.1% | 38.95%
B | A, B North | dalton | 2030 | Initial | Grandfathering | IE wind priority | 40.8 | 124.0912 | 120.5027 | 0 | 3.5886 | 0 | 3.5886 | 0% | 2.892% | 0% | 2.892%
B | A, B North | dalton | 2030 | Initial | Grandfathering | IE Solar not priority | 4 | 5.1251 | 3.8942 | 0.40522 | 0.06628 | 0.75943 | 1.2309 | 7.907% | 1.293% | 14.82% | 24.02%
J | J Country | mount lucas | 2035 | 66% ECP | Grandfathering | IE wind priority | 79.2 | 244.2514 | 241.8676 | 0 | 2.3837 | 0 | 2.3837 | 0% | 0.9759% | 0% | 0.9759%
B | A, B North | dalton | 2030 | 33% ECP | Grandfathering | IE wind priority | 40.8 | 124.0912 | 120.0909 | 0 | 4.0003 | 0 | 4.0003 | 0% | 3.224% | 0% | 3.224%
B | A, B North | dalton | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 10.6667 | 13.6671 | 10.272 | 1.8572 | 0.2531 | 1.2848 | 3.3951 | 13.59% | 1.852% | 9.401% | 24.84%
J | J Country | mount lucas | 2035 | 66% ECP | Grandfathering | IE wind not priority | 56.4 | 173.9366 | 103.9908 | 32.18 | 0.61016 | 37.1556 | 69.9458 | 18.5% | 0.3508% | 21.36% | 40.21%
B | A, B North | dalton | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 40.8 | 124.0912 | 119.5926 | 0 | 4.4986 | 0 | 4.4986 | 0% | 3.625% | 0% | 3.625%
B | A, B North | dalton | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 10.6667 | 13.6671 | 10.0305 | 2.2653 | 0.25501 | 1.1163 | 3.6366 | 16.57% | 1.866% | 8.168% | 26.61%
B | A, B North | dalton | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 40.8 | 124.0912 | 119.1922 | 0 | 4.899 | 0 | 4.899 | 0% | 3.948% | 0% | 3.948%
B | A, B North | dalton | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 10.6667 | 13.6671 | 9.7558 | 2.6485 | 0.25291 | 1.0099 | 3.9113 | 19.38% | 1.851% | 7.389% | 28.62%
B | A, B North | dalton | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 40.8 | 124.0912 | 119.1287 | 0 | 4.9625 | 0 | 4.9625 | 0% | 3.999% | 0% | 3.999%
B | A, B North | dalton | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 10.6667 | 13.6671 | 9.2863 | 3.0808 | 0.28622 | 1.0137 | 4.3808 | 22.54% | 2.094% | 7.417% | 32.05%
J | J Country | mount lucas | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 79.2 | 244.2514 | 234.3578 | 0 | 9.8935 | 0 | 9.8935 | 0% | 4.051% | 0% | 4.051%
J | J Country | mount lucas | 2035 | 100% ECP | Grandfathering | IE wind priority | 79.2 | 244.2514 | 241.5713 | 0 | 2.68 | 0 | 2.68 | 0% | 1.097% | 0% | 1.097%
B | A, B North | castlebar | 2030 | 33% ECP | Grandfathering | IE wind not priority | 6.8 | 20.6819 | 9.8883 | 3.7051 | 0.35832 | 6.7302 | 10.7936 | 17.91% | 1.733% | 32.54% | 52.19%
B | A, B North | sligo | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 13.65 | 41.5158 | 40.7949 | 0 | 0.72089 | 0 | 0.72089 | 0% | 1.736% | 0% | 1.736%
B | A, B North | sligo | 2035 | 100% ECP | Grandfathering | IE wind not priority | 4.08 | 12.4091 | 6.7611 | 2.4012 | 0.042122 | 3.2048 | 5.6481 | 19.35% | 0.3394% | 25.83% | 45.52%
J | J Country | dunfirth | 2030 | Initial | Grandfathering | IE Solar not priority | 31.5 | 40.3605 | 31.9572 | 3.1911 | 0.52195 | 4.6902 | 8.4033 | 7.907% | 1.293% | 11.62% | 20.82%
B | C | cashla | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 207.3331 | 265.6532 | 194.1481 | 58.3657 | 2.2697 | 10.8697 | 71.5051 | 21.97% | 0.8544% | 4.092% | 26.92%
B | C | cashla | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 311 | 398.4803 | 274.2654 | 87.6173 | 3.6112 | 32.9863 | 124.2149 | 21.99% | 0.9062% | 8.278% | 31.17%
B | C | cloon | 2030 | Initial | Grandfathering | IE Solar not priority | 20 | 25.6257 | 23.1295 | 2.0261 | 0.3314 | 0.13871 | 2.4962 | 7.907% | 1.293% | 0.5413% | 9.741%
B | C | cloon | 2030 | 33% ECP | Grandfathering | IE wind not priority | 26.2633 | 79.8786 | 55.9494 | 14.3099 | 1.3839 | 8.2353 | 23.9291 | 17.91% | 1.733% | 10.31% | 29.96%
B | C | cloon | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 47.9933 | 61.4932 | 50.0259 | 8.3561 | 1.1388 | 1.9724 | 11.4673 | 13.59% | 1.852% | 3.207% | 18.65%
J | J Country | derryiron | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 132 | 169.1299 | 62.0211 | 37.1881 | 1.5327 | 68.388 | 107.1088 | 21.99% | 0.9062% | 40.44% | 63.33%
B | C | cloon | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 26.2633 | 79.8786 | 51.1658 | 19.394 | 1.4067 | 7.9121 | 28.7128 | 24.28% | 1.761% | 9.905% | 35.95%
B | C | cloon | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 47.9933 | 61.4932 | 48.2802 | 10.1924 | 1.1474 | 1.8732 | 13.213 | 16.57% | 1.866% | 3.046% | 21.49%
J | J Country | derryiron | 2035 | 100% ECP | Grandfathering | IE wind not priority | 156 | 481.1012 | 254.2611 | 97.5781 | 1.8126 | 127.4494 | 226.8401 | 20.28% | 0.3768% | 26.49% | 47.15%
B | C | cashla | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 207.3331 | 265.6532 | 217.6921 | 40.693 | 1.9153 | 5.3529 | 47.9611 | 15.32% | 0.721% | 2.015% | 18.05%
B | C | cloon | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 26.2633 | 79.8786 | 45.396 | 24.5989 | 1.3823 | 8.5014 | 34.4826 | 30.8% | 1.731% | 10.64% | 43.17%
J | J Country | derryiron | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 132 | 169.1299 | 79.2302 | 37.1589 | 1.445 | 51.2958 | 89.8997 | 21.97% | 0.8544% | 30.33% | 53.15%
B | C | cloon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 26.2633 | 79.8786 | 43.5282 | 26.1536 | 1.3735 | 8.8232 | 36.3504 | 32.74% | 1.72% | 11.05% | 45.51%
B | C | cloon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 47.9933 | 61.4932 | 44.6095 | 13.8618 | 1.2878 | 1.734 | 16.8837 | 22.54% | 2.094% | 2.82% | 27.46%
J | J Country | derryiron | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 137.6666 | 424.5614 | 244.8573 | 139.9489 | 2.7406 | 37.0145 | 179.7041 | 32.96% | 0.6455% | 8.718% | 42.33%
B | C | cloon | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 26.2633 | 79.8786 | 57.3644 | 14.3099 | 1.3839 | 6.8204 | 22.5142 | 17.91% | 1.733% | 8.538% | 28.19%
B | C | cloon | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 47.9933 | 61.4932 | 50.2769 | 8.3561 | 1.1388 | 1.7214 | 11.2163 | 13.59% | 1.852% | 2.799% | 18.24%
J | J Country | derryiron | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 132 | 169.1299 | 83.3147 | 25.9074 | 1.2194 | 58.6884 | 85.8152 | 15.32% | 0.721% | 34.7% | 50.74%
B | C | cloon | 2030 | 100% ECP | Grandfathering | IE wind not priority | 78.79 | 239.636 | 155.9959 | 69.6922 | 4.1713 | 9.7766 | 83.6401 | 29.08% | 1.741% | 4.08% | 34.9%
B | C | cloon | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 103.98 | 133.2282 | 80.1526 | 42.0434 | 2.9353 | 8.097 | 53.0756 | 31.56% | 2.203% | 6.078% | 39.84%
J | J Country | derryiron | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 137.6666 | 424.5614 | 259.2059 | 78.5482 | 1.4893 | 85.318 | 165.3555 | 18.5% | 0.3508% | 20.1% | 38.95%
B | C | cloon | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 78.79 | 239.636 | 160.5865 | 69.6922 | 4.1713 | 5.1859 | 79.0494 | 29.08% | 1.741% | 2.164% | 32.99%
B | C | cloon | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 103.98 | 133.2282 | 80.6365 | 42.0434 | 2.9353 | 7.6131 | 52.5917 | 31.56% | 2.203% | 5.714% | 39.47%
J | J Country | derryiron | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 132 | 169.1299 | 78.3663 | 25.9074 | 1.2194 | 63.6367 | 90.7636 | 15.32% | 0.721% | 37.63% | 53.67%
B | C | cloon | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 47.9933 | 61.4932 | 46.6534 | 11.9166 | 1.1379 | 1.7853 | 14.8398 | 19.38% | 1.851% | 2.903% | 24.13%
B | C | cashla | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 207.3331 | 265.6532 | 205.9378 | 40.693 | 1.9153 | 17.1071 | 59.7154 | 15.32% | 0.721% | 6.44% | 22.48%
J | J Country | dunfirth | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 31.5 | 40.3605 | 26.7559 | 5.4845 | 0.74744 | 7.3727 | 13.6046 | 13.59% | 1.852% | 18.27% | 33.71%
J | J Country | dunfirth | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 31.5 | 40.3605 | 18.9072 | 8.8675 | 0.34483 | 12.241 | 21.4533 | 21.97% | 0.8544% | 30.33% | 53.15%
B | B South | uggool | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 169 | 747.4128 | 724.564 | 0 | 22.8488 | 0 | 22.8488 | 0% | 3.057% | 0% | 3.057%
B | B South | uggool | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 169 | 747.4128 | 721.9168 | 0 | 25.496 | 0 | 25.496 | 0% | 3.411% | 0% | 3.411%
J | J Country | dunfirth | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 31.5 | 40.3605 | 19.8819 | 6.1825 | 0.29099 | 14.0052 | 20.4786 | 15.32% | 0.721% | 34.7% | 50.74%
B | B South | uggool | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 169 | 747.4128 | 721.269 | 0 | 26.1438 | 0 | 26.1438 | 0% | 3.498% | 0% | 3.498%
B | B South | uggool | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 169 | 747.4128 | 727.4864 | 0 | 19.9265 | 0 | 19.9265 | 0% | 2.666% | 0% | 2.666%
J | J Country | dunfirth | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 31.5 | 40.3605 | 18.701 | 6.1825 | 0.29099 | 15.186 | 21.6595 | 15.32% | 0.721% | 37.63% | 53.67%
B | B South | uggool | 2030 | 100% ECP | Grandfathering | IE wind priority | 169 | 747.4128 | 723.3299 | 0 | 24.0829 | 0 | 24.0829 | 0% | 3.222% | 0% | 3.222%
B | B South | uggool | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 169 | 747.4128 | 723.3299 | 0 | 24.0829 | 0 | 24.0829 | 0% | 3.222% | 0% | 3.222%
B | B South | uggool | 2035 | 66% ECP | Grandfathering | IE wind priority | 169 | 747.4128 | 741.9565 | 0 | 5.4563 | 0 | 5.4563 | 0% | 0.73% | 0% | 0.73%
J | J Country | dunfirth | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 31.5 | 40.3605 | 17.8093 | 12.7367 | 0.88922 | 8.9253 | 22.5512 | 31.56% | 2.203% | 22.11% | 55.87%
B | B South | uggool | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 169 | 747.4128 | 741.9565 | 0 | 5.4563 | 0 | 5.4563 | 0% | 0.73% | 0% | 0.73%
B | B South | uggool | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 169 | 747.4128 | 736.3285 | 0 | 11.0843 | 0 | 11.0843 | 0% | 1.483% | 0% | 1.483%
J | J Country | dunfirth | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 31.5 | 40.3605 | 17.0009 | 12.7367 | 0.88922 | 9.7336 | 23.3596 | 31.56% | 2.203% | 24.12% | 57.88%
B | B South | uggool | 2035 | 100% ECP | Grandfathering | IE wind priority | 169 | 747.4128 | 741.2045 | 0 | 6.2083 | 0 | 6.2083 | 0% | 0.8306% | 0% | 0.8306%
J | J Country | dunfirth | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 31.5 | 40.3605 | 27.9972 | 5.4845 | 0.74744 | 6.1314 | 12.3633 | 13.59% | 1.852% | 15.19% | 30.63%
B | C | cashla | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 103.6666 | 132.8266 | 108.0571 | 18.0493 | 2.4598 | 4.2603 | 24.7695 | 13.59% | 1.852% | 3.207% | 18.65%
B | C | cashla | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 103.6666 | 132.8266 | 104.2862 | 22.0159 | 2.4783 | 4.0462 | 28.5404 | 16.57% | 1.866% | 3.046% | 21.49%
J | J Country | dunfirth | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 31.5 | 40.3605 | 21.6833 | 9.0981 | 0.84523 | 8.7339 | 18.6772 | 22.54% | 2.094% | 21.64% | 46.28%
B | C | cashla | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 103.6666 | 132.8266 | 100.7723 | 25.7401 | 2.458 | 3.8563 | 32.0544 | 19.38% | 1.851% | 2.903% | 24.13%
B | C | cashla | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 103.6666 | 132.8266 | 96.3576 | 29.9419 | 2.7817 | 3.7455 | 36.469 | 22.54% | 2.094% | 2.82% | 27.46%
J | J Country | dunfirth | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 31.5 | 40.3605 | 26.0022 | 7.8213 | 0.74688 | 5.7901 | 14.3583 | 19.38% | 1.851% | 14.35% | 35.58%
B | C | cashla | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 103.6666 | 132.8266 | 108.5992 | 18.0493 | 2.4598 | 3.7183 | 24.2275 | 13.59% | 1.852% | 2.799% | 18.24%
B | C | cashla | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 311 | 398.4803 | 239.7332 | 125.75 | 8.7793 | 24.2178 | 158.747 | 31.56% | 2.203% | 6.078% | 39.84%
J | J Country | dunfirth | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 31.5 | 40.3605 | 26.5314 | 6.6897 | 0.75307 | 6.3863 | 13.8291 | 16.57% | 1.866% | 15.82% | 34.26%
B | C | cashla | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 311 | 398.4803 | 241.1805 | 125.75 | 8.7793 | 22.7705 | 157.2998 | 31.56% | 2.203% | 5.714% | 39.47%
B | B South | uggool | 2030 | 33% ECP | Grandfathering | IE wind priority | 169 | 747.4128 | 727.4864 | 0 | 19.9265 | 0 | 19.9265 | 0% | 2.666% | 0% | 2.666%
B | C | cloon | 2035 | 66% ECP | Grandfathering | IE wind not priority | 52.5266 | 159.7572 | 127.6202 | 27.8561 | 0.49228 | 3.7886 | 32.137 | 17.44% | 0.3081% | 2.371% | 20.12%
C | C | athlone | 2030 | Initial | Grandfathering | IE Solar not priority | 4 | 5.1251 | 4.6259 | 0.40522 | 0.06628 | 0.027743 | 0.49925 | 7.907% | 1.293% | 0.5413% | 9.741%
J | J Country | derryiron | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 119.3333 | 368.0218 | 227.4862 | 119.6404 | 6.905 | 13.9902 | 140.5356 | 32.51% | 1.876% | 3.801% | 38.19%
C | C | athlone | 2030 | 33% ECP | Grandfathering | IE wind not priority | 42.4633 | 136.2799 | 98.5764 | 21.3066 | 2.3467 | 14.0502 | 37.7035 | 15.63% | 1.722% | 10.31% | 27.67%
C | C | athlone | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 46.9966 | 60.2162 | 48.987 | 8.1826 | 1.1151 | 1.9314 | 11.2291 | 13.59% | 1.852% | 3.207% | 18.65%
J | J Country | derryiron | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 132 | 169.1299 | 111.1793 | 28.0331 | 3.1557 | 26.7618 | 57.9506 | 16.57% | 1.866% | 15.82% | 34.26%
C | C | athlone | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 42.4633 | 136.2799 | 90.6382 | 29.7463 | 2.3966 | 13.4988 | 45.6417 | 21.83% | 1.759% | 9.905% | 33.49%
C | C | athlone | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 46.9966 | 60.2162 | 47.2775 | 9.9808 | 1.1235 | 1.8343 | 12.9386 | 16.57% | 1.866% | 3.046% | 21.49%
J | J Country | derryiron | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 119.3333 | 368.0218 | 243.8035 | 93.9128 | 6.9875 | 23.318 | 124.2182 | 25.52% | 1.899% | 6.336% | 33.75%
C | C | athlone | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 42.4633 | 136.2799 | 80.7846 | 38.5803 | 2.4109 | 14.5042 | 55.4953 | 28.31% | 1.769% | 10.64% | 40.72%
C | C | athlone | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 46.9966 | 60.2162 | 45.6845 | 11.6691 | 1.1143 | 1.7482 | 14.5317 | 19.38% | 1.851% | 2.903% | 24.13%
J | J Country | derryiron | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 132 | 169.1299 | 112.1202 | 22.9825 | 3.1321 | 30.8951 | 57.0097 | 13.59% | 1.852% | 18.27% | 33.71%
C | C | athlone | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 42.4633 | 136.2799 | 77.444 | 41.3452 | 2.4375 | 15.0532 | 58.8359 | 30.34% | 1.789% | 11.05% | 43.17%
C | C | athlone | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 46.9966 | 60.2162 | 43.6831 | 13.574 | 1.2611 | 1.698 | 16.533 | 22.54% | 2.094% | 2.82% | 27.46%
J | J Country | derryiron | 2030 | 33% ECP | Grandfathering | IE wind not priority | 119.3333 | 368.0218 | 250.4113 | 68.695 | 6.9184 | 41.997 | 117.6105 | 18.67% | 1.88% | 11.41% | 31.96%
C | C | athlone | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 46.9966 | 60.2162 | 49.2328 | 8.1826 | 1.1151 | 1.6857 | 10.9834 | 13.59% | 1.852% | 2.799% | 18.24%
J | J Country | derryiron | 2030 | Initial | Grandfathering | IE Solar not priority | 132 | 169.1299 | 133.916 | 13.3724 | 2.1872 | 19.6542 | 35.2139 | 7.907% | 1.293% | 11.62% | 20.82%
C | C | athlone | 2030 | 100% ECP | Grandfathering | IE wind not priority | 127.39 | 408.8402 | 279.0562 | 106.1222 | 6.9821 | 16.6798 | 129.7841 | 25.96% | 1.708% | 4.08% | 31.74%
C | C | athlone | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 132.99 | 170.3984 | 102.5149 | 53.7733 | 3.7542 | 10.356 | 67.8835 | 31.56% | 2.203% | 6.078% | 39.84%
J | J Country | derryiron | 2030 | Initial | Grandfathering | IE wind not priority | 101 | 311.4822 | 218.8097 | 42.8869 | 6.0566 | 43.7289 | 92.6725 | 13.77% | 1.944% | 14.04% | 29.75%
C | C | athlone | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 127.39 | 408.8402 | 286.8883 | 106.1222 | 6.9821 | 8.8477 | 121.9519 | 25.96% | 1.708% | 2.164% | 29.83%
C | C | athlone | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 132.99 | 170.3984 | 103.1337 | 53.7733 | 3.7542 | 9.7371 | 67.2646 | 31.56% | 2.203% | 5.714% | 39.47%
J | J Country | cushaling | 2035 | 100% ECP | Grandfathering | IE wind not priority | 75 | 231.2986 | 122.2409 | 46.9126 | 0.87142 | 61.2738 | 109.0577 | 20.28% | 0.3768% | 26.49% | 47.15%
C | C | athlone | 2035 | 66% ECP | Grandfathering | IE wind not priority | 84.9266 | 272.5599 | 223.0076 | 42.254 | 0.83462 | 6.4636 | 49.5523 | 15.5% | 0.3062% | 2.371% | 18.18%
C | C | athlone | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 89.9932 | 115.3072 | 89.3876 | 17.6628 | 0.83135 | 7.4254 | 25.9196 | 15.32% | 0.721% | 6.44% | 22.48%
C | C | athlone | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 42.4633 | 136.2799 | 100.9904 | 21.3066 | 2.3467 | 11.6362 | 35.2895 | 15.63% | 1.722% | 8.538% | 25.89%
J | J Country | derryiron | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 132 | 169.1299 | 108.9617 | 32.7752 | 3.1298 | 24.2633 | 60.1682 | 19.38% | 1.851% | 14.35% | 35.58%
B | C | shantallow | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 35 | 44.845 | 30.8659 | 9.8605 | 0.40641 | 3.7123 | 13.9792 | 21.99% | 0.9062% | 8.278% | 31.17%
B | C | shantallow | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 23.3333 | 29.8967 | 21.8495 | 6.5685 | 0.25543 | 1.2233 | 8.0472 | 21.97% | 0.8544% | 4.092% | 26.92%
B | C | cloon | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 75.9866 | 97.3607 | 75.4752 | 14.9138 | 0.70196 | 6.2697 | 21.8854 | 15.32% | 0.721% | 6.44% | 22.48%
B | C | cloon | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 52.5266 | 159.7572 | 131.0344 | 27.8561 | 0.49228 | 0.37436 | 28.7228 | 17.44% | 0.3081% | 0.2343% | 17.98%
B | C | cloon | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 75.9866 | 97.3607 | 79.7831 | 14.9138 | 0.70196 | 1.9618 | 17.5775 | 15.32% | 0.721% | 2.015% | 18.05%
B | C | cloon | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 52.5266 | 159.7572 | 108.5973 | 49.0085 | 0.92753 | 1.2238 | 51.1598 | 30.68% | 0.5806% | 0.766% | 32.02%
B | C | cloon | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 75.9866 | 97.3607 | 71.1544 | 21.3908 | 0.83182 | 3.9837 | 26.2063 | 21.97% | 0.8544% | 4.092% | 26.92%
J | J Country | derryiron | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 132 | 169.1299 | 74.6295 | 53.373 | 3.7263 | 37.4012 | 94.5004 | 31.56% | 2.203% | 22.11% | 55.87%
B | C | cloon | 2035 | 100% ECP | Grandfathering | IE wind not priority | 78.79 | 239.636 | 184.2075 | 46.3697 | 0.81344 | 8.2454 | 55.4285 | 19.35% | 0.3394% | 3.441% | 23.13%
B | C | cloon | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 103.98 | 133.2282 | 91.6981 | 29.2941 | 1.2074 | 11.0287 | 41.5301 | 21.99% | 0.9062% | 8.278% | 31.17%
J | J Country | derryiron | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 156 | 481.1012 | 268.674 | 144.184 | 8.8464 | 59.3967 | 212.4271 | 29.97% | 1.839% | 12.35% | 44.15%
J | J Country | derryiron | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 132 | 169.1299 | 71.242 | 53.373 | 3.7263 | 40.7886 | 97.8878 | 31.56% | 2.203% | 24.12% | 57.88%
B | C | shantallow | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 11.6667 | 14.9483 | 12.1608 | 2.0313 | 0.27683 | 0.47946 | 2.7876 | 13.59% | 1.852% | 3.207% | 18.65%
B | C | shantallow | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 11.6667 | 14.9483 | 11.7364 | 2.4777 | 0.27891 | 0.45536 | 3.2119 | 16.57% | 1.866% | 3.046% | 21.49%
J | J Country | derryiron | 2030 | 100% ECP | Grandfathering | IE wind not priority | 156 | 481.1012 | 254.8062 | 144.184 | 8.8464 | 73.2646 | 226.295 | 29.97% | 1.839% | 15.23% | 47.04%
B | C | shantallow | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 11.6667 | 14.9483 | 11.3409 | 2.8968 | 0.27662 | 0.43399 | 3.6074 | 19.38% | 1.851% | 2.903% | 24.13%
B | C | shantallow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 11.6667 | 14.9483 | 10.8441 | 3.3697 | 0.31305 | 0.42152 | 4.1042 | 22.54% | 2.094% | 2.82% | 27.46%
J | J Country | derryiron | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 132 | 169.1299 | 117.3217 | 22.9825 | 3.1321 | 25.6936 | 51.8082 | 13.59% | 1.852% | 15.19% | 30.63%
B | C | shantallow | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 11.6667 | 14.9483 | 12.2218 | 2.0313 | 0.27683 | 0.41846 | 2.7266 | 13.59% | 1.852% | 2.799% | 18.24%
B | C | shantallow | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 35 | 44.845 | 26.9796 | 14.1519 | 0.98802 | 2.7255 | 17.8654 | 31.56% | 2.203% | 6.078% | 39.84%
J | J Country | derryiron | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 119.3333 | 368.0218 | 261.9393 | 68.695 | 6.9184 | 30.4691 | 106.0825 | 18.67% | 1.88% | 8.279% | 28.83%
B | C | shantallow | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 35 | 44.845 | 27.1425 | 14.1519 | 0.98802 | 2.5626 | 17.7025 | 31.56% | 2.203% | 5.714% | 39.47%
J | J Country | derryiron | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 132 | 169.1299 | 90.8633 | 38.1254 | 3.5419 | 36.5992 | 78.2665 | 22.54% | 2.094% | 21.64% | 46.28%
B | C | shantallow | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 23.3333 | 29.8967 | 23.1763 | 4.5796 | 0.21555 | 1.9252 | 6.7204 | 15.32% | 0.721% | 6.44% | 22.48%
B | C | shantallow | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 23.3333 | 29.8967 | 24.4991 | 4.5796 | 0.21555 | 0.60241 | 5.3976 | 15.32% | 0.721% | 2.015% | 18.05%
J | J Country | derryiron | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 119.3333 | 368.0218 | 214.5241 | 127.7256 | 6.8137 | 18.9583 | 153.4976 | 34.71% | 1.851% | 5.151% | 41.71%
J | J Country | derryiron | 2035 | 66% ECP | Grandfathering | IE wind not priority | 137.6666 | 424.5614 | 253.8309 | 78.5482 | 1.4893 | 90.6929 | 170.7304 | 18.5% | 0.3508% | 21.36% | 40.21%
J | J Country | kinnegad | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 25 | 32.0321 | 21.2349 | 4.3527 | 0.5932 | 5.8513 | 10.7973 | 13.59% | 1.852% | 18.27% | 33.71%
B | B South | uggool | 2030 | Initial | Grandfathering | IE wind priority | 169 | 747.4128 | 729.9137 | 0 | 17.4991 | 0 | 17.4991 | 0% | 2.341% | 0% | 2.341%
B | A, B North | tonroe | 2030 | 100% ECP | Grandfathering | IE wind not priority | 4.99 | 15.1768 | 5.884 | 4.4138 | 0.26418 | 4.6149 | 9.2929 | 29.08% | 1.741% | 30.41% | 61.23%
J | J Country | kilteel | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 15 | 19.2193 | 12.634 | 3.1856 | 0.3586 | 3.0411 | 6.5853 | 16.57% | 1.866% | 15.82% | 34.26%
B | A, B North | tonroe | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 4.99 | 15.1768 | 6.1947 | 4.4138 | 0.26418 | 4.3041 | 8.9821 | 29.08% | 1.741% | 28.36% | 59.18%
J | J Country | kilteel | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 15 | 19.2193 | 12.7409 | 2.6116 | 0.35592 | 3.5108 | 6.4784 | 13.59% | 1.852% | 18.27% | 33.71%
B | A, B North | tonroe | 2035 | 66% ECP | Grandfathering | IE wind not priority | 3.3267 | 10.1179 | 6.0832 | 1.7642 | 0.031178 | 2.2393 | 4.0347 | 17.44% | 0.3081% | 22.13% | 39.88%
B | A, B North | tonroe | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 3.3267 | 10.1179 | 6.3261 | 1.7642 | 0.031178 | 1.9964 | 3.7918 | 17.44% | 0.3081% | 19.73% | 37.48%
J | J Country | kilteel | 2030 | Initial | Grandfathering | IE Solar not priority | 15 | 19.2193 | 15.2177 | 1.5196 | 0.24855 | 2.2334 | 4.0016 | 7.907% | 1.293% | 11.62% | 20.82%
B | A, B North | tonroe | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 3.3267 | 10.1179 | 5.5356 | 3.1039 | 0.058743 | 1.4196 | 4.5822 | 30.68% | 0.5806% | 14.03% | 45.29%
B | A, B North | tonroe | 2035 | 100% ECP | Grandfathering | IE wind not priority | 4.99 | 15.1768 | 8.269 | 2.9367 | 0.051517 | 3.9196 | 6.9078 | 19.35% | 0.3394% | 25.83% | 45.52%
B | B South | galway | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 0.4 | 0.51251 | 0.43338 | 0.069644 | 0.0094913 | 0 | 0.079135 | 13.59% | 1.852% | 0% | 15.44%
B | A, B North | tonroe | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 1.6633 | 5.0589 | 2.608 | 0.90629 | 0.087648 | 1.457 | 2.4509 | 17.91% | 1.733% | 28.8% | 48.45%
J | J Country | harristown | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 42.3 | 54.1984 | 19.8749 | 11.9171 | 0.49117 | 21.9152 | 34.3235 | 21.99% | 0.9062% | 40.44% | 63.33%
B | B South | galway | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 0.4 | 0.51251 | 0.40371 | 0.099319 | 0.0094842 | 0 | 0.1088 | 19.38% | 1.851% | 0% | 21.23%
J | J Country | harristown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 42.3 | 54.1984 | 25.3897 | 11.9077 | 0.46306 | 16.438 | 28.8088 | 21.97% | 0.8544% | 30.33% | 53.15%
B | B South | galway | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 0.4 | 0.51251 | 0.38625 | 0.11553 | 0.010733 | 0 | 0.12626 | 22.54% | 2.094% | 0% | 24.64%
B | B South | galway | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 0.4 | 0.51251 | 0.43338 | 0.069644 | 0.0094913 | 0 | 0.079135 | 13.59% | 1.852% | 0% | 15.44%
J | J Country | harristown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 42.3 | 54.1984 | 26.6986 | 8.3022 | 0.39076 | 18.807 | 27.4999 | 15.32% | 0.721% | 34.7% | 50.74%
B | B South | galway | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 1.2 | 1.5375 | 1.0167 | 0.48521 | 0.033875 | 0.0017877 | 0.52087 | 31.56% | 2.203% | 0.1163% | 33.88%
B | B South | galway | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 1.2 | 1.5375 | 1.0185 | 0.48521 | 0.033875 | 0 | 0.51908 | 31.56% | 2.203% | 0% | 33.76%
J | J Country | harristown | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 42.3 | 54.1984 | 25.1128 | 8.3022 | 0.39076 | 20.3927 | 29.0856 | 15.32% | 0.721% | 37.63% | 53.67%
B | B South | galway | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 0.8 | 1.025 | 0.84864 | 0.15701 | 0.0073903 | 0.011987 | 0.17639 | 15.32% | 0.721% | 1.169% | 17.21%
B | B South | galway | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 0.8 | 1.025 | 0.85918 | 0.15701 | 0.0073903 | 0.0014434 | 0.16585 | 15.32% | 0.721% | 0.1408% | 16.18%
B | B South | galway | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 0.8 | 1.025 | 0.78746 | 0.22521 | 0.0087576 | 0.0036073 | 0.23757 | 21.97% | 0.8544% | 0.3519% | 23.18%
B | B South | galway | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 0.4 | 0.51251 | 0.41794 | 0.084949 | 0.0095627 | 6.56e-05 | 0.094577 | 16.57% | 1.866% | 0.0128% | 18.45%
D | D and E North | tullabrack | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 13.8 | 42.8684 | 41.3574 | 0 | 1.511 | 0 | 1.511 | 0% | 3.525% | 0% | 3.525%
B | A, B North | tonroe | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 1.6633 | 5.0589 | 2.0055 | 1.6564 | 0.086989 | 1.31 | 3.0534 | 32.74% | 1.72% | 25.9% | 60.36%
B | A, B North | tonroe | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 1.6633 | 5.0589 | 2.1655 | 1.5579 | 0.087546 | 1.2479 | 2.8934 | 30.8% | 1.731% | 24.67% | 57.19%
B | A, B North | sligo | 2035 | 100% ECP | Grandfathering | IE wind priority | 13.65 | 41.5158 | 41.088 | 0 | 0.42785 | 0 | 0.42785 | 0% | 1.031% | 0% | 1.031%
J | J Country | kilteel | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 15 | 19.2193 | 7.0478 | 4.2259 | 0.17417 | 7.7714 | 12.1715 | 21.99% | 0.9062% | 40.44% | 63.33%
B | A, B North | tawnaghmore | 2030 | Initial | Grandfathering | IE wind priority | 19.2 | 58.3959 | 56.7071 | 0 | 1.6887 | 0 | 1.6887 | 0% | 2.892% | 0% | 2.892%
B | A, B North | tawnaghmore | 2030 | 33% ECP | Grandfathering | IE wind priority | 19.2 | 58.3959 | 56.5134 | 0 | 1.8825 | 0 | 1.8825 | 0% | 3.224% | 0% | 3.224%
J | J Country | kilteel | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 15 | 19.2193 | 9.0034 | 4.2226 | 0.1642 | 5.8291 | 10.2159 | 21.97% | 0.8544% | 30.33% | 53.15%
B | A, B North | tawnaghmore | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 19.2 | 58.3959 | 56.2789 | 0 | 2.117 | 0 | 2.117 | 0% | 3.625% | 0% | 3.625%
B | A, B North | tawnaghmore | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 19.2 | 58.3959 | 56.0905 | 0 | 2.3054 | 0 | 2.3054 | 0% | 3.948% | 0% | 3.948%
J | J Country | kilteel | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 15 | 19.2193 | 9.4676 | 2.944 | 0.13857 | 6.6691 | 9.7517 | 15.32% | 0.721% | 34.7% | 50.74%
B | A, B North | tawnaghmore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 19.2 | 58.3959 | 56.0606 | 0 | 2.3353 | 0 | 2.3353 | 0% | 3.999% | 0% | 3.999%
B | A, B North | tawnaghmore | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 19.2 | 58.3959 | 56.5134 | 0 | 1.8825 | 0 | 1.8825 | 0% | 3.224% | 0% | 3.224%
J | J Country | kilteel | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 15 | 19.2193 | 8.9053 | 2.944 | 0.13857 | 7.2314 | 10.314 | 15.32% | 0.721% | 37.63% | 53.67%
B | A, B North | tawnaghmore | 2030 | 100% ECP | Grandfathering | IE wind priority | 19.2 | 58.3959 | 56.1475 | 0 | 2.2484 | 0 | 2.2484 | 0% | 3.85% | 0% | 3.85%
B | A, B North | tawnaghmore | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 19.2 | 58.3959 | 56.1475 | 0 | 2.2484 | 0 | 2.2484 | 0% | 3.85% | 0% | 3.85%
B | A, B North | tawnaghmore | 2035 | 66% ECP | Grandfathering | IE wind priority | 19.2 | 58.3959 | 57.8744 | 0 | 0.52151 | 0 | 0.52151 | 0% | 0.8931% | 0% | 0.8931%
J | J Country | kilteel | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 15 | 19.2193 | 8.4806 | 6.0651 | 0.42344 | 4.2501 | 10.7387 | 31.56% | 2.203% | 22.11% | 55.87%
B | A, B North | tawnaghmore | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 19.2 | 58.3959 | 57.8744 | 0 | 0.52151 | 0 | 0.52151 | 0% | 0.8931% | 0% | 0.8931%
B | A, B North | tawnaghmore | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 19.2 | 58.3959 | 57.3819 | 0 | 1.014 | 0 | 1.014 | 0% | 1.736% | 0% | 1.736%
J | J Country | kilteel | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 15 | 19.2193 | 8.0957 | 6.0651 | 0.42344 | 4.6351 | 11.1236 | 31.56% | 2.203% | 24.12% | 57.88%
B | A, B North | tawnaghmore | 2035 | 100% ECP | Grandfathering | IE wind priority | 19.2 | 58.3959 | 57.7941 | 0 | 0.60181 | 0 | 0.60181 | 0% | 1.031% | 0% | 1.031%
J | J Country | kilteel | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 15 | 19.2193 | 13.332 | 2.6116 | 0.35592 | 2.9197 | 5.8873 | 13.59% | 1.852% | 15.19% | 30.63%
B | A, B North | tonroe | 2030 | 33% ECP | Grandfathering | IE wind not priority | 1.6633 | 5.0589 | 2.4187 | 0.90629 | 0.087648 | 1.6463 | 2.6402 | 17.91% | 1.733% | 32.54% | 52.19%
B | A, B North | tonroe | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 1.6633 | 5.0589 | 2.3107 | 1.2283 | 0.089088 | 1.4309 | 2.7483 | 24.28% | 1.761% | 28.28% | 54.33%
J | J Country | kilteel | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 15 | 19.2193 | 10.3254 | 4.3324 | 0.40249 | 4.159 | 8.8939 | 22.54% | 2.094% | 21.64% | 46.28%
J | J Country | harristown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 42.3 | 54.1984 | 23.9154 | 17.1036 | 1.1941 | 11.9854 | 30.2831 | 31.56% | 2.203% | 22.11% | 55.87%
J | J Country | dunfirth | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 31.5 | 40.3605 | 14.8005 | 8.8744 | 0.36577 | 16.3199 | 25.5601 | 21.99% | 0.9062% | 40.44% | 63.33%
B | B South | galway | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 1.2 | 1.5375 | 1.1617 | 0.33807 | 0.013934 | 0.023811 | 0.37582 | 21.99% | 0.9062% | 1.549% | 24.44%
J | J Country | harristown | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 42.3 | 54.1984 | 22.8298 | 17.1036 | 1.1941 | 13.0709 | 31.3686 | 31.56% | 2.203% | 24.12% | 57.88%
B | B South | knockranny | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 140.7333 | 622.4016 | 302.3188 | 157.8386 | 3.3705 | 158.8737 | 320.0828 | 25.36% | 0.5415% | 25.53% | 51.43%
B | B South | knockranny | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 33.6 | 148.598 | 146.3943 | 0 | 2.2037 | 0 | 2.2037 | 0% | 1.483% | 0% | 1.483%
B | B South | knockranny | 2035 | 100% ECP | Grandfathering | IE wind not priority | 156.5 | 692.1308 | 314.219 | 104.8706 | 2.0761 | 270.965 | 377.9118 | 15.15% | 0.3% | 39.15% | 54.6%
B | B South | knockranny | 2035 | 100% ECP | Grandfathering | IE wind priority | 33.6 | 148.598 | 147.3637 | 0 | 1.2343 | 0 | 1.2343 | 0% | 0.8306% | 0% | 0.8306%
J | J Country | fosterstown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 83.79 | 107.359 | 47.3728 | 33.8797 | 2.3653 | 23.7412 | 59.9863 | 31.56% | 2.203% | 22.11% | 55.87%
J | J Country | fosterstown | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 83.79 | 107.359 | 45.2225 | 33.8797 | 2.3653 | 25.8915 | 62.1365 | 31.56% | 2.203% | 24.12% | 57.88%
B | B South | salthill | 2030 | Initial | Grandfathering | IE wind priority | 40.9 | 124.3954 | 120.798 | 0 | 3.5974 | 0 | 3.5974 | 0% | 2.892% | 0% | 2.892%
B | B South | salthill | 2030 | 33% ECP | Grandfathering | IE wind priority | 40.9 | 124.3954 | 120.3853 | 0 | 4.0101 | 0 | 4.0101 | 0% | 3.224% | 0% | 3.224%
J | J Country | fosterstown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 27.93 | 35.7863 | 24.8242 | 4.8629 | 0.66273 | 5.4365 | 10.9621 | 13.59% | 1.852% | 15.19% | 30.63%
B | B South | salthill | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 40.9 | 124.3954 | 119.8858 | 0 | 4.5096 | 0 | 4.5096 | 0% | 3.625% | 0% | 3.625%
J | J Country | fosterstown | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 55.8599 | 71.5726 | 33.1632 | 10.9635 | 0.51603 | 26.9299 | 38.4095 | 15.32% | 0.721% | 37.63% | 53.67%
B | B South | salthill | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 40.9 | 124.3954 | 119.4843 | 0 | 4.911 | 0 | 4.911 | 0% | 3.948% | 0% | 3.948%
B | B South | salthill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 40.9 | 124.3954 | 119.4207 | 0 | 4.9747 | 0 | 4.9747 | 0% | 3.999% | 0% | 3.999%
B | B South | salthill | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 40.9 | 124.3954 | 120.3853 | 0 | 4.0101 | 0 | 4.0101 | 0% | 3.224% | 0% | 3.224%
J | J Country | fosterstown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 27.93 | 35.7863 | 23.0553 | 6.9349 | 0.66223 | 5.1339 | 12.731 | 19.38% | 1.851% | 14.35% | 35.58%
B | B South | salthill | 2030 | 100% ECP | Grandfathering | IE wind priority | 40.9 | 124.3954 | 119.6059 | 0 | 4.7895 | 0 | 4.7895 | 0% | 3.85% | 0% | 3.85%
B | B South | salthill | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 40.9 | 124.3954 | 119.6059 | 0 | 4.7895 | 0 | 4.7895 | 0% | 3.85% | 0% | 3.85%
J | J Country | fosterstown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 27.93 | 35.7863 | 23.5245 | 5.9315 | 0.66772 | 5.6625 | 12.2618 | 16.57% | 1.866% | 15.82% | 34.26%
B | B South | salthill | 2035 | 66% ECP | Grandfathering | IE wind priority | 40.9 | 124.3954 | 123.2844 | 0 | 1.1109 | 0 | 1.1109 | 0% | 0.8931% | 0% | 0.8931%
J | J Country | fosterstown | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 27.93 | 35.7863 | 23.7236 | 4.8629 | 0.66273 | 6.5371 | 12.0627 | 13.59% | 1.852% | 18.27% | 33.71%
B | B South | salthill | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 40.9 | 124.3954 | 123.2844 | 0 | 1.1109 | 0 | 1.1109 | 0% | 0.8931% | 0% | 0.8931%
B | B South | salthill | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 40.9 | 124.3954 | 122.2353 | 0 | 2.16 | 0 | 2.16 | 0% | 1.736% | 0% | 1.736%
B | B South | salthill | 2035 | 100% ECP | Grandfathering | IE wind priority | 40.9 | 124.3954 | 123.1134 | 0 | 1.282 | 0 | 1.282 | 0% | 1.031% | 0% | 1.031%
J | J Country | fosterstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 27.93 | 35.7863 | 19.2258 | 8.067 | 0.74944 | 7.7441 | 16.5605 | 22.54% | 2.094% | 21.64% | 46.28%
B | B South | knockranny | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 33.6 | 148.598 | 147.5132 | 0 | 1.0848 | 0 | 1.0848 | 0% | 0.73% | 0% | 0.73%
B | B South | knockranny | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 140.7333 | 622.4016 | 348.4536 | 84.5541 | 1.7138 | 187.6802 | 273.9481 | 13.59% | 0.2754% | 30.15% | 44.01%
J | J Country | fosterstown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 55.8599 | 71.5726 | 35.2572 | 10.9635 | 0.51603 | 24.8358 | 36.3154 | 15.32% | 0.721% | 34.7% | 50.74%
B | B South | knockranny | 2030 | Initial | Grandfathering | IE wind not priority | 109.2 | 482.9437 | 280.3283 | 46.8655 | 7.3878 | 148.3621 | 202.6154 | 9.704% | 1.53% | 30.72% | 41.95%
B | B South | knockranny | 2030 | Initial | Grandfathering | IE wind priority | 33.6 | 148.598 | 145.1189 | 0 | 3.4791 | 0 | 3.4791 | 0% | 2.341% | 0% | 2.341%
J | J Country | harristown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 42.3 | 54.1984 | 37.5963 | 7.3648 | 1.0037 | 8.2336 | 16.6022 | 13.59% | 1.852% | 15.19% | 30.63%
B | B South | knockranny | 2030 | 33% ECP | Grandfathering | IE wind not priority | 124.9667 | 552.6726 | 309.8369 | 75.1819 | 8.438 | 159.2158 | 242.8357 | 13.6% | 1.527% | 28.81% | 43.94%
B | B South | knockranny | 2030 | 33% ECP | Grandfathering | IE wind priority | 33.6 | 148.598 | 144.6363 | 0 | 3.9617 | 0 | 3.9617 | 0% | 2.666% | 0% | 2.666%
J | J Country | harristown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 42.3 | 54.1984 | 29.1176 | 12.2174 | 1.135 | 11.7284 | 25.0809 | 22.54% | 2.094% | 21.64% | 46.28%
B | B South | knockranny | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 124.9667 | 552.6726 | 301.2235 | 105.0169 | 8.7586 | 137.6736 | 251.4491 | 19% | 1.585% | 24.91% | 45.5%
B | B South | knockranny | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 33.6 | 148.598 | 144.0553 | 0 | 4.5427 | 0 | 4.5427 | 0% | 3.057% | 0% | 3.057%
J | J Country | harristown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 42.3 | 54.1984 | 34.9173 | 10.5029 | 1.003 | 7.7753 | 19.2812 | 19.38% | 1.851% | 14.35% | 35.58%
B | B South | knockranny | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 124.9667 | 552.6726 | 291.7217 | 137.4212 | 8.9587 | 114.5711 | 260.9509 | 24.86% | 1.621% | 20.73% | 47.22%
B | B South | knockranny | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 33.6 | 148.598 | 143.529 | 0 | 5.069 | 0 | 5.069 | 0% | 3.411% | 0% | 3.411%
J | J Country | harristown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 42.3 | 54.1984 | 35.6279 | 8.9833 | 1.0113 | 8.5759 | 18.5705 | 16.57% | 1.866% | 15.82% | 34.26%
B | B South | knockranny | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 124.9667 | 552.6726 | 276.4426 | 147.7561 | 9.0809 | 119.393 | 276.23 | 26.73% | 1.643% | 21.6% | 49.98%
B | B South | knockranny | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 33.6 | 148.598 | 143.4002 | 0 | 5.1978 | 0 | 5.1978 | 0% | 3.498% | 0% | 3.498%
J | J Country | harristown | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 42.3 | 54.1984 | 35.9294 | 7.3648 | 1.0037 | 9.9005 | 18.269 | 13.59% | 1.852% | 18.27% | 33.71%
B | B South | knockranny | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 124.9667 | 552.6726 | 346.8824 | 75.1819 | 8.438 | 122.1704 | 205.7903 | 13.6% | 1.527% | 22.11% | 37.24%
B | B South | knockranny | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 33.6 | 148.598 | 144.6363 | 0 | 3.9617 | 0 | 3.9617 | 0% | 2.666% | 0% | 2.666%
J | J Country | harristown | 2030 | Initial | Grandfathering | IE Solar not priority | 42.3 | 54.1984 | 42.914 | 4.2852 | 0.70091 | 6.2983 | 11.2844 | 7.907% | 1.293% | 11.62% | 20.82%
B | B South | knockranny | 2030 | 100% ECP | Grandfathering | IE wind not priority | 156.5 | 692.1308 | 349.4956 | 159.0534 | 10.7296 | 172.8522 | 342.6352 | 22.98% | 1.55% | 24.97% | 49.5%
B | B South | knockranny | 2030 | 100% ECP | Grandfathering | IE wind priority | 33.6 | 148.598 | 143.81 | 0 | 4.7881 | 0 | 4.7881 | 0% | 3.222% | 0% | 3.222%
B | B South | knockranny | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 156.5 | 692.1308 | 387.6276 | 159.0534 | 10.7296 | 134.7201 | 304.5032 | 22.98% | 1.55% | 19.46% | 44%
B | B South | knockranny | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 33.6 | 148.598 | 143.81 | 0 | 4.7881 | 0 | 4.7881 | 0% | 3.222% | 0% | 3.222%
J | J Country | fosterstown | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 83.79 | 107.359 | 39.3693 | 23.606 | 0.97294 | 43.4108 | 67.9898 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J Country | fosterstown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 55.8599 | 71.5726 | 33.5287 | 15.725 | 0.6115 | 21.7074 | 38.0439 | 21.97% | 0.8544% | 30.33% | 53.15%
B | B South | knockranny | 2035 | 66% ECP | Grandfathering | IE wind not priority | 140.7333 | 622.4016 | 299.6229 | 84.5541 | 1.7138 | 236.5109 | 322.7787 | 13.59% | 0.2754% | 38% | 51.86%
B | B South | knockranny | 2035 | 66% ECP | Grandfathering | IE wind priority | 33.6 | 148.598 | 147.5132 | 0 | 1.0848 | 0 | 1.0848 | 0% | 0.73% | 0% | 0.73%
J | J Country | cushaling | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 75 | 231.2986 | 133.3969 | 76.2434 | 1.4931 | 20.1653 | 97.9018 | 32.96% | 0.6455% | 8.718% | 42.33%
B | A, B North | castlebar | 2030 | Initial | Grandfathering | IE wind priority | 8.5 | 25.8523 | 25.1047 | 0 | 0.74762 | 0 | 0.74762 | 0% | 2.892% | 0% | 2.892%
B | A, B North | castlebar | 2030 | Initial | Grandfathering | IE wind not priority | 6.8 | 20.6819 | 9.7786 | 2.7139 | 0.36995 | 7.8195 | 10.9033 | 13.12% | 1.789% | 37.81% | 52.72%
K | H2 & K | dungarvan | 2030 | Initial | Grandfathering | IE Solar not priority | 12.94 | 15.1503 | 12.6337 | 1.253 | 0.19521 | 1.0683 | 2.5166 | 8.271% | 1.289% | 7.052% | 16.61%
A | A, B North | croaghonagh | 2030 | Initial | Grandfathering | IE wind not priority | 138.1 | 399.4844 | 191.563 | 49.6984 | 7.1843 | 151.0387 | 207.9214 | 12.44% | 1.798% | 37.81% | 52.05%
A | A, B North | croaghonagh | 2030 | 33% ECP | Grandfathering | IE wind not priority | 138.1 | 399.4844 | 194.7029 | 67.7065 | 7.0761 | 129.9989 | 204.7815 | 16.95% | 1.771% | 32.54% | 51.26%
A | A, B North | croaghonagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 138.1 | 399.4844 | 186.8858 | 92.4869 | 7.1181 | 112.9936 | 212.5986 | 23.15% | 1.782% | 28.28% | 53.22%
A | A, B North | croaghonagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 138.1 | 399.4844 | 176.5397 | 117.3042 | 7.0952 | 98.5454 | 222.9447 | 29.36% | 1.776% | 24.67% | 55.81%
K | H2 & K | cullenagh | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 50 | 64.0644 | 47.2539 | 14.0864 | 0.58058 | 2.1435 | 16.8104 | 21.99% | 0.9062% | 3.346% | 26.24%
A | A, B North | croaghonagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 138.1 | 399.4844 | 163.2294 | 125.6648 | 7.1421 | 103.448 | 236.255 | 31.46% | 1.788% | 25.9% | 59.14%
A | A, B North | croaghonagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 138.1 | 399.4844 | 209.6498 | 67.7065 | 7.0761 | 115.052 | 189.8346 | 16.95% | 1.771% | 28.8% | 47.52%
K | H2 & K | cullenagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 33.3333 | 42.7095 | 31.4895 | 9.3836 | 0.3649 | 1.4716 | 11.22 | 21.97% | 0.8544% | 3.445% | 26.27%
A | A, B North | croaghonagh | 2030 | 100% ECP | Grandfathering | IE wind not priority | 138.1 | 399.4844 | 160.872 | 110.276 | 6.8639 | 121.4725 | 238.6125 | 27.6% | 1.718% | 30.41% | 59.73%
A | A, B North | croaghonagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 138.1 | 399.4844 | 169.0512 | 110.276 | 6.8639 | 113.2933 | 230.4332 | 27.6% | 1.718% | 28.36% | 57.68%
K | H2 & K | cullenagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 33.3333 | 42.7095 | 35.3236 | 6.5423 | 0.30793 | 0.53576 | 7.386 | 15.32% | 0.721% | 1.254% | 17.29%
K | H2 & K | cullenagh | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 33.3333 | 42.7095 | 34.204 | 6.5423 | 0.30793 | 1.6553 | 8.5055 | 15.32% | 0.721% | 3.876% | 19.91%
A | A, B North | croaghonagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 138.1 | 399.4844 | 252.1267 | 67.264 | 1.2682 | 78.8255 | 147.3577 | 16.84% | 0.3175% | 19.73% | 36.89%
A | A, B North | croaghonagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 138.1 | 399.4844 | 223.067 | 118.0529 | 2.3126 | 56.0519 | 176.4174 | 29.55% | 0.5789% | 14.03% | 44.16%
A | A, B North | croaghonagh | 2035 | 100% ECP | Grandfathering | IE wind not priority | 138.1 | 399.4844 | 220.5082 | 74.3966 | 1.4091 | 103.1705 | 178.9762 | 18.62% | 0.3527% | 25.83% | 44.8%
K | H2 & K | cullenagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 50 | 64.0644 | 42.3738 | 20.217 | 1.4115 | 0.06206 | 21.6906 | 31.56% | 2.203% | 0.09687% | 33.86%
A | A, B North | garvagh | 2030 | Initial | Grandfathering | IE wind not priority | 34 | 98.3524 | 47.1625 | 12.2357 | 1.7688 | 37.1855 | 51.1899 | 12.44% | 1.798% | 37.81% | 52.05%
A | A, B North | garvagh | 2030 | Initial | Grandfathering | IE wind priority | 48 | 138.8505 | 134.8999 | 0 | 3.9506 | 0 | 3.9506 | 0% | 2.845% | 0% | 2.845%
K | H2 & K | cullenagh | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 50 | 64.0644 | 41.6235 | 20.217 | 1.4115 | 0.81234 | 22.4408 | 31.56% | 2.203% | 1.268% | 35.03%
A | A, B North | garvagh | 2030 | Initial | Grandfathering | IE Solar not priority | 40 | 42.117 | 32.1704 | 3.1666 | 0.53912 | 6.2408 | 9.9466 | 7.519% | 1.28% | 14.82% | 23.62%
A | A, B North | garvagh | 2030 | 33% ECP | Grandfathering | IE wind not priority | 50 | 144.6359 | 70.4934 | 24.5136 | 2.5619 | 47.0669 | 74.1424 | 16.95% | 1.771% | 32.54% | 51.26%
K | H2 & K | cullenagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 17.9586 | 2.9018 | 0.39547 | 0.098894 | 3.3962 | 13.59% | 1.852% | 0.4631% | 15.9%
A | A, B North | croaghonagh | 2035 | 66% ECP | Grandfathering | IE wind not priority | 138.1 | 399.4844 | 242.5393 | 67.264 | 1.2682 | 88.4129 | 156.9451 | 16.84% | 0.3175% | 22.13% | 39.29%
K | H2 & K | dungarvan | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 52.6066 | 61.5924 | 49.6793 | 8.5343 | 1.1449 | 2.2338 | 11.9131 | 13.86% | 1.859% | 3.627% | 19.34%
A | A, B North | corderry | 2035 | 100% ECP | Grandfathering | IE wind priority | 45.655 | 132.0671 | 130.7314 | 0 | 1.3357 | 0 | 1.3357 | 0% | 1.011% | 0% | 1.011%
K | H2 & K | dungarvan | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 92.2733 | 108.0344 | 79.1424 | 24.2398 | 0.92985 | 3.7223 | 28.892 | 22.44% | 0.8607% | 3.445% | 26.74%
A | A, B North | corderry | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 23.0833 | 66.7736 | 29.5085 | 19.6073 | 1.186 | 16.4718 | 37.2651 | 29.36% | 1.776% | 24.67% | 55.81%
A | A, B North | corderry | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 45.655 | 132.0671 | 126.8882 | 0 | 5.1789 | 0 | 5.1789 | 0% | 3.921% | 0% | 3.921%
K | H2 & K | dungarvan | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 92.2733 | 108.0344 | 88.7347 | 17.1516 | 0.79292 | 1.3552 | 19.2997 | 15.88% | 0.7339% | 1.254% | 17.86%
A | A, B North | corderry | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 23.0833 | 66.7736 | 27.2837 | 21.0048 | 1.1938 | 17.2913 | 39.4899 | 31.46% | 1.788% | 25.9% | 59.14%
A | A, B North | corderry | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 45.655 | 132.0671 | 126.7995 | 0 | 5.2675 | 0 | 5.2675 | 0% | 3.989% | 0% | 3.989%
K | H2 & K | dungarvan | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 92.2733 | 108.0344 | 85.9029 | 17.1516 | 0.79292 | 4.187 | 22.1315 | 15.88% | 0.7339% | 3.876% | 20.49%
A | A, B North | corderry | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 23.0833 | 66.7736 | 35.0428 | 11.3171 | 1.1828 | 19.2309 | 31.7307 | 16.95% | 1.771% | 28.8% | 47.52%
A | A, B North | corderry | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 45.655 | 132.0671 | 127.8355 | 0 | 4.2315 | 0 | 4.2315 | 0% | 3.204% | 0% | 3.204%
A | A, B North | corderry | 2030 | 100% ECP | Grandfathering | IE wind not priority | 36.55 | 105.7289 | 42.5769 | 29.186 | 1.8166 | 32.1493 | 63.152 | 27.6% | 1.718% | 30.41% | 59.73%
A | A, B North | corderry | 2030 | 100% ECP | Grandfathering | IE wind priority | 45.655 | 132.0671 | 127.1402 | 0 | 4.9269 | 0 | 4.9269 | 0% | 3.731% | 0% | 3.731%
K | H2 & K | dungarvan | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 131.94 | 154.4767 | 101.9123 | 49.024 | 3.3908 | 0.14964 | 52.5644 | 31.74% | 2.195% | 0.09687% | 34.03%
A | A, B North | corderry | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 36.55 | 105.7289 | 44.7417 | 29.186 | 1.8166 | 29.9846 | 60.9872 | 27.6% | 1.718% | 28.36% | 57.68%
A | A, B North | corderry | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 45.655 | 132.0671 | 127.1402 | 0 | 4.9269 | 0 | 4.9269 | 0% | 3.731% | 0% | 3.731%
K | H2 & K | dungarvan | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 131.94 | 154.4767 | 100.1032 | 49.024 | 3.3908 | 1.9588 | 54.3735 | 31.74% | 2.195% | 1.268% | 35.2%
K | H2 & K | dungarvan | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 52.6066 | 61.5924 | 51.6279 | 8.5343 | 1.1449 | 0.28523 | 9.9645 | 13.86% | 1.859% | 0.4631% | 16.18%
A | A, B North | corderry | 2035 | 66% ECP | Grandfathering | IE wind not priority | 29.8167 | 86.2512 | 52.3658 | 14.5227 | 0.27381 | 19.0889 | 33.8854 | 16.84% | 0.3175% | 22.13% | 39.29%
A | A, B North | corderry | 2035 | 66% ECP | Grandfathering | IE wind priority | 45.655 | 132.0671 | 130.8915 | 0 | 1.1755 | 0 | 1.1755 | 0% | 0.8901% | 0% | 0.8901%
K | H2 & K | dungarvan | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 52.6066 | 61.5924 | 44.0889 | 14.0196 | 1.3093 | 2.1746 | 17.5034 | 22.76% | 2.126% | 3.531% | 28.42%
A | A, B North | corderry | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 29.8167 | 86.2512 | 54.4357 | 14.5227 | 0.27381 | 17.0189 | 31.8154 | 16.84% | 0.3175% | 19.73% | 36.89%
A | A, B North | corderry | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 45.655 | 132.0671 | 130.8915 | 0 | 1.1755 | 0 | 1.1755 | 0% | 0.8901% | 0% | 0.8901%
K | H2 & K | dungarvan | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 52.6066 | 61.5924 | 46.2163 | 12.0545 | 1.1645 | 2.1571 | 15.3761 | 19.57% | 1.891% | 3.502% | 24.96%
A | A, B North | corderry | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 29.8167 | 86.2512 | 48.1616 | 25.4884 | 0.49931 | 12.102 | 38.0896 | 29.55% | 0.5789% | 14.03% | 44.16%
A | A, B North | corderry | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 45.655 | 132.0671 | 129.7898 | 0 | 2.2772 | 0 | 2.2772 | 0% | 1.724% | 0% | 1.724%
K | H2 & K | dungarvan | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 52.6066 | 61.5924 | 48.4364 | 10.3548 | 1.1646 | 1.6365 | 13.1559 | 16.81% | 1.891% | 2.657% | 21.36%
A | A, B North | corderry | 2035 | 100% ECP | Grandfathering | IE wind not priority | 36.55 | 105.7289 | 58.3604 | 19.69 | 0.37294 | 27.3054 | 47.3684 | 18.62% | 0.3527% | 25.83% | 44.8%
A | A, B North | garvagh | 2030 | 33% ECP | Grandfathering | IE wind priority | 48 | 138.8505 | 134.4016 | 0 | 4.4489 | 0 | 4.4489 | 0% | 3.204% | 0% | 3.204%
A | A, B North | corderry | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 45.655 | 132.0671 | 127.3436 | 0 | 4.7235 | 0 | 4.7235 | 0% | 3.577% | 0% | 3.577%
A | A, B North | garvagh | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 40 | 42.117 | 31.8276 | 5.5532 | 0.77694 | 3.9593 | 10.2894 | 13.19% | 1.845% | 9.401% | 24.43%
A | A, B North | garvagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 50 | 144.6359 | 67.6632 | 33.4855 | 2.5772 | 40.91 | 76.9727 | 23.15% | 1.782% | 28.28% | 53.22%
A | A, B North | garvagh | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 40 | 42.117 | 33.0549 | 6.3886 | 0.30798 | 2.3655 | 9.0621 | 15.17% | 0.7313% | 5.617% | 21.52%
K | H2 & K | butlerstown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 22.4466 | 26.2808 | 22.029 | 3.6415 | 0.48852 | 0.12171 | 4.2517 | 13.86% | 1.859% | 0.4631% | 16.18%
A | A, B North | garvagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 66 | 190.9193 | 120.495 | 32.1464 | 0.60609 | 37.6718 | 70.4243 | 16.84% | 0.3175% | 19.73% | 36.89%
A | A, B North | garvagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 48 | 138.8505 | 137.6146 | 0 | 1.2359 | 0 | 1.2359 | 0% | 0.8901% | 0% | 0.8901%
K | H2 & K | butlerstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 22.4466 | 26.2808 | 18.8122 | 5.982 | 0.55866 | 0.92786 | 7.4685 | 22.76% | 2.126% | 3.531% | 28.42%
A | A, B North | garvagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 40 | 42.117 | 33.9227 | 6.3886 | 0.30798 | 1.4977 | 8.1943 | 15.17% | 0.7313% | 3.556% | 19.46%
A | A, B North | garvagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 66 | 190.9193 | 106.6069 | 56.4192 | 1.1052 | 26.788 | 84.3124 | 29.55% | 0.5789% | 14.03% | 44.16%
K | H2 & K | butlerstown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 22.4466 | 26.2808 | 19.72 | 5.1435 | 0.4969 | 0.92039 | 6.5608 | 19.57% | 1.891% | 3.502% | 24.96%
A | A, B North | garvagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 48 | 138.8505 | 136.4563 | 0 | 2.3942 | 0 | 2.3942 | 0% | 1.724% | 0% | 1.724%
A | A, B North | garvagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 40 | 42.117 | 31.2795 | 9.0849 | 0.36185 | 1.3907 | 10.8375 | 21.57% | 0.8592% | 3.302% | 25.73%
K | H2 & K | butlerstown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 22.4466 | 26.2808 | 20.6673 | 4.4183 | 0.49694 | 0.69827 | 5.6135 | 16.81% | 1.891% | 2.657% | 21.36%
A | A, B North | garvagh | 2035 | 100% ECP | Grandfathering | IE wind not priority | 82 | 237.2029 | 130.9317 | 44.1747 | 0.83669 | 61.2598 | 106.2712 | 18.62% | 0.3527% | 25.83% | 44.8%
A | A, B North | garvagh | 2035 | 100% ECP | Grandfathering | IE wind priority | 48 | 138.8505 | 137.4462 | 0 | 1.4043 | 0 | 1.4043 | 0% | 1.011% | 0% | 1.011%
A | A, B North | garvagh | 2035 | 66% ECP | Grandfathering | IE wind priority | 48 | 138.8505 | 137.6146 | 0 | 1.2359 | 0 | 1.2359 | 0% | 0.8901% | 0% | 0.8901%
K | H2 & K | butlerstown | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 22.4466 | 26.2808 | 21.1976 | 3.6415 | 0.48852 | 0.95313 | 5.0832 | 13.86% | 1.859% | 3.627% | 19.34%
K | H2 & K | butlerstown | 2030 | Initial | Grandfathering | IE Solar not priority | 3.95 | 4.6247 | 3.8565 | 0.38249 | 0.05959 | 0.32611 | 0.76819 | 8.271% | 1.289% | 7.052% | 16.61%
A | A, B North | golagh | 2030 | Initial | Grandfathering | IE wind not priority | 48 | 138.8505 | 66.5823 | 17.2739 | 2.4971 | 52.4972 | 72.2681 | 12.44% | 1.798% | 37.81% | 52.05%
A | A, B North | golagh | 2030 | 33% ECP | Grandfathering | IE wind not priority | 48 | 138.8505 | 67.6737 | 23.533 | 2.4595 | 45.1843 | 71.1768 | 16.95% | 1.771% | 32.54% | 51.26%
J | J Country | timahoe | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 683 | 875.119 | 320.9121 | 192.4201 | 7.9307 | 353.8562 | 554.207 | 21.99% | 0.9062% | 40.44% | 63.33%
A | A, B North | golagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 48 | 138.8505 | 64.9567 | 32.1461 | 2.4741 | 39.2737 | 73.8938 | 23.15% | 1.782% | 28.28% | 53.22%
A | A, B North | golagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 48 | 138.8505 | 61.3606 | 40.7719 | 2.4661 | 34.2518 | 77.4898 | 29.36% | 1.776% | 24.67% | 55.81%
J | J Country | timahoe | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 478.6663 | 613.3089 | 287.3091 | 134.7479 | 5.2399 | 186.0119 | 325.9997 | 21.97% | 0.8544% | 30.33% | 53.15%
A | A, B North | golagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 48 | 138.8505 | 56.7343 | 43.6778 | 2.4824 | 35.9559 | 82.1161 | 31.46% | 1.788% | 25.9% | 59.14%
A | A, B North | golagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 48 | 138.8505 | 72.8689 | 23.533 | 2.4595 | 39.9891 | 65.9816 | 16.95% | 1.771% | 28.8% | 47.52%
A | A, B North | garvagh | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 40 | 42.117 | 30.6196 | 9.2339 | 0.38692 | 1.8766 | 11.4974 | 21.92% | 0.9187% | 4.456% | 27.3%
K | H2 & K | butlerstown | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 59.44 | 69.5929 | 45.0973 | 22.0857 | 1.5276 | 0.88244 | 24.4957 | 31.74% | 2.195% | 1.268% | 35.2%
A | A, B North | garvagh | 2035 | 66% ECP | Grandfathering | IE wind not priority | 66 | 190.9193 | 115.913 | 32.1464 | 0.60609 | 42.2538 | 75.0063 | 16.84% | 0.3175% | 22.13% | 39.29%
A | A, B North | garvagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 48 | 138.8505 | 133.8844 | 0 | 4.9661 | 0 | 4.9661 | 0% | 3.577% | 0% | 3.577%
K | H2 & K | cullenagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 16.0734 | 4.1383 | 0.39517 | 0.74787 | 5.2813 | 19.38% | 1.851% | 3.502% | 24.73%
A | A, B North | garvagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 40 | 42.117 | 31.1379 | 6.7492 | 0.78987 | 3.44 | 10.9791 | 16.02% | 1.875% | 8.168% | 26.07%
A | A, B North | garvagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 50 | 144.6359 | 63.9173 | 42.4707 | 2.5688 | 35.679 | 80.7186 | 29.36% | 1.776% | 24.67% | 55.81%
K | H2 & K | cullenagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 16.8494 | 3.5395 | 0.39845 | 0.56739 | 4.5054 | 16.57% | 1.866% | 2.657% | 21.1%
A | A, B North | garvagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 48 | 138.8505 | 133.4056 | 0 | 5.4449 | 0 | 5.4449 | 0% | 3.921% | 0% | 3.921%
A | A, B North | garvagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 40 | 42.117 | 30.3247 | 7.8962 | 0.78404 | 3.112 | 11.7923 | 18.75% | 1.862% | 7.389% | 28%
K | H2 & K | cullenagh | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 17.283 | 2.9018 | 0.39547 | 0.77448 | 4.0718 | 13.59% | 1.852% | 3.627% | 19.07%
A | A, B North | garvagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 50 | 144.6359 | 59.0983 | 45.4977 | 2.5859 | 37.454 | 85.5376 | 31.46% | 1.788% | 25.9% | 59.14%
A | A, B North | garvagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 48 | 138.8505 | 133.3124 | 0 | 5.5381 | 0 | 5.5381 | 0% | 3.989% | 0% | 3.989%
A | A, B North | garvagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 40 | 42.117 | 28.8438 | 9.2691 | 0.88022 | 3.1239 | 13.2732 | 22.01% | 2.09% | 7.417% | 31.52%
A | A, B North | garvagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 50 | 144.6359 | 75.9051 | 24.5136 | 2.5619 | 41.6553 | 68.7308 | 16.95% | 1.771% | 28.8% | 47.52%
K | H2 & K | butlerstown | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 59.44 | 69.5929 | 50.9644 | 15.6721 | 0.62808 | 2.3284 | 18.6286 | 22.52% | 0.9025% | 3.346% | 26.77%
A | A, B North | garvagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 48 | 138.8505 | 134.4016 | 0 | 4.4489 | 0 | 4.4489 | 0% | 3.204% | 0% | 3.204%
A | A, B North | garvagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 40 | 42.117 | 32.1066 | 5.5532 | 0.77694 | 3.6802 | 10.0104 | 13.19% | 1.845% | 8.738% | 23.77%
K | H2 & K | butlerstown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 40.9433 | 47.9368 | 35.1169 | 10.7556 | 0.41259 | 1.6517 | 12.8199 | 22.44% | 0.8607% | 3.445% | 26.74%
A | A, B North | garvagh | 2030 | 100% ECP | Grandfathering | IE wind not priority | 82 | 237.2029 | 95.5214 | 65.4789 | 4.0756 | 72.1271 | 141.6815 | 27.6% | 1.718% | 30.41% | 59.73%
A | A, B North | garvagh | 2030 | 100% ECP | Grandfathering | IE wind priority | 48 | 138.8505 | 133.6706 | 0 | 5.1799 | 0 | 5.1799 | 0% | 3.731% | 0% | 3.731%
K | H2 & K | butlerstown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 40.9433 | 47.9368 | 39.3732 | 7.6105 | 0.35183 | 0.60134 | 8.5636 | 15.88% | 0.7339% | 1.254% | 17.86%
A | A, B North | garvagh | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 40 | 42.117 | 26.1871 | 13.1608 | 0.92465 | 1.8444 | 15.9299 | 31.25% | 2.195% | 4.379% | 37.82%
A | A, B North | garvagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 82 | 237.2029 | 100.378 | 65.4789 | 4.0756 | 67.2704 | 136.8249 | 27.6% | 1.718% | 28.36% | 57.68%
K | H2 & K | butlerstown | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 40.9433 | 47.9368 | 38.1167 | 7.6105 | 0.35183 | 1.8579 | 9.8202 | 15.88% | 0.7339% | 3.876% | 20.49%
A | A, B North | garvagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 48 | 138.8505 | 133.6706 | 0 | 5.1799 | 0 | 5.1799 | 0% | 3.731% | 0% | 3.731%
A | A, B North | garvagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 40 | 42.117 | 26.293 | 13.1608 | 0.92465 | 1.7386 | 15.824 | 31.25% | 2.195% | 4.128% | 37.57%
K | H2 & K | butlerstown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 59.44 | 69.5929 | 45.9123 | 22.0857 | 1.5276 | 0.067415 | 23.6807 | 31.74% | 2.195% | 0.09687% | 34.03%
K | H2 & K | cullenagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 15.3398 | 4.8138 | 0.44721 | 0.75394 | 6.015 | 22.54% | 2.094% | 3.531% | 28.17%
J | J Country | timahoe | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 478.6663 | 613.3089 | 302.1207 | 93.9471 | 4.4219 | 212.8192 | 311.1882 | 15.32% | 0.721% | 34.7% | 50.74%
A | A, B North | corderry | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 23.0833 | 66.7736 | 31.2378 | 15.4591 | 1.1898 | 18.8868 | 35.5357 | 23.15% | 1.782% | 28.28% | 53.22%
A | A, B North | corderry | 2030 | 33% ECP | Grandfathering | IE wind priority | 45.655 | 132.0671 | 127.8355 | 0 | 4.2315 | 0 | 4.2315 | 0% | 3.204% | 0% | 3.204%
A | A, B North | arigna | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 1 | 2.8927 | 1.8257 | 0.48707 | 0.0091832 | 0.57078 | 1.067 | 16.84% | 0.3175% | 19.73% | 36.89%
K | H2 & K | woodhouse | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 20 | 60.6801 | 58.4204 | 0 | 2.2597 | 0 | 2.2597 | 0% | 3.724% | 0% | 3.724%
A | A, B North | arigna | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 1 | 2.8927 | 1.6153 | 0.85484 | 0.016746 | 0.40588 | 1.2775 | 29.55% | 0.5789% | 14.03% | 44.16%
A | A, B North | arigna | 2035 | 100% ECP | Grandfathering | IE wind not priority | 1.5 | 4.3391 | 2.3951 | 0.80807 | 0.015305 | 1.1206 | 1.944 | 18.62% | 0.3527% | 25.83% | 44.8%
K | H2 & K | woodhouse | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 227 | 688.7191 | 484.3978 | 188.3764 | 11.9538 | 3.9911 | 204.3213 | 27.35% | 1.736% | 0.5795% | 29.67%
A | A, B North | binbane | 2030 | Initial | Grandfathering | IE wind not priority | 23.6 | 68.2682 | 32.7363 | 8.493 | 1.2277 | 25.8111 | 35.5318 | 12.44% | 1.798% | 37.81% | 52.05%
K | H2 & K | woodhouse | 2030 | 100% ECP | Grandfathering | IE wind priority | 20 | 60.6801 | 58.4204 | 0 | 2.2597 | 0 | 2.2597 | 0% | 3.724% | 0% | 3.724%
A | A, B North | binbane | 2030 | Initial | Grandfathering | IE wind priority | 35.54 | 102.8072 | 99.8821 | 0 | 2.9251 | 0 | 2.9251 | 0% | 2.845% | 0% | 2.845%
A | A, B North | binbane | 2030 | 33% ECP | Grandfathering | IE wind not priority | 30.1333 | 87.1672 | 42.484 | 14.7735 | 1.544 | 28.3657 | 44.6832 | 16.95% | 1.771% | 32.54% | 51.26%
K | H2 & K | woodhouse | 2030 | 100% ECP | Grandfathering | IE wind not priority | 227 | 688.7191 | 473.1804 | 188.3764 | 11.9538 | 15.2085 | 215.5388 | 27.35% | 1.736% | 2.208% | 31.3%
A | A, B North | binbane | 2030 | 33% ECP | Grandfathering | IE wind priority | 35.54 | 102.8072 | 99.5132 | 0 | 3.294 | 0 | 3.294 | 0% | 3.204% | 0% | 3.204%
A | A, B North | binbane | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 30.1333 | 87.1672 | 40.7783 | 20.1806 | 1.5532 | 24.6551 | 46.3889 | 23.15% | 1.782% | 28.28% | 53.22%
A | A, B North | arigna | 2035 | 66% ECP | Grandfathering | IE wind not priority | 1 | 2.8927 | 1.7563 | 0.48707 | 0.0091832 | 0.64021 | 1.1365 | 16.84% | 0.3175% | 22.13% | 39.29%
K | H2 & K | woodhouse | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 20 | 60.6801 | 58.8181 | 0 | 1.862 | 0 | 1.862 | 0% | 3.069% | 0% | 3.069%
A | A, B North | binbane | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 30.1333 | 87.1672 | 38.5208 | 25.5957 | 1.5482 | 21.5025 | 48.6464 | 29.36% | 1.776% | 24.67% | 55.81%
K | H2 & K | woodhouse | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 98.3333 | 298.3436 | 241.173 | 49.3703 | 5.021 | 2.7794 | 57.1706 | 16.55% | 1.683% | 0.9316% | 19.16%
A | A, B North | binbane | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 35.54 | 102.8072 | 98.7757 | 0 | 4.0315 | 0 | 4.0315 | 0% | 3.921% | 0% | 3.921%
A | A, B North | binbane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 30.1333 | 87.1672 | 35.6166 | 27.42 | 1.5584 | 22.5723 | 51.5507 | 31.46% | 1.788% | 25.9% | 59.14%
K | H2 & K | woodhouse | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 20 | 60.6801 | 58.2692 | 0 | 2.4109 | 0 | 2.4109 | 0% | 3.973% | 0% | 3.973%
A | A, B North | binbane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 35.54 | 102.8072 | 98.7067 | 0 | 4.1005 | 0 | 4.1005 | 0% | 3.989% | 0% | 3.989%
A | A, B North | binbane | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 30.1333 | 87.1672 | 45.7455 | 14.7735 | 1.544 | 25.1043 | 41.4218 | 16.95% | 1.771% | 28.8% | 47.52%
K | H2 & K | woodhouse | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 98.3333 | 298.3436 | 178.69 | 94.5218 | 5.3046 | 19.8273 | 119.6536 | 31.68% | 1.778% | 6.646% | 40.11%
A | A, B North | binbane | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 35.54 | 102.8072 | 99.5132 | 0 | 3.294 | 0 | 3.294 | 0% | 3.204% | 0% | 3.204%
A | A, B North | binbane | 2030 | 100% ECP | Grandfathering | IE wind not priority | 43.2 | 124.9654 | 50.3234 | 34.4962 | 2.1472 | 37.9986 | 74.642 | 27.6% | 1.718% | 30.41% | 59.73%
K | H2 & K | woodhouse | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 20 | 60.6801 | 58.3055 | 0 | 2.3746 | 0 | 2.3746 | 0% | 3.913% | 0% | 3.913%
A | A, B North | binbane | 2030 | 100% ECP | Grandfathering | IE wind priority | 35.54 | 102.8072 | 98.9719 | 0 | 3.8353 | 0 | 3.8353 | 0% | 3.731% | 0% | 3.731%
A | A, B North | binbane | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 43.2 | 124.9654 | 52.8821 | 34.4962 | 2.1472 | 35.44 | 72.0834 | 27.6% | 1.718% | 28.36% | 57.68%
A | A, B North | binbane | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 35.54 | 102.8072 | 99.1302 | 0 | 3.677 | 0 | 3.677 | 0% | 3.577% | 0% | 3.577%
A | A, B North | arigna | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 1.5 | 4.3391 | 1.8362 | 1.1978 | 0.074554 | 1.2306 | 2.5029 | 27.6% | 1.718% | 28.36% | 57.68%
A | A, B North | ardnagappary | 2030 | 33% ECP | Grandfathering | IE wind not priority | 20.96 | 60.6314 | 29.5509 | 10.2761 | 1.074 | 19.7305 | 31.0805 | 16.95% | 1.771% | 32.54% | 51.26%
A | A, B North | ardnagappary | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 20.96 | 60.6314 | 28.3644 | 14.0371 | 1.0803 | 17.1495 | 32.267 | 23.15% | 1.782% | 28.28% | 53.22%
A | A, B North | ardnagappary | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 20.96 | 60.6314 | 26.7941 | 17.8037 | 1.0769 | 14.9566 | 33.8372 | 29.36% | 1.776% | 24.67% | 55.81%
K | H2 & K | woodhouse | 2035 | 100% ECP | Grandfathering | IE wind priority | 20 | 60.6801 | 60.0875 | 0 | 0.59265 | 0 | 0.59265 | 0% | 0.9767% | 0% | 0.9767%
A | A, B North | ardnagappary | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 20.96 | 60.6314 | 24.774 | 19.0727 | 1.084 | 15.7007 | 35.8574 | 31.46% | 1.788% | 25.9% | 59.14%
A | A, B North | ardnagappary | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 20.96 | 60.6314 | 31.8194 | 10.2761 | 1.074 | 17.4619 | 28.812 | 16.95% | 1.771% | 28.8% | 47.52%
K | H2 & K | woodhouse | 2035 | 100% ECP | Grandfathering | IE wind not priority | 227 | 688.7191 | 511.2759 | 124.3047 | 2.348 | 50.7906 | 177.4432 | 18.05% | 0.3409% | 7.375% | 25.76%
A | A, B North | ardnagappary | 2030 | 100% ECP | Grandfathering | IE wind not priority | 26.96 | 77.9877 | 31.4056 | 21.5282 | 1.34 | 23.714 | 46.5821 | 27.6% | 1.718% | 30.41% | 59.73%
A | A, B North | ardnagappary | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 26.96 | 77.9877 | 33.0023 | 21.5282 | 1.34 | 22.1172 | 44.9854 | 27.6% | 1.718% | 28.36% | 57.68%
K | H2 & K | woodhouse | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 20 | 60.6801 | 59.6188 | 0 | 1.0613 | 0 | 1.0613 | 0% | 1.749% | 0% | 1.749%
A | A, B North | ardnagappary | 2035 | 66% ECP | Grandfathering | IE wind not priority | 23.96 | 69.3095 | 42.08 | 11.6701 | 0.22003 | 15.3394 | 27.2296 | 16.84% | 0.3175% | 22.13% | 39.29%
K | H2 & K | woodhouse | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 162.6665 | 493.5311 | 312.1853 | 148.2773 | 3.067 | 30.0015 | 181.3458 | 30.04% | 0.6214% | 6.079% | 36.74%
A | A, B North | ardnagappary | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 23.96 | 69.3095 | 43.7433 | 11.6701 | 0.22003 | 13.676 | 25.5662 | 16.84% | 0.3175% | 19.73% | 36.89%
A | A, B North | ardnagappary | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 23.96 | 69.3095 | 38.7015 | 20.4819 | 0.40124 | 9.7249 | 30.608 | 29.55% | 0.5789% | 14.03% | 44.16%
K | H2 & K | woodhouse | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 20 | 60.6801 | 60.1493 | 0 | 0.53078 | 0 | 0.53078 | 0% | 0.8747% | 0% | 0.8747%
A | A, B North | ardnagappary | 2035 | 100% ECP | Grandfathering | IE wind not priority | 26.96 | 77.9877 | 43.0478 | 14.5238 | 0.27509 | 20.141 | 34.9399 | 18.62% | 0.3527% | 25.83% | 44.8%
K | H2 & K | woodhouse | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 162.6665 | 493.5311 | 392.1361 | 79.9587 | 1.5935 | 19.8427 | 101.395 | 16.2% | 0.3229% | 4.021% | 20.54%
A | A, B North | arigna | 2030 | 33% ECP | Grandfathering | IE wind not priority | 0.5 | 1.4464 | 0.70493 | 0.24514 | 0.025619 | 0.47067 | 0.74142 | 16.95% | 1.771% | 32.54% | 51.26%
A | A, B North | arigna | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 0.5 | 1.4464 | 0.67663 | 0.33485 | 0.025772 | 0.4091 | 0.76973 | 23.15% | 1.782% | 28.28% | 53.22%
K | H2 & K | woodhouse | 2035 | 66% ECP | Grandfathering | IE wind priority | 20 | 60.6801 | 60.1493 | 0 | 0.53078 | 0 | 0.53078 | 0% | 0.8747% | 0% | 0.8747%
A | A, B North | arigna | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 0.5 | 1.4464 | 0.63917 | 0.42471 | 0.025688 | 0.35679 | 0.80719 | 29.36% | 1.776% | 24.67% | 55.81%
A | A, B North | arigna | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 0.5 | 1.4464 | 0.59098 | 0.45498 | 0.025859 | 0.37454 | 0.85538 | 31.46% | 1.788% | 25.9% | 59.14%
K | H2 & K | woodhouse | 2035 | 66% ECP | Grandfathering | IE wind not priority | 162.6665 | 493.5311 | 381.7717 | 79.9587 | 1.5935 | 30.2071 | 111.7594 | 16.2% | 0.3229% | 6.121% | 22.64%
A | A, B North | arigna | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 0.5 | 1.4464 | 0.75905 | 0.24514 | 0.025619 | 0.41655 | 0.68731 | 16.95% | 1.771% | 28.8% | 47.52%
A | A, B North | arigna | 2030 | 100% ECP | Grandfathering | IE wind not priority | 1.5 | 4.3391 | 1.7473 | 1.1978 | 0.074554 | 1.3194 | 2.5917 | 27.6% | 1.718% | 30.41% | 59.73%
K | H2 & K | woodhouse | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 98.3333 | 298.3436 | 189.1538 | 88.3257 | 5.2823 | 15.5819 | 109.1899 | 29.61% | 1.771% | 5.223% | 36.6%
K | H2 & K | dungarvan | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 131.94 | 154.4767 | 113.1265 | 34.7876 | 1.3942 | 5.1685 | 41.3502 | 22.52% | 0.9025% | 3.346% | 26.77%
A | A, B North | binbane | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 35.54 | 102.8072 | 98.9719 | 0 | 3.8353 | 0 | 3.8353 | 0% | 3.731% | 0% | 3.731%
K | H2 & K | woodhouse | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 20 | 60.6801 | 58.5525 | 0 | 2.1276 | 0 | 2.1276 | 0% | 3.506% | 0% | 3.506%
A | A, B North | cathaleen's fall | 2030 | 100% ECP | Grandfathering | IE wind not priority | 37.5 | 108.4769 | 43.6835 | 29.9446 | 1.8638 | 32.9849 | 64.7934 | 27.6% | 1.718% | 30.41% | 59.73%
A | A, B North | cathaleen's fall | 2030 | 100% ECP | Grandfathering | IE wind priority | 17.5 | 50.6226 | 48.7341 | 0 | 1.8885 | 0 | 1.8885 | 0% | 3.731% | 0% | 3.731%
K | H2 & K | rathnaskilloge | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 95 | 111.227 | 73.3793 | 35.2984 | 2.4414 | 0.10775 | 37.8476 | 31.74% | 2.195% | 0.09687% | 34.03%
A | A, B North | cathaleen's fall | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 37.5 | 108.4769 | 45.9046 | 29.9446 | 1.8638 | 30.7639 | 62.5724 | 27.6% | 1.718% | 28.36% | 57.68%
A | A, B North | cathaleen's fall | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 17.5 | 50.6226 | 48.7341 | 0 | 1.8885 | 0 | 1.8885 | 0% | 3.731% | 0% | 3.731%
K | H2 & K | rathnaskilloge | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 95 | 111.227 | 72.0767 | 35.2984 | 2.4414 | 1.4104 | 39.1502 | 31.74% | 2.195% | 1.268% | 35.2%
K | H2 & K | rathnaskilloge | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 95 | 111.227 | 93.2325 | 15.4118 | 2.0676 | 0.51509 | 17.9944 | 13.86% | 1.859% | 0.4631% | 16.18%
A | A, B North | cathaleen's fall | 2035 | 66% ECP | Grandfathering | IE wind not priority | 25 | 72.3179 | 43.9064 | 12.1767 | 0.22958 | 16.0052 | 28.4115 | 16.84% | 0.3175% | 22.13% | 39.29%
A | A, B North | cathaleen's fall | 2035 | 66% ECP | Grandfathering | IE wind priority | 17.5 | 50.6226 | 50.172 | 0 | 0.45059 | 0 | 0.45059 | 0% | 0.8901% | 0% | 0.8901%
K | H2 & K | rathnaskilloge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 95 | 111.227 | 79.6182 | 25.3174 | 2.3644 | 3.9269 | 31.6087 | 22.76% | 2.126% | 3.531% | 28.42%
A | A, B North | cathaleen's fall | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 25 | 72.3179 | 45.642 | 12.1767 | 0.22958 | 14.2696 | 26.6759 | 16.84% | 0.3175% | 19.73% | 36.89%
A | A, B North | cathaleen's fall | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 17.5 | 50.6226 | 50.172 | 0 | 0.45059 | 0 | 0.45059 | 0% | 0.8901% | 0% | 0.8901%
A | A, B North | cathaleen's fall | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 25 | 72.3179 | 40.3814 | 21.3709 | 0.41865 | 10.147 | 31.9365 | 29.55% | 0.5789% | 14.03% | 44.16%
A | A, B North | cathaleen's fall | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 17.5 | 50.6226 | 49.7497 | 0 | 0.87288 | 0 | 0.87288 | 0% | 1.724% | 0% | 1.724%
K | H2 & K | rathnaskilloge | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 95 | 111.227 | 87.4692 | 18.6993 | 2.1032 | 2.9553 | 23.7577 | 16.81% | 1.891% | 2.657% | 21.36%
A | A, B North | cathaleen's fall | 2035 | 100% ECP | Grandfathering | IE wind not priority | 37.5 | 108.4769 | 59.8773 | 20.2018 | 0.38263 | 28.0152 | 48.5996 | 18.62% | 0.3527% | 25.83% | 44.8%
A | A, B North | cathaleen's fall | 2035 | 100% ECP | Grandfathering | IE wind priority | 17.5 | 50.6226 | 50.1106 | 0 | 0.51197 | 0 | 0.51197 | 0% | 1.011% | 0% | 1.011%
K | H2 & K | rathnaskilloge | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 95 | 111.227 | 89.7137 | 15.4118 | 2.0676 | 4.0339 | 21.5133 | 13.86% | 1.859% | 3.627% | 19.34%
K | H2 & K | rathnaskilloge | 2030 | Initial | Grandfathering | IE Solar not priority | 95 | 111.227 | 92.7514 | 9.1991 | 1.4332 | 7.8433 | 18.4755 | 8.271% | 1.289% | 7.052% | 16.61%
A | A, B North | corderry | 2030 | Initial | Grandfathering | IE wind not priority | 16.35 | 47.2959 | 22.6796 | 5.8839 | 0.85057 | 17.8818 | 24.6163 | 12.44% | 1.798% | 37.81% | 52.05%
A | A, B North | corderry | 2030 | Initial | Grandfathering | IE wind priority | 45.655 | 132.0671 | 128.3094 | 0 | 3.7576 | 0 | 3.7576 | 0% | 2.845% | 0% | 2.845%
A | A, B North | corderry | 2030 | 33% ECP | Grandfathering | IE wind not priority | 23.0833 | 66.7736 | 32.5445 | 11.3171 | 1.1828 | 21.7292 | 34.2291 | 16.95% | 1.771% | 32.54% | 51.26%
K | H2 & K | rathnaskilloge | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 95 | 111.227 | 83.4599 | 21.7687 | 2.103 | 3.8953 | 27.767 | 19.57% | 1.891% | 3.502% | 24.96%
A | A, B North | cathaleen's fall | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 17.5 | 50.6226 | 49.0006 | 0 | 1.622 | 0 | 1.622 | 0% | 3.204% | 0% | 3.204%
A | A, B North | cathaleen's fall | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 12.5 | 36.1589 | 18.9763 | 6.1284 | 0.64048 | 10.4138 | 17.1827 | 16.95% | 1.771% | 28.8% | 47.52%
K | H2 & K | rathnaskilloge | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 95 | 111.227 | 88.4414 | 17.6584 | 0.81635 | 4.3108 | 22.7855 | 15.88% | 0.7339% | 3.876% | 20.49%
A | A, B North | binbane | 2035 | 66% ECP | Grandfathering | IE wind not priority | 36.6667 | 106.0663 | 64.3961 | 17.8591 | 0.33672 | 23.4743 | 41.6702 | 16.84% | 0.3175% | 22.13% | 39.29%
K | H2 & K | woodhouse | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 98.3333 | 298.3436 | 217.2915 | 67.8483 | 5.2314 | 7.9725 | 81.0522 | 22.74% | 1.753% | 2.672% | 27.17%
A | A, B North | binbane | 2035 | 66% ECP | Grandfathering | IE wind priority | 35.54 | 102.8072 | 101.8921 | 0 | 0.91508 | 0 | 0.91508 | 0% | 0.8901% | 0% | 0.8901%
A | A, B North | binbane | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 36.6667 | 106.0663 | 66.9417 | 17.8591 | 0.33672 | 20.9288 | 39.1246 | 16.84% | 0.3175% | 19.73% | 36.89%
K | H2 & K | woodhouse | 2030 | 33% ECP | Grandfathering | IE wind priority | 20 | 60.6801 | 58.8181 | 0 | 1.862 | 0 | 1.862 | 0% | 3.069% | 0% | 3.069%
A | A, B North | binbane | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 35.54 | 102.8072 | 101.8921 | 0 | 0.91508 | 0 | 0.91508 | 0% | 0.8901% | 0% | 0.8901%
A | A, B North | binbane | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 36.6667 | 106.0663 | 59.2261 | 31.344 | 0.61402 | 14.8822 | 46.8402 | 29.55% | 0.5789% | 14.03% | 44.16%
K | H2 & K | woodhouse | 2030 | 33% ECP | Grandfathering | IE wind not priority | 98.3333 | 298.3436 | 229.1719 | 49.3703 | 5.021 | 14.7804 | 69.1717 | 16.55% | 1.683% | 4.954% | 23.19%
A | A, B North | binbane | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 35.54 | 102.8072 | 101.0345 | 0 | 1.7727 | 0 | 1.7727 | 0% | 1.724% | 0% | 1.724%
A | A, B North | binbane | 2035 | 100% ECP | Grandfathering | IE wind not priority | 43.2 | 124.9654 | 68.9787 | 23.2725 | 0.44079 | 32.2735 | 55.9868 | 18.62% | 0.3527% | 25.83% | 44.8%
K | H2 & K | woodhouse | 2030 | Initial | Grandfathering | IE wind priority | 20 | 60.6801 | 59.0229 | 0 | 1.6572 | 0 | 1.6572 | 0% | 2.731% | 0% | 2.731%
A | A, B North | binbane | 2035 | 100% ECP | Grandfathering | IE wind priority | 35.54 | 102.8072 | 101.7675 | 0 | 1.0397 | 0 | 1.0397 | 0% | 1.011% | 0% | 1.011%
K | H2 & K | woodhouse | 2030 | Initial | Grandfathering | IE wind not priority | 34 | 103.1562 | 61.3367 | 12.5345 | 1.7729 | 27.512 | 41.8195 | 12.15% | 1.719% | 26.67% | 40.54%
A | A, B North | cathaleen's fall | 2030 | Initial | Grandfathering | IE wind priority | 17.5 | 50.6226 | 49.1822 | 0 | 1.4403 | 0 | 1.4403 | 0% | 2.845% | 0% | 2.845%
A | A, B North | cathaleen's fall | 2030 | 33% ECP | Grandfathering | IE wind not priority | 12.5 | 36.1589 | 17.6233 | 6.1284 | 0.64048 | 11.7667 | 18.5356 | 16.95% | 1.771% | 32.54% | 51.26%
A | A, B North | cathaleen's fall | 2030 | 33% ECP | Grandfathering | IE wind priority | 17.5 | 50.6226 | 49.0006 | 0 | 1.622 | 0 | 1.622 | 0% | 3.204% | 0% | 3.204%
K | H2 & K | rathnaskilloge | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 95 | 111.227 | 81.4538 | 25.0479 | 1.0038 | 3.7214 | 29.7731 | 22.52% | 0.9025% | 3.346% | 26.77%
A | A, B North | cathaleen's fall | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 12.5 | 36.1589 | 16.9158 | 8.3714 | 0.64429 | 10.2275 | 19.2432 | 23.15% | 1.782% | 28.28% | 53.22%
A | A, B North | cathaleen's fall | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 17.5 | 50.6226 | 48.812 | 0 | 1.8106 | 0 | 1.8106 | 0% | 3.577% | 0% | 3.577%
K | H2 & K | rathnaskilloge | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 95 | 111.227 | 81.4812 | 24.9561 | 0.95733 | 3.8323 | 29.7458 | 22.44% | 0.8607% | 3.445% | 26.74%
A | A, B North | cathaleen's fall | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 12.5 | 36.1589 | 15.9793 | 10.6177 | 0.64221 | 8.9197 | 20.1796 | 29.36% | 1.776% | 24.67% | 55.81%
A | A, B North | cathaleen's fall | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 17.5 | 50.6226 | 48.6375 | 0 | 1.9851 | 0 | 1.9851 | 0% | 3.921% | 0% | 3.921%
K | H2 & K | rathnaskilloge | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 95 | 111.227 | 91.3569 | 17.6584 | 0.81635 | 1.3953 | 19.8701 | 15.88% | 0.7339% | 1.254% | 17.86%
A | A, B North | cathaleen's fall | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 12.5 | 36.1589 | 14.7746 | 11.3744 | 0.64646 | 9.3635 | 21.3844 | 31.46% | 1.788% | 25.9% | 59.14%
A | A, B North | cathaleen's fall | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 17.5 | 50.6226 | 48.6035 | 0 | 2.0191 | 0 | 2.0191 | 0% | 3.989% | 0% | 3.989%
J | J Country | newbridge | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 12 | 15.3754 | 10.6656 | 2.0893 | 0.28474 | 2.3358 | 4.7098 | 13.59% | 1.852% | 15.19% | 30.63%
A | A, B North | golagh | 2030 | 100% ECP | Grandfathering | IE wind not priority | 48 | 138.8505 | 55.9149 | 38.3291 | 2.3857 | 42.2207 | 82.9355 | 27.6% | 1.718% | 30.41% | 59.73%
J | J Country | timahoe | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 478.6663 | 613.3089 | 284.1765 | 93.9471 | 4.4219 | 230.7633 | 329.1323 | 15.32% | 0.721% | 37.63% | 53.67%
A | G North | gortawee | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 1.4 | 4.0498 | 2.653 | 1.2739 | 0.072404 | 0.050462 | 1.3968 | 31.46% | 1.788% | 1.246% | 34.49%
J | J Country | philipstown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 33.3333 | 42.7095 | 20.0076 | 9.3836 | 0.3649 | 12.9535 | 22.7019 | 21.97% | 0.8544% | 30.33% | 53.15%
A | G North | gortawee | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 1.6667 | 1.7549 | 1.319 | 0.38621 | 0.036676 | 0.012955 | 0.43584 | 22.01% | 2.09% | 0.7382% | 24.84%
A | G North | gortawee | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 1.4 | 4.0498 | 3.2745 | 0.68638 | 0.071734 | 0.017154 | 0.77527 | 16.95% | 1.771% | 0.4236% | 19.14%
J | J Country | philipstown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 50 | 154.1991 | 88.9312 | 50.8289 | 0.99539 | 13.4435 | 65.2678 | 32.96% | 0.6455% | 8.718% | 42.33%
A | G North | gortawee | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 1.6667 | 1.7549 | 1.4907 | 0.23138 | 0.032372 | 0.00043816 | 0.26419 | 13.19% | 1.845% | 0.02497% | 15.05%
A | G North | gortawee | 2030 | 100% ECP | Grandfathering | IE wind not priority | 4.2 | 12.1494 | 8.0644 | 3.3538 | 0.20875 | 0.52251 | 4.0851 | 27.6% | 1.718% | 4.301% | 33.62%
J | J Country | philipstown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 33.3333 | 42.7095 | 21.039 | 6.5423 | 0.30793 | 14.8203 | 21.6705 | 15.32% | 0.721% | 34.7% | 50.74%
A | G North | gortawee | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 5 | 5.2646 | 3.4267 | 1.6451 | 0.11558 | 0.077227 | 1.8379 | 31.25% | 2.195% | 1.467% | 34.91%
A | G North | gortawee | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 4.2 | 12.1494 | 8.5479 | 3.3538 | 0.20875 | 0.038979 | 3.6015 | 27.6% | 1.718% | 0.3208% | 29.64%
J | J Country | philipstown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 50 | 154.1991 | 94.1426 | 28.5284 | 0.54092 | 30.9872 | 60.0565 | 18.5% | 0.3508% | 20.1% | 38.95%
A | G North | gortawee | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 5 | 5.2646 | 3.497 | 1.6451 | 0.11558 | 0.0069198 | 1.7676 | 31.25% | 2.195% | 0.1314% | 33.58%
A | G North | gortawee | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 1.6667 | 1.7549 | 1.3786 | 0.32901 | 0.032668 | 0.014615 | 0.37629 | 18.75% | 1.862% | 0.8328% | 21.44%
J | J Country | philipstown | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 33.3333 | 42.7095 | 19.7895 | 6.5423 | 0.30793 | 16.0699 | 22.9201 | 15.32% | 0.721% | 37.63% | 53.67%
A | G North | gortawee | 2035 | 66% ECP | Grandfathering | IE wind not priority | 2.8 | 8.0996 | 6.5889 | 1.3638 | 0.025713 | 0.12118 | 1.5107 | 16.84% | 0.3175% | 1.496% | 18.65%
J | J Country | philipstown | 2035 | 66% ECP | Grandfathering | IE wind not priority | 50 | 154.1991 | 92.1904 | 28.5284 | 0.54092 | 32.9393 | 62.0087 | 18.5% | 0.3508% | 21.36% | 40.21%
A | G North | gortawee | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 3.3333 | 3.5097 | 2.899 | 0.53238 | 0.025665 | 0.052716 | 0.61076 | 15.17% | 0.7313% | 1.502% | 17.4%
A | G North | gortawee | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 2.8 | 8.0996 | 6.682 | 1.3638 | 0.025713 | 0.028079 | 1.4176 | 16.84% | 0.3175% | 0.3467% | 17.5%
A | G North | gortawee | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 3.3333 | 3.5097 | 2.9053 | 0.53238 | 0.025665 | 0.046391 | 0.60444 | 15.17% | 0.7313% | 1.322% | 17.22%
A | G North | gortawee | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 2.8 | 8.0996 | 5.6441 | 2.3935 | 0.046889 | 0.015055 | 2.4555 | 29.55% | 0.5789% | 0.1859% | 30.32%
A | G North | gortawee | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 3.3333 | 3.5097 | 2.6874 | 0.75708 | 0.030154 | 0.035075 | 0.8223 | 21.57% | 0.8592% | 0.9994% | 23.43%
A | G North | gortawee | 2035 | 100% ECP | Grandfathering | IE wind not priority | 4.2 | 12.1494 | 9.6624 | 2.2626 | 0.042855 | 0.18151 | 2.487 | 18.62% | 0.3527% | 1.494% | 20.47%
J | J Country | philipstown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 50 | 64.0644 | 28.2687 | 20.217 | 1.4115 | 14.1671 | 35.7956 | 31.56% | 2.203% | 22.11% | 55.87%
A | G North | gortawee | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 5 | 5.2646 | 3.9876 | 1.1542 | 0.048365 | 0.074451 | 1.2771 | 21.92% | 0.9187% | 1.414% | 24.26%
J | J Country | philipstown | 2035 | 100% ECP | Grandfathering | IE wind not priority | 50 | 154.1991 | 81.4939 | 31.275 | 0.58095 | 40.8492 | 72.7052 | 20.28% | 0.3768% | 26.49% | 47.15%
A | G North | gortawee | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 1.4 | 4.0498 | 2.741 | 1.1892 | 0.071928 | 0.047735 | 1.3088 | 29.36% | 1.776% | 1.179% | 32.32%
A | G North | gortawee | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 1.6667 | 1.7549 | 1.431 | 0.28122 | 0.032911 | 0.0097404 | 0.32387 | 16.02% | 1.875% | 0.555% | 18.46%
A | A, B North | tievebrack | 2035 | 100% ECP | Grandfathering | IE wind not priority | 29.9 | 86.4923 | 47.7422 | 16.1076 | 0.30509 | 22.3374 | 38.7501 | 18.62% | 0.3527% | 25.83% | 44.8%
J | J Country | portlaoise | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 1.3333 | 1.7084 | 1.1006 | 0.33106 | 0.031614 | 0.24508 | 0.60776 | 19.38% | 1.851% | 14.35% | 35.58%
A | A, B North | trillick | 2030 | Initial | Grandfathering | IE wind priority | 30.89 | 89.3561 | 86.8137 | 0 | 2.5424 | 0 | 2.5424 | 0% | 2.845% | 0% | 2.845%
J | J Country | portlaoise | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 45.001 | 138.7823 | 85.7858 | 45.1168 | 2.6039 | 5.2758 | 52.9964 | 32.51% | 1.876% | 3.801% | 38.19%
A | A, B North | trillick | 2030 | 33% ECP | Grandfathering | IE wind priority | 30.89 | 89.3561 | 86.493 | 0 | 2.863 | 0 | 2.863 | 0% | 3.204% | 0% | 3.204%
A | A, B North | trillick | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 30.89 | 89.3561 | 86.1602 | 0 | 3.1959 | 0 | 3.1959 | 0% | 3.577% | 0% | 3.577%
J | J Country | portlaoise | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 1.3333 | 1.7084 | 1.123 | 0.28316 | 0.031876 | 0.27032 | 0.58536 | 16.57% | 1.866% | 15.82% | 34.26%
A | A, B North | trillick | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 30.89 | 89.3561 | 85.8521 | 0 | 3.504 | 0 | 3.504 | 0% | 3.921% | 0% | 3.921%
A | A, B North | trillick | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 30.89 | 89.3561 | 85.7921 | 0 | 3.564 | 0 | 3.564 | 0% | 3.989% | 0% | 3.989%
J | J Country | portlaoise | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 45.001 | 138.7823 | 91.9391 | 35.4148 | 2.635 | 8.7933 | 46.8431 | 25.52% | 1.899% | 6.336% | 33.75%
A | A, B North | trillick | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 30.89 | 89.3561 | 86.493 | 0 | 2.863 | 0 | 2.863 | 0% | 3.204% | 0% | 3.204%
A | A, B North | trillick | 2030 | 100% ECP | Grandfathering | IE wind priority | 30.89 | 89.3561 | 86.0226 | 0 | 3.3335 | 0 | 3.3335 | 0% | 3.731% | 0% | 3.731%
J | J Country | portlaoise | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 1.3333 | 1.7084 | 1.1325 | 0.23215 | 0.031638 | 0.31207 | 0.57586 | 13.59% | 1.852% | 18.27% | 33.71%
A | A, B North | trillick | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 30.89 | 89.3561 | 86.0226 | 0 | 3.3335 | 0 | 3.3335 | 0% | 3.731% | 0% | 3.731%
J | J Country | portlaoise | 2030 | 33% ECP | Grandfathering | IE wind not priority | 45.001 | 138.7823 | 94.431 | 25.9051 | 2.6089 | 15.8372 | 44.3513 | 18.67% | 1.88% | 11.41% | 31.96%
A | A, B North | trillick | 2035 | 66% ECP | Grandfathering | IE wind priority | 30.89 | 89.3561 | 88.5607 | 0 | 0.79536 | 0 | 0.79536 | 0% | 0.8901% | 0% | 0.8901%
A | A, B North | trillick | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 30.89 | 89.3561 | 88.5607 | 0 | 0.79536 | 0 | 0.79536 | 0% | 0.8901% | 0% | 0.8901%
J | J Country | portlaoise | 2030 | Initial | Grandfathering | IE wind not priority | 45.001 | 138.7823 | 97.4916 | 19.1085 | 2.6986 | 19.4836 | 41.2906 | 13.77% | 1.944% | 14.04% | 29.75%
A | A, B North | trillick | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 30.89 | 89.3561 | 87.8153 | 0 | 1.5408 | 0 | 1.5408 | 0% | 1.724% | 0% | 1.724%
A | A, B North | trillick | 2035 | 100% ECP | Grandfathering | IE wind priority | 30.89 | 89.3561 | 88.4524 | 0 | 0.9037 | 0 | 0.9037 | 0% | 1.011% | 0% | 1.011%
A | G North | gortawee | 2030 | 33% ECP | Grandfathering | IE wind not priority | 1.4 | 4.0498 | 3.0888 | 0.68638 | 0.071734 | 0.2029 | 0.96101 | 16.95% | 1.771% | 5.01% | 23.73%
A | G North | gortawee | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 1.6667 | 1.7549 | 1.4733 | 0.23138 | 0.032372 | 0.01786 | 0.28162 | 13.19% | 1.845% | 1.018% | 16.05%
A | G North | gortawee | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 1.4 | 4.0498 | 2.9271 | 0.93759 | 0.072161 | 0.11296 | 1.1227 | 23.15% | 1.782% | 2.789% | 27.72%
J | J Country | philipstown | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 50 | 64.0644 | 23.4928 | 14.0864 | 0.58058 | 25.9046 | 40.5715 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J Country | philipstown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 50 | 154.1991 | 86.1135 | 46.2128 | 2.8354 | 19.0374 | 68.0856 | 29.97% | 1.839% | 12.35% | 44.15%
A | A, B North | tievebrack | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 19.9333 | 57.6615 | 32.1974 | 17.0397 | 0.3338 | 8.0905 | 25.464 | 29.55% | 0.5789% | 14.03% | 44.16%
J | J Country | philipstown | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 50 | 64.0644 | 26.9856 | 20.217 | 1.4115 | 15.4502 | 37.0787 | 31.56% | 2.203% | 24.12% | 57.88%
B | A, B North | bellacorick | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 6.45 | 19.6174 | 18.8621 | 0 | 0.75531 | 0 | 0.75531 | 0% | 3.85% | 0% | 3.85%
J | J Country | philipstown | 2030 | Initial | Grandfathering | IE wind not priority | 50 | 154.1991 | 108.3216 | 21.2312 | 2.9983 | 21.648 | 45.8775 | 13.77% | 1.944% | 14.04% | 29.75%
B | A, B North | bellacorick | 2035 | 66% ECP | Grandfathering | IE wind not priority | 105.6 | 321.1772 | 193.1032 | 56.0022 | 0.98969 | 71.0821 | 128.074 | 17.44% | 0.3081% | 22.13% | 39.88%
B | A, B North | bellacorick | 2035 | 66% ECP | Grandfathering | IE wind not priority | 271.2665 | 825.044 | 496.0459 | 143.8592 | 2.5423 | 182.5966 | 328.9981 | 17.44% | 0.3081% | 22.13% | 39.88%
J | J Country | newbridge | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 12 | 15.3754 | 5.6383 | 3.3807 | 0.13934 | 6.2171 | 9.7372 | 21.99% | 0.9062% | 40.44% | 63.33%
B | A, B North | bellacorick | 2035 | 66% ECP | Grandfathering | IE wind priority | 6.45 | 19.6174 | 19.4422 | 0 | 0.1752 | 0 | 0.1752 | 0% | 0.8931% | 0% | 0.8931%
B | A, B North | bellacorick | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 105.6 | 321.1772 | 200.8113 | 56.0022 | 0.98969 | 63.3741 | 120.366 | 17.44% | 0.3081% | 19.73% | 37.48%
J | J Country | newbridge | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 12 | 15.3754 | 7.2027 | 3.3781 | 0.13136 | 4.6633 | 8.1727 | 21.97% | 0.8544% | 30.33% | 53.15%
B | A, B North | bellacorick | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 271.2665 | 825.044 | 515.8465 | 143.8592 | 2.5423 | 162.7961 | 309.1976 | 17.44% | 0.3081% | 19.73% | 37.48%
J | J Country | philipstown | 2030 | 33% ECP | Grandfathering | IE wind not priority | 50 | 154.1991 | 104.921 | 28.7828 | 2.8988 | 17.5965 | 49.2781 | 18.67% | 1.88% | 11.41% | 31.96%
B | A, B North | bellacorick | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 6.45 | 19.6174 | 19.4422 | 0 | 0.1752 | 0 | 0.1752 | 0% | 0.8931% | 0% | 0.8931%
B | A, B North | bellacorick | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 105.6 | 321.1772 | 175.7208 | 98.5272 | 1.8647 | 45.0646 | 145.4565 | 30.68% | 0.5806% | 14.03% | 45.29%
B | A, B North | bellacorick | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 271.2665 | 825.044 | 451.3937 | 253.0978 | 4.7901 | 115.7625 | 373.6504 | 30.68% | 0.5806% | 14.03% | 45.29%
J | J Country | newbridge | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 12 | 15.3754 | 7.1242 | 2.3552 | 0.11085 | 5.7852 | 8.2512 | 15.32% | 0.721% | 37.63% | 53.67%
B | A, B North | bellacorick | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 6.45 | 19.6174 | 19.2767 | 0 | 0.34064 | 0 | 0.34064 | 0% | 1.736% | 0% | 1.736%
B | A, B North | bellacorick | 2035 | 100% ECP | Grandfathering | IE wind not priority | 116.9 | 355.5457 | 193.7176 | 68.7983 | 1.2069 | 91.8229 | 161.8281 | 19.35% | 0.3394% | 25.83% | 45.52%
B | A, B North | bellacorick | 2035 | 100% ECP | Grandfathering | IE wind not priority | 345.3 | 1050.2133 | 572.2044 | 203.2168 | 3.5649 | 271.2272 | 478.0089 | 19.35% | 0.3394% | 25.83% | 45.52%
B | A, B North | bellacorick | 2035 | 100% ECP | Grandfathering | IE wind priority | 6.45 | 19.6174 | 19.4152 | 0 | 0.20217 | 0 | 0.20217 | 0% | 1.031% | 0% | 1.031%
J | J Country | newbridge | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 12 | 15.3754 | 6.7845 | 4.8521 | 0.33875 | 3.4001 | 8.5909 | 31.56% | 2.203% | 22.11% | 55.87%
J | J Country | newbridge | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 12 | 15.3754 | 6.4765 | 4.8521 | 0.33875 | 3.7081 | 8.8989 | 31.56% | 2.203% | 24.12% | 57.88%
J | J Country | newbridge | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 12 | 15.3754 | 7.5741 | 2.3552 | 0.11085 | 5.3353 | 7.8014 | 15.32% | 0.721% | 34.7% | 50.74%
B | A, B North | bellacorick | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 345.3 | 1050.2133 | 428.6647 | 305.4286 | 18.2809 | 297.8391 | 621.5486 | 29.08% | 1.741% | 28.36% | 59.18%
B | A, B North | bellacorick | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 116.9 | 355.5457 | 145.1228 | 103.4017 | 6.1889 | 100.8323 | 210.4229 | 29.08% | 1.741% | 28.36% | 59.18%
J | J Country | philipstown | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 14.1566 | 2.9018 | 0.39547 | 3.9009 | 7.1982 | 13.59% | 1.852% | 18.27% | 33.71%
B | A, B North | bellacorick | 2030 | Initial | Grandfathering | IE wind not priority | 123.2 | 374.7069 | 177.1649 | 49.1688 | 6.7025 | 141.6707 | 197.542 | 13.12% | 1.789% | 37.81% | 52.72%
B | A, B North | bellacorick | 2030 | Initial | Grandfathering | IE wind priority | 6.45 | 19.6174 | 19.0501 | 0 | 0.56731 | 0 | 0.56731 | 0% | 2.892% | 0% | 2.892%
J | J Country | philipstown | 2030 | 100% ECP | Grandfathering | IE wind not priority | 50 | 154.1991 | 81.6686 | 46.2128 | 2.8354 | 23.4822 | 72.5304 | 29.97% | 1.839% | 15.23% | 47.04%
B | A, B North | bellacorick | 2030 | 33% ECP | Grandfathering | IE wind not priority | 94.3 | 286.8089 | 137.1269 | 51.3805 | 4.9691 | 93.3324 | 149.6819 | 17.91% | 1.733% | 32.54% | 52.19%
B | A, B North | bellacorick | 2030 | 33% ECP | Grandfathering | IE wind not priority | 197.2333 | 599.8755 | 286.808 | 107.4649 | 10.3931 | 195.2095 | 313.0674 | 17.91% | 1.733% | 32.54% | 52.19%
J | J Country | philipstown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 14.8133 | 2.9018 | 0.39547 | 3.2441 | 6.5414 | 13.59% | 1.852% | 15.19% | 30.63%
B | A, B North | bellacorick | 2030 | 33% ECP | Grandfathering | IE wind priority | 6.45 | 19.6174 | 18.985 | 0 | 0.6324 | 0 | 0.6324 | 0% | 3.224% | 0% | 3.224%
B | A, B North | bellacorick | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 94.3 | 286.8089 | 130.9992 | 69.6354 | 5.0507 | 81.1235 | 155.8096 | 24.28% | 1.761% | 28.28% | 54.33%
J | J Country | philipstown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 50 | 154.1991 | 109.7511 | 28.7828 | 2.8988 | 12.7664 | 44.448 | 18.67% | 1.88% | 8.279% | 28.83%
B | A, B North | bellacorick | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 197.2333 | 599.8755 | 273.9916 | 145.6461 | 10.5639 | 169.6739 | 325.8838 | 24.28% | 1.761% | 28.28% | 54.33%
B | A, B North | bellacorick | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 6.45 | 19.6174 | 18.9062 | 0 | 0.71117 | 0 | 0.71117 | 0% | 3.625% | 0% | 3.625%
J | J Country | philipstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 11.4726 | 4.8138 | 0.44721 | 4.6211 | 9.8821 | 22.54% | 2.094% | 21.64% | 46.28%
B | A, B North | bellacorick | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 94.3 | 286.8089 | 122.7714 | 88.3238 | 4.9633 | 70.7504 | 164.0375 | 30.8% | 1.731% | 24.67% | 57.19%
B | A, B North | bellacorick | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 197.2333 | 599.8755 | 256.7827 | 184.7337 | 10.3809 | 147.9782 | 343.0927 | 30.8% | 1.731% | 24.67% | 57.19%
J | J Country | philipstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 50 | 154.1991 | 89.8844 | 53.5163 | 2.8549 | 7.9434 | 64.3147 | 34.71% | 1.851% | 5.151% | 41.71%
B | A, B North | bellacorick | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 6.45 | 19.6174 | 18.8429 | 0 | 0.77448 | 0 | 0.77448 | 0% | 3.948% | 0% | 3.948%
B | A, B North | bellacorick | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 94.3 | 286.8089 | 113.7008 | 93.9061 | 4.9317 | 74.2703 | 173.1081 | 32.74% | 1.72% | 25.9% | 60.36%
J | J Country | philipstown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 13.7578 | 4.1383 | 0.39517 | 3.0635 | 7.597 | 19.38% | 1.851% | 14.35% | 35.58%
B | A, B North | bellacorick | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 197.2333 | 599.8755 | 237.811 | 196.4094 | 10.3149 | 155.3401 | 362.0644 | 32.74% | 1.72% | 25.9% | 60.36%
B | A, B North | bellacorick | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 6.45 | 19.6174 | 18.8328 | 0 | 0.78451 | 0 | 0.78451 | 0% | 3.999% | 0% | 3.999%
J | J Country | philipstown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 50 | 154.1991 | 95.3155 | 50.1287 | 2.8931 | 5.8618 | 58.8836 | 32.51% | 1.876% | 3.801% | 38.19%
B | A, B North | bellacorick | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 94.3 | 286.8089 | 147.858 | 51.3805 | 4.9691 | 82.6013 | 138.9508 | 17.91% | 1.733% | 28.8% | 48.45%
B | A, B North | bellacorick | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 197.2333 | 599.8755 | 309.2526 | 107.4649 | 10.3931 | 172.7649 | 290.6228 | 17.91% | 1.733% | 28.8% | 48.45%
J | J Country | philipstown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 16.6667 | 21.3548 | 14.0378 | 3.5395 | 0.39845 | 3.379 | 7.317 | 16.57% | 1.866% | 15.82% | 34.26%
B | A, B North | bellacorick | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 6.45 | 19.6174 | 18.985 | 0 | 0.6324 | 0 | 0.6324 | 0% | 3.224% | 0% | 3.224%
B | A, B North | bellacorick | 2030 | 100% ECP | Grandfathering | IE wind not priority | 116.9 | 355.5457 | 137.8432 | 103.4017 | 6.1889 | 108.1119 | 217.7026 | 29.08% | 1.741% | 30.41% | 61.23%
J | J Country | philipstown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 50 | 154.1991 | 102.1523 | 39.3489 | 2.9277 | 9.7701 | 52.0468 | 25.52% | 1.899% | 6.336% | 33.75%
B | A, B North | bellacorick | 2030 | 100% ECP | Grandfathering | IE wind not priority | 345.3 | 1050.2133 | 407.162 | 305.4286 | 18.2809 | 319.3418 | 643.0513 | 29.08% | 1.741% | 30.41% | 61.23%
B | A, B North | bellacorick | 2030 | 100% ECP | Grandfathering | IE wind priority | 6.45 | 19.6174 | 18.8621 | 0 | 0.75531 | 0 | 0.75531 | 0% | 3.85% | 0% | 3.85%
B | A, B North | bellacorick | 2030 | Initial | Grandfathering | IE wind not priority | 83 | 252.4405 | 119.3562 | 33.1251 | 4.5155 | 95.4437 | 133.0843 | 13.12% | 1.789% | 37.81% | 52.72%
A | A, B North | golagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 48 | 138.8505 | 58.7578 | 38.3291 | 2.3857 | 39.3778 | 80.0926 | 27.6% | 1.718% | 28.36% | 57.68%
J | J Country | portlaoise | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 45.001 | 138.7823 | 80.8978 | 48.1658 | 2.5695 | 7.1492 | 57.8845 | 34.71% | 1.851% | 5.151% | 41.71%
A | A, B North | tievebrack | 2035 | 66% ECP | Grandfathering | IE wind not priority | 19.9333 | 57.6615 | 35.0081 | 9.7089 | 0.18305 | 12.7615 | 22.6534 | 16.84% | 0.3175% | 22.13% | 39.29%
A | A, B North | letterkenny | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 70.1333 | 202.8758 | 94.9088 | 46.9689 | 3.6149 | 57.3831 | 107.967 | 23.15% | 1.782% | 28.28% | 53.22%
A | A, B North | letterkenny | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 70.1333 | 202.8758 | 89.6546 | 59.5723 | 3.6032 | 50.0457 | 113.2212 | 29.36% | 1.776% | 24.67% | 55.81%
J | J Country | thornsberry | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 164.4665 | 210.7288 | 98.7175 | 46.2985 | 1.8004 | 63.9124 | 112.0113 | 21.97% | 0.8544% | 30.33% | 53.15%
A | A, B North | letterkenny | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 70.1333 | 202.8758 | 82.8951 | 63.8181 | 3.6271 | 52.5355 | 119.9807 | 31.46% | 1.788% | 25.9% | 59.14%
A | A, B North | letterkenny | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 70.1333 | 202.8758 | 106.4694 | 34.3844 | 3.5935 | 58.4285 | 96.4064 | 16.95% | 1.771% | 28.8% | 47.52%
J | J Country | thornsberry | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 164.4665 | 210.7288 | 103.8066 | 32.2796 | 1.5193 | 73.1232 | 106.9222 | 15.32% | 0.721% | 34.7% | 50.74%
A | A, B North | letterkenny | 2030 | 100% ECP | Grandfathering | IE wind not priority | 170.4 | 492.9192 | 198.4981 | 136.0683 | 8.4693 | 149.8836 | 294.4212 | 27.6% | 1.718% | 30.41% | 59.73%
A | A, B North | letterkenny | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 170.4 | 492.9192 | 208.5904 | 136.0683 | 8.4693 | 139.7912 | 284.3288 | 27.6% | 1.718% | 28.36% | 57.68%
J | J Country | thornsberry | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 164.4665 | 210.7288 | 97.6412 | 32.2796 | 1.5193 | 79.2887 | 113.0876 | 15.32% | 0.721% | 37.63% | 53.67%
A | A, B North | letterkenny | 2035 | 66% ECP | Grandfathering | IE wind not priority | 120.2666 | 347.8973 | 211.2192 | 58.5779 | 1.1044 | 76.9957 | 136.6781 | 16.84% | 0.3175% | 22.13% | 39.29%
A | A, B North | letterkenny | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 120.2666 | 347.8973 | 219.5685 | 58.5779 | 1.1044 | 68.6464 | 128.3288 | 16.84% | 0.3175% | 19.73% | 36.89%
J | J Country | thornsberry | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 243.8 | 312.3778 | 114.551 | 68.6852 | 2.8309 | 126.3106 | 197.8267 | 21.99% | 0.9062% | 40.44% | 63.33%
A | A, B North | letterkenny | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 120.2666 | 347.8973 | 194.2614 | 102.8082 | 2.014 | 48.8137 | 153.6359 | 29.55% | 0.5789% | 14.03% | 44.16%
A | A, B North | letterkenny | 2035 | 100% ECP | Grandfathering | IE wind not priority | 170.4 | 492.9192 | 272.0825 | 91.7971 | 1.7387 | 127.3009 | 220.8367 | 18.62% | 0.3527% | 25.83% | 44.8%
J | J Country | thornsberry | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 243.8 | 312.3778 | 131.5819 | 98.5783 | 6.8823 | 75.3353 | 180.7959 | 31.56% | 2.203% | 24.12% | 57.88%
A | A, B North | meentycat | 2030 | Initial | Grandfathering | IE wind priority | 84.96 | 245.7654 | 238.7728 | 0 | 6.9926 | 0 | 6.9926 | 0% | 2.845% | 0% | 2.845%
A | A, B North | meentycat | 2030 | 33% ECP | Grandfathering | IE wind priority | 84.96 | 245.7654 | 237.8909 | 0 | 7.8745 | 0 | 7.8745 | 0% | 3.204% | 0% | 3.204%
J | J Country | thornsberry | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 85.1333 | 109.0801 | 75.6665 | 14.8225 | 2.0201 | 16.5711 | 33.4136 | 13.59% | 1.852% | 15.19% | 30.63%
A | A, B North | meentycat | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 84.96 | 245.7654 | 236.9754 | 0 | 8.79 | 0 | 8.79 | 0% | 3.577% | 0% | 3.577%
A | A, B North | meentycat | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 84.96 | 245.7654 | 236.1279 | 0 | 9.6375 | 0 | 9.6375 | 0% | 3.921% | 0% | 3.921%
J | J Country | thornsberry | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 85.1333 | 109.0801 | 58.6022 | 24.5889 | 2.2844 | 23.6046 | 50.4779 | 22.54% | 2.094% | 21.64% | 46.28%
A | A, B North | meentycat | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 84.96 | 245.7654 | 235.9629 | 0 | 9.8024 | 0 | 9.8024 | 0% | 3.989% | 0% | 3.989%
A | A, B North | meentycat | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 84.96 | 245.7654 | 237.8909 | 0 | 7.8745 | 0 | 7.8745 | 0% | 3.204% | 0% | 3.204%
J | J Country | thornsberry | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 85.1333 | 109.0801 | 70.2747 | 21.1383 | 2.0186 | 15.6486 | 38.8054 | 19.38% | 1.851% | 14.35% | 35.58%
A | A, B North | meentycat | 2030 | 100% ECP | Grandfathering | IE wind priority | 84.96 | 245.7654 | 236.5969 | 0 | 9.1685 | 0 | 9.1685 | 0% | 3.731% | 0% | 3.731%
J | J Country | thornsberry | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 243.8 | 312.3778 | 137.8384 | 98.5783 | 6.8823 | 69.0788 | 174.5393 | 31.56% | 2.203% | 22.11% | 55.87%
A | A, B North | letterkenny | 2030 | 33% ECP | Grandfathering | IE wind not priority | 70.1333 | 202.8758 | 98.8788 | 34.3844 | 3.5935 | 66.0192 | 103.9971 | 16.95% | 1.771% | 32.54% | 51.26%
A | A, B North | letterkenny | 2030 | Initial | Grandfathering | IE wind not priority | 20 | 57.8544 | 27.7426 | 7.1975 | 1.0405 | 21.8738 | 30.1117 | 12.44% | 1.798% | 37.81% | 52.05%
A | A, B North | golagh | 2035 | 66% ECP | Grandfathering | IE wind not priority | 48 | 138.8505 | 84.3004 | 23.3792 | 0.44079 | 30.73 | 54.5501 | 16.84% | 0.3175% | 22.13% | 39.29%
A | A, B North | golagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 48 | 138.8505 | 87.6328 | 23.3792 | 0.44079 | 27.3977 | 51.2177 | 16.84% | 0.3175% | 19.73% | 36.89%
A | A, B North | golagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 48 | 138.8505 | 77.5323 | 41.0321 | 0.80381 | 19.4822 | 61.3182 | 29.55% | 0.5789% | 14.03% | 44.16%
J | J Country | timahoe | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 683 | 875.119 | 386.1511 | 276.1647 | 19.2805 | 193.5226 | 488.9679 | 31.56% | 2.203% | 22.11% | 55.87%
A | A, B North | golagh | 2035 | 100% ECP | Grandfathering | IE wind not priority | 48 | 138.8505 | 76.643 | 25.8583 | 0.48977 | 35.8594 | 62.2075 | 18.62% | 0.3527% | 25.83% | 44.8%
J | J Country | timahoe | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 683 | 875.119 | 368.6236 | 276.1647 | 19.2805 | 211.0502 | 506.4954 | 31.56% | 2.203% | 24.12% | 57.88%
A | A, B North | lenalea | 2030 | Initial | Grandfathering | IE wind not priority | 30.1 | 87.0708 | 41.7527 | 10.8322 | 1.5659 | 32.9201 | 45.3181 | 12.44% | 1.798% | 37.81% | 52.05%
A | A, B North | lenalea | 2030 | 33% ECP | Grandfathering | IE wind not priority | 54.1 | 156.496 | 76.2739 | 26.5237 | 2.772 | 50.9264 | 80.2221 | 16.95% | 1.771% | 32.54% | 51.26%
J | J Country | timahoe | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 274.3331 | 351.4995 | 243.8275 | 47.764 | 6.5094 | 53.3985 | 107.672 | 13.59% | 1.852% | 15.19% | 30.63%
A | A, B North | lenalea | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 54.1 | 156.496 | 73.2115 | 36.2313 | 2.7885 | 44.2647 | 83.2844 | 23.15% | 1.782% | 28.28% | 53.22%
A | A, B North | lenalea | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 54.1 | 156.496 | 69.1585 | 45.9533 | 2.7795 | 38.6047 | 87.3375 | 29.36% | 1.776% | 24.67% | 55.81%
J | J Country | timahoe | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 274.3331 | 351.4995 | 188.8396 | 79.2353 | 7.3611 | 76.0635 | 162.6599 | 22.54% | 2.094% | 21.64% | 46.28%
A | A, B North | lenalea | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 54.1 | 156.496 | 63.9443 | 49.2285 | 2.7979 | 40.5252 | 92.5517 | 31.46% | 1.788% | 25.9% | 59.14%
A | A, B North | lenalea | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 54.1 | 156.496 | 82.1293 | 26.5237 | 2.772 | 45.071 | 74.3667 | 16.95% | 1.771% | 28.8% | 47.52%
J | J Country | timahoe | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 274.3331 | 351.4995 | 226.453 | 68.116 | 6.5046 | 50.4259 | 125.0465 | 19.38% | 1.851% | 14.35% | 35.58%
A | A, B North | lenalea | 2030 | 100% ECP | Grandfathering | IE wind not priority | 102.1 | 295.3465 | 118.9357 | 81.5292 | 5.0746 | 89.807 | 176.4108 | 27.6% | 1.718% | 30.41% | 59.73%
A | A, B North | lenalea | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 102.1 | 295.3465 | 124.9828 | 81.5292 | 5.0746 | 83.7599 | 170.3637 | 27.6% | 1.718% | 28.36% | 57.68%
J | J Country | timahoe | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 274.3331 | 351.4995 | 231.0619 | 58.2607 | 6.5584 | 55.6184 | 120.4376 | 16.57% | 1.866% | 15.82% | 34.26%
A | A, B North | lenalea | 2035 | 66% ECP | Grandfathering | IE wind not priority | 78.1 | 225.9212 | 137.1637 | 38.0399 | 0.7172 | 50.0003 | 88.7574 | 16.84% | 0.3175% | 22.13% | 39.29%
J | J Country | timahoe | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 274.3331 | 351.4995 | 233.0172 | 47.764 | 6.5094 | 64.2088 | 118.4822 | 13.59% | 1.852% | 18.27% | 33.71%
A | A, B North | lenalea | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 78.1 | 225.9212 | 142.5857 | 38.0399 | 0.7172 | 44.5783 | 83.3355 | 16.84% | 0.3175% | 19.73% | 36.89%
A | A, B North | lenalea | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 78.1 | 225.9212 | 126.1515 | 66.7627 | 1.3079 | 31.6991 | 99.7697 | 29.55% | 0.5789% | 14.03% | 44.16%
J | J Country | timahoe | 2030 | Initial | Grandfathering | IE Solar not priority | 70 | 89.6901 | 71.0161 | 7.0914 | 1.1599 | 10.4227 | 18.674 | 7.907% | 1.293% | 11.62% | 20.82%
A | A, B North | lenalea | 2035 | 100% ECP | Grandfathering | IE wind not priority | 102.1 | 295.3465 | 163.026 | 55.0028 | 1.0418 | 76.2759 | 132.3206 | 18.62% | 0.3527% | 25.83% | 44.8%
A | A, B North | meentycat | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 84.96 | 245.7654 | 236.5969 | 0 | 9.1685 | 0 | 9.1685 | 0% | 3.731% | 0% | 3.731%
A | A, B North | tievebrack | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 19.9333 | 57.6615 | 36.3919 | 9.7089 | 0.18305 | 11.3776 | 21.2696 | 16.84% | 0.3175% | 19.73% | 36.89%
J | J Country | thornsberry | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 85.1333 | 109.0801 | 71.705 | 18.0799 | 2.0353 | 17.26 | 37.3752 | 16.57% | 1.866% | 15.82% | 34.26%
A | A, B North | meentycat | 2035 | 66% ECP | Grandfathering | IE wind priority | 84.96 | 245.7654 | 243.5778 | 0 | 2.1876 | 0 | 2.1876 | 0% | 0.8901% | 0% | 0.8901%
J | J Country | portlaoise | 2035 | 66% ECP | Grandfathering | IE wind not priority | 45.001 | 138.7823 | 82.9732 | 25.6761 | 0.48684 | 29.6461 | 55.809 | 18.5% | 0.3508% | 21.36% | 40.21%
A | A, B North | sorne hill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 48.1 | 139.1398 | 133.5901 | 0 | 5.5496 | 0 | 5.5496 | 0% | 3.989% | 0% | 3.989%
A | A, B North | sorne hill | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 48.1 | 139.1398 | 134.6816 | 0 | 4.4581 | 0 | 4.4581 | 0% | 3.204% | 0% | 3.204%
A | A, B North | sorne hill | 2030 | 100% ECP | Grandfathering | IE wind priority | 48.1 | 139.1398 | 133.949 | 0 | 5.1907 | 0 | 5.1907 | 0% | 3.731% | 0% | 3.731%
A | A, B North | sorne hill | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 48.1 | 139.1398 | 133.949 | 0 | 5.1907 | 0 | 5.1907 | 0% | 3.731% | 0% | 3.731%
A | A, B North | sorne hill | 2035 | 66% ECP | Grandfathering | IE wind priority | 48.1 | 139.1398 | 137.9013 | 0 | 1.2385 | 0 | 1.2385 | 0% | 0.8901% | 0% | 0.8901%
J | J Country | portlaoise | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4 | 5.1251 | 2.2615 | 1.6174 | 0.11292 | 1.1334 | 2.8636 | 31.56% | 2.203% | 22.11% | 55.87%
A | A, B North | sorne hill | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 48.1 | 139.1398 | 137.9013 | 0 | 1.2385 | 0 | 1.2385 | 0% | 0.8901% | 0% | 0.8901%
A | A, B North | sorne hill | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 48.1 | 139.1398 | 136.7406 | 0 | 2.3992 | 0 | 2.3992 | 0% | 1.724% | 0% | 1.724%
J | J Country | portlaoise | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 45.001 | 138.7823 | 77.5038 | 41.5925 | 2.5519 | 17.1341 | 61.2784 | 29.97% | 1.839% | 12.35% | 44.15%
A | A, B North | sorne hill | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 48.1 | 139.1398 | 133.6835 | 0 | 5.4562 | 0 | 5.4562 | 0% | 3.921% | 0% | 3.921%
A | A, B North | sorne hill | 2035 | 100% ECP | Grandfathering | IE wind priority | 48.1 | 139.1398 | 137.7326 | 0 | 1.4072 | 0 | 1.4072 | 0% | 1.011% | 0% | 1.011%
J | J Country | portlaoise | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 4 | 5.1251 | 2.1588 | 1.6174 | 0.11292 | 1.236 | 2.9663 | 31.56% | 2.203% | 24.12% | 57.88%
A | A, B North | tievebrack | 2030 | 33% ECP | Grandfathering | IE wind not priority | 9.9667 | 28.8307 | 14.0517 | 4.8864 | 0.51068 | 9.382 | 14.779 | 16.95% | 1.771% | 32.54% | 51.26%
A | A, B North | tievebrack | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 9.9667 | 28.8307 | 13.4875 | 6.6748 | 0.51371 | 8.1547 | 15.3432 | 23.15% | 1.782% | 28.28% | 53.22%
J | J Country | portlaoise | 2030 | 100% ECP | Grandfathering | IE wind not priority | 45.001 | 138.7823 | 73.5034 | 41.5925 | 2.5519 | 21.1345 | 65.2789 | 29.97% | 1.839% | 15.23% | 47.04%
A | A, B North | tievebrack | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 9.9667 | 28.8307 | 12.7408 | 8.4658 | 0.51206 | 7.112 | 16.0899 | 29.36% | 1.776% | 24.67% | 55.81%
A | A, B North | tievebrack | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 9.9667 | 28.8307 | 11.7802 | 9.0692 | 0.51545 | 7.4658 | 17.0505 | 31.46% | 1.788% | 25.9% | 59.14%
J | J Country | portlaoise | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 1.3333 | 1.7084 | 1.1851 | 0.23215 | 0.031638 | 0.25953 | 0.52331 | 13.59% | 1.852% | 15.19% | 30.63%
A | A, B North | tievebrack | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 9.9667 | 28.8307 | 15.1304 | 4.8864 | 0.51068 | 8.3033 | 13.7003 | 16.95% | 1.771% | 28.8% | 47.52%
A | A, B North | tievebrack | 2030 | 100% ECP | Grandfathering | IE wind not priority | 29.9 | 86.4923 | 34.8304 | 23.8758 | 1.4861 | 26.3 | 51.6619 | 27.6% | 1.718% | 30.41% | 59.73%
J | J Country | portlaoise | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 45.001 | 138.7823 | 98.7782 | 25.9051 | 2.6089 | 11.49 | 40.0041 | 18.67% | 1.88% | 8.279% | 28.83%
A | A, B North | tievebrack | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 29.9 | 86.4923 | 36.6012 | 23.8758 | 1.4861 | 24.5291 | 49.891 | 27.6% | 1.718% | 28.36% | 57.68%
J | J Country | portlaoise | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 1.3333 | 1.7084 | 0.91781 | 0.3851 | 0.035777 | 0.36969 | 0.79057 | 22.54% | 2.094% | 21.64% | 46.28%
A | A, B North | sorne hill | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 48.1 | 139.1398 | 134.1633 | 0 | 4.9764 | 0 | 4.9764 | 0% | 3.577% | 0% | 3.577%
J | J Country | portlaoise | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 2.6667 | 3.4168 | 1.5832 | 0.52338 | 0.024634 | 1.2856 | 1.8336 | 15.32% | 0.721% | 37.63% | 53.67%
A | A, B North | sorne hill | 2030 | 33% ECP | Grandfathering | IE wind priority | 48.1 | 139.1398 | 134.6816 | 0 | 4.4581 | 0 | 4.4581 | 0% | 3.204% | 0% | 3.204%
J | J Country | thornsberry | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 85.1333 | 109.0801 | 72.3118 | 14.8225 | 2.0201 | 19.9258 | 36.7684 | 13.59% | 1.852% | 18.27% | 33.71%
A | A, B North | meentycat | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 84.96 | 245.7654 | 243.5778 | 0 | 2.1876 | 0 | 2.1876 | 0% | 0.8901% | 0% | 0.8901%
A | A, B North | meentycat | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 84.96 | 245.7654 | 241.5276 | 0 | 4.2377 | 0 | 4.2377 | 0% | 1.724% | 0% | 1.724%
J | J Country | thornsberry | 2030 | Initial | Grandfathering | IE Solar not priority | 5.8 | 7.4315 | 5.8842 | 0.58758 | 0.096106 | 0.86359 | 1.5473 | 7.907% | 1.293% | 11.62% | 20.82%
A | A, B North | meentycat | 2035 | 100% ECP | Grandfathering | IE wind priority | 84.96 | 245.7654 | 243.2798 | 0 | 2.4856 | 0 | 2.4856 | 0% | 1.011% | 0% | 1.011%
A | A, B North | mulreavy | 2030 | Initial | Grandfathering | IE wind priority | 95.25 | 275.5314 | 267.6919 | 0 | 7.8395 | 0 | 7.8395 | 0% | 2.845% | 0% | 2.845%
A | A, B North | mulreavy | 2030 | 33% ECP | Grandfathering | IE wind priority | 95.25 | 275.5314 | 266.7032 | 0 | 8.8282 | 0 | 8.8282 | 0% | 3.204% | 0% | 3.204%
A | A, B North | mulreavy | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 95.25 | 275.5314 | 265.6768 | 0 | 9.8546 | 0 | 9.8546 | 0% | 3.577% | 0% | 3.577%
A | A, B North | mulreavy | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 95.25 | 275.5314 | 264.7267 | 0 | 10.8047 | 0 | 10.8047 | 0% | 3.921% | 0% | 3.921%
J | J Country | portlaoise | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 4 | 5.1251 | 1.8794 | 1.1269 | 0.046446 | 2.0724 | 3.2457 | 21.99% | 0.9062% | 40.44% | 63.33%
A | A, B North | mulreavy | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 95.25 | 275.5314 | 264.5418 | 0 | 10.9896 | 0 | 10.9896 | 0% | 3.989% | 0% | 3.989%
A | A, B North | mulreavy | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 95.25 | 275.5314 | 266.7032 | 0 | 8.8282 | 0 | 8.8282 | 0% | 3.204% | 0% | 3.204%
J | J Country | portlaoise | 2035 | 100% ECP | Grandfathering | IE wind not priority | 45.001 | 138.7823 | 73.3462 | 28.1482 | 0.52287 | 36.7651 | 65.4361 | 20.28% | 0.3768% | 26.49% | 47.15%
A | A, B North | mulreavy | 2030 | 100% ECP | Grandfathering | IE wind priority | 95.25 | 275.5314 | 265.2525 | 0 | 10.2789 | 0 | 10.2789 | 0% | 3.731% | 0% | 3.731%
A | A, B North | mulreavy | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 95.25 | 275.5314 | 265.2525 | 0 | 10.2789 | 0 | 10.2789 | 0% | 3.731% | 0% | 3.731%
J | J Country | portlaoise | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 2.6667 | 3.4168 | 1.6006 | 0.75068 | 0.029192 | 1.0363 | 1.8162 | 21.97% | 0.8544% | 30.33% | 53.15%
A | A, B North | mulreavy | 2035 | 66% ECP | Grandfathering | IE wind priority | 95.25 | 275.5314 | 273.0789 | 0 | 2.4525 | 0 | 2.4525 | 0% | 0.8901% | 0% | 0.8901%
J | J Country | portlaoise | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 45.001 | 138.7823 | 80.0399 | 45.747 | 0.89587 | 12.0995 | 58.7424 | 32.96% | 0.6455% | 8.718% | 42.33%
A | A, B North | mulreavy | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 95.25 | 275.5314 | 273.0789 | 0 | 2.4525 | 0 | 2.4525 | 0% | 0.8901% | 0% | 0.8901%
A | A, B North | mulreavy | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 95.25 | 275.5314 | 270.7804 | 0 | 4.751 | 0 | 4.751 | 0% | 1.724% | 0% | 1.724%
J | J Country | portlaoise | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 2.6667 | 3.4168 | 1.6831 | 0.52338 | 0.024634 | 1.1856 | 1.7336 | 15.32% | 0.721% | 34.7% | 50.74%
A | A, B North | mulreavy | 2035 | 100% ECP | Grandfathering | IE wind priority | 95.25 | 275.5314 | 272.7448 | 0 | 2.7866 | 0 | 2.7866 | 0% | 1.011% | 0% | 1.011%
J | J Country | portlaoise | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 45.001 | 138.7823 | 84.7302 | 25.6761 | 0.48684 | 27.8891 | 54.052 | 18.5% | 0.3508% | 20.1% | 38.95%
A | A, B North | sorne hill | 2030 | Initial | Grandfathering | IE wind priority | 48.1 | 139.1398 | 135.1809 | 0 | 3.9588 | 0 | 3.9588 | 0% | 2.845% | 0% | 2.845%
C | C | athlone | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 84.9266 | 272.5599 | 228.8325 | 42.254 | 0.83462 | 0.6387 | 43.7274 | 15.5% | 0.3062% | 0.2343% | 16.04%
C | C | stonestown | 2030 | Initial | Grandfathering | IE wind not priority | 105 | 336.9827 | 211.8755 | 38.1861 | 5.956 | 80.9651 | 125.1072 | 11.33% | 1.767% | 24.03% | 37.13%
D | D and E North | ardnacrusha | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 98.7332 | 306.7052 | 249.4751 | 51.4559 | 5.1786 | 0.5955 | 57.23 | 16.78% | 1.688% | 0.1942% | 18.66%
C | C | somerset | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 35.3333 | 45.2721 | 32.8421 | 10.2053 | 0.94809 | 1.2766 | 12.43 | 22.54% | 2.094% | 2.82% | 27.46%
J | J City, G South | poolbeg south 220kv | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 450 | 1885.2836 | 1217.9436 | 512.6939 | 33.4354 | 121.2106 | 667.3399 | 27.19% | 1.773% | 6.429% | 35.4%
J | J Country | coolnabacky | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 26.6666 | 34.1676 | 22.6505 | 4.6429 | 0.63275 | 6.2414 | 11.5171 | 13.59% | 1.852% | 18.27% | 33.71%
D | D and E North | coolshamroge | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 20 | 23.4162 | 19.7312 | 3.2446 | 0.43527 | 0.0051388 | 3.685 | 13.86% | 1.859% | 0.02195% | 15.74%
D | D and E North | coolshamroge | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 60 | 70.2486 | 46.0367 | 22.2937 | 1.542 | 0.3762 | 24.2119 | 31.74% | 2.195% | 0.5355% | 34.47%
C | C | lanesboro | 2030 | Initial | Grandfathering | IE Solar not priority | 60.6 | 77.646 | 70.0824 | 6.1392 | 1.0041 | 0.4203 | 7.5636 | 7.907% | 1.293% | 0.5413% | 9.741%
D | D and E North | coolshamroge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 20 | 23.4162 | 17.5613 | 5.33 | 0.49776 | 0.027139 | 5.8549 | 22.76% | 2.126% | 0.1159% | 25%
D | D and E North | ardnacrusha | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 7.5 | 23.298 | 22.5799 | 0 | 0.71812 | 0 | 0.71812 | 0% | 3.082% | 0% | 3.082%
C | C | somerset | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 35.3333 | 45.2721 | 34.3468 | 8.7731 | 0.83777 | 1.3144 | 10.9253 | 19.38% | 1.851% | 2.903% | 24.13%
C | C | lanesboro | 2030 | 33% ECP | Grandfathering | IE wind not priority | 33.15 | 106.3901 | 76.956 | 16.6335 | 1.832 | 10.9686 | 29.4341 | 15.63% | 1.722% | 10.31% | 27.67%
J | J City, G South | poolbeg south 220kv | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 450 | 1885.2836 | 1187.4071 | 552.012 | 34.1156 | 111.7489 | 697.8764 | 29.28% | 1.81% | 5.927% | 37.02%
D | D and E North | coolshamroge | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 20 | 23.4162 | 18.3332 | 4.5829 | 0.44274 | 0.057334 | 5.083 | 19.57% | 1.891% | 0.2448% | 21.71%
J | J Country | bracklone | 2030 | 100% ECP | Grandfathering | IE wind not priority | 122.4 | 377.4794 | 199.9248 | 113.129 | 6.941 | 57.4845 | 177.5545 | 29.97% | 1.839% | 15.23% | 47.04%
C | C | derrycarney | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 444.25 | 569.2117 | 391.7762 | 125.1576 | 5.1585 | 47.1196 | 177.4356 | 21.99% | 0.9062% | 8.278% | 31.17%
C | C | somerset | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 35.3333 | 45.2721 | 37.0145 | 6.1519 | 0.8384 | 1.2673 | 8.2576 | 13.59% | 1.852% | 2.799% | 18.24%
J | J Country | coolnabacky | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 26.6666 | 34.1676 | 22.4604 | 5.6633 | 0.63752 | 5.4064 | 11.7072 | 16.57% | 1.866% | 15.82% | 34.26%
C | C | somerset | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 98 | 125.5661 | 75.999 | 39.6254 | 2.7665 | 7.1753 | 49.5671 | 31.56% | 2.203% | 5.714% | 39.47%
C | C | derrycarney | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 34 | 109.1182 | 91.6121 | 16.9162 | 0.33414 | 0.2557 | 17.5061 | 15.5% | 0.3062% | 0.2343% | 16.04%
J | J Country | coolnabacky | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 26.6666 | 34.1676 | 18.3562 | 7.7021 | 0.71554 | 7.3938 | 15.8114 | 22.54% | 2.094% | 21.64% | 46.28%
C | C | derrycarney | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 296.1664 | 379.4741 | 310.9637 | 58.1281 | 2.736 | 7.6463 | 68.5104 | 15.32% | 0.721% | 2.015% | 18.05%
D | D and E North | coolshamroge | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 40 | 46.8324 | 38.4134 | 7.4351 | 0.34372 | 0.64011 | 8.419 | 15.88% | 0.7339% | 1.367% | 17.98%
C | C | derrycarney | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 34 | 109.1182 | 76.2855 | 31.345 | 0.65181 | 0.83589 | 32.8327 | 28.73% | 0.5973% | 0.766% | 30.09%
C | C | somerset | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 98 | 125.5661 | 75.543 | 39.6254 | 2.7665 | 7.6313 | 50.0232 | 31.56% | 2.203% | 6.078% | 39.84%
J | J Country | coolnabacky | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 26.6666 | 34.1676 | 22.0124 | 6.6212 | 0.63228 | 4.9017 | 12.1552 | 19.38% | 1.851% | 14.35% | 35.58%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 39.673 | 46.4495 | 34.8355 | 10.5728 | 0.98739 | 0.053834 | 11.614 | 22.76% | 2.126% | 0.1159% | 25%
J | J City, G South | poolbeg south 220kv | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 450 | 1885.2836 | 1264.3157 | 391.7414 | 32.9498 | 196.2767 | 620.9678 | 20.78% | 1.748% | 10.41% | 32.94%
C | C | derrycarney | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 296.1664 | 379.4741 | 277.3322 | 83.3729 | 3.2421 | 15.5269 | 102.1419 | 21.97% | 0.8544% | 4.092% | 26.92%
J | J Country | bracklone | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 106.9999 | 137.0976 | 95.1016 | 18.6297 | 2.5389 | 20.8274 | 41.996 | 13.59% | 1.852% | 15.19% | 30.63%
C | C | derrycarney | 2035 | 100% ECP | Grandfathering | IE wind not priority | 34 | 109.1182 | 86.2863 | 18.7129 | 0.36446 | 3.7545 | 22.8319 | 17.15% | 0.334% | 3.441% | 20.92%
D | D and E North | coolshamroge | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 60 | 70.2486 | 46.2798 | 22.2937 | 1.542 | 0.13308 | 23.9688 | 31.74% | 2.195% | 0.1894% | 34.12%
C | C | lanesboro | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 112.2666 | 143.8458 | 117.0214 | 19.5467 | 2.6639 | 4.6138 | 26.8244 | 13.59% | 1.852% | 3.207% | 18.65%
D | D and E North | coolshamroge | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 40 | 46.8324 | 39.053 | 7.4351 | 0.34372 | 0.00048078 | 7.7793 | 15.88% | 0.7339% | 0.001027% | 16.61%
J | J City, G South | stephenstown | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 9.99 | 12.8001 | 9.8521 | 2.8145 | 0.116 | 0.017531 | 2.948 | 21.99% | 0.9062% | 0.137% | 23.03%
C | C | lanesboro | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 33.15 | 106.3901 | 70.7589 | 23.2221 | 1.871 | 10.5381 | 35.6313 | 21.83% | 1.759% | 9.905% | 33.49%
J | J Country | clonfad | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 100 | 128.1287 | 59.3684 | 19.6268 | 0.92379 | 48.2097 | 68.7603 | 15.32% | 0.721% | 37.63% | 53.67%
C | C | lanesboro | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 33.15 | 106.3901 | 78.8405 | 16.6335 | 1.832 | 9.0841 | 27.5496 | 15.63% | 1.722% | 8.538% | 25.89%
D | D and E North | booltiagh | 2035 | 100% ECP | Grandfathering | IE wind priority | 31.45 | 97.6964 | 96.7348 | 0 | 0.96161 | 0 | 0.96161 | 0% | 0.9843% | 0% | 0.9843%
C | C | lanesboro | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 112.2666 | 143.8458 | 117.6084 | 19.5467 | 2.6639 | 4.0267 | 26.2373 | 13.59% | 1.852% | 2.799% | 18.24%
D | D and E North | booltiagh | 2035 | 100% ECP | Grandfathering | IE wind not priority | 164.579 | 511.2486 | 386.5777 | 94.1836 | 1.7487 | 28.7387 | 124.671 | 18.42% | 0.342% | 5.621% | 24.39%
J | J City, G South | stephenstown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 6.66 | 8.5334 | 6.5838 | 1.8748 | 0.072907 | 0.0018043 | 1.9495 | 21.97% | 0.8544% | 0.02114% | 22.85%
D | D and E North | ardnacrusha | 2030 | 100% ECP | Grandfathering | IE wind priority | 7.5 | 23.298 | 22.4319 | 0 | 0.86617 | 0 | 0.86617 | 0% | 3.718% | 0% | 3.718%
C | C | sliabh bawn | 2035 | 100% ECP | Grandfathering | IE wind priority | 58 | 186.1428 | 184.3933 | 0 | 1.7495 | 0 | 1.7495 | 0% | 0.9399% | 0% | 0.9399%
D | D and E North | booltiagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 31.45 | 97.6964 | 96.0297 | 0 | 1.6667 | 0 | 1.6667 | 0% | 1.706% | 0% | 1.706%
C | C | lanesboro | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 215.6 | 276.2455 | 166.1945 | 87.1759 | 6.0862 | 16.7889 | 110.051 | 31.56% | 2.203% | 6.078% | 39.84%
J | J Country | clonfad | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 100 | 128.1287 | 56.5375 | 40.4341 | 2.8229 | 28.3342 | 71.5912 | 31.56% | 2.203% | 22.11% | 55.87%
J | J City, G South | richardstown | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 36.6666 | 46.9805 | 39.4551 | 6.384 | 0.87003 | 0.27136 | 7.5254 | 13.59% | 1.852% | 0.5776% | 16.02%
J | J Country | bracklone | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 321 | 411.2931 | 181.4854 | 129.7934 | 9.0616 | 90.9528 | 229.8078 | 31.56% | 2.203% | 22.11% | 55.87%
C | C | lanesboro | 2030 | 100% ECP | Grandfathering | IE wind not priority | 99.45 | 319.1707 | 217.8518 | 82.8468 | 5.4507 | 13.0215 | 101.319 | 25.96% | 1.708% | 4.08% | 31.74%
J | J Country | bracklone | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 122.4 | 377.4794 | 210.8058 | 113.129 | 6.941 | 46.6036 | 166.6736 | 29.97% | 1.839% | 12.35% | 44.15%
D | D and E North | ardnacrusha | 2030 | 100% ECP | Grandfathering | IE wind not priority | 296.2 | 920.1165 | 642.6291 | 254.6168 | 15.6063 | 7.2642 | 277.4873 | 27.67% | 1.696% | 0.7895% | 30.16%
C | C | lanesboro | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 112.2666 | 143.8458 | 104.3513 | 32.4258 | 3.0124 | 4.0562 | 39.4945 | 22.54% | 2.094% | 2.82% | 27.46%
C | C | somerset | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 35.3333 | 45.2721 | 35.5445 | 7.5038 | 0.84471 | 1.3791 | 9.7276 | 16.57% | 1.866% | 3.046% | 21.49%
D | D and E North | coolshamroge | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 20 | 23.4162 | 18.9492 | 3.9367 | 0.44278 | 0.087487 | 4.467 | 16.81% | 1.891% | 0.3736% | 19.08%
J | J Country | bracklone | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 321 | 411.2931 | 173.2477 | 129.7934 | 9.0616 | 99.1905 | 238.0454 | 31.56% | 2.203% | 24.12% | 57.88%
C | C | lanesboro | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 112.2666 | 143.8458 | 112.9377 | 23.8423 | 2.6839 | 4.3818 | 30.9081 | 16.57% | 1.866% | 3.046% | 21.49%
D | D and E North | ardnacrusha | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 39.673 | 46.4495 | 39.1398 | 6.4361 | 0.86343 | 0.010194 | 7.3097 | 13.86% | 1.859% | 0.02195% | 15.74%
J | J Country | clonfad | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 100 | 128.1287 | 60.0228 | 28.1507 | 1.0947 | 38.8605 | 68.1059 | 21.97% | 0.8544% | 30.33% | 53.15%
C | C | lanesboro | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 33.15 | 106.3901 | 63.0664 | 30.1186 | 1.8821 | 11.323 | 43.3237 | 28.31% | 1.769% | 10.64% | 40.72%
D | D and E North | coolshamroge | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 20 | 23.4162 | 19.6073 | 3.2446 | 0.43527 | 0.12906 | 3.8089 | 13.86% | 1.859% | 0.5511% | 16.27%
C | C | somerset | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 35.3333 | 45.2721 | 36.8298 | 6.1519 | 0.8384 | 1.4521 | 8.4423 | 13.59% | 1.852% | 3.207% | 18.65%
C | C | lanesboro | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 112.2666 | 143.8458 | 109.1322 | 27.8754 | 2.6619 | 4.1762 | 34.7136 | 19.38% | 1.851% | 2.903% | 24.13%
J | J Country | clonfad | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 100 | 128.1287 | 63.1172 | 19.6268 | 0.92379 | 44.4609 | 65.0115 | 15.32% | 0.721% | 34.7% | 50.74%
J | J City, G South | poolbeg south 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 450 | 1885.2836 | 1303.5174 | 528.7179 | 11.2395 | 41.8088 | 581.7662 | 28.04% | 0.5962% | 2.218% | 30.86%
C | C | lanesboro | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 33.15 | 106.3901 | 60.4585 | 32.2771 | 1.9029 | 11.7516 | 45.9316 | 30.34% | 1.789% | 11.05% | 43.17%
C | C | somerset | 2030 | Initial | Grandfathering | IE Solar not priority | 4 | 5.1251 | 4.6259 | 0.40522 | 0.06628 | 0.027743 | 0.49925 | 7.907% | 1.293% | 0.5413% | 9.741%
J | J Country | clonfad | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 100 | 128.1287 | 46.9857 | 28.1728 | 1.1612 | 51.8091 | 81.143 | 21.99% | 0.9062% | 40.44% | 63.33%
C | C | lanesboro | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 99.45 | 319.1707 | 223.9661 | 82.8468 | 5.4507 | 6.9071 | 95.2046 | 25.96% | 1.708% | 2.164% | 29.83%
J | J Country | bracklone | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 40.8 | 125.8263 | 89.5568 | 23.4868 | 2.3654 | 10.4173 | 36.2695 | 18.67% | 1.88% | 8.279% | 28.83%
C | C | derrycarney | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 34 | 109.1182 | 72.5733 | 23.8176 | 1.919 | 10.8084 | 36.5449 | 21.83% | 1.759% | 9.905% | 33.49%
J | J Country | coolnabacky | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 80 | 102.503 | 37.5885 | 22.5382 | 0.92893 | 41.4473 | 64.9144 | 21.99% | 0.9062% | 40.44% | 63.33%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 39.673 | 46.4495 | 37.5886 | 7.809 | 0.87831 | 0.17354 | 8.8609 | 16.81% | 1.891% | 0.3736% | 19.08%
J | J Country | athy | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 4.2029 | 1.0597 | 0.1193 | 1.0117 | 2.1907 | 16.57% | 1.866% | 15.82% | 34.26%
D | D and E North | derrybrien | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 70 | 89.6901 | 59.2403 | 28.3039 | 1.976 | 0.1699 | 30.4498 | 31.56% | 2.203% | 0.1894% | 33.95%
C | C | derrycarney | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 148.0832 | 189.7371 | 154.3549 | 25.7827 | 3.5137 | 6.0857 | 35.3822 | 13.59% | 1.852% | 3.207% | 18.65%
C | C | derrycarney | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 148.0832 | 189.7371 | 148.9683 | 31.4487 | 3.5402 | 5.7798 | 40.7687 | 16.57% | 1.866% | 3.046% | 21.49%
C | C | athlone | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 89.9932 | 115.3072 | 94.4896 | 17.6628 | 0.83135 | 2.3234 | 20.8176 | 15.32% | 0.721% | 2.015% | 18.05%
C | C | derrycarney | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 34 | 109.1182 | 64.6836 | 30.8909 | 1.9304 | 11.6134 | 44.4346 | 28.31% | 1.769% | 10.64% | 40.72%
J | J Country | bracklone | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 106.9999 | 137.0976 | 88.3249 | 26.5677 | 2.537 | 19.6679 | 48.7727 | 19.38% | 1.851% | 14.35% | 35.58%
D | D and E North | derrybrien | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 70 | 89.6901 | 58.9299 | 28.3039 | 1.976 | 0.48032 | 30.7602 | 31.56% | 2.203% | 0.5355% | 34.3%
C | C | derrycarney | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 148.0832 | 189.7371 | 143.9488 | 36.7686 | 3.5111 | 5.5086 | 45.7883 | 19.38% | 1.851% | 2.903% | 24.13%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 98.7332 | 306.7052 | 210.2081 | 90.3202 | 5.3314 | 0.84561 | 96.4971 | 29.45% | 1.738% | 0.2757% | 31.46%
J | J City, G South | poolbeg north 220kv | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 400 | 1675.8076 | 1123.8362 | 348.2145 | 29.2887 | 174.4682 | 551.9714 | 20.78% | 1.748% | 10.41% | 32.94%
C | C | stonestown | 2030 | 33% ECP | Grandfathering | IE wind not priority | 105 | 336.9827 | 243.7523 | 52.6854 | 5.8027 | 34.7423 | 93.2304 | 15.63% | 1.722% | 10.31% | 27.67%
J | J Country | bracklone | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 40.8 | 125.8263 | 77.7773 | 40.9049 | 2.3608 | 4.7832 | 48.049 | 32.51% | 1.876% | 3.801% | 38.19%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 98.7332 | 306.7052 | 229.3027 | 70.5784 | 5.3476 | 1.4764 | 77.4025 | 23.01% | 1.744% | 0.4814% | 25.24%
D | D and E North | derrybrien | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 70 | 89.6901 | 67.9374 | 19.7209 | 0.81281 | 1.2189 | 21.7527 | 21.99% | 0.9062% | 1.359% | 24.25%
C | C | dallow | 2035 | 100% ECP | Grandfathering | IE wind priority | 9.99 | 32.0615 | 31.7602 | 0 | 0.30134 | 0 | 0.30134 | 0% | 0.9399% | 0% | 0.9399%
J | J Country | craddanstown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 60.6666 | 187.0947 | 123.9447 | 47.7433 | 3.5523 | 11.8544 | 63.15 | 25.52% | 1.899% | 6.336% | 33.75%
D | D and E North | derrybrien | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 46.6666 | 59.7933 | 45.6219 | 13.137 | 0.51086 | 0.52363 | 14.1715 | 21.97% | 0.8544% | 0.8757% | 23.7%
C | C | stonestown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 105 | 336.9827 | 199.758 | 95.3984 | 5.9614 | 35.8649 | 137.2247 | 28.31% | 1.769% | 10.64% | 40.72%
J | J Country | athy | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 4.1191 | 1.239 | 0.11832 | 0.91722 | 2.2745 | 19.38% | 1.851% | 14.35% | 35.58%
J | J City, G South | griffinrath | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 70.7 | 90.587 | 69.7238 | 19.9182 | 0.82094 | 0.12407 | 20.8632 | 21.99% | 0.9062% | 0.137% | 23.03%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 7.5 | 23.298 | 22.4768 | 0 | 0.8212 | 0 | 0.8212 | 0% | 3.525% | 0% | 3.525%
D | D and E North | derrybrien | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 46.6666 | 59.7933 | 50.2024 | 9.1592 | 0.4311 | 0.00061384 | 9.5909 | 15.32% | 0.721% | 0.001027% | 16.04%
J | J Country | craddanstown | 2030 | 33% ECP | Grandfathering | IE wind not priority | 60.6666 | 187.0947 | 127.304 | 34.9231 | 3.5172 | 21.3504 | 59.7907 | 18.67% | 1.88% | 11.41% | 31.96%
C | C | derrycarney | 2030 | Initial | Grandfathering | IE wind not priority | 34 | 109.1182 | 68.6073 | 12.365 | 1.9286 | 26.2173 | 40.5109 | 11.33% | 1.767% | 24.03% | 37.13%
C | C | stonestown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 105 | 336.9827 | 224.1233 | 73.5544 | 5.9262 | 33.3788 | 112.8594 | 21.83% | 1.759% | 9.905% | 33.49%
D | D and E North | derrybrien | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 46.6666 | 59.7933 | 49.3858 | 9.1592 | 0.4311 | 0.81726 | 10.4076 | 15.32% | 0.721% | 1.367% | 17.41%
C | C | derrycarney | 2030 | 33% ECP | Grandfathering | IE wind not priority | 34 | 109.1182 | 78.9293 | 17.06 | 1.879 | 11.2499 | 30.1889 | 15.63% | 1.722% | 10.31% | 27.67%
D | D and E North | derrybrien | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 23.3333 | 29.8967 | 25.2739 | 4.0626 | 0.55366 | 0.0065609 | 4.6228 | 13.59% | 1.852% | 0.02195% | 15.46%
C | C | derrycarney | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 296.1664 | 379.4741 | 294.1733 | 58.1281 | 2.736 | 24.4368 | 85.3008 | 15.32% | 0.721% | 6.44% | 22.48%
C | C | derrycarney | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 34 | 109.1182 | 62.0088 | 33.1048 | 1.9516 | 12.053 | 47.1094 | 30.34% | 1.789% | 11.05% | 43.17%
J | J City, G South | poolbeg north 220kv | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 400 | 1675.8076 | 1082.6166 | 455.7279 | 29.7203 | 107.7428 | 593.191 | 27.19% | 1.773% | 6.429% | 35.4%
C | C | derrycarney | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 444.25 | 569.2117 | 344.5158 | 179.6284 | 12.5408 | 32.5267 | 224.6959 | 31.56% | 2.203% | 5.714% | 39.47%
J | J Country | bracklone | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 106.9999 | 137.0976 | 73.6543 | 30.9046 | 2.8711 | 29.6675 | 63.4433 | 22.54% | 2.094% | 21.64% | 46.28%
C | C | somerset | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 66.6666 | 85.4191 | 66.218 | 13.0846 | 0.61586 | 5.5007 | 19.2011 | 15.32% | 0.721% | 6.44% | 22.48%
J | J Country | coolnabacky | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 80 | 102.503 | 43.177 | 32.3473 | 2.2583 | 24.7204 | 59.326 | 31.56% | 2.203% | 24.12% | 57.88%
J | J Country | coolnabacky | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 80 | 102.503 | 45.23 | 32.3473 | 2.2583 | 22.6674 | 57.273 | 31.56% | 2.203% | 22.11% | 55.87%
D | D and E North | coolshamroge | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 60 | 70.2486 | 52.8402 | 15.8197 | 0.634 | 0.95469 | 17.4084 | 22.52% | 0.9025% | 1.359% | 24.78%
J | J Country | athy | 2030 | Initial | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 5.0624 | 0.50552 | 0.082684 | 0.74299 | 1.3312 | 7.907% | 1.293% | 11.62% | 20.82%
C | C | derrycarney | 2035 | 66% ECP | Grandfathering | IE wind not priority | 34 | 109.1182 | 89.2802 | 16.9162 | 0.33414 | 2.5877 | 19.8381 | 15.5% | 0.3062% | 2.371% | 18.18%
J | J City, G South | poolbeg north 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 400 | 1675.8076 | 1158.6821 | 469.9715 | 9.9907 | 37.1634 | 517.1255 | 28.04% | 0.5962% | 2.218% | 30.86%
D | D and E North | coolshamroge | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 40 | 46.8324 | 35.5113 | 10.5078 | 0.40308 | 0.41012 | 11.321 | 22.44% | 0.8607% | 0.8757% | 24.17%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 7.5 | 23.298 | 22.3853 | 0 | 0.91275 | 0 | 0.91275 | 0% | 3.918% | 0% | 3.918%
J | J Country | coolnabacky | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 26.6666 | 34.1676 | 23.7013 | 4.6429 | 0.63275 | 5.1906 | 10.4663 | 13.59% | 1.852% | 15.19% | 30.63%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 98.7332 | 306.7052 | 203.1175 | 96.4263 | 5.3129 | 1.8485 | 103.5877 | 31.44% | 1.732% | 0.6027% | 33.77%
C | C | derrycarney | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 34 | 109.1182 | 76.5696 | 28.3237 | 1.8635 | 2.3614 | 32.5486 | 25.96% | 1.708% | 2.164% | 29.83%
C | C | somerset | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 66.6666 | 85.4191 | 69.9975 | 13.0846 | 0.61586 | 1.7212 | 15.4216 | 15.32% | 0.721% | 2.015% | 18.05%
D | D and E North | derrybrien | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 23.3333 | 29.8967 | 25.1157 | 4.0626 | 0.55366 | 0.16477 | 4.781 | 13.59% | 1.852% | 0.5511% | 15.99%
C | C | derrycarney | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 148.0832 | 189.7371 | 137.6426 | 42.7707 | 3.9735 | 5.3503 | 52.0944 | 22.54% | 2.094% | 2.82% | 27.46%
D | D and E North | derrybrien | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 23.3333 | 29.8967 | 22.4966 | 6.7393 | 0.6261 | 0.03465 | 7.4001 | 22.54% | 2.094% | 0.1159% | 24.75%
C | C | somerset | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 98 | 125.5661 | 86.4245 | 27.6093 | 1.1379 | 10.3944 | 39.1417 | 21.99% | 0.9062% | 8.278% | 31.17%
C | C | derrycarney | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 34 | 109.1182 | 80.8622 | 17.06 | 1.879 | 9.317 | 28.256 | 15.63% | 1.722% | 8.538% | 25.89%
J | J Country | bracklone | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 40.8 | 125.8263 | 73.3456 | 43.6693 | 2.3296 | 6.4818 | 52.4807 | 34.71% | 1.851% | 5.151% | 41.71%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 7.5 | 23.298 | 22.3965 | 0 | 0.90151 | 0 | 0.90151 | 0% | 3.869% | 0% | 3.869%
J | J Country | coolnabacky | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 53.3333 | 68.3352 | 31.6631 | 10.4676 | 0.49269 | 25.7118 | 36.6721 | 15.32% | 0.721% | 37.63% | 53.67%
C | C | derrycarney | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 148.0832 | 189.7371 | 155.1292 | 25.7827 | 3.5137 | 5.3114 | 34.6079 | 13.59% | 1.852% | 2.799% | 18.24%
D | D and E North | derrybrien | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 23.3333 | 29.8967 | 23.4766 | 5.7936 | 0.55324 | 0.073202 | 6.42 | 19.38% | 1.851% | 0.2448% | 21.47%
J | J City, G South | poolbeg north 220kv | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 400 | 1675.8076 | 1055.473 | 490.6773 | 30.3249 | 99.3323 | 620.3346 | 29.28% | 1.81% | 5.927% | 37.02%
C | C | derrycarney | 2030 | 100% ECP | Grandfathering | IE wind not priority | 34 | 109.1182 | 74.4792 | 28.3237 | 1.8635 | 4.4518 | 34.639 | 25.96% | 1.708% | 4.08% | 31.74%
D | D and E North | derrybrien | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 23.3333 | 29.8967 | 24.2718 | 4.9553 | 0.55783 | 0.1117 | 5.6249 | 16.57% | 1.866% | 0.3736% | 18.81%
C | C | somerset | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 66.6666 | 85.4191 | 62.4271 | 18.7671 | 0.7298 | 3.4951 | 22.992 | 21.97% | 0.8544% | 4.092% | 26.92%
J | J Country | athy | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 4.2385 | 0.86881 | 0.1184 | 1.1679 | 2.1551 | 13.59% | 1.852% | 18.27% | 33.71%
C | C | derrycarney | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 444.25 | 569.2117 | 342.4485 | 179.6284 | 12.5408 | 34.594 | 226.7632 | 31.56% | 2.203% | 6.078% | 39.84%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 39.673 | 46.4495 | 36.3667 | 9.0908 | 0.87823 | 0.11373 | 10.0828 | 19.57% | 1.891% | 0.2448% | 21.71%
J | J Country | coolnabacky | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 53.3333 | 68.3352 | 33.6625 | 10.4676 | 0.49269 | 23.7124 | 34.6728 | 15.32% | 0.721% | 34.7% | 50.74%
J | J Country | bracklone | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 106.9999 | 137.0976 | 90.1225 | 22.7238 | 2.558 | 21.6932 | 46.975 | 16.57% | 1.866% | 15.82% | 34.26%
D | D and E North | booltiagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 148.579 | 461.5461 | 314.9354 | 137.33 | 2.7502 | 6.5305 | 146.6107 | 29.75% | 0.5959% | 1.415% | 31.77%
C | C | lanesboro | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 215.6 | 276.2455 | 167.1978 | 87.1759 | 6.0862 | 15.7856 | 109.0477 | 31.56% | 2.203% | 5.714% | 39.47%
J | J Country | bracklyn | 2030 | 100% ECP | Grandfathering | IE wind not priority | 64.8 | 199.842 | 105.8426 | 59.8918 | 3.6747 | 30.433 | 93.9995 | 29.97% | 1.839% | 15.23% | 47.04%
J | J City, G South | richardstown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 73.3333 | 93.961 | 72.4945 | 20.6438 | 0.80278 | 0.019867 | 21.4665 | 21.97% | 0.8544% | 0.02114% | 22.85%
J | J Country | bracklone | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 81.5999 | 251.6527 | 145.1356 | 82.9527 | 1.6245 | 21.9398 | 106.517 | 32.96% | 0.6455% | 8.718% | 42.33%
D | D and E North | booltiagh | 2030 | 33% ECP | Grandfathering | IE wind not priority | 132.579 | 411.8437 | 332.4559 | 69.095 | 6.9538 | 3.339 | 79.3878 | 16.78% | 1.688% | 0.8107% | 19.28%
C | C | shannonbridge | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 43.3333 | 55.5224 | 40.5776 | 12.1986 | 0.47437 | 2.2718 | 14.9448 | 21.97% | 0.8544% | 4.092% | 26.92%
D | D and E North | ardnacrusha | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 79.3459 | 92.899 | 76.1987 | 14.7487 | 0.68183 | 1.2698 | 16.7003 | 15.88% | 0.7339% | 1.367% | 17.98%
C | C | richmond | 2035 | 66% ECP | Grandfathering | IE wind not priority | 12.3333 | 39.5821 | 32.3859 | 6.1363 | 0.12121 | 0.93867 | 7.1961 | 15.5% | 0.3062% | 2.371% | 18.18%
J | J Country | bracklyn | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 21.6 | 66.6139 | 47.4124 | 12.4342 | 1.2523 | 5.5151 | 19.2015 | 18.67% | 1.88% | 8.279% | 28.83%
C | C | richmond | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 24.6667 | 31.6051 | 24.5007 | 4.8413 | 0.22787 | 2.0353 | 7.1044 | 15.32% | 0.721% | 6.44% | 22.48%
J | J City, G South | richardstown | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 110 | 140.9416 | 108.4812 | 30.9901 | 1.2773 | 0.19304 | 32.4604 | 21.99% | 0.9062% | 0.137% | 23.03%
D | D and E North | ardnacrusha | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 197.4665 | 613.4104 | 500.8818 | 101.8916 | 1.9714 | 8.6656 | 112.5286 | 16.61% | 0.3214% | 1.413% | 18.34%
D | D and E North | booltiagh | 2030 | Initial | Grandfathering | IE wind not priority | 116.579 | 362.1413 | 307.2188 | 43.7428 | 6.2324 | 4.9472 | 54.9225 | 12.08% | 1.721% | 1.366% | 15.17%
C | C | richmond | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 12.3333 | 39.5821 | 33.2318 | 6.1363 | 0.12121 | 0.092754 | 6.3502 | 15.5% | 0.3062% | 0.2343% | 16.04%
J | J City, G South | stephenstown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 3.33 | 4.2667 | 3.5853 | 0.57978 | 0.079015 | 0.02262 | 0.68142 | 13.59% | 1.852% | 0.5302% | 15.97%
D | D and E North | booltiagh | 2030 | Initial | Grandfathering | IE wind priority | 31.45 | 97.6964 | 95.0317 | 0 | 2.6647 | 0 | 2.6647 | 0% | 2.727% | 0% | 2.727%
C | C | shannonbridge | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 65 | 83.2837 | 57.3223 | 18.3123 | 0.75475 | 6.8943 | 25.9613 | 21.99% | 0.9062% | 8.278% | 31.17%
D | D and E North | booltiagh | 2030 | 33% ECP | Grandfathering | IE wind priority | 31.45 | 97.6964 | 94.6851 | 0 | 3.0113 | 0 | 3.0113 | 0% | 3.082% | 0% | 3.082%
C | C | richmond | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 31 | 39.7199 | 24.0405 | 12.5346 | 0.87511 | 2.2697 | 15.6794 | 31.56% | 2.203% | 5.714% | 39.47%
J | J City, G South | richardstown | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 73.3333 | 93.961 | 78.7532 | 14.393 | 0.67744 | 0.13733 | 15.2078 | 15.32% | 0.721% | 0.1462% | 16.19%
J | J Country | bracklyn | 2035 | 66% ECP | Grandfathering | IE wind not priority | 43.2 | 133.2279 | 79.6525 | 24.6485 | 0.46735 | 28.4596 | 53.5754 | 18.5% | 0.3508% | 21.36% | 40.21%
D | D and E North | booltiagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 132.579 | 411.8437 | 282.2674 | 121.2819 | 7.1589 | 1.1355 | 129.5763 | 29.45% | 1.738% | 0.2757% | 31.46%
C | C | richmond | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 18.3333 | 23.4903 | 19.2057 | 3.192 | 0.43502 | 0.65757 | 4.2846 | 13.59% | 1.852% | 2.799% | 18.24%
C | C | sliabh bawn | 2030 | Initial | Grandfathering | IE wind priority | 58 | 186.1428 | 181.0813 | 0 | 5.0615 | 0 | 5.0615 | 0% | 2.719% | 0% | 2.719%
C | C | richmond | 2030 | 100% ECP | Grandfathering | IE wind not priority | 18.5 | 59.3731 | 40.5255 | 15.4114 | 1.014 | 2.4223 | 18.8477 | 25.96% | 1.708% | 4.08% | 31.74%
D | D and E North | ardnacrusha | 2035 | 66% ECP | Grandfathering | IE wind priority | 7.5 | 23.298 | 23.0941 | 0 | 0.20392 | 0 | 0.20392 | 0% | 0.8753% | 0% | 0.8753%
D | D and E North | booltiagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 31.45 | 97.6964 | 94.2528 | 0 | 3.4436 | 0 | 3.4436 | 0% | 3.525% | 0% | 3.525%
C | C | richmond | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 31 | 39.7199 | 23.8962 | 12.5346 | 0.87511 | 2.414 | 15.8237 | 31.56% | 2.203% | 6.078% | 39.84%
J | J Country | bracklone | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 213.9998 | 274.1951 | 135.0706 | 42.0014 | 1.9769 | 95.1462 | 139.1245 | 15.32% | 0.721% | 34.7% | 50.74%
J | J City, G South | richardstown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 73.3333 | 93.961 | 78.87 | 14.393 | 0.67744 | 0.020458 | 15.0909 | 15.32% | 0.721% | 0.02177% | 16.06%
D | D and E North | booltiagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 132.579 | 411.8437 | 307.9077 | 94.7727 | 7.1808 | 1.9826 | 103.936 | 23.01% | 1.744% | 0.4814% | 25.24%
C | C | richmond | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 18.5 | 59.3731 | 41.6629 | 15.4114 | 1.014 | 1.2849 | 17.7103 | 25.96% | 1.708% | 2.164% | 29.83%
J | J Country | bracklyn | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 64.8 | 199.842 | 111.6031 | 59.8918 | 3.6747 | 24.6725 | 88.239 | 29.97% | 1.839% | 12.35% | 44.15%
J | J City, G South | stephenstown | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 9.99 | 12.8001 | 7.9673 | 4.0394 | 0.28201 | 0.51134 | 4.8327 | 31.56% | 2.203% | 3.995% | 37.76%
C | C | shannonbridge | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 43.3333 | 55.5224 | 45.4984 | 8.505 | 0.40031 | 1.1188 | 10.024 | 15.32% | 0.721% | 2.015% | 18.05%
D | D and E North | booltiagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 31.45 | 97.6964 | 93.916 | 0 | 3.7803 | 0 | 3.7803 | 0% | 3.869% | 0% | 3.869%
J | J Country | bracklyn | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 21.6 | 66.6139 | 38.83 | 23.119 | 1.2333 | 3.4316 | 27.7839 | 34.71% | 1.851% | 5.151% | 41.71%
J | J Country | bracklone | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 213.9998 | 274.1951 | 128.4488 | 60.2424 | 2.3426 | 83.1613 | 145.7464 | 21.97% | 0.8544% | 30.33% | 53.15%
J | J City, G South | stephenstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 3.33 | 4.2667 | 3.2026 | 0.9618 | 0.089353 | 0.012919 | 1.0641 | 22.54% | 2.094% | 0.3028% | 24.94%
D | D and E North | ardnacrusha | 2035 | 100% ECP | Grandfathering | IE wind priority | 7.5 | 23.298 | 23.0687 | 0 | 0.22932 | 0 | 0.22932 | 0% | 0.9843% | 0% | 0.9843%
D | D and E North | ardnacrusha | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 197.4665 | 613.4104 | 418.5598 | 182.5162 | 3.6551 | 8.6793 | 194.8506 | 29.75% | 0.5959% | 1.415% | 31.77%
C | C | shannonbridge | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 21.6666 | 27.7612 | 22.5843 | 3.7724 | 0.51411 | 0.89043 | 5.1769 | 13.59% | 1.852% | 3.207% | 18.65%
J | J City, G South | stephenstown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 3.33 | 4.2667 | 3.4719 | 0.7072 | 0.07961 | 0.0079578 | 0.79477 | 16.57% | 1.866% | 0.1865% | 18.63%
D | D and E North | ardnacrusha | 2035 | 100% ECP | Grandfathering | IE wind not priority | 296.2 | 920.1165 | 695.7407 | 169.5063 | 3.1472 | 51.7224 | 224.3758 | 18.42% | 0.342% | 5.621% | 24.39%
C | C | shannonbridge | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 65 | 83.2837 | 50.105 | 26.2821 | 1.8349 | 5.0616 | 33.1786 | 31.56% | 2.203% | 6.078% | 39.84%
J | J Country | bracklone | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 321 | 411.2931 | 150.824 | 90.4346 | 3.7273 | 166.3072 | 260.4692 | 21.99% | 0.9062% | 40.44% | 63.33%
C | C | shannonbridge | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 21.6666 | 27.7612 | 21.0617 | 5.3798 | 0.51373 | 0.80598 | 6.6995 | 19.38% | 1.851% | 2.903% | 24.13%
D | D and E North | ardnacrusha | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 79.3459 | 92.899 | 70.442 | 20.8439 | 0.79958 | 0.81354 | 22.457 | 22.44% | 0.8607% | 0.8757% | 24.17%
C | C | shannonbridge | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 21.6666 | 27.7612 | 22.6976 | 3.7724 | 0.51411 | 0.77713 | 5.0636 | 13.59% | 1.852% | 2.799% | 18.24%
J | J City, G South | stephenstown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 3.33 | 4.2667 | 3.3461 | 0.82683 | 0.078956 | 0.014778 | 0.92056 | 19.38% | 1.851% | 0.3464% | 21.58%
C | C | shannonbridge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 21.6666 | 27.7612 | 20.139 | 6.2579 | 0.58138 | 0.78282 | 7.6221 | 22.54% | 2.094% | 2.82% | 27.46%
C | C | shannonbridge | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 21.6666 | 27.7612 | 21.7962 | 4.6014 | 0.51798 | 0.84566 | 5.965 | 16.57% | 1.866% | 3.046% | 21.49%
J | J Country | bracklyn | 2030 | 33% ECP | Grandfathering | IE wind not priority | 21.6 | 66.6139 | 45.3258 | 12.4342 | 1.2523 | 7.6017 | 21.2881 | 18.67% | 1.88% | 11.41% | 31.96%
C | C | shannonbridge | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 65 | 83.2837 | 50.4075 | 26.2821 | 1.8349 | 4.7591 | 32.8762 | 31.56% | 2.203% | 5.714% | 39.47%
D | D and E North | ardnacrusha | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 7.5 | 23.298 | 23.0941 | 0 | 0.20392 | 0 | 0.20392 | 0% | 0.8753% | 0% | 0.8753%
C | C | richmond | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 12.3333 | 39.5821 | 27.6722 | 11.3702 | 0.23644 | 0.30321 | 11.9099 | 28.73% | 0.5973% | 0.766% | 30.09%
J | J Country | bracklyn | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 21.6 | 66.6139 | 41.1762 | 21.6556 | 1.2498 | 2.5323 | 25.4377 | 32.51% | 1.876% | 3.801% | 38.19%
C | C | shannonbridge | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 43.3333 | 55.5224 | 43.0417 | 8.505 | 0.40031 | 3.5754 | 12.4807 | 15.32% | 0.721% | 6.44% | 22.48%
C | C | richmond | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 24.6667 | 31.6051 | 23.098 | 6.9438 | 0.27003 | 1.2932 | 8.507 | 21.97% | 0.8544% | 4.092% | 26.92%
C | C | richmond | 2035 | 100% ECP | Grandfathering | IE wind not priority | 18.5 | 59.3731 | 46.9499 | 10.182 | 0.19831 | 2.0429 | 12.4233 | 17.15% | 0.334% | 3.441% | 20.92%
J | J Country | bracklyn | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 21.6 | 66.6139 | 44.1298 | 16.9987 | 1.2648 | 4.2207 | 22.4842 | 25.52% | 1.899% | 6.336% | 33.75%
D | D and E North | ardnacrusha | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 79.3459 | 92.899 | 77.4675 | 14.7487 | 0.68183 | 0.00095371 | 15.4315 | 15.88% | 0.7339% | 0.001027% | 16.61%
C | C | richmond | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 31 | 39.7199 | 27.3383 | 8.7336 | 0.35996 | 3.288 | 12.3815 | 21.99% | 0.9062% | 8.278% | 31.17%
J | J City, G South | stephenstown | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 3.33 | 4.2667 | 3.5832 | 0.57978 | 0.079015 | 0.024644 | 0.68344 | 13.59% | 1.852% | 0.5776% | 16.02%
D | D and E North | ardnacrusha | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 119.019 | 139.3486 | 104.8164 | 31.3808 | 1.2576 | 1.8938 | 34.5322 | 22.52% | 0.9025% | 1.359% | 24.78%
J | J Country | bracklone | 2035 | 100% ECP | Grandfathering | IE wind not priority | 122.4 | 377.4794 | 199.4971 | 76.5613 | 1.4222 | 99.9988 | 177.9822 | 20.28% | 0.3768% | 26.49% | 47.15%
C | C | richmond | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 24.6667 | 31.6051 | 25.8991 | 4.8413 | 0.22787 | 0.63684 | 5.706 | 15.32% | 0.721% | 2.015% | 18.05%
C | C | sliabh bawn | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 58 | 186.1428 | 182.9833 | 0 | 3.1595 | 0 | 3.1595 | 0% | 1.697% | 0% | 1.697%
C | C | richmond | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 6.1667 | 19.791 | 14.6662 | 3.0942 | 0.34079 | 1.6898 | 5.1249 | 15.63% | 1.722% | 8.538% | 25.89%
C | C | sliabh bawn | 2030 | 33% ECP | Grandfathering | IE wind priority | 58 | 186.1428 | 180.5068 | 0 | 5.636 | 0 | 5.636 | 0% | 3.028% | 0% | 3.028%
C | C | lanesboro | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 163.9332 | 210.0455 | 172.1238 | 32.1749 | 1.5144 | 4.2324 | 37.9217 | 15.32% | 0.721% | 2.015% | 18.05%
J | J Country | clonfad | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 100 | 128.1287 | 82.5467 | 24.8297 | 2.371 | 18.3813 | 45.582 | 19.38% | 1.851% | 14.35% | 35.58%
C | C | lanesboro | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 66.2999 | 212.7803 | 148.7565 | 61.1228 | 1.271 | 1.63 | 64.0238 | 28.73% | 0.5973% | 0.766% | 30.09%
J | J City, G South | richardstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 36.6666 | 46.9805 | 35.264 | 10.5904 | 0.98387 | 0.14225 | 11.7165 | 22.54% | 2.094% | 0.3028% | 24.94%
D | D and E North | booltiagh | 2035 | 66% ECP | Grandfathering | IE wind not priority | 148.579 | 461.5461 | 363.445 | 76.6659 | 1.4833 | 19.9519 | 98.1011 | 16.61% | 0.3214% | 4.323% | 21.25%
J | J City, G South | stephenstown | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 6.66 | 8.5334 | 7.1522 | 1.3071 | 0.061524 | 0.012472 | 1.3811 | 15.32% | 0.721% | 0.1462% | 16.19%
C | C | lanesboro | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 163.9332 | 210.0455 | 153.5082 | 46.1484 | 1.7946 | 8.5944 | 56.5373 | 21.97% | 0.8544% | 4.092% | 26.92%
J | J Country | clonfad | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 100 | 128.1287 | 84.2267 | 21.2372 | 2.3907 | 20.2741 | 43.902 | 16.57% | 1.866% | 15.82% | 34.26%
C | C | sliabh bawn | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 58 | 186.1428 | 179.4594 | 0 | 6.6834 | 0 | 6.6834 | 0% | 3.59% | 0% | 3.59%
C | C | lanesboro | 2035 | 100% ECP | Grandfathering | IE wind not priority | 99.45 | 319.1707 | 252.3874 | 54.7354 | 1.0661 | 10.982 | 66.7834 | 17.15% | 0.334% | 3.441% | 20.92%
D | D and E North | booltiagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 31.45 | 97.6964 | 94.0642 | 0 | 3.6321 | 0 | 3.6321 | 0% | 3.718% | 0% | 3.718%
C | C | lanesboro | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 215.6 | 276.2455 | 190.1338 | 60.7405 | 2.5035 | 22.8677 | 86.1117 | 21.99% | 0.9062% | 8.278% | 31.17%
D | D and E North | ardnacrusha | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 119.019 | 139.3486 | 91.8029 | 44.223 | 3.0587 | 0.26398 | 47.5457 | 31.74% | 2.195% | 0.1894% | 34.12%
D | D and E North | ardnacrusha | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 7.5 | 23.298 | 22.4319 | 0 | 0.86617 | 0 | 0.86617 | 0% | 3.718% | 0% | 3.718%
C | C | lanesboro | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 66.2999 | 212.7803 | 178.6435 | 32.9866 | 0.65157 | 0.49861 | 34.1368 | 15.5% | 0.3062% | 0.2343% | 16.04%
J | J City, G South | richardstown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 36.6666 | 46.9805 | 36.8442 | 9.1042 | 0.86938 | 0.16272 | 10.1363 | 19.38% | 1.851% | 0.3464% | 21.58%
D | D and E North | ardnacrusha | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 119.019 | 139.3486 | 91.3207 | 44.223 | 3.0587 | 0.74626 | 48.028 | 31.74% | 2.195% | 0.5355% | 34.47%
J | J City, G South | stephenstown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 6.66 | 8.5334 | 7.1628 | 1.3071 | 0.061524 | 0.0018579 | 1.3705 | 15.32% | 0.721% | 0.02177% | 16.06%
J | J Country | clonfad | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 100 | 128.1287 | 53.9712 | 40.4341 | 2.8229 | 30.9005 | 74.1575 | 31.56% | 2.203% | 24.12% | 57.88%
D | D and E North | booltiagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 31.45 | 97.6964 | 96.8412 | 0 | 0.85512 | 0 | 0.85512 | 0% | 0.8753% | 0% | 0.8753%
C | C | sliabh bawn | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 58 | 186.1428 | 184.5984 | 0 | 1.5444 | 0 | 1.5444 | 0% | 0.8297% | 0% | 0.8297%
J | J City, G South | richardstown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 36.6666 | 46.9805 | 38.2293 | 7.787 | 0.87658 | 0.087624 | 8.7512 | 16.57% | 1.866% | 0.1865% | 18.63%
D | D and E North | booltiagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 148.579 | 461.5461 | 376.8766 | 76.6659 | 1.4833 | 6.5202 | 84.6695 | 16.61% | 0.3214% | 1.413% | 18.34%
J | J Country | clonfad | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 100 | 128.1287 | 88.8801 | 17.411 | 2.3728 | 19.4648 | 39.2486 | 13.59% | 1.852% | 15.19% | 30.63%
C | C | lanesboro | 2035 | 66% ECP | Grandfathering | IE wind not priority | 66.2999 | 212.7803 | 174.0961 | 32.9866 | 0.65157 | 5.046 | 38.6842 | 15.5% | 0.3062% | 2.371% | 18.18%
D | D and E North | ardnacrusha | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 296.2 | 920.1165 | 644.5948 | 254.6168 | 15.6063 | 5.2986 | 275.5217 | 27.67% | 1.696% | 0.5759% | 29.94%
C | C | sliabh bawn | 2035 | 66% ECP | Grandfathering | IE wind priority | 58 | 186.1428 | 184.5984 | 0 | 1.5444 | 0 | 1.5444 | 0% | 0.8297% | 0% | 0.8297%
C | C | lanesboro | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 163.9332 | 210.0455 | 162.83 | 32.1749 | 1.5144 | 13.5262 | 47.2155 | 15.32% | 0.721% | 6.44% | 22.48%
D | D and E North | booltiagh | 2035 | 66% ECP | Grandfathering | IE wind priority | 31.45 | 97.6964 | 96.8412 | 0 | 0.85512 | 0 | 0.85512 | 0% | 0.8753% | 0% | 0.8753%
J | J Country | clonfad | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 100 | 128.1287 | 68.8359 | 28.8829 | 2.6833 | 27.7267 | 59.2928 | 22.54% | 2.094% | 21.64% | 46.28%
J | J Country | clonfad | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 100 | 128.1287 | 84.9395 | 17.411 | 2.3728 | 23.4054 | 43.1892 | 13.59% | 1.852% | 18.27% | 33.71%
D | D and E North | ardnacrusha | 2035 | 66% ECP | Grandfathering | IE wind not priority | 197.4665 | 613.4104 | 483.0307 | 101.8916 | 1.9714 | 26.5167 | 130.3797 | 16.61% | 0.3214% | 4.323% | 21.25%
C | C | sliabh bawn | 2030 | 100% ECP | Grandfathering | IE wind priority | 58 | 186.1428 | 179.4594 | 0 | 6.6834 | 0 | 6.6834 | 0% | 3.59% | 0% | 3.59%
D | D and E North | booltiagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 164.579 | 511.2486 | 358.1592 | 141.4739 | 8.6714 | 2.9441 | 153.0894 | 27.67% | 1.696% | 0.5759% | 29.94%
C | C | sliabh bawn | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 58 | 186.1428 | 179.0388 | 0 | 7.104 | 0 | 7.104 | 0% | 3.816% | 0% | 3.816%
C | C | richmond | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 18.3333 | 23.4903 | 18.4429 | 3.8935 | 0.43829 | 0.71556 | 5.0473 | 16.57% | 1.866% | 3.046% | 21.49%
D | D and E North | booltiagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 132.579 | 411.8437 | 334.9952 | 69.095 | 6.9538 | 0.79963 | 76.8485 | 16.78% | 1.688% | 0.1942% | 18.66%
C | C | richmond | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 6.1667 | 19.791 | 11.7318 | 5.6028 | 0.35011 | 2.1063 | 8.0592 | 28.31% | 1.769% | 10.64% | 40.72%
J | J Country | bracklyn | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 43.2 | 133.2279 | 76.8365 | 43.9161 | 0.86001 | 11.6152 | 56.3914 | 32.96% | 0.6455% | 8.718% | 42.33%
D | D and E North | booltiagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 31.45 | 97.6964 | 93.8689 | 0 | 3.8275 | 0 | 3.8275 | 0% | 3.918% | 0% | 3.918%
J | J Country | bracklone | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 213.9998 | 274.1951 | 127.0483 | 42.0014 | 1.9769 | 103.1686 | 147.1469 | 15.32% | 0.721% | 37.63% | 53.67%
C | C | sliabh bawn | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 58 | 186.1428 | 179.7507 | 0 | 6.3921 | 0 | 6.3921 | 0% | 3.434% | 0% | 3.434%
J | J City, G South | stephenstown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 9.99 | 12.8001 | 7.8837 | 4.0394 | 0.28201 | 0.595 | 4.9164 | 31.56% | 2.203% | 4.648% | 38.41%
J | J Country | bracklone | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 81.5999 | 251.6527 | 153.6406 | 46.5583 | 0.88278 | 50.571 | 98.0121 | 18.5% | 0.3508% | 20.1% | 38.95%
C | C | richmond | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 6.1667 | 19.791 | 11.2467 | 6.0043 | 0.35398 | 2.1861 | 8.5443 | 30.34% | 1.789% | 11.05% | 43.17%
D | D and E North | booltiagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 132.579 | 411.8437 | 272.7461 | 129.4813 | 7.1341 | 2.4822 | 139.0976 | 31.44% | 1.732% | 0.6027% | 33.77%
J | J Country | bracklyn | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 43.2 | 133.2279 | 81.3391 | 24.6485 | 0.46735 | 26.7729 | 51.8888 | 18.5% | 0.3508% | 20.1% | 38.95%
C | C | richmond | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 18.3333 | 23.4903 | 17.0407 | 5.2952 | 0.49193 | 0.66239 | 6.4495 | 22.54% | 2.094% | 2.82% | 27.46%
C | C | richmond | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 18.3333 | 23.4903 | 17.8215 | 4.5521 | 0.43469 | 0.68199 | 5.6688 | 19.38% | 1.851% | 2.903% | 24.13%
J | J Country | bracklyn | 2035 | 100% ECP | Grandfathering | IE wind not priority | 64.8 | 199.842 | 105.6161 | 40.5325 | 0.75291 | 52.9405 | 94.2259 | 20.28% | 0.3768% | 26.49% | 47.15%
J | J City, G South | richardstown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 110 | 140.9416 | 86.8073 | 44.4775 | 3.1052 | 6.5516 | 54.1342 | 31.56% | 2.203% | 4.648% | 38.41%
C | C | richmond | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 6.1667 | 19.791 | 13.1628 | 4.3199 | 0.34805 | 1.9603 | 6.6282 | 21.83% | 1.759% | 9.905% | 33.49%
J | J Country | bracklone | 2035 | 66% ECP | Grandfathering | IE wind not priority | 81.5999 | 251.6527 | 150.4546 | 46.5583 | 0.88278 | 53.7569 | 101.198 | 18.5% | 0.3508% | 21.36% | 40.21%
J | J Country | clonfad | 2030 | Initial | Grandfathering | IE Solar not priority | 100 | 128.1287 | 101.4515 | 10.1306 | 1.657 | 14.8896 | 26.6772 | 7.907% | 1.293% | 11.62% | 20.82%
C | C | sliabh bawn | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 58 | 186.1428 | 180.5068 | 0 | 5.636 | 0 | 5.636 | 0% | 3.028% | 0% | 3.028%
C | C | richmond | 2030 | Initial | Grandfathering | IE Solar not priority | 12 | 15.3754 | 13.8777 | 1.2157 | 0.19884 | 0.083228 | 1.4977 | 7.907% | 1.293% | 0.5413% | 9.741%
D | D and E North | booltiagh | 2030 | 100% ECP | Grandfathering | IE wind priority | 31.45 | 97.6964 | 94.0642 | 0 | 3.6321 | 0 | 3.6321 | 0% | 3.718% | 0% | 3.718%
J | J City, G South | richardstown | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 110 | 140.9416 | 87.7285 | 44.4775 | 3.1052 | 5.6303 | 53.213 | 31.56% | 2.203% | 3.995% | 37.76%
C | C | richmond | 2030 | 33% ECP | Grandfathering | IE wind not priority | 6.1667 | 19.791 | 14.3156 | 3.0942 | 0.34079 | 2.0404 | 5.4754 | 15.63% | 1.722% | 10.31% | 27.67%
D | D and E North | booltiagh | 2030 | 100% ECP | Grandfathering | IE wind not priority | 164.579 | 511.2486 | 357.0671 | 141.4739 | 8.6714 | 4.0363 | 154.1816 | 27.67% | 1.696% | 0.7895% | 30.16%
C | C | richmond | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 18.3333 | 23.4903 | 19.1098 | 3.192 | 0.43502 | 0.75344 | 4.3805 | 13.59% | 1.852% | 3.207% | 18.65%
C | C | sliabh bawn | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 58 | 186.1428 | 178.8908 | 0 | 7.252 | 0 | 7.252 | 0% | 3.896% | 0% | 3.896%
D | D and E North | booltiagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 31.45 | 97.6964 | 94.6851 | 0 | 3.0113 | 0 | 3.0113 | 0% | 3.082% | 0% | 3.082%
J | J City, G South | richardstown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 36.6666 | 46.9805 | 39.4774 | 6.384 | 0.87003 | 0.24907 | 7.5031 | 13.59% | 1.852% | 0.5302% | 15.97%
C | C | stonestown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 105 | 336.9827 | 191.4977 | 102.2354 | 6.0271 | 37.2224 | 145.4849 | 30.34% | 1.789% | 11.05% | 43.17%
J | J Country | coolnabacky | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 53.3333 | 68.3352 | 32.0122 | 15.0137 | 0.58384 | 20.7256 | 36.3231 | 21.97% | 0.8544% | 30.33% | 53.15%
J | J City, G South | griffinrath | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 52.3 | 67.0113 | 51.7018 | 14.7228 | 0.57253 | 0.014169 | 15.3095 | 21.97% | 0.8544% | 0.02114% | 22.85%
J | J Country | athy | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 3.1495 | 0.97938 | 0.046097 | 2.2186 | 3.2441 | 15.32% | 0.721% | 34.7% | 50.74%
C | J Country | mullingar | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 17.6167 | 22.572 | 12.1266 | 5.0882 | 0.4727 | 4.8845 | 10.4454 | 22.54% | 2.094% | 21.64% | 46.28%
C | C | carrick on shannon | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 13.3133 | 17.0582 | 12.4667 | 3.7478 | 0.14574 | 0.69797 | 4.5915 | 21.97% | 0.8544% | 4.092% | 26.92%
J | J City, G South | grange | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 39.99 | 51.2387 | 39.5326 | 11.2575 | 0.43777 | 0.010834 | 11.7061 | 21.97% | 0.8544% | 0.02114% | 22.85%
J | J Country | curraghdoo | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 2.6667 | 3.4168 | 1.6831 | 0.52338 | 0.024634 | 1.1856 | 1.7336 | 15.32% | 0.721% | 34.7% | 50.74%
D | D and E North | ennis | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 92.09 | 107.8199 | 81.1009 | 24.2806 | 0.97308 | 1.4653 | 26.719 | 22.52% | 0.9025% | 1.359% | 24.78%
J | J Country | blundelstown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 60 | 76.8772 | 33.9225 | 24.2604 | 1.6938 | 17.0005 | 42.9547 | 31.56% | 2.203% | 22.11% | 55.87%
C | C | carrick on shannon | 2035 | 100% ECP | Grandfathering | IE wind not priority | 6.9 | 22.1446 | 17.511 | 3.7976 | 0.073965 | 0.76195 | 4.6335 | 17.15% | 0.334% | 3.441% | 20.92%
C | C | carrick on shannon | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 19.97 | 25.5873 | 17.6112 | 5.6261 | 0.23188 | 2.1181 | 7.9761 | 21.99% | 0.9062% | 8.278% | 31.17%
C | J Country | mullingar | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 38.8333 | 124.63 | 78.1699 | 37.8108 | 2.2291 | 6.4202 | 46.4601 | 30.34% | 1.789% | 5.151% | 37.28%
D | D and E North | ennis | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 67.4933 | 79.0218 | 59.9194 | 17.7302 | 0.68014 | 0.69202 | 19.1024 | 22.44% | 0.8607% | 0.8757% | 24.17%
J | J Country | curraghdoo | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 2.6667 | 3.4168 | 1.5832 | 0.52338 | 0.024634 | 1.2856 | 1.8336 | 15.32% | 0.721% | 37.63% | 53.67%
J | J City, G South | grange | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 39.99 | 51.2387 | 39.4378 | 11.2663 | 0.46435 | 0.070178 | 11.8008 | 21.99% | 0.9062% | 0.137% | 23.03%
D | D and E North | ennis | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 67.4933 | 79.0218 | 65.8955 | 12.5455 | 0.57998 | 0.00081124 | 13.1263 | 15.88% | 0.7339% | 0.001027% | 16.61%
C | J Country | shanonagh | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 66.6666 | 85.419 | 59.2533 | 11.6073 | 1.5819 | 12.9766 | 26.1657 | 13.59% | 1.852% | 15.19% | 30.63%
C | C | carrick on shannon | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 4.6 | 14.763 | 10.321 | 4.2408 | 0.088186 | 0.11309 | 4.4421 | 28.73% | 0.5973% | 0.766% | 30.09%
C | C | carrick on shannon | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 13.3133 | 17.0582 | 13.9785 | 2.613 | 0.12299 | 0.34372 | 3.0797 | 15.32% | 0.721% | 2.015% | 18.05%
J | J City, G South | grange | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 39.99 | 51.2387 | 42.9456 | 7.8488 | 0.36942 | 0.074887 | 8.2931 | 15.32% | 0.721% | 0.1462% | 16.19%
D | D and E North | slievecallan | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 71.875 | 223.2727 | 215.4029 | 0 | 7.8698 | 0 | 7.8698 | 0% | 3.525% | 0% | 3.525%
C | C | carrick on shannon | 2035 | 66% ECP | Grandfathering | IE wind not priority | 4.6 | 14.763 | 12.0791 | 2.2887 | 0.045207 | 0.3501 | 2.684 | 15.5% | 0.3062% | 2.371% | 18.18%
C | J Country | shanonagh | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 66.6666 | 85.419 | 55.0311 | 16.5531 | 1.5807 | 12.2542 | 30.388 | 19.38% | 1.851% | 14.35% | 35.58%
J | J Country | blundelstown | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 60 | 76.8772 | 32.3827 | 24.2604 | 1.6938 | 18.5403 | 44.4945 | 31.56% | 2.203% | 24.12% | 57.88%
J | J Country | curraghdoo | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 2.6667 | 3.4168 | 1.6006 | 0.75068 | 0.029192 | 1.0363 | 1.8162 | 21.97% | 0.8544% | 30.33% | 53.15%
C | J Country | mullingar | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 17.6167 | 22.572 | 15.6577 | 3.0672 | 0.41801 | 3.4291 | 6.9143 | 13.59% | 1.852% | 15.19% | 30.63%
D | D and E North | slievecallan | 2030 | 33% ECP | Grandfathering | IE wind priority | 71.875 | 223.2727 | 216.3907 | 0 | 6.882 | 0 | 6.882 | 0% | 3.082% | 0% | 3.082%
J | J Country | curraghdoo | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 4 | 5.1251 | 1.8794 | 1.1269 | 0.046446 | 2.0724 | 3.2457 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J City, G South | grange | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 39.99 | 51.2387 | 43.0093 | 7.8488 | 0.36942 | 0.011156 | 8.2294 | 15.32% | 0.721% | 0.02177% | 16.06%
C | C | carrick on shannon | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 4.6 | 14.763 | 12.3946 | 2.2887 | 0.045207 | 0.034595 | 2.3685 | 15.5% | 0.3062% | 0.2343% | 16.04%
C | J Country | shanonagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 66.6666 | 85.419 | 45.8905 | 19.2552 | 1.7889 | 18.4844 | 39.5285 | 22.54% | 2.094% | 21.64% | 46.28%
D | D and E North | slievecallan | 2030 | Initial | Grandfathering | IE wind priority | 71.875 | 223.2727 | 217.1829 | 0 | 6.0898 | 0 | 6.0898 | 0% | 2.727% | 0% | 2.727%
C | J Country | mullingar | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 38.8333 | 124.63 | 92.6804 | 19.4852 | 2.1461 | 10.3183 | 31.9496 | 15.63% | 1.722% | 8.279% | 25.64%
C | C | carrick on shannon | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 13.3133 | 17.0582 | 13.2237 | 2.613 | 0.12299 | 1.0985 | 3.8345 | 15.32% | 0.721% | 6.44% | 22.48%
C | J Country | mullingar | 2030 | 100% ECP | Grandfathering | IE wind not priority | 97.5 | 312.9125 | 178.6944 | 81.2223 | 5.3438 | 47.6519 | 134.2181 | 25.96% | 1.708% | 15.23% | 42.89%
C | J Country | shanonagh | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 200 | 256.2574 | 107.9425 | 80.8681 | 5.6458 | 61.8009 | 148.3149 | 31.56% | 2.203% | 24.12% | 57.88%
C | C | cregg | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 75 | 96.0965 | 57.8135 | 30.3256 | 2.1172 | 5.8403 | 38.283 | 31.56% | 2.203% | 6.078% | 39.84%
C | J Country | mullingar | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 38.8333 | 124.63 | 87.3382 | 27.2034 | 2.1918 | 7.8966 | 37.2918 | 21.83% | 1.759% | 6.336% | 29.92%
J | J Country | curraghdoo | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 1.3333 | 1.7084 | 1.1851 | 0.23215 | 0.031638 | 0.25953 | 0.52331 | 13.59% | 1.852% | 15.19% | 30.63%
C | C | cregg | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 75 | 96.0965 | 58.1625 | 30.3256 | 2.1172 | 5.4913 | 37.934 | 31.56% | 2.203% | 5.714% | 39.47%
D | D and E North | ennis | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 42.8966 | 50.2238 | 42.3201 | 6.9591 | 0.93359 | 0.011022 | 7.9037 | 13.86% | 1.859% | 0.02195% | 15.74%
J | J City, G South | griffinrath | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 33.9 | 43.4356 | 36.478 | 5.9023 | 0.80439 | 0.25088 | 6.9576 | 13.59% | 1.852% | 0.5776% | 16.02%
J | J Country | curraghdoo | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 1.3333 | 1.7084 | 0.91781 | 0.3851 | 0.035777 | 0.36969 | 0.79057 | 22.54% | 2.094% | 21.64% | 46.28%
D | D and E North | ennis | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 42.8966 | 50.2238 | 37.6661 | 11.4319 | 1.0676 | 0.058208 | 12.5577 | 22.76% | 2.126% | 0.1159% | 25%
C | J Country | mullingar | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 17.6167 | 22.572 | 14.9635 | 3.0672 | 0.41801 | 4.1233 | 7.6085 | 13.59% | 1.852% | 18.27% | 33.71%
C | C | cregg | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 49.9999 | 64.0643 | 49.6635 | 9.8134 | 0.46189 | 4.1255 | 14.4008 | 15.32% | 0.721% | 6.44% | 22.48%
C | J Country | shanonagh | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 133.3332 | 170.8381 | 79.1578 | 26.1691 | 1.2317 | 64.2795 | 91.6803 | 15.32% | 0.721% | 37.63% | 53.67%
D | D and E North | ennis | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 42.8966 | 50.2238 | 39.3217 | 9.8295 | 0.94959 | 0.12297 | 10.9021 | 19.57% | 1.891% | 0.2448% | 21.71%
C | C | cregg | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 49.9999 | 64.0643 | 52.4981 | 9.8134 | 0.46189 | 1.2909 | 11.5662 | 15.32% | 0.721% | 2.015% | 18.05%
J | J Country | blundelstown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 60 | 76.8772 | 37.8703 | 11.7761 | 0.55427 | 26.6765 | 39.0069 | 15.32% | 0.721% | 34.7% | 50.74%
D | D and E North | ennis | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 92.09 | 107.8199 | 70.6586 | 34.2172 | 2.3667 | 0.57741 | 37.1613 | 31.74% | 2.195% | 0.5355% | 34.47%
C | C | cregg | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 25 | 32.0321 | 26.1895 | 4.3527 | 0.5932 | 0.89669 | 5.8426 | 13.59% | 1.852% | 2.799% | 18.24%
C | J Country | mullingar | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 17.6167 | 22.572 | 14.542 | 4.3742 | 0.4177 | 3.2382 | 8.03 | 19.38% | 1.851% | 14.35% | 35.58%
C | C | cregg | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 25 | 32.0321 | 26.0588 | 4.3527 | 0.5932 | 1.0274 | 5.9734 | 13.59% | 1.852% | 3.207% | 18.65%
D | D and E North | ennis | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 67.4933 | 79.0218 | 64.8162 | 12.5455 | 0.57998 | 1.0801 | 14.2056 | 15.88% | 0.7339% | 1.367% | 17.98%
J | J Country | athy | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 2.9625 | 0.97938 | 0.046097 | 2.4057 | 3.4311 | 15.32% | 0.721% | 37.63% | 53.67%
C | C | cregg | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 25 | 32.0321 | 25.1494 | 5.3093 | 0.59767 | 0.97576 | 6.8827 | 16.57% | 1.866% | 3.046% | 21.49%
C | J Country | mullingar | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 38.8333 | 124.63 | 82.4053 | 35.2822 | 2.2048 | 4.7378 | 42.2248 | 28.31% | 1.769% | 3.801% | 33.88%
J | J City, G South | griffinrath | 2030 | Initial | Grandfathering | IE Solar not priority | 15.5 | 19.8599 | 18.0208 | 1.5702 | 0.25683 | 0.012079 | 1.8392 | 7.907% | 1.293% | 0.06082% | 9.261%
J | J Country | curraghdoo | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4 | 5.1251 | 2.2615 | 1.6174 | 0.11292 | 1.1334 | 2.8636 | 31.56% | 2.203% | 22.11% | 55.87%
C | J Country | shanonagh | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 200 | 256.2574 | 113.075 | 80.8681 | 5.6458 | 56.6684 | 143.1824 | 31.56% | 2.203% | 22.11% | 55.87%
C | C | cregg | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 25 | 32.0321 | 24.302 | 6.2074 | 0.59276 | 0.92998 | 7.7302 | 19.38% | 1.851% | 2.903% | 24.13%
C | C | cregg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 25 | 32.0321 | 23.2374 | 7.2207 | 0.67082 | 0.90326 | 8.7948 | 22.54% | 2.094% | 2.82% | 27.46%
D | D and E North | ennis | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 92.09 | 107.8199 | 71.0318 | 34.2172 | 2.3667 | 0.20425 | 36.7881 | 31.74% | 2.195% | 0.1894% | 34.12%
J | J Country | blundelstown | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 60 | 76.8772 | 35.621 | 11.7761 | 0.55427 | 28.9258 | 41.2562 | 15.32% | 0.721% | 37.63% | 53.67%
C | J Country | mullingar | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 17.6167 | 22.572 | 14.8379 | 3.7413 | 0.42116 | 3.5716 | 7.7341 | 16.57% | 1.866% | 15.82% | 34.26%
J | J Country | curraghdoo | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 4 | 5.1251 | 2.1588 | 1.6174 | 0.11292 | 1.236 | 2.9663 | 31.56% | 2.203% | 24.12% | 57.88%
C | C | dallow | 2035 | 100% ECP | Grandfathering | IE wind not priority | 67.09 | 215.3159 | 170.2631 | 36.925 | 0.71917 | 7.4086 | 45.0528 | 17.15% | 0.334% | 3.441% | 20.92%
D | D and E North | slievecallan | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 71.875 | 223.2727 | 214.6333 | 0 | 8.6394 | 0 | 8.6394 | 0% | 3.869% | 0% | 3.869%
J | J Country | athy | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 2.9951 | 1.4047 | 0.054625 | 1.9391 | 3.3985 | 21.97% | 0.8544% | 30.33% | 53.15%
C | J Country | mullingar | 2035 | 100% ECP | Grandfathering | IE wind not priority | 97.5 | 312.9125 | 175.311 | 53.6621 | 1.0452 | 82.8942 | 137.6015 | 17.15% | 0.334% | 26.49% | 43.97%
J | J Country | blundelstown | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 60 | 76.8772 | 50.536 | 12.7423 | 1.4344 | 12.1644 | 26.3412 | 16.57% | 1.866% | 15.82% | 34.26%
C | J Country | mullingar | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 28.85 | 36.9651 | 13.5554 | 8.1278 | 0.335 | 14.9469 | 23.4098 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J Country | cushaling | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 75 | 231.2986 | 129.1702 | 69.3192 | 4.2531 | 28.5561 | 102.1284 | 29.97% | 1.839% | 12.35% | 44.15%
C | C | carrick on shannon | 2030 | 33% ECP | Grandfathering | IE wind not priority | 2.3 | 7.3815 | 5.3393 | 1.1541 | 0.12711 | 0.76102 | 2.0422 | 15.63% | 1.722% | 10.31% | 27.67%
C | J Country | mullingar | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 23.2333 | 29.7686 | 13.7933 | 4.56 | 0.21463 | 11.2007 | 15.9753 | 15.32% | 0.721% | 37.63% | 53.67%
D | D and E North | slievecallan | 2035 | 100% ECP | Grandfathering | IE wind priority | 71.875 | 223.2727 | 221.075 | 0 | 2.1976 | 0 | 2.1976 | 0% | 0.9843% | 0% | 0.9843%
C | C | carrick on shannon | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 6.6567 | 8.5291 | 6.9386 | 1.159 | 0.15795 | 0.27357 | 1.5905 | 13.59% | 1.852% | 3.207% | 18.65%
J | J Country | cushaling | 2030 | 100% ECP | Grandfathering | IE wind not priority | 75 | 231.2986 | 122.503 | 69.3192 | 4.2531 | 35.2234 | 108.7957 | 29.97% | 1.839% | 15.23% | 47.04%
C | C | carrick on shannon | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 2.3 | 7.3815 | 4.9094 | 1.6112 | 0.12981 | 0.73115 | 2.4722 | 21.83% | 1.759% | 9.905% | 33.49%
C | J Country | mullingar | 2035 | 66% ECP | Grandfathering | IE wind not priority | 68.1666 | 218.7711 | 137.4529 | 33.9153 | 0.66991 | 46.7329 | 81.3182 | 15.5% | 0.3062% | 21.36% | 37.17%
D | D and E North | slievecallan | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 71.875 | 223.2727 | 219.4638 | 0 | 3.8089 | 0 | 3.8089 | 0% | 1.706% | 0% | 1.706%
J | J City, G South | grange | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 39.99 | 51.2387 | 38.4602 | 11.5503 | 1.073 | 0.15515 | 12.7784 | 22.54% | 2.094% | 0.3028% | 24.94%
J | J Country | blundelstown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 60 | 76.8772 | 49.528 | 14.8978 | 1.4226 | 11.0288 | 27.3492 | 19.38% | 1.851% | 14.35% | 35.58%
D | D and E North | tullabrack | 2030 | Initial | Grandfathering | IE wind priority | 13.8 | 42.8684 | 41.6991 | 0 | 1.1692 | 0 | 1.1692 | 0% | 2.727% | 0% | 2.727%
C | J Country | mullingar | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 68.1666 | 218.7711 | 140.2226 | 33.9153 | 0.66991 | 43.9633 | 78.5485 | 15.5% | 0.3062% | 20.1% | 35.9%
C | J Country | mullingar | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 68.1666 | 218.7711 | 135.5475 | 62.8437 | 1.3068 | 19.0731 | 83.2236 | 28.73% | 0.5973% | 8.718% | 38.04%
C | J Country | mullingar | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 23.2333 | 29.7686 | 13.9453 | 6.5403 | 0.25433 | 9.0286 | 15.8233 | 21.97% | 0.8544% | 30.33% | 53.15%
J | J Country | cushaling | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 75 | 231.2986 | 141.2139 | 42.7926 | 0.81138 | 46.4808 | 90.0847 | 18.5% | 0.3508% | 20.1% | 38.95%
C | C | athlone | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 84.9266 | 272.5599 | 190.5489 | 78.2949 | 1.6281 | 2.0879 | 82.0109 | 28.73% | 0.5973% | 0.766% | 30.09%
D | D and E North | tullabrack | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 10.5 | 32.6172 | 24.3857 | 7.5058 | 0.56871 | 0.15702 | 8.2315 | 23.01% | 1.744% | 0.4814% | 25.24%
J | J City, G South | grange | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 39.99 | 51.2387 | 41.6943 | 8.4928 | 0.95604 | 0.095566 | 9.5444 | 16.57% | 1.866% | 0.1865% | 18.63%
J | J Country | blundelstown | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 60 | 76.8772 | 50.9637 | 10.4466 | 1.4237 | 14.0432 | 25.9135 | 13.59% | 1.852% | 18.27% | 33.71%
J | J City, G South | grange | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 39.99 | 51.2387 | 40.1836 | 9.9294 | 0.94818 | 0.17747 | 11.055 | 19.38% | 1.851% | 0.3464% | 21.58%
C | C | athlone | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 89.9932 | 115.3072 | 84.2703 | 25.3337 | 0.98515 | 4.718 | 31.0369 | 21.97% | 0.8544% | 4.092% | 26.92%
D | D and E North | tullabrack | 2030 | 33% ECP | Grandfathering | IE wind priority | 13.8 | 42.8684 | 41.547 | 0 | 1.3213 | 0 | 1.3213 | 0% | 3.082% | 0% | 3.082%
J | J Country | cushaling | 2035 | 66% ECP | Grandfathering | IE wind not priority | 75 | 231.2986 | 138.2857 | 42.7926 | 0.81138 | 49.409 | 93.013 | 18.5% | 0.3508% | 21.36% | 40.21%
C | C | athlone | 2035 | 100% ECP | Grandfathering | IE wind not priority | 127.39 | 408.8402 | 323.2944 | 70.113 | 1.3656 | 14.0673 | 85.5459 | 17.15% | 0.334% | 3.441% | 20.92%
J | J Country | blundelstown | 2030 | Initial | Grandfathering | IE Solar not priority | 60 | 76.8772 | 60.8709 | 6.0784 | 0.9942 | 8.9337 | 16.0063 | 7.907% | 1.293% | 11.62% | 20.82%
D | D and E North | tullabrack | 2030 | 33% ECP | Grandfathering | IE wind not priority | 10.5 | 32.6172 | 26.3298 | 5.4722 | 0.55073 | 0.26444 | 6.2874 | 16.78% | 1.688% | 0.8107% | 19.28%
C | C | athlone | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 132.99 | 170.3984 | 117.2815 | 37.467 | 1.5442 | 14.1056 | 53.1168 | 21.99% | 0.9062% | 8.278% | 31.17%
C | J Country | mullingar | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 23.2333 | 29.7686 | 14.6642 | 4.56 | 0.21463 | 10.3297 | 15.1043 | 15.32% | 0.721% | 34.7% | 50.74%
C | C | carrick on shannon | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 6.6567 | 8.5291 | 6.6964 | 1.4137 | 0.15914 | 0.25981 | 1.8326 | 16.57% | 1.866% | 3.046% | 21.49%
J | J Country | cushaling | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 75 | 231.2986 | 164.6267 | 43.1743 | 4.3481 | 19.1495 | 66.672 | 18.67% | 1.88% | 8.279% | 28.83%
J | J Country | cushaling | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 75 | 231.2986 | 153.2285 | 59.0234 | 4.3916 | 14.6551 | 78.0701 | 25.52% | 1.899% | 6.336% | 33.75%
C | J Country | shanonagh | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 66.6666 | 85.419 | 56.6263 | 11.6073 | 1.5819 | 15.6036 | 28.7928 | 13.59% | 1.852% | 18.27% | 33.71%
C | J Country | mullingar | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 97.5 | 312.9125 | 187.7141 | 81.2223 | 5.3438 | 38.6322 | 125.1984 | 25.96% | 1.708% | 12.35% | 40.01%
C | C | carrick on shannon | 2030 | 100% ECP | Grandfathering | IE wind not priority | 6.9 | 22.1446 | 15.1149 | 5.748 | 0.37818 | 0.90345 | 7.0297 | 25.96% | 1.708% | 4.08% | 31.74%
D | D and E North | slievecallan | 2030 | 100% ECP | Grandfathering | IE wind priority | 71.875 | 223.2727 | 214.9719 | 0 | 8.3008 | 0 | 8.3008 | 0% | 3.718% | 0% | 3.718%
C | C | carrick on shannon | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 19.97 | 25.5873 | 15.3938 | 8.0747 | 0.56374 | 1.5551 | 10.1935 | 31.56% | 2.203% | 6.078% | 39.84%
D | D and E North | slievecallan | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 71.875 | 223.2727 | 216.3907 | 0 | 6.882 | 0 | 6.882 | 0% | 3.082% | 0% | 3.082%
C | C | carrick on shannon | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 6.6567 | 8.5291 | 6.9734 | 1.159 | 0.15795 | 0.23876 | 1.5557 | 13.59% | 1.852% | 2.799% | 18.24%
J | J Country | blundelstown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 60 | 76.8772 | 53.328 | 10.4466 | 1.4237 | 11.6789 | 23.5492 | 13.59% | 1.852% | 15.19% | 30.63%
C | C | carrick on shannon | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 6.9 | 22.1446 | 15.5391 | 5.748 | 0.37818 | 0.47923 | 6.6055 | 25.96% | 1.708% | 2.164% | 29.83%
C | J Country | shanonagh | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 66.6666 | 85.419 | 56.1511 | 14.1581 | 1.5938 | 13.516 | 29.2679 | 16.57% | 1.866% | 15.82% | 34.26%
D | D and E North | slievecallan | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 71.875 | 223.2727 | 214.5255 | 0 | 8.7472 | 0 | 8.7472 | 0% | 3.918% | 0% | 3.918%
C | J Country | mullingar | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 28.85 | 36.9651 | 15.5707 | 11.6652 | 0.81441 | 8.9148 | 21.3944 | 31.56% | 2.203% | 24.12% | 57.88%
C | C | carrick on shannon | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 19.97 | 25.5873 | 15.4867 | 8.0747 | 0.56374 | 1.4621 | 10.1006 | 31.56% | 2.203% | 5.714% | 39.47%
J | J Country | cushaling | 2030 | Initial | Grandfathering | IE wind not priority | 75 | 231.2986 | 162.4824 | 31.8467 | 4.4975 | 32.472 | 68.8162 | 13.77% | 1.944% | 14.04% | 29.75%
J | J Country | cushaling | 2030 | 33% ECP | Grandfathering | IE wind not priority | 75 | 231.2986 | 157.3814 | 43.1743 | 4.3481 | 26.3948 | 73.9172 | 18.67% | 1.88% | 11.41% | 31.96%
J | J City, G South | grange | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 39.99 | 51.2387 | 31.5584 | 16.1696 | 1.1289 | 2.3818 | 19.6803 | 31.56% | 2.203% | 4.648% | 38.41%
D | D and E North | slievecallan | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 71.875 | 223.2727 | 214.9719 | 0 | 8.3008 | 0 | 8.3008 | 0% | 3.718% | 0% | 3.718%
J | J Country | athy | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 2.3446 | 1.4058 | 0.057942 | 2.5853 | 4.049 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J City, G South | grange | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 39.99 | 51.2387 | 43.0555 | 6.9626 | 0.94889 | 0.27164 | 8.1832 | 13.59% | 1.852% | 0.5302% | 15.97%
C | C | carrick on shannon | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 2.3 | 7.3815 | 4.3756 | 2.0897 | 0.13058 | 0.78561 | 3.0059 | 28.31% | 1.769% | 10.64% | 40.72%
D | D and E North | slievecallan | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 71.875 | 223.2727 | 221.3184 | 0 | 1.9543 | 0 | 1.9543 | 0% | 0.8753% | 0% | 0.8753%
C | C | carrick on shannon | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 6.6567 | 8.5291 | 6.4708 | 1.6528 | 0.15783 | 0.24762 | 2.0583 | 19.38% | 1.851% | 2.903% | 24.13%
D | D and E North | slievecallan | 2035 | 66% ECP | Grandfathering | IE wind priority | 71.875 | 223.2727 | 221.3184 | 0 | 1.9543 | 0 | 1.9543 | 0% | 0.8753% | 0% | 0.8753%
J | J Country | cushaling | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 75 | 231.2986 | 134.8266 | 80.2745 | 4.2824 | 11.9151 | 96.472 | 34.71% | 1.851% | 5.151% | 41.71%
C | C | carrick on shannon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 2.3 | 7.3815 | 4.1947 | 2.2394 | 0.13202 | 0.81535 | 3.1868 | 30.34% | 1.789% | 11.05% | 43.17%
J | J City, G South | grange | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 39.99 | 51.2387 | 31.8933 | 16.1696 | 1.1289 | 2.0469 | 19.3454 | 31.56% | 2.203% | 3.995% | 37.76%
C | C | carrick on shannon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 6.6567 | 8.5291 | 6.1873 | 1.9226 | 0.17862 | 0.24051 | 2.3418 | 22.54% | 2.094% | 2.82% | 27.46%
J | J Country | cushaling | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 75 | 231.2986 | 142.9732 | 75.193 | 4.3397 | 8.7927 | 88.3254 | 32.51% | 1.876% | 3.801% | 38.19%
J | J Country | blundelstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 60 | 76.8772 | 41.3015 | 17.3297 | 1.61 | 16.636 | 35.5757 | 22.54% | 2.094% | 21.64% | 46.28%
C | J Country | mullingar | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 28.85 | 36.9651 | 16.3111 | 11.6652 | 0.81441 | 8.1744 | 20.6541 | 31.56% | 2.203% | 22.11% | 55.87%
C | C | carrick on shannon | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 2.3 | 7.3815 | 5.4701 | 1.1541 | 0.12711 | 0.63027 | 1.9114 | 15.63% | 1.722% | 8.538% | 25.89%
J | J City, G South | griffinrath | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 33.9 | 43.4356 | 35.3447 | 7.1994 | 0.81044 | 0.081012 | 8.0909 | 16.57% | 1.866% | 0.1865% | 18.63%
J | J Country | curraghdoo | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 1.3333 | 1.7084 | 1.1006 | 0.33106 | 0.031614 | 0.24508 | 0.60776 | 19.38% | 1.851% | 14.35% | 35.58%
D | D and E North | ardnacrusha | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 7.5 | 23.298 | 22.9006 | 0 | 0.39745 | 0 | 0.39745 | 0% | 1.706% | 0% | 1.706%
C | C | stonestown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 105 | 336.9827 | 235.5875 | 96.8009 | 2.0129 | 2.5814 | 101.3952 | 28.73% | 0.5973% | 0.766% | 30.09%
C | C | stonestown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 105 | 336.9827 | 236.465 | 87.4702 | 5.7549 | 7.2926 | 100.5177 | 25.96% | 1.708% | 2.164% | 29.83%
C | C | stonestown | 2035 | 100% ECP | Grandfathering | IE wind not priority | 105 | 336.9827 | 266.4723 | 57.79 | 1.1256 | 11.5948 | 70.5104 | 17.15% | 0.334% | 3.441% | 20.92%
J | J Country | craddanstown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 121.3332 | 374.1894 | 215.8063 | 123.3447 | 2.4155 | 32.623 | 158.3831 | 32.96% | 0.6455% | 8.718% | 42.33%
C | C | dallow | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind priority | 9.99 | 32.0615 | 30.8379 | 0 | 1.2236 | 0 | 1.2236 | 0% | 3.816% | 0% | 3.816%
D | D and E North | drumline | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 74.7933 | 87.5687 | 73.0227 | 13.9024 | 0.64271 | 0.00089899 | 14.546 | 15.88% | 0.7339% | 0.001027% | 16.61%
J | J Country | athy | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 2.6932 | 2.0177 | 0.14086 | 1.5419 | 3.7005 | 31.56% | 2.203% | 24.12% | 57.88%
J | J Country | craddanstown | 2030 | 100% ECP | Grandfathering | IE wind not priority | 182 | 561.2847 | 297.2739 | 168.2147 | 10.3208 | 85.4753 | 264.0108 | 29.97% | 1.839% | 15.23% | 47.04%
C | C | dallow | 2035 | 66% ECP | Grandfathering | IE wind not priority | 44.7266 | 143.5438 | 117.4471 | 22.2531 | 0.43955 | 3.4041 | 26.0967 | 15.5% | 0.3062% | 2.371% | 18.18%
C | J Country | shanonagh | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 200 | 256.2574 | 93.9713 | 56.3456 | 2.3223 | 103.6182 | 162.2861 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J City, G South | griffinrath | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 33.9 | 43.4356 | 36.4986 | 5.9023 | 0.80439 | 0.23027 | 6.937 | 13.59% | 1.852% | 0.5302% | 15.97%
C | C | dallow | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 22.3633 | 71.7719 | 42.5452 | 20.3183 | 1.2697 | 7.6386 | 29.2266 | 28.31% | 1.769% | 10.64% | 40.72%
D | D and E North | drumline | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 74.7933 | 87.5687 | 66.4002 | 19.6479 | 0.7537 | 0.76686 | 21.1685 | 22.44% | 0.8607% | 0.8757% | 24.17%
D | D and E North | ardnacrusha | 2030 | 33% ECP | Grandfathering | IE wind priority | 7.5 | 23.298 | 22.5799 | 0 | 0.71812 | 0 | 0.71812 | 0% | 3.082% | 0% | 3.082%
J | J City, G South | griffinrath | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 52.3 | 67.0113 | 56.1653 | 10.2648 | 0.48314 | 0.097939 | 10.8459 | 15.32% | 0.721% | 0.1462% | 16.19%
C | C | stonestown | 2035 | 66% ECP | Grandfathering | IE wind not priority | 105 | 336.9827 | 275.7181 | 52.2413 | 1.0319 | 7.9914 | 61.2646 | 15.5% | 0.3062% | 2.371% | 18.18%
J | J Country | craddanstown | 2035 | 100% ECP | Grandfathering | IE wind not priority | 182 | 561.2847 | 296.6379 | 113.8411 | 2.1147 | 148.691 | 264.6468 | 20.28% | 0.3768% | 26.49% | 47.15%
C | C | dallow | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind priority | 9.99 | 32.0615 | 30.9605 | 0 | 1.101 | 0 | 1.101 | 0% | 3.434% | 0% | 3.434%
D | D and E North | drumline | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 39.3966 | 46.126 | 37.3268 | 7.7546 | 0.8722 | 0.17233 | 8.7991 | 16.81% | 1.891% | 0.3736% | 19.08%
C | C | dallow | 2035 | 66% ECP | Grandfathering | IE wind priority | 9.99 | 32.0615 | 31.7955 | 0 | 0.26601 | 0 | 0.26601 | 0% | 0.8297% | 0% | 0.8297%
J | J Country | craddanstown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 60.6666 | 187.0947 | 133.1646 | 34.9231 | 3.5172 | 15.4898 | 53.9302 | 18.67% | 1.88% | 8.279% | 28.83%
D | D and E North | drumline | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 110.19 | 129.0116 | 97.041 | 29.0529 | 1.1643 | 1.7533 | 31.9706 | 22.52% | 0.9025% | 1.359% | 24.78%
C | C | dallow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 22.3633 | 71.7719 | 40.7859 | 21.7745 | 1.2837 | 7.9278 | 30.986 | 30.34% | 1.789% | 11.05% | 43.17%
D | D and E North | drumline | 2035 | 66% ECP | Grandfathering | IE Solar not priority | 74.7933 | 87.5687 | 71.8267 | 13.9024 | 0.64271 | 1.1969 | 15.742 | 15.88% | 0.7339% | 1.367% | 17.98%
D | D and E North | drumline | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 39.3966 | 46.126 | 36.1134 | 9.0275 | 0.87211 | 0.11294 | 10.0126 | 19.57% | 1.891% | 0.2448% | 21.71%
J | J Country | bracklone | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 106.9999 | 137.0976 | 90.8852 | 18.6297 | 2.5389 | 25.0438 | 46.2124 | 13.59% | 1.852% | 18.27% | 33.71%
C | C | dallow | 2030 | 100% ECP | Grandfathering | IE wind priority | 9.99 | 32.0615 | 30.9103 | 0 | 1.1512 | 0 | 1.1512 | 0% | 3.59% | 0% | 3.59%
C | C | dallow | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 67.09 | 215.3159 | 151.0899 | 55.8893 | 3.6771 | 4.6596 | 64.226 | 25.96% | 1.708% | 2.164% | 29.83%
D | D and E North | drumline | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 39.3966 | 46.126 | 38.8671 | 6.3913 | 0.85742 | 0.010123 | 7.2588 | 13.86% | 1.859% | 0.02195% | 15.74%
D | D and E North | ardnacrusha | 2030 | Initial | Grandfathering | IE wind priority | 7.5 | 23.298 | 22.6626 | 0 | 0.63545 | 0 | 0.63545 | 0% | 2.727% | 0% | 2.727%
D | D and E North | drumline | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 110.19 | 129.0116 | 84.5464 | 40.9425 | 2.8318 | 0.6909 | 44.4652 | 31.74% | 2.195% | 0.5355% | 34.47%
J | J City, G South | griffinrath | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 70.7 | 90.587 | 55.7934 | 28.5869 | 1.9958 | 4.2109 | 34.7936 | 31.56% | 2.203% | 4.648% | 38.41%
D | D and E North | drumline | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 110.19 | 129.0116 | 84.9929 | 40.9425 | 2.8318 | 0.24439 | 44.0187 | 31.74% | 2.195% | 0.1894% | 34.12%
C | C | dallow | 2030 | 100% ECP | Grandfathering | IE wind not priority | 67.09 | 215.3159 | 146.9651 | 55.8893 | 3.6771 | 8.7844 | 68.3508 | 25.96% | 1.708% | 4.08% | 31.74%
J | J Country | craddanstown | 2035 | 66% ECP | Grandfathering | IE wind not priority | 121.3332 | 374.1894 | 223.7152 | 69.2288 | 1.3126 | 79.9327 | 150.4742 | 18.5% | 0.3508% | 21.36% | 40.21%
J | J Country | bracklone | 2030 | 33% ECP | Grandfathering | IE wind not priority | 40.8 | 125.8263 | 85.6154 | 23.4868 | 2.3654 | 14.3587 | 40.2109 | 18.67% | 1.88% | 11.41% | 31.96%
C | C | dallow | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 22.3633 | 71.7719 | 47.7347 | 15.6659 | 1.2622 | 7.1091 | 24.0372 | 21.83% | 1.759% | 9.905% | 33.49%
C | C | dallow | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 9.99 | 32.0615 | 30.9103 | 0 | 1.1512 | 0 | 1.1512 | 0% | 3.59% | 0% | 3.59%
C | C | dallow | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 9.99 | 32.0615 | 31.0907 | 0 | 0.97075 | 0 | 0.97075 | 0% | 3.028% | 0% | 3.028%
C | C | stonestown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 105 | 336.9827 | 282.9199 | 52.2413 | 1.0319 | 0.78966 | 54.0628 | 15.5% | 0.3062% | 0.2343% | 16.04%
J | J Country | craddanstown | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 182 | 561.2847 | 313.453 | 168.2147 | 10.3208 | 69.2962 | 247.8317 | 29.97% | 1.839% | 12.35% | 44.15%
D | D and E North | drumline | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 39.3966 | 46.126 | 34.5928 | 10.4992 | 0.98051 | 0.053459 | 11.5331 | 22.76% | 2.126% | 0.1159% | 25%
D | D and E North | ardnacrusha | 2030 | 33% ECP | Grandfathering | IE wind not priority | 98.7332 | 306.7052 | 247.5841 | 51.4559 | 5.1786 | 2.4866 | 59.1211 | 16.78% | 1.688% | 0.8107% | 19.28%
C | C | dallow | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 22.3633 | 71.7719 | 53.1866 | 11.2211 | 1.2359 | 6.1282 | 18.5852 | 15.63% | 1.722% | 8.538% | 25.89%
J | J Country | craddanstown | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 121.3332 | 374.1894 | 228.4525 | 69.2288 | 1.3126 | 75.1955 | 145.7369 | 18.5% | 0.3508% | 20.1% | 38.95%
J | J City, G South | griffinrath | 2030 | 100% ECP | Grandfathering | IE Solar not priority | 70.7 | 90.587 | 56.3855 | 28.5869 | 1.9958 | 3.6188 | 34.2015 | 31.56% | 2.203% | 3.995% | 37.76%
C | C | dallow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind priority | 9.99 | 32.0615 | 30.8124 | 0 | 1.2491 | 0 | 1.2491 | 0% | 3.896% | 0% | 3.896%
J | J Country | athy | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 4.4351 | 0.86881 | 0.1184 | 0.9713 | 1.9585 | 13.59% | 1.852% | 15.19% | 30.63%
C | C | stonestown | 2030 | 100% ECP | Grandfathering | IE wind not priority | 105 | 336.9827 | 230.0094 | 87.4702 | 5.7549 | 13.7481 | 106.9733 | 25.96% | 1.708% | 4.08% | 31.74%
J | J City, G South | griffinrath | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 52.3 | 67.0113 | 56.2487 | 10.2648 | 0.48314 | 0.01459 | 10.7626 | 15.32% | 0.721% | 0.02177% | 16.06%
C | C | dallow | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind priority | 9.99 | 32.0615 | 31.7955 | 0 | 0.26601 | 0 | 0.26601 | 0% | 0.8297% | 0% | 0.8297%
J | J Country | athy | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 3.4349 | 1.4413 | 0.1339 | 1.3836 | 2.9587 | 22.54% | 2.094% | 21.64% | 46.28%
J | J Country | curraghdoo | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 1.3333 | 1.7084 | 1.1325 | 0.23215 | 0.031638 | 0.31207 | 0.57586 | 13.59% | 1.852% | 18.27% | 33.71%
D | D and E North | ardnacrusha | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 39.673 | 46.4495 | 38.8939 | 6.4361 | 0.86343 | 0.256 | 7.5556 | 13.86% | 1.859% | 0.5511% | 16.27%
D | D and E North | ennis | 2030 | Initial | Grandfathering | IE Solar not priority | 18.3 | 21.4258 | 19.1228 | 1.772 | 0.27607 | 0.2549 | 2.303 | 8.271% | 1.289% | 1.19% | 10.75%
C | C | dallow | 2030 | Initial | Grandfathering | IE wind priority | 9.99 | 32.0615 | 31.1897 | 0 | 0.8718 | 0 | 0.8718 | 0% | 2.719% | 0% | 2.719%
J | J City, G South | griffinrath | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE Solar not priority | 33.9 | 43.4356 | 34.0641 | 8.4173 | 0.80379 | 0.15044 | 9.3715 | 19.38% | 1.851% | 0.3464% | 21.58%
D | D and E North | drumline | 2030 | Initial | Grandfathering | IE Solar not priority | 4 | 4.6832 | 4.1798 | 0.38733 | 0.060344 | 0.055717 | 0.50339 | 8.271% | 1.289% | 1.19% | 10.75%
J | J Country | craddanstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE wind not priority | 60.6666 | 187.0947 | 109.0597 | 64.9331 | 3.464 | 9.638 | 78.035 | 34.71% | 1.851% | 5.151% | 41.71%
C | C | dallow | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind not priority | 44.7266 | 143.5438 | 100.3527 | 41.234 | 0.85745 | 1.0996 | 43.1911 | 28.73% | 0.5973% | 0.766% | 30.09%
D | D and E North | drumline | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 39.3966 | 46.126 | 38.623 | 6.3913 | 0.85742 | 0.25422 | 7.5029 | 13.86% | 1.859% | 0.5511% | 16.27%
C | C | stonestown | 2030 | 33% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 105 | 336.9827 | 249.7214 | 52.6854 | 5.8027 | 28.7731 | 87.2613 | 15.63% | 1.722% | 8.538% | 25.89%
J | J Country | curraghdoo | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 1.3333 | 1.7084 | 1.123 | 0.28316 | 0.031876 | 0.27032 | 0.58536 | 16.57% | 1.866% | 15.82% | 34.26%
D | D and E North | ennis | 2030 | 33% ECP | Grandfathering | IE Solar not priority | 42.8966 | 50.2238 | 42.0543 | 6.9591 | 0.93359 | 0.2768 | 8.1695 | 13.86% | 1.859% | 0.5511% | 16.27%
C | C | cregg | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 75 | 96.0965 | 66.1412 | 21.1296 | 0.87087 | 7.9549 | 29.9554 | 21.99% | 0.9062% | 8.278% | 31.17%
J | J Country | blundelstown | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 60 | 76.8772 | 36.0137 | 16.8904 | 0.65682 | 23.3163 | 40.8635 | 21.97% | 0.8544% | 30.33% | 53.15%
D | D and E North | ennis | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE Solar not priority | 42.8966 | 50.2238 | 40.6429 | 8.4435 | 0.94968 | 0.18764 | 9.5809 | 16.81% | 1.891% | 0.3736% | 19.08%
C | C | dallow | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE wind priority | 9.99 | 32.0615 | 31.5173 | 0 | 0.54419 | 0 | 0.54419 | 0% | 1.697% | 0% | 1.697%
C | J Country | mullingar | 2030 | 33% ECP | Grandfathering | IE wind not priority | 38.8333 | 124.63 | 88.7765 | 19.4852 | 2.1461 | 14.2222 | 35.8535 | 15.63% | 1.722% | 11.41% | 28.77%
J | J Country | craddanstown | 2030 | 33% ECP + 2.6 GW Offshore | Grandfathering | IE wind not priority | 60.6666 | 187.0947 | 115.6493 | 60.8227 | 3.5104 | 7.1123 | 71.4454 | 32.51% | 1.876% | 3.801% | 38.19%
C | C | cregg | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 49.9999 | 64.0643 | 46.8203 | 14.0753 | 0.54735 | 2.6213 | 17.244 | 21.97% | 0.8544% | 4.092% | 26.92%
C | J Country | shanonagh | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 133.3332 | 170.8381 | 84.1562 | 26.1691 | 1.2317 | 59.2811 | 86.6819 | 15.32% | 0.721% | 34.7% | 50.74%
J | J Country | athy | 2030 | 100% ECP Maintenance Sensitivity | Grandfathering | IE Solar not priority | 4.99 | 6.3936 | 2.8212 | 2.0177 | 0.14086 | 1.4139 | 3.5724 | 31.56% | 2.203% | 22.11% | 55.87%
C | J Country | mullingar | 2030 | Initial | Grandfathering | IE Solar not priority | 12 | 15.3754 | 12.1742 | 1.2157 | 0.19884 | 1.7867 | 3.2013 | 7.907% | 1.293% | 11.62% | 20.82%
C | C | dallow | 2030 | 33% ECP | Grandfathering | IE wind priority | 9.99 | 32.0615 | 31.0907 | 0 | 0.97075 | 0 | 0.97075 | 0% | 3.028% | 0% | 3.028%
C | J Country | shanonagh | 2035 | 66% ECP + 4.7 GW Offshore | Grandfathering | IE Solar not priority | 133.3332 | 170.8381 | 80.0304 | 37.5342 | 1.4596 | 51.8139 | 90.8077 | 21.97% | 0.8544% | 30.33% | 53.15%
J | J City, G South | griffinrath | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Grandfathering | IE Solar not priority | 33.9 | 43.4356 | 32.6032 | 9.7913 | 0.90963 | 0.13152 | 10.8324 | 22.54% | 2.094% | 0.3028% | 24.94%
C | J Country | mullingar | 2030 | Initial | Grandfathering | IE wind not priority | 9.5 | 30.4889 | 22.2148 | 3.4549 | 0.53888 | 4.2803 | 8.2741 | 11.33% | 1.767% | 14.04% | 27.14%
C | C | dallow | 2035 | 66% ECP Maintenance Sensitivity | Grandfathering | IE wind not priority | 44.7266 | 143.5438 | 120.5148 | 22.2531 | 0.43955 | 0.33637 | 23.029 | 15.5% | 0.3062% | 0.2343% | 16.04%
J | J Country | bracklone | 2030 | 33% ECP + 1.3 GW Offshore | Grandfathering | IE wind not priority | 40.8 | 125.8263 | 83.3562 | 32.1087 | 2.389 | 7.9724 | 42.4701 | 25.52% | 1.899% | 6.336% | 33.75%
J | J Country | blundelstown | 2035 | 100% ECP | Grandfathering | IE Solar not priority | 60 | 76.8772 | 28.1914 | 16.9037 | 0.6967 | 31.0855 | 48.6858 | 21.99% | 0.9062% | 40.44% | 63.33%
C | C | dallow | 2030 | 33% ECP | Grandfathering | IE wind not priority | 22.3633 | 71.7719 | 51.9153 | 11.2211 | 1.2359 | 7.3995 | 19.8566 | 15.63% | 1.722% | 10.31% | 27.67%
J | J City, G South | belcamp 220kv | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 250 | 1047.3798 | 659.6706 | 306.6733 | 18.9531 | 62.0827 | 387.7091 | 29.28% | 1.81% | 5.927% | 37.02%
H2 | H2 & K | carlow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 31.0966 | 36.4083 | 26.0617 | 8.2872 | 0.77394 | 1.2854 | 10.3466 | 22.76% | 2.126% | 3.531% | 28.42%
J | J Country | athy | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 4.2385 | 0.86881 | 0.1184 | 1.1679 | 2.1551 | 13.59% | 1.852% | 18.27% | 33.71%
I | E,F & I | trabeg | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 3.9331 | 1.3051 | 0.052305 | 0.50501 | 1.8624 | 22.52% | 0.9025% | 8.714% | 32.14%
J | J Country | portlaoise | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 45.001 | 138.7823 | 78.8714 | 41.5925 | 2.5519 | 15.7665 | 59.9108 | 29.97% | 1.839% | 11.36% | 43.17%
J | J Country | portlaoise | 2030 | Initial | Pro-rata | IE wind not priority | 45.001 | 138.7823 | 100.7301 | 19.1085 | 2.6986 | 16.2451 | 38.0521 | 13.77% | 1.944% | 11.71% | 27.42%
J | J Country | thornsberry | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 164.4665 | 210.7288 | 98.7175 | 46.2985 | 1.8004 | 63.9124 | 112.0113 | 21.97% | 0.8544% | 30.33% | 53.15%
H2 | H2 & K | ballywater | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 42 | 118.8065 | 113.73 | 0 | 4.5741 | 0.50242 | 5.0765 | 0% | 3.85% | 0.4229% | 4.273%
H2 | H2 & K | carlow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 30.49 | 86.2478 | 78.3341 | 0 | 3.5862 | 4.3276 | 7.9138 | 0% | 4.158% | 5.018% | 9.176%
H2 | H2 & K | carlow | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 7 | 19.8011 | 12.649 | 5.9936 | 0.3776 | 0.7808 | 7.152 | 30.27% | 1.907% | 3.943% | 36.12%
H2 | H2 & K | carlow | 2035 | 100% ECP | Pro-rata | IE wind not priority | 21 | 59.4032 | 45.3054 | 10.6882 | 0.2127 | 3.1969 | 14.0978 | 17.99% | 0.3581% | 5.382% | 23.73%
J | J City, G South | stephenstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 3.33 | 4.2667 | 3.2026 | 0.9618 | 0.089353 | 0.012919 | 1.0641 | 22.54% | 2.094% | 0.3028% | 24.94%
J | J Country | portlaoise | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 45.001 | 138.7823 | 87.4228 | 25.6761 | 0.48684 | 25.1965 | 51.3595 | 18.5% | 0.3508% | 18.16% | 37.01%
H2 | H2 & K | carlow | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 30.49 | 86.2478 | 79.9938 | 0 | 1.5861 | 4.668 | 6.254 | 0% | 1.839% | 5.412% | 7.251%
J | J City, G South | belcamp 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 250 | 1047.3798 | 724.1763 | 293.7322 | 6.2442 | 23.2271 | 323.2034 | 28.04% | 0.5962% | 2.218% | 30.86%
H2 | H2 & K | carlow | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 31.0966 | 36.4083 | 30.5181 | 5.0448 | 0.67678 | 0.16861 | 5.8902 | 13.86% | 1.859% | 0.4631% | 16.18%
H2 | H2 & K | carlow | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 7 | 19.8011 | 16.1156 | 3.2346 | 0.35467 | 0.09622 | 3.6855 | 16.34% | 1.791% | 0.4859% | 18.61%
J | J City, G South | stephenstown | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 9.99 | 12.8001 | 7.9673 | 4.0394 | 0.28201 | 0.51134 | 4.8327 | 31.56% | 2.203% | 3.995% | 37.76%
I | E,F & I | trabeg | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.0323 | 1.3003 | 0.049882 | 0.41295 | 1.7632 | 22.44% | 0.8607% | 7.125% | 30.42%
H2 | H2 & K | banoge | 2030 | Initial | Pro-rata | IE Solar not priority | 8 | 9.3665 | 7.8106 | 0.77466 | 0.12069 | 0.66049 | 1.5558 | 8.271% | 1.289% | 7.052% | 16.61%
H2 | H2 & K | carlow | 2035 | 100% ECP | Pro-rata | IE wind priority | 30.49 | 86.2478 | 80.783 | 0 | 0.82325 | 4.6416 | 5.4649 | 0% | 0.9545% | 5.382% | 6.336%
J | J Country | athy | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 4.1191 | 1.239 | 0.11832 | 0.91722 | 2.2745 | 19.38% | 1.851% | 14.35% | 35.58%
J | J Country | thornsberry | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 164.4665 | 210.7288 | 97.6412 | 32.2796 | 1.5193 | 79.2887 | 113.0876 | 15.32% | 0.721% | 37.63% | 53.67%
J | J Country | thornsberry | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 243.8 | 312.3778 | 114.551 | 68.6852 | 2.8309 | 126.3106 | 197.8267 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J Country | thornsberry | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 164.4665 | 210.7288 | 103.8066 | 32.2796 | 1.5193 | 73.1232 | 106.9222 | 15.32% | 0.721% | 34.7% | 50.74%
H2 | H2 & K | carlow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 7 | 19.8011 | 12.0065 | 6.42 | 0.38102 | 0.99353 | 7.7946 | 32.42% | 1.924% | 5.018% | 39.36%
J | J City, G South | arodstown | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 155.1998 | 198.8555 | 167.0025 | 27.0218 | 3.6826 | 1.1486 | 31.853 | 13.59% | 1.852% | 0.5776% | 16.02%
H2 | H2 & K | carlow | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 30.49 | 86.2478 | 83.0922 | 0 | 2.7365 | 0.41911 | 3.1556 | 0% | 3.173% | 0.4859% | 3.659%
J | J Country | portlaoise | 2035 | 66% ECP | Pro-rata | IE wind not priority | 45.001 | 138.7823 | 85.8354 | 25.6761 | 0.48684 | 26.7839 | 52.9468 | 18.5% | 0.3508% | 19.3% | 38.15%
J | J Country | portlaoise | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 2.6667 | 3.4168 | 1.5832 | 0.52338 | 0.024634 | 1.2856 | 1.8336 | 15.32% | 0.721% | 37.63% | 53.67%
H2 | H2 & K | carlow | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 93.29 | 109.2249 | 79.9876 | 24.597 | 0.98576 | 3.6544 | 29.2372 | 22.52% | 0.9025% | 3.346% | 26.77%
H2 | H2 & K | carlow | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 31.0966 | 36.4083 | 27.3192 | 7.1256 | 0.68838 | 1.2751 | 9.0891 | 19.57% | 1.891% | 3.502% | 24.96%
H2 | H2 & K | ballywater | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 42 | 118.8065 | 110.1915 | 0 | 2.1848 | 6.4301 | 8.6149 | 0% | 1.839% | 5.412% | 7.251%
J | J Country | philipstown | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 50 | 64.0644 | 23.4928 | 14.0864 | 0.58058 | 25.9046 | 40.5715 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J City, G South | stephenstown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 3.33 | 4.2667 | 3.5853 | 0.57978 | 0.079015 | 0.02262 | 0.68142 | 13.59% | 1.852% | 0.5302% | 15.97%
H2 | H2 & K | carlow | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 30.49 | 86.2478 | 79.31 | 0 | 3.5369 | 3.4009 | 6.9378 | 0% | 4.101% | 3.943% | 8.044%
H2 | H2 & K | ballywater | 2035 | 66% ECP | Pro-rata | IE wind priority | 42 | 118.8065 | 113.0115 | 0 | 1.0348 | 4.7602 | 5.795 | 0% | 0.871% | 4.007% | 4.878%
J | J Country | athy | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 4.2029 | 1.0597 | 0.1193 | 1.0117 | 2.1907 | 16.57% | 1.866% | 15.82% | 34.26%
J | J City, G South | stephenstown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 3.33 | 4.2667 | 3.3461 | 0.82683 | 0.078956 | 0.014778 | 0.92056 | 19.38% | 1.851% | 0.3464% | 21.58%
H2 | H2 & K | ballywater | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 42 | 118.8065 | 114.6447 | 0 | 1.0348 | 3.1269 | 4.1617 | 0% | 0.871% | 2.632% | 3.503%
J | J Country | athy | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 2.3446 | 1.4058 | 0.057942 | 2.5853 | 4.049 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J Country | athy | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 3.4349 | 1.4413 | 0.1339 | 1.3836 | 2.9587 | 22.54% | 2.094% | 21.64% | 46.28%
H2 | H2 & K | carlow | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 62.1933 | 72.8165 | 53.3429 | 16.3379 | 0.62673 | 2.5089 | 19.4736 | 22.44% | 0.8607% | 3.445% | 26.74%
I | E,F & I | trabeg | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.5653 | 0.80304 | 0.10773 | 0.31945 | 1.2302 | 13.86% | 1.859% | 5.512% | 21.23%
I | E,F & I | trabeg | 2030 | Initial | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.3648 | 0.47932 | 0.074676 | 0.87675 | 1.4308 | 8.271% | 1.289% | 15.13% | 24.69%
J | J City, G South | arodstown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 155.1998 | 198.8555 | 161.8142 | 32.9601 | 3.7103 | 0.37089 | 37.0414 | 16.57% | 1.866% | 0.1865% | 18.63%
H2 | H2 & K | ballywater | 2035 | 100% ECP | Pro-rata | IE wind priority | 42 | 118.8065 | 111.2786 | 0 | 1.134 | 6.3938 | 7.5279 | 0% | 0.9545% | 5.382% | 6.336%
J | J Country | portlaoise | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4 | 5.1251 | 2.2615 | 1.6174 | 0.11292 | 1.1334 | 2.8636 | 31.56% | 2.203% | 22.11% | 55.87%
J | J Country | athy | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 2.8212 | 2.0177 | 0.14086 | 1.4139 | 3.5724 | 31.56% | 2.203% | 22.11% | 55.87%
J | J City, G South | arodstown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 155.1998 | 198.8555 | 155.9513 | 38.5356 | 3.6799 | 0.68875 | 42.9042 | 19.38% | 1.851% | 0.3464% | 21.58%
J | J City, G South | stephenstown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 6.66 | 8.5334 | 7.1628 | 1.3071 | 0.061524 | 0.0018579 | 1.3705 | 15.32% | 0.721% | 0.02177% | 16.06%
H2 | H2 & K | banoge | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 8 | 9.3665 | 7.4477 | 1.487 | 0.068745 | 0.36301 | 1.9188 | 15.88% | 0.7339% | 3.876% | 20.49%
J | J Country | portlaoise | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 1.3333 | 1.7084 | 1.1006 | 0.33106 | 0.031614 | 0.24508 | 0.60776 | 19.38% | 1.851% | 14.35% | 35.58%
H2 | H2 & K | carlow | 2030 | 33% ECP | Pro-rata | IE wind not priority | 7 | 19.8011 | 15.7001 | 3.2346 | 0.35467 | 0.51169 | 4.101 | 16.34% | 1.791% | 2.584% | 20.71%
J | J Country | thornsberry | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 85.1333 | 109.0801 | 72.3118 | 14.8225 | 2.0201 | 19.9258 | 36.7684 | 13.59% | 1.852% | 18.27% | 33.71%
J | J Country | athy | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 2.6932 | 2.0177 | 0.14086 | 1.5419 | 3.7005 | 31.56% | 2.203% | 24.12% | 57.88%
H2 | H2 & K | carlow | 2035 | 66% ECP | Pro-rata | IE wind not priority | 14 | 39.6021 | 31.4584 | 6.4269 | 0.13016 | 1.5867 | 8.1438 | 16.23% | 0.3287% | 4.007% | 20.56%
J | J Country | portlaoise | 2035 | 100% ECP | Pro-rata | IE wind not priority | 45.001 | 138.7823 | 76.2807 | 28.1482 | 0.52287 | 33.8306 | 62.5016 | 20.28% | 0.3768% | 24.38% | 45.04%
J | J City, G South | arodstown | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 310.3997 | 397.7111 | 333.3407 | 60.9217 | 2.8674 | 0.58127 | 64.3704 | 15.32% | 0.721% | 0.1462% | 16.19%
H2 | H2 & K | carlow | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 21 | 59.4032 | 41.7325 | 16.3339 | 1.0856 | 0.25121 | 17.6708 | 27.5% | 1.828% | 0.4229% | 29.75%
J | J Country | portlaoise | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 45.001 | 138.7823 | 86.4302 | 45.1168 | 2.6039 | 4.6313 | 52.352 | 32.51% | 1.876% | 3.337% | 37.72%
I | E,F & I | trabeg | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.7231 | 0.80304 | 0.10773 | 0.16162 | 1.0724 | 13.86% | 1.859% | 2.789% | 18.5%
J | J Country | thornsberry | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 85.1333 | 109.0801 | 71.705 | 18.0799 | 2.0353 | 17.26 | 37.3752 | 16.57% | 1.866% | 15.82% | 34.26%
J | J Country | portlaoise | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 1.3333 | 1.7084 | 1.1851 | 0.23215 | 0.031638 | 0.25953 | 0.52331 | 13.59% | 1.852% | 15.19% | 30.63%
H2 | H2 & K | carlow | 2030 | 33% ECP | Pro-rata | IE wind priority | 30.49 | 86.2478 | 81.2826 | 0 | 2.7365 | 2.2288 | 4.9653 | 0% | 3.173% | 2.584% | 5.757%
H2 | H2 & K | banoge | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 8 | 9.3665 | 6.1793 | 2.9725 | 0.2056 | 0.0090734 | 3.1872 | 31.74% | 2.195% | 0.09687% | 34.03%
J | J City, G South | arodstown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 155.1998 | 198.8555 | 167.0969 | 27.0218 | 3.6826 | 1.0542 | 31.7586 | 13.59% | 1.852% | 0.5302% | 15.97%
J | J City, G South | arodstown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 310.3997 | 397.7111 | 333.8354 | 60.9217 | 2.8674 | 0.086592 | 63.8757 | 15.32% | 0.721% | 0.02177% | 16.06%
J | J City, G South | arodstown | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 465.6 | 596.5672 | 371.331 | 188.2611 | 13.1435 | 23.8317 | 225.2362 | 31.56% | 2.203% | 3.995% | 37.76%
H2 | H2 & K | carlow | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 30.49 | 86.2478 | 82.5626 | 0 | 3.3206 | 0.36473 | 3.6853 | 0% | 3.85% | 0.4229% | 4.273%
J | J Country | portlaoise | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 45.001 | 138.7823 | 100.1816 | 25.9051 | 2.6089 | 10.0865 | 38.6006 | 18.67% | 1.88% | 7.268% | 27.81%
J | J City, G South | arodstown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 465.6 | 596.5672 | 367.4317 | 188.2611 | 13.1435 | 27.7309 | 229.1355 | 31.56% | 2.203% | 4.648% | 38.41%
H2 | H2 & K | banoge | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 8 | 9.3665 | 6.8593 | 2.1093 | 0.084533 | 0.31338 | 2.5072 | 22.52% | 0.9025% | 3.346% | 26.77%
I | E,F & I | trabeg | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 3.7803 | 1.8392 | 0.12721 | 0.04881 | 2.0153 | 31.74% | 2.195% | 0.8422% | 34.77%
J | J City, G South | stephenstown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 6.66 | 8.5334 | 6.5838 | 1.8748 | 0.072907 | 0.0018043 | 1.9495 | 21.97% | 0.8544% | 0.02114% | 22.85%
H2 | H2 & K | carlow | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 93.29 | 109.2249 | 72.0585 | 34.6631 | 2.3975 | 0.10581 | 37.1664 | 31.74% | 2.195% | 0.09687% | 34.03%
H2 | H2 & K | banoge | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 8 | 9.3665 | 6.8616 | 2.1016 | 0.080617 | 0.32272 | 2.5049 | 22.44% | 0.8607% | 3.445% | 26.74%
J | J Country | portlaoise | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 45.001 | 138.7823 | 81.771 | 48.1658 | 2.5695 | 6.276 | 57.0112 | 34.71% | 1.851% | 4.522% | 41.08%
J | J City, G South | stephenstown | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 9.99 | 12.8001 | 9.8521 | 2.8145 | 0.116 | 0.017531 | 2.948 | 21.99% | 0.9062% | 0.137% | 23.03%
H2 | H2 & K | carlow | 2030 | Initial | Pro-rata | IE wind priority | 30.49 | 86.2478 | 78.7189 | 0 | 2.4228 | 5.1061 | 7.529 | 0% | 2.809% | 5.92% | 8.729%
J | J Country | portlaoise | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 4 | 5.1251 | 1.8794 | 1.1269 | 0.046446 | 2.0724 | 3.2457 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J Country | thornsberry | 2030 | Initial | Pro-rata | IE Solar not priority | 5.8 | 7.4315 | 5.8842 | 0.58758 | 0.096106 | 0.86359 | 1.5473 | 7.907% | 1.293% | 11.62% | 20.82%
H2 | H2 & K | banoge | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 8 | 9.3665 | 7.6932 | 1.487 | 0.068745 | 0.1175 | 1.6733 | 15.88% | 0.7339% | 1.254% | 17.86%
I | E,F & I | trabeg | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 3.7285 | 1.8392 | 0.12721 | 0.10056 | 2.067 | 31.74% | 2.195% | 1.735% | 35.67%
I | E,F & I | trabeg | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.2253 | 0.9201 | 0.042536 | 0.6076 | 1.5702 | 15.88% | 0.7339% | 10.48% | 27.09%
J | J City, G South | stephenstown | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 6.66 | 8.5334 | 7.1522 | 1.3071 | 0.061524 | 0.012472 | 1.3811 | 15.32% | 0.721% | 0.1462% | 16.19%
H2 | H2 & K | carlow | 2035 | 66% ECP | Pro-rata | IE wind priority | 30.49 | 86.2478 | 82.0409 | 0 | 0.7512 | 3.4557 | 4.2069 | 0% | 0.871% | 4.007% | 4.878%
J | J Country | athy | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 2.9625 | 0.97938 | 0.046097 | 2.4057 | 3.4311 | 15.32% | 0.721% | 37.63% | 53.67%
I | E,F & I | trabeg | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.5537 | 0.9201 | 0.042536 | 0.27919 | 1.2418 | 15.88% | 0.7339% | 4.817% | 21.43%
J | J Country | athy | 2030 | Initial | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 5.0624 | 0.50552 | 0.082684 | 0.74299 | 1.3312 | 7.907% | 1.293% | 11.62% | 20.82%
I | E,F & I | trabeg | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.3232 | 1.1343 | 0.10958 | 0.22851 | 1.4723 | 19.57% | 1.891% | 3.943% | 25.4%
J | J Country | athy | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 4.4351 | 0.86881 | 0.1184 | 0.9713 | 1.9585 | 13.59% | 1.852% | 15.19% | 30.63%
J | J Country | portlaoise | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 1.3333 | 1.7084 | 0.91781 | 0.3851 | 0.035777 | 0.36969 | 0.79057 | 22.54% | 2.094% | 21.64% | 46.28%
H2 | H2 & K | carlow | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 30.49 | 86.2478 | 81.9266 | 0 | 3.119 | 1.2022 | 4.3212 | 0% | 3.616% | 1.394% | 5.01%
J | J Country | thornsberry | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 243.8 | 312.3778 | 131.5819 | 98.5783 | 6.8823 | 75.3353 | 180.7959 | 31.56% | 2.203% | 24.12% | 57.88%
J | J Country | portlaoise | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 4 | 5.1251 | 2.1588 | 1.6174 | 0.11292 | 1.236 | 2.9663 | 31.56% | 2.203% | 24.12% | 57.88%
H2 | H2 & K | carlow | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 62.1933 | 72.8165 | 59.8083 | 11.5604 | 0.53443 | 0.91344 | 13.0082 | 15.88% | 0.7339% | 1.254% | 17.86%
H2 | H2 & K | banoge | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 8 | 9.3665 | 7.3658 | 1.5747 | 0.17711 | 0.24886 | 2.0007 | 16.81% | 1.891% | 2.657% | 21.36%
J | J City, G South | stephenstown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 9.99 | 12.8001 | 7.8837 | 4.0394 | 0.28201 | 0.595 | 4.9164 | 31.56% | 2.203% | 4.648% | 38.41%
J | J Country | portlaoise | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 2.6667 | 3.4168 | 1.6831 | 0.52338 | 0.024634 | 1.1856 | 1.7336 | 15.32% | 0.721% | 34.7% | 50.74%
J | J Country | athy | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 2.9951 | 1.4047 | 0.054625 | 1.9391 | 3.3985 | 21.97% | 0.8544% | 30.33% | 53.15%
H2 | H2 & K | carlow | 2030 | 100% ECP | Pro-rata | IE wind not priority | 21 | 59.4032 | 41.0264 | 16.3339 | 1.0856 | 0.95727 | 18.3768 | 27.5% | 1.828% | 1.611% | 30.94%
H2 | H2 & K | banoge | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 8 | 9.3665 | 7.5548 | 1.2978 | 0.17411 | 0.3397 | 1.8116 | 13.86% | 1.859% | 3.627% | 19.34%
J | J Country | portlaoise | 2030 | 33% ECP | Pro-rata | IE wind not priority | 45.001 | 138.7823 | 96.3654 | 25.9051 | 2.6089 | 13.9028 | 42.4169 | 18.67% | 1.88% | 10.02% | 30.56%
H2 | H2 & K | carlow | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 31.0966 | 36.4083 | 28.6316 | 6.1209 | 0.68844 | 0.96736 | 7.7767 | 16.81% | 1.891% | 2.657% | 21.36%
H2 | H2 & K | carlow | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 14 | 39.6021 | 24.9156 | 12.2765 | 0.26661 | 2.1434 | 14.6865 | 31% | 0.6732% | 5.412% | 37.09%
J | J Country | thornsberry | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 243.8 | 312.3778 | 137.8384 | 98.5783 | 6.8823 | 69.0788 | 174.5393 | 31.56% | 2.203% | 22.11% | 55.87%
J | J City, G South | belcamp 220kv | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 250 | 1047.3798 | 676.6354 | 284.83 | 18.5752 | 67.3392 | 370.7444 | 27.19% | 1.773% | 6.429% | 35.4%
H2 | H2 & K | banoge | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 8 | 9.3665 | 7.0282 | 1.8332 | 0.17709 | 0.32803 | 2.3383 | 19.57% | 1.891% | 3.502% | 24.96%
I | E,F & I | trabeg | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.4283 | 0.97433 | 0.10959 | 0.2833 | 1.3672 | 16.81% | 1.891% | 4.888% | 23.59%
H2 | H2 & K | carlow | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 30.49 | 86.2478 | 83.2266 | 0 | 0.7512 | 2.27 | 3.0212 | 0% | 0.871% | 2.632% | 3.503%
J | J Country | portlaoise | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 45.001 | 138.7823 | 81.208 | 45.747 | 0.89587 | 10.9313 | 57.5742 | 32.96% | 0.6455% | 7.877% | 41.49%
J | J Country | thornsberry | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 85.1333 | 109.0801 | 70.2747 | 21.1383 | 2.0186 | 15.6486 | 38.8054 | 19.38% | 1.851% | 14.35% | 35.58%
J | J Country | portlaoise | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 2.6667 | 3.4168 | 1.6006 | 0.75068 | 0.029192 | 1.0363 | 1.8162 | 21.97% | 0.8544% | 30.33% | 53.15%
J | J Country | portlaoise | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 1.3333 | 1.7084 | 1.123 | 0.28316 | 0.031876 | 0.27032 | 0.58536 | 16.57% | 1.866% | 15.82% | 34.26%
H2 | H2 & K | banoge | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 8 | 9.3665 | 6.0696 | 2.9725 | 0.2056 | 0.11877 | 3.2969 | 31.74% | 2.195% | 1.268% | 35.2%
H2 | H2 & K | carlow | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 62.1933 | 72.8165 | 57.8996 | 11.5604 | 0.53443 | 2.8221 | 14.9169 | 15.88% | 0.7339% | 3.876% | 20.49%
J | J City, G South | arodstown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 310.3997 | 397.7111 | 306.8494 | 87.3797 | 3.3979 | 0.08409 | 90.8617 | 21.97% | 0.8544% | 0.02114% | 22.85%
H2 | H2 & K | carlow | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 31.0966 | 36.4083 | 29.3663 | 5.0448 | 0.67678 | 1.3204 | 7.042 | 13.86% | 1.859% | 3.627% | 19.34%
H2 | H2 & K | carlow | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 93.29 | 109.2249 | 70.7793 | 34.6631 | 2.3975 | 1.385 | 38.4455 | 31.74% | 2.195% | 1.268% | 35.2%
I | E,F & I | trabeg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.1838 | 1.3192 | 0.1232 | 0.16931 | 1.6117 | 22.76% | 2.126% | 2.921% | 27.81%
H2 | H2 & K | banoge | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 8 | 9.3665 | 7.8512 | 1.2978 | 0.17411 | 0.043376 | 1.5153 | 13.86% | 1.859% | 0.4631% | 16.18%
J | J Country | thornsberry | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 85.1333 | 109.0801 | 58.6022 | 24.5889 | 2.2844 | 23.6046 | 50.4779 | 22.54% | 2.094% | 21.64% | 46.28%
H2 | H2 & K | carlow | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 14 | 39.6021 | 32.0028 | 6.4269 | 0.13016 | 1.0423 | 7.5993 | 16.23% | 0.3287% | 2.632% | 19.19%
J | J Country | portlaoise | 2030 | 100% ECP | Pro-rata | IE wind not priority | 45.001 | 138.7823 | 75.1903 | 41.5925 | 2.5519 | 19.4476 | 63.592 | 29.97% | 1.839% | 14.01% | 45.82%
J | J City, G South | arodstown | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 465.6 | 596.5672 | 459.1713 | 131.1725 | 5.4064 | 0.81707 | 137.3959 | 21.99% | 0.9062% | 0.137% | 23.03%
J | J Country | portlaoise | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 45.001 | 138.7823 | 93.0132 | 35.4148 | 2.635 | 7.7192 | 45.7691 | 25.52% | 1.899% | 5.562% | 32.98%
H2 | H2 & K | carlow | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 7 | 19.8011 | 14.6205 | 4.5388 | 0.36576 | 0.276 | 5.1805 | 22.92% | 1.847% | 1.394% | 26.16%
H2 | H2 & K | banoge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 8 | 9.3665 | 6.7047 | 2.132 | 0.19911 | 0.33069 | 2.6618 | 22.76% | 2.126% | 3.531% | 28.42%
J | J Country | athy | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 3.1495 | 0.97938 | 0.046097 | 2.2186 | 3.2441 | 15.32% | 0.721% | 34.7% | 50.74%
H2 | H2 & K | carlow | 2030 | 100% ECP | Pro-rata | IE wind priority | 30.49 | 86.2478 | 81.5374 | 0 | 3.3206 | 1.3899 | 4.7104 | 0% | 3.85% | 1.611% | 5.461%
J | J Country | thornsberry | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 85.1333 | 109.0801 | 75.6665 | 14.8225 | 2.0201 | 16.5711 | 33.4136 | 13.59% | 1.852% | 15.19% | 30.63%
J | J City, G South | arodstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 155.1998 | 198.8555 | 149.2628 | 44.8262 | 4.1645 | 0.60213 | 49.5927 | 22.54% | 2.094% | 0.3028% | 24.94%
J | J Country | portlaoise | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 1.3333 | 1.7084 | 1.1325 | 0.23215 | 0.031638 | 0.31207 | 0.57586 | 13.59% | 1.852% | 18.27% | 33.71%
K | H2 & K | butlerstown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 40.9433 | 47.9368 | 35.1169 | 10.7556 | 0.41259 | 1.6517 | 12.8199 | 22.44% | 0.8607% | 3.445% | 26.74%
H2 | H2 & K | arklow | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 53.2 | 150.4882 | 144.058 | 0 | 5.7938 | 0.6364 | 6.4302 | 0% | 3.85% | 0.4229% | 4.273%
J | J City, G South | griffinrath | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 33.9 | 43.4356 | 32.6032 | 9.7913 | 0.90963 | 0.13152 | 10.8324 | 22.54% | 2.094% | 0.3028% | 24.94%
H2 | H2 & K | arklow | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 128.89 | 150.9057 | 99.5564 | 47.8907 | 3.3124 | 0.14618 | 51.3493 | 31.74% | 2.195% | 0.09687% | 34.03%
K | H2 & K | rathnaskilloge | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 95 | 111.227 | 88.4414 | 17.6584 | 0.81635 | 4.3108 | 22.7855 | 15.88% | 0.7339% | 3.876% | 20.49%
J | J City, G South | gallanstown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 161.4 | 206.7997 | 173.7723 | 28.1013 | 3.8297 | 1.0964 | 33.0274 | 13.59% | 1.852% | 0.5302% | 15.97%
J | J City, G South | griffinrath | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 33.9 | 43.4356 | 36.4986 | 5.9023 | 0.80439 | 0.23027 | 6.937 | 13.59% | 1.852% | 0.5302% | 15.97%
J | J City, G South | gallanstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 161.4 | 206.7997 | 155.2258 | 46.6169 | 4.3308 | 0.62618 | 51.5739 | 22.54% | 2.094% | 0.3028% | 24.94%
K | H2 & K | rathnaskilloge | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 95 | 111.227 | 73.3793 | 35.2984 | 2.4414 | 0.10775 | 37.8476 | 31.74% | 2.195% | 0.09687% | 34.03%
J | J City, G South | griffinrath | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 70.7 | 90.587 | 56.3855 | 28.5869 | 1.9958 | 3.6188 | 34.2015 | 31.56% | 2.203% | 3.995% | 37.76%
J | J City, G South | gallanstown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 161.4 | 206.7997 | 162.1815 | 40.0751 | 3.8269 | 0.71626 | 44.6182 | 19.38% | 1.851% | 0.3464% | 21.58%
H2 | H2 & K | arklow | 2035 | 66% ECP | Pro-rata | IE wind not priority | 26.66 | 75.4137 | 59.9057 | 12.2386 | 0.24786 | 3.0216 | 15.508 | 16.23% | 0.3287% | 4.007% | 20.56%
K | H2 & K | rathnaskilloge | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 95 | 111.227 | 72.0767 | 35.2984 | 2.4414 | 1.4104 | 39.1502 | 31.74% | 2.195% | 1.268% | 35.2%
H2 | H2 & K | arklow | 2035 | 66% ECP | Pro-rata | IE wind priority | 53.2 | 150.4882 | 143.1479 | 0 | 1.3107 | 6.0296 | 7.3403 | 0% | 0.871% | 4.007% | 4.878%
K | H2 & K | rathnaskilloge | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 95 | 111.227 | 91.3569 | 17.6584 | 0.81635 | 1.3953 | 19.8701 | 15.88% | 0.7339% | 1.254% | 17.86%
J | J City, G South | gallanstown | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 183 | 234.4755 | 145.9484 | 73.9944 | 5.1659 | 9.3668 | 88.5271 | 31.56% | 2.203% | 3.995% | 37.76%
H2 | H2 & K | arklow | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 39.99 | 113.1207 | 79.4706 | 31.1045 | 2.0673 | 0.47838 | 33.6502 | 27.5% | 1.828% | 0.4229% | 29.75%
K | H2 & K | rathnaskilloge | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 95 | 111.227 | 81.4812 | 24.9561 | 0.95733 | 3.8323 | 29.7458 | 22.44% | 0.8607% | 3.445% | 26.74%
H2 | H2 & K | arklow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 80.9633 | 94.7927 | 67.8543 | 21.5766 | 2.015 | 3.3467 | 26.9384 | 22.76% | 2.126% | 3.531% | 28.42%
J | J City, G South | gallanstown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 172.2 | 220.6376 | 185.2014 | 33.7974 | 1.5908 | 0.048038 | 35.4362 | 15.32% | 0.721% | 0.02177% | 16.06%
J | J City, G South | griffinrath | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 33.9 | 43.4356 | 36.478 | 5.9023 | 0.80439 | 0.25088 | 6.9576 | 13.59% | 1.852% | 0.5776% | 16.02%
H2 | H2 & K | arklow | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 13.33 | 37.7069 | 30.6886 | 6.1596 | 0.67539 | 0.18323 | 7.0183 | 16.34% | 1.791% | 0.4859% | 18.61%
K | H2 & K | woodhouse | 2030 | Initial | Pro-rata | IE wind priority | 20 | 60.6801 | 55.4304 | 0 | 1.6572 | 3.5924 | 5.2497 | 0% | 2.731% | 5.92% | 8.651%
H2 | H2 & K | arklow | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 53.2 | 150.4882 | 144.9822 | 0 | 4.7747 | 0.73127 | 5.506 | 0% | 3.173% | 0.4859% | 3.659%
J | J City, G South | gallanstown | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 172.2 | 220.6376 | 184.9269 | 33.7974 | 1.5908 | 0.32247 | 35.7107 | 15.32% | 0.721% | 0.1462% | 16.19%
K | H2 & K | woodhouse | 2030 | Initial | Pro-rata | IE wind not priority | 34 | 103.1562 | 82.7416 | 12.5345 | 1.7729 | 6.1072 | 20.4146 | 12.15% | 1.719% | 5.92% | 19.79%
K | H2 & K | rathnaskilloge | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 95 | 111.227 | 93.2325 | 15.4118 | 2.0676 | 0.51509 | 17.9944 | 13.86% | 1.859% | 0.4631% | 16.18%
H2 | H2 & K | arklow | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 80.9633 | 94.7927 | 79.457 | 13.1346 | 1.7621 | 0.43898 | 15.3357 | 13.86% | 1.859% | 0.4631% | 16.18%
H2 | H2 & K | arklow | 2030 | 100% ECP | Pro-rata | IE wind not priority | 39.99 | 113.1207 | 78.126 | 31.1045 | 2.0673 | 1.8229 | 34.9947 | 27.5% | 1.828% | 1.611% | 30.94%
H2 | H2 & K | arklow | 2030 | 100% ECP | Pro-rata | IE wind priority | 53.2 | 150.4882 | 142.2693 | 0 | 5.7938 | 2.4251 | 8.2189 | 0% | 3.85% | 1.611% | 5.461%
K | H2 & K | rathnaskilloge | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 95 | 111.227 | 81.4538 | 25.0479 | 1.0038 | 3.7214 | 29.7731 | 22.52% | 0.9025% | 3.346% | 26.77%
J | J City, G South | griffinrath | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 33.9 | 43.4356 | 34.0641 | 8.4173 | 0.80379 | 0.15044 | 9.3715 | 19.38% | 1.851% | 0.3464% | 21.58%
J | J City, G South | gallanstown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 183 | 234.4755 | 144.4158 | 73.9944 | 5.1659 | 10.8994 | 90.0597 | 31.56% | 2.203% | 4.648% | 38.41%
H2 | H2 & K | arklow | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 128.89 | 150.9057 | 97.7891 | 47.8907 | 3.3124 | 1.9135 | 53.1166 | 31.74% | 2.195% | 1.268% | 35.2%
J | J City, G South | griffinrath | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 33.9 | 43.4356 | 35.3447 | 7.1994 | 0.81044 | 0.081012 | 8.0909 | 16.57% | 1.866% | 0.1865% | 18.63%
J | J City, G South | gallanstown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 161.4 | 206.7997 | 168.2786 | 34.2769 | 3.8586 | 0.3857 | 38.5211 | 16.57% | 1.866% | 0.1865% | 18.63%
H2 | H2 & K | arklow | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 104.9266 | 122.8491 | 97.6827 | 19.5036 | 0.90165 | 4.7612 | 25.1664 | 15.88% | 0.7339% | 3.876% | 20.49%
J | J City, G South | griffinrath | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 70.7 | 90.587 | 55.7934 | 28.5869 | 1.9958 | 4.2109 | 34.7936 | 31.56% | 2.203% | 4.648% | 38.41%
K | H2 & K | dungarvan | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 131.94 | 154.4767 | 113.1265 | 34.7876 | 1.3942 | 5.1685 | 41.3502 | 22.52% | 0.9025% | 3.346% | 26.77%
H2 | H2 & K | arklow | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 128.89 | 150.9057 | 110.5114 | 33.9834 | 1.3619 | 5.049 | 40.3943 | 22.52% | 0.9025% | 3.346% | 26.77%
J | J City, G South | griffinrath | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 52.3 | 67.0113 | 51.7018 | 14.7228 | 0.57253 | 0.014169 | 15.3095 | 21.97% | 0.8544% | 0.02114% | 22.85%
K | H2 & K | dungarvan | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 92.2733 | 108.0344 | 79.1424 | 24.2398 | 0.92985 | 3.7223 | 28.892 | 22.44% | 0.8607% | 3.445% | 26.74%
J | J City, G South | finglas | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 137.4666 | 176.1342 | 147.8456 | 26.9804 | 1.2699 | 0.038349 | 28.2886 | 15.32% | 0.721% | 0.02177% | 16.06%
K | H2 & K | dungarvan | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 92.2733 | 108.0344 | 88.7347 | 17.1516 | 0.79292 | 1.3552 | 19.2997 | 15.88% | 0.7339% | 1.254% | 17.86%
J | J City, G South | finglas | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 137.4666 | 176.1342 | 135.8943 | 38.6978 | 1.5048 | 0.037241 | 40.2399 | 21.97% | 0.8544% | 0.02114% | 22.85%
J | J City, G South | griffinrath | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 70.7 | 90.587 | 69.7238 | 19.9182 | 0.82094 | 0.12407 | 20.8632 | 21.99% | 0.9062% | 0.137% | 23.03%
J | J City, G South | finglas | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 137.4666 | 176.1342 | 147.6265 | 26.9804 | 1.2699 | 0.25743 | 28.5077 | 15.32% | 0.721% | 0.1462% | 16.19%
K | H2 & K | dungarvan | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 92.2733 | 108.0344 | 85.9029 | 17.1516 | 0.79292 | 4.187 | 22.1315 | 15.88% | 0.7339% | 3.876% | 20.49%
H2 | H2 & K | arklow 220kv | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 400 | 1608.368 | 1070.6382 | 445.6441 | 28.6643 | 63.4214 | 537.7298 | 27.71% | 1.782% | 3.943% | 33.43%
H2 | H2 & K | arklow 220kv | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 400 | 1608.368 | 1019.7078 | 478.8116 | 29.1476 | 80.7011 | 588.6602 | 29.77% | 1.812% | 5.018% | 36.6%
K | H2 & K | woodhouse | 2030 | 33% ECP | Pro-rata | IE wind not priority | 98.3333 | 298.3436 | 236.2427 | 49.3703 | 5.021 | 7.7096 | 62.1009 | 16.55% | 1.683% | 2.584% | 20.82%
H2 | H2 & K | arklow | 2035 | 100% ECP | Pro-rata | IE wind priority | 53.2 | 150.4882 | 140.9529 | 0 | 1.4364 | 8.0989 | 9.5353 | 0% | 0.9545% | 5.382% | 6.336%
J | J City, G South | griffinrath | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 52.3 | 67.0113 | 56.2487 | 10.2648 | 0.48314 | 0.01459 | 10.7626 | 15.32% | 0.721% | 0.02177% | 16.06%
K | H2 & K | rathnaskilloge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 95 | 111.227 | 79.6182 | 25.3174 | 2.3644 | 3.9269 | 31.6087 | 22.76% | 2.126% | 3.531% | 28.42%
H2 | H2 & K | arklow | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 26.66 | 75.4137 | 60.9425 | 12.2386 | 0.24786 | 1.9849 | 14.4713 | 16.23% | 0.3287% | 2.632% | 19.19%
J | J City, G South | gallanstown | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 161.4 | 206.7997 | 173.6742 | 28.1013 | 3.8297 | 1.1945 | 33.1255 | 13.59% | 1.852% | 0.5776% | 16.02%
H2 | H2 & K | arklow | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 53.2 | 150.4882 | 145.2167 | 0 | 1.3107 | 3.9608 | 5.2715 | 0% | 0.871% | 2.632% | 3.503%
K | H2 & K | rathnaskilloge | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 95 | 111.227 | 83.4599 | 21.7687 | 2.103 | 3.8953 | 27.767 | 19.57% | 1.891% | 3.502% | 24.96%
H2 | H2 & K | arklow | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 104.9266 | 122.8491 | 100.9028 | 19.5036 | 0.90165 | 1.5411 | 21.9463 | 15.88% | 0.7339% | 1.254% | 17.86%
J | J City, G South | gallanstown | 2030 | Initial | Pro-rata | IE Solar not priority | 150.6 | 192.9618 | 175.0923 | 15.2567 | 2.4954 | 0.11736 | 17.8695 | 7.907% | 1.293% | 0.06082% | 9.261%
K | H2 & K | rathnaskilloge | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 95 | 111.227 | 87.4692 | 18.6993 | 2.1032 | 2.9553 | 23.7577 | 16.81% | 1.891% | 2.657% | 21.36%
J | J City, G South | griffinrath | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 52.3 | 67.0113 | 56.1653 | 10.2648 | 0.48314 | 0.097939 | 10.8459 | 15.32% | 0.721% | 0.1462% | 16.19%
K | H2 & K | rathnaskilloge | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 95 | 111.227 | 89.7137 | 15.4118 | 2.0676 | 4.0339 | 21.5133 | 13.86% | 1.859% | 3.627% | 19.34%
H2 | H2 & K | arklow | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 53.2 | 150.4882 | 139.5759 | 0 | 2.7674 | 8.1448 | 10.9123 | 0% | 1.839% | 5.412% | 7.251%
H2 | H2 & K | arklow | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 104.9266 | 122.8491 | 89.9952 | 27.5638 | 1.0574 | 4.2328 | 32.8539 | 22.44% | 0.8607% | 3.445% | 26.74%
K | H2 & K | rathnaskilloge | 2030 | Initial | Pro-rata | IE Solar not priority | 95 | 111.227 | 92.7514 | 9.1991 | 1.4332 | 7.8433 | 18.4755 | 8.271% | 1.289% | 7.052% | 16.61%
J | J City, G South | finglas | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 164.49 | 210.7589 | 162.2188 | 46.3414 | 1.91 | 0.28866 | 48.5401 | 21.99% | 0.9062% | 0.137% | 23.03%
H2 | H2 & K | arklow | 2035 | 100% ECP | Pro-rata | IE wind not priority | 39.99 | 113.1207 | 86.2745 | 20.3534 | 0.40504 | 6.0878 | 26.8462 | 17.99% | 0.3581% | 5.382% | 23.73%
H2 | H2 & K | arklow | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 26.66 | 75.4137 | 47.4465 | 23.3779 | 0.5077 | 4.0816 | 27.9672 | 31% | 0.6732% | 5.412% | 37.09%
H2 | H2 & K | arklow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 53.2 | 150.4882 | 136.68 | 0 | 6.2574 | 7.5509 | 13.8082 | 0% | 4.158% | 5.018% | 9.176%
J | J City, G South | gallanstown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 172.2 | 220.6376 | 170.2304 | 48.4755 | 1.8851 | 0.046651 | 50.4072 | 21.97% | 0.8544% | 0.02114% | 22.85%
K | H2 & K | woodhouse | 2030 | 33% ECP | Pro-rata | IE wind priority | 20 | 60.6801 | 57.25 | 0 | 1.862 | 1.5681 | 3.4301 | 0% | 3.069% | 2.584% | 5.653%
K | H2 & K | woodhouse | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 162.6665 | 493.5311 | 398.9893 | 79.9587 | 1.5935 | 12.9895 | 94.5418 | 16.2% | 0.3229% | 2.632% | 19.16%
H1 | H1 | tipperary | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 12.3333 | 14.44 | 10.4794 | 2.8261 | 0.27302 | 0.86143 | 3.9606 | 19.57% | 1.891% | 5.966% | 27.43%
J | J City, G South | grange | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 39.99 | 51.2387 | 43.0555 | 6.9626 | 0.94889 | 0.27164 | 8.1832 | 13.59% | 1.852% | 0.5302% | 15.97%
H1 | H1 | tipperary | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 12.3333 | 14.44 | 9.9654 | 3.2868 | 0.30695 | 0.88077 | 4.4745 | 22.76% | 2.126% | 6.1% | 30.99%
K | H2 & K | woodhouse | 2035 | 66% ECP | Pro-rata | IE wind priority | 20 | 60.6801 | 57.718 | 0 | 0.53078 | 2.4313 | 2.9621 | 0% | 0.8747% | 4.007% | 4.881%
J | J City, G South | glasmore | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 4 | 5.1251 | 4.2956 | 0.78507 | 0.036952 | 0.0074906 | 0.82952 | 15.32% | 0.721% | 0.1462% | 16.19%
H1 | H1 | tipperary | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 12.3333 | 14.44 | 11.3963 | 2.0008 | 0.26842 | 0.77442 | 3.0437 | 13.86% | 1.859% | 5.363% | 21.08%
K | H2 & K | woodhouse | 2035 | 66% ECP | Pro-rata | IE wind not priority | 162.6665 | 493.5311 | 392.2045 | 79.9587 | 1.5935 | 19.7743 | 101.3266 | 16.2% | 0.3229% | 4.007% | 20.53%
J | J City, G South | glasmore | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4 | 5.1251 | 4.302 | 0.78507 | 0.036952 | 0.0011159 | 0.82314 | 15.32% | 0.721% | 0.02177% | 16.06%
H1 | H1 | tipperary | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 29 | 33.9535 | 19.3575 | 10.7753 | 0.74528 | 3.0754 | 14.596 | 31.74% | 2.195% | 9.058% | 42.99%
J | J City, G South | grange | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 39.99 | 51.2387 | 31.8933 | 16.1696 | 1.1289 | 2.0469 | 19.3454 | 31.56% | 2.203% | 3.995% | 37.76%
H1 | H1 | tipperary | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 29 | 33.9535 | 19.5619 | 10.7753 | 0.74528 | 2.8709 | 14.3915 | 31.74% | 2.195% | 8.456% | 42.39%
J | J City, G South | glasmore | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4 | 5.1251 | 3.1566 | 1.6174 | 0.11292 | 0.23824 | 1.9685 | 31.56% | 2.203% | 4.648% | 38.41%
J | J City, G South | grange | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 39.99 | 51.2387 | 31.5584 | 16.1696 | 1.1289 | 2.3818 | 19.6803 | 31.56% | 2.203% | 4.648% | 38.41%
H1 | H1 | tipperary | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 20.6667 | 24.1967 | 16.6475 | 3.8415 | 0.17759 | 3.5302 | 7.5492 | 15.88% | 0.7339% | 14.59% | 31.2%
K | H2 & K | woodhouse | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 20 | 60.6801 | 58.1638 | 0 | 2.2597 | 0.25661 | 2.5163 | 0% | 3.724% | 0.4229% | 4.147%
H1 | H1 | tipperary | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 12.3333 | 14.44 | 10.8115 | 2.4276 | 0.27305 | 0.92782 | 3.6285 | 16.81% | 1.891% | 6.425% | 25.13%
K | H2 & K | woodhouse | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 20 | 60.6801 | 58.5522 | 0 | 0.53078 | 1.5971 | 2.1279 | 0% | 0.8747% | 2.632% | 3.507%
H1 | H1 | timoney | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 166.56 | 195.0101 | 134.168 | 30.9599 | 1.4313 | 28.451 | 60.8421 | 15.88% | 0.7339% | 14.59% | 31.2%
J | J City, G South | grange | 2030 | Initial | Pro-rata | IE Solar not priority | 39.99 | 51.2387 | 46.4936 | 4.0512 | 0.66263 | 0.031163 | 4.745 | 7.907% | 1.293% | 0.06082% | 9.261%
H1 | H1 | timoney | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 166.56 | 195.0101 | 140.6552 | 30.9599 | 1.4313 | 21.9638 | 54.3549 | 15.88% | 0.7339% | 11.26% | 27.87%
K | H2 & K | woodhouse | 2035 | 100% ECP | Pro-rata | IE wind priority | 20 | 60.6801 | 56.8218 | 0 | 0.59265 | 3.2656 | 3.8583 | 0% | 0.9767% | 5.382% | 6.358%
J | J City, G South | grange | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 39.99 | 51.2387 | 41.6943 | 8.4928 | 0.95604 | 0.095566 | 9.5444 | 16.57% | 1.866% | 0.1865% | 18.63%
H1 | H1 | timoney | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 166.56 | 195.0101 | 129.0534 | 43.7547 | 1.6784 | 20.5235 | 65.9567 | 22.44% | 0.8607% | 10.52% | 33.82%
J | J City, G South | grange | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 39.99 | 51.2387 | 38.4602 | 11.5503 | 1.073 | 0.15515 | 12.7784 | 22.54% | 2.094% | 0.3028% | 24.94%
K | H2 & K | woodhouse | 2035 | 100% ECP | Pro-rata | IE wind not priority | 227 | 688.7191 | 525.0015 | 124.3047 | 2.348 | 37.065 | 163.7176 | 18.05% | 0.3409% | 5.382% | 23.77%
K | H2 & K | woodhouse | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 20 | 60.6801 | 56.3346 | 0 | 1.0613 | 3.2842 | 4.3455 | 0% | 1.749% | 5.412% | 7.161%
J | J City, G South | glasmore | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 4 | 5.1251 | 3.9448 | 1.1269 | 0.046446 | 0.0070195 | 1.1804 | 21.99% | 0.9062% | 0.137% | 23.03%
J | J City, G South | grange | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 39.99 | 51.2387 | 40.1836 | 9.9294 | 0.94818 | 0.17747 | 11.055 | 19.38% | 1.851% | 0.3464% | 21.58%
H1 | H1 | tipperary | 2030 | Initial | Pro-rata | IE Solar not priority | 4 | 4.6832 | 4.055 | 0.38733 | 0.060344 | 0.18061 | 0.62828 | 8.271% | 1.289% | 3.857% | 13.42%
K | H2 & K | woodhouse | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 162.6665 | 493.5311 | 315.4755 | 148.2773 | 3.067 | 26.7112 | 178.0555 | 30.04% | 0.6214% | 5.412% | 36.08%
J | J City, G South | glasmore | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 4 | 5.1251 | 3.9542 | 1.126 | 0.043788 | 0.0010836 | 1.1709 | 21.97% | 0.8544% | 0.02114% | 22.85%
H1 | H1 | tipperary | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 12.3333 | 14.44 | 11.2112 | 2.0008 | 0.26842 | 0.95952 | 3.2288 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | timoney | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 171.56 | 200.8642 | 122.5912 | 45.2339 | 1.8128 | 31.2262 | 78.2729 | 22.52% | 0.9025% | 15.55% | 38.97%
K | H2 & K | dungarvan | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 131.94 | 154.4767 | 101.9123 | 49.024 | 3.3908 | 0.14964 | 52.5644 | 31.74% | 2.195% | 0.09687% | 34.03%
J | J City, G South | glasmore | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 4 | 5.1251 | 3.1901 | 1.6174 | 0.11292 | 0.20474 | 1.935 | 31.56% | 2.203% | 3.995% | 37.76%
K | H2 & K | woodhouse | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 227 | 688.7191 | 485.4764 | 188.3764 | 11.9538 | 2.9125 | 203.2428 | 27.35% | 1.736% | 0.4229% | 29.51%
K | H2 & K | woodhouse | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 98.3333 | 298.3436 | 183.5477 | 94.5218 | 5.3046 | 14.9696 | 114.7959 | 31.68% | 1.778% | 5.018% | 38.48%
H2 | H2 & K | arklow | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 13.33 | 37.7069 | 27.8417 | 8.6431 | 0.69651 | 0.52559 | 9.8652 | 22.92% | 1.847% | 1.394% | 26.16%
H2 | H2 & K | arklow | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 53.2 | 150.4882 | 142.9484 | 0 | 5.4422 | 2.0976 | 7.5398 | 0% | 3.616% | 1.394% | 5.01%
K | H2 & K | woodhouse | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 20 | 60.6801 | 55.9128 | 0 | 2.3746 | 2.3927 | 4.7673 | 0% | 3.913% | 3.943% | 7.856%
J | J City, G South | glasmore | 2030 | Initial | Pro-rata | IE Solar not priority | 4 | 5.1251 | 4.6505 | 0.40522 | 0.06628 | 0.0031171 | 0.47462 | 7.907% | 1.293% | 0.06082% | 9.261%
J | J City, G South | grange | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 39.99 | 51.2387 | 39.4378 | 11.2663 | 0.46435 | 0.070178 | 11.8008 | 21.99% | 0.9062% | 0.137% | 23.03%
H2 | H2 & K | arklow | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 80.9633 | 94.7927 | 74.5452 | 15.9364 | 1.7924 | 2.5186 | 20.2474 | 16.81% | 1.891% | 2.657% | 21.36%
K | H2 & K | woodhouse | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 98.3333 | 298.3436 | 192.9713 | 88.3257 | 5.2823 | 11.7643 | 105.3724 | 29.61% | 1.771% | 3.943% | 35.32%
J | J City, G South | glasmore | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 4 | 5.1251 | 4.3042 | 0.69644 | 0.094913 | 0.029603 | 0.82095 | 13.59% | 1.852% | 0.5776% | 16.02%
H2 | H2 & K | arklow | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 13.33 | 37.7069 | 24.0873 | 11.4136 | 0.71906 | 1.4869 | 13.6195 | 30.27% | 1.907% | 3.943% | 36.12%
K | H2 & K | woodhouse | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 20 | 60.6801 | 57.7067 | 0 | 2.1276 | 0.8458 | 2.9734 | 0% | 3.506% | 1.394% | 4.9%
H2 | H2 & K | arklow | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 53.2 | 150.4882 | 138.3829 | 0 | 6.1713 | 5.9341 | 12.1053 | 0% | 4.101% | 3.943% | 8.044%
J | J City, G South | gallanstown | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 183 | 234.4755 | 180.4733 | 51.5562 | 2.1249 | 0.32114 | 54.0023 | 21.99% | 0.9062% | 0.137% | 23.03%
H2 | H2 & K | arklow | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 80.9633 | 94.7927 | 71.1283 | 18.5523 | 1.7923 | 3.3198 | 23.6643 | 19.57% | 1.891% | 3.502% | 24.96%
K | H2 & K | woodhouse | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 98.3333 | 298.3436 | 221.1054 | 67.8483 | 5.2314 | 4.1585 | 77.2382 | 22.74% | 1.753% | 1.394% | 25.89%
H2 | H2 & K | arklow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 13.33 | 37.7069 | 22.8638 | 12.2255 | 0.72557 | 1.892 | 14.8431 | 32.42% | 1.924% | 5.018% | 39.36%
J | J City, G South | griffinrath | 2030 | Initial | Pro-rata | IE Solar not priority | 15.5 | 19.8599 | 18.0208 | 1.5702 | 0.25683 | 0.012079 | 1.8392 | 7.907% | 1.293% | 0.06082% | 9.261%
H1 | H1 | tipperary | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 20.6667 | 24.1967 | 17.4524 | 3.8415 | 0.17759 | 2.7253 | 6.7443 | 15.88% | 0.7339% | 11.26% | 27.87%
J | J City, G South | grange | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 39.99 | 51.2387 | 39.5326 | 11.2575 | 0.43777 | 0.010834 | 11.7061 | 21.97% | 0.8544% | 0.02114% | 22.85%
K | H2 & K | woodhouse | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 20 | 60.6801 | 55.2245 | 0 | 2.4109 | 3.0447 | 5.4556 | 0% | 3.973% | 5.018% | 8.991%
H1 | H1 | tipperary | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 20.6667 | 24.1967 | 16.0129 | 5.429 | 0.20826 | 2.5465 | 8.1839 | 22.44% | 0.8607% | 10.52% | 33.82%
J | J City, G South | glasmore | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4 | 5.1251 | 4.3066 | 0.69644 | 0.094913 | 0.027171 | 0.81852 | 13.59% | 1.852% | 0.5302% | 15.97%
H1 | H1 | tipperary | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 29 | 33.9535 | 20.7225 | 7.6462 | 0.30643 | 5.2784 | 13.231 | 22.52% | 0.9025% | 15.55% | 38.97%
K | H2 & K | woodhouse | 2030 | 100% ECP | Pro-rata | IE wind priority | 20 | 60.6801 | 57.4425 | 0 | 2.2597 | 0.97785 | 3.2376 | 0% | 3.724% | 1.611% | 5.335%
J | J City, G South | glasmore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 4 | 5.1251 | 3.847 | 1.1553 | 0.10733 | 0.015519 | 1.2782 | 22.54% | 2.094% | 0.3028% | 24.94%
K | H2 & K | woodhouse | 2030 | 100% ECP | Pro-rata | IE wind not priority | 227 | 688.7191 | 477.2903 | 188.3764 | 11.9538 | 11.0986 | 211.4288 | 27.35% | 1.736% | 1.611% | 30.7%
H2 | H2 & K | arklow | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 80.9633 | 94.7927 | 76.4581 | 13.1346 | 1.7621 | 3.4379 | 18.3346 | 13.86% | 1.859% | 3.627% | 19.34%
J | J City, G South | grange | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 39.99 | 51.2387 | 42.9456 | 7.8488 | 0.36942 | 0.074887 | 8.2931 | 15.32% | 0.721% | 0.1462% | 16.19%
K | H2 & K | woodhouse | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 20 | 60.6801 | 58.5232 | 0 | 1.862 | 0.29486 | 2.1569 | 0% | 3.069% | 0.4859% | 3.555%
H2 | H2 & K | arklow | 2030 | Initial | Pro-rata | IE Solar not priority | 57 | 66.7362 | 55.6509 | 5.5195 | 0.8599 | 4.706 | 11.0853 | 8.271% | 1.289% | 7.052% | 16.61%
J | J City, G South | glasmore | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 4 | 5.1251 | 4.0194 | 0.99319 | 0.094842 | 0.017751 | 1.1058 | 19.38% | 1.851% | 0.3464% | 21.58%
J | J City, G South | grange | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 39.99 | 51.2387 | 43.0093 | 7.8488 | 0.36942 | 0.011156 | 8.2294 | 15.32% | 0.721% | 0.02177% | 16.06%
H2 | H2 & K | arklow | 2030 | 33% ECP | Pro-rata | IE wind not priority | 13.33 | 37.7069 | 29.8974 | 6.1596 | 0.67539 | 0.9744 | 7.8094 | 16.34% | 1.791% | 2.584% | 20.71%
K | H2 & K | woodhouse | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 98.3333 | 298.3436 | 242.5026 | 49.3703 | 5.021 | 1.4497 | 55.841 | 16.55% | 1.683% | 0.4859% | 18.72%
J | J City, G South | glasmore | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 4 | 5.1251 | 4.1705 | 0.84949 | 0.095627 | 0.009559 | 0.95468 | 16.57% | 1.866% | 0.1865% | 18.63%
H2 | H2 & K | arklow | 2030 | 33% ECP | Pro-rata | IE wind priority | 53.2 | 150.4882 | 141.8246 | 0 | 4.7747 | 3.8888 | 8.6636 | 0% | 3.173% | 2.584% | 5.757%
H2 | H2 & K | arklow | 2030 | Initial | Pro-rata | IE wind priority | 53.2 | 150.4882 | 137.3514 | 0 | 4.2275 | 8.9094 | 13.1368 | 0% | 2.809% | 5.92% | 8.729%
J | J City, G South | finglas | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 164.49 | 210.7589 | 129.8085 | 66.51 | 4.6434 | 9.797 | 80.9504 | 31.56% | 2.203% | 4.648% | 38.41%
H2 | H2 & K | arklow 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 400 | 1608.368 | 1050.7759 | 460.83 | 9.7129 | 87.0493 | 557.5921 | 28.65% | 0.6039% | 5.412% | 34.67%
J | J City, G South | poolbeg north 220kv | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 400 | 1675.8076 | 1123.8362 | 348.2145 | 29.2887 | 174.4682 | 551.9714 | 20.78% | 1.748% | 10.41% | 32.94%
J | J City, G South | richardstown | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 110 | 140.9416 | 87.7285 | 44.4775 | 3.1052 | 5.6303 | 53.213 | 31.56% | 2.203% | 3.995% | 37.76%
K | H2 & K | butlerstown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 22.4466 | 26.2808 | 20.6673 | 4.4183 | 0.49694 | 0.69827 | 5.6135 | 16.81% | 1.891% | 2.657% | 21.36%
J | J City, G South | crakenstown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 381.333 | 488.597 | 410.1242 | 74.8436 | 3.5227 | 0.10638 | 78.4727 | 15.32% | 0.721% | 0.02177% | 16.06%
H2 | H2 & K | ballyragget | 2035 | 66% ECP | Pro-rata | IE wind not priority | 110.5999 | 312.8568 | 248.5212 | 50.7722 | 1.0283 | 12.5352 | 64.3357 | 16.23% | 0.3287% | 4.007% | 20.56%
J | J City, G South | richardstown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 110 | 140.9416 | 86.8073 | 44.4775 | 3.1052 | 6.5516 | 54.1342 | 31.56% | 2.203% | 4.648% | 38.41%
K | H2 & K | butlerstown | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 22.4466 | 26.2808 | 21.1976 | 3.6415 | 0.48852 | 0.95313 | 5.0832 | 13.86% | 1.859% | 3.627% | 19.34%
K | H2 & K | butlerstown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 22.4466 | 26.2808 | 19.72 | 5.1435 | 0.4969 | 0.92039 | 6.5608 | 19.57% | 1.891% | 3.502% | 24.96%
H2 | H2 & K | ballyragget | 2035 | 66% ECP | Pro-rata | IE wind priority | 9.2 | 26.0243 | 24.7549 | 0 | 0.22667 | 1.0427 | 1.2694 | 0% | 0.871% | 4.007% | 4.878%
K | H2 & K | butlerstown | 2030 | Initial | Pro-rata | IE Solar not priority | 3.95 | 4.6247 | 3.8565 | 0.38249 | 0.05959 | 0.32611 | 0.76819 | 8.271% | 1.289% | 7.052% | 16.61%
H2 | H2 & K | ballyragget | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 39.99 | 46.8207 | 37.2292 | 7.4333 | 0.34364 | 1.8146 | 9.5915 | 15.88% | 0.7339% | 3.876% | 20.49%
H2 | H2 & K | ballyragget | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 110.5999 | 312.8568 | 252.8221 | 50.7722 | 1.0283 | 8.2343 | 60.0347 | 16.23% | 0.3287% | 2.632% | 19.19%
H2 | H2 & K | ballyragget | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 9.2 | 26.0243 | 25.1127 | 0 | 0.22667 | 0.68495 | 0.91161 | 0% | 0.871% | 2.632% | 3.503%
J | J Country | timahoe | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 683 | 875.119 | 320.9121 | 192.4201 | 7.9307 | 353.8562 | 554.207 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J City, G South | crakenstown | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 381.333 | 488.597 | 409.5165 | 74.8436 | 3.5227 | 0.7141 | 79.0805 | 15.32% | 0.721% | 0.1462% | 16.19%
J | J City, G South | crakenstown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 572 | 732.8962 | 451.3981 | 231.2829 | 16.1471 | 34.0681 | 281.4981 | 31.56% | 2.203% | 4.648% | 38.41%
J | J City, G South | crakenstown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 381.333 | 488.597 | 376.9713 | 107.3479 | 4.1744 | 0.10331 | 111.6256 | 21.97% | 0.8544% | 0.02114% | 22.85%
K | H2 & K | butlerstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 22.4466 | 26.2808 | 18.8122 | 5.982 | 0.55866 | 0.92786 | 7.4685 | 22.76% | 2.126% | 3.531% | 28.42%
H2 | H2 & K | ballyragget | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 39.99 | 46.8207 | 39.246 | 6.4876 | 0.87033 | 0.21683 | 7.5747 | 13.86% | 1.859% | 0.4631% | 16.18%
J | J City, G South | dunstown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 230.5998 | 295.4645 | 240.4275 | 48.973 | 5.5129 | 0.55107 | 55.037 | 16.57% | 1.866% | 0.1865% | 18.63%
J | J City, G South | richardstown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 36.6666 | 46.9805 | 36.8442 | 9.1042 | 0.86938 | 0.16272 | 10.1363 | 19.38% | 1.851% | 0.3464% | 21.58%
H2 | H2 & K | ballyragget | 2030 | 100% ECP | Pro-rata | IE wind not priority | 143.4 | 405.6392 | 280.1518 | 111.5375 | 7.4132 | 6.5368 | 125.4875 | 27.5% | 1.828% | 1.611% | 30.94%
H2 | H2 & K | ballyragget | 2030 | 100% ECP | Pro-rata | IE wind priority | 9.2 | 26.0243 | 24.603 | 0 | 1.0019 | 0.41938 | 1.4213 | 0% | 3.85% | 1.611% | 5.461%
J | J City, G South | dunstown | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 230.5998 | 295.4645 | 248.1365 | 40.1496 | 5.4717 | 1.7066 | 47.328 | 13.59% | 1.852% | 0.5776% | 16.02%
K | H2 & K | butlerstown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 59.44 | 69.5929 | 45.9123 | 22.0857 | 1.5276 | 0.067415 | 23.6807 | 31.74% | 2.195% | 0.09687% | 34.03%
H2 | H2 & K | ballyragget | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 39.99 | 46.8207 | 30.3405 | 14.8588 | 1.0277 | 0.59369 | 16.4802 | 31.74% | 2.195% | 1.268% | 35.2%
K | H2 & K | butlerstown | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 59.44 | 69.5929 | 45.0973 | 22.0857 | 1.5276 | 0.88244 | 24.4957 | 31.74% | 2.195% | 1.268% | 35.2%
H2 | H2 & K | ballyragget | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 143.4 | 405.6392 | 284.9732 | 111.5375 | 7.4132 | 1.7154 | 120.666 | 27.5% | 1.828% | 0.4229% | 29.75%
H2 | H2 & K | ballyragget | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 9.2 | 26.0243 | 24.9123 | 0 | 1.0019 | 0.11005 | 1.112 | 0% | 3.85% | 0.4229% | 4.273%
K | H2 & K | butlerstown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 22.4466 | 26.2808 | 22.029 | 3.6415 | 0.48852 | 0.12171 | 4.2517 | 13.86% | 1.859% | 0.4631% | 16.18%
J | J City, G South | richardstown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 36.6666 | 46.9805 | 39.4774 | 6.384 | 0.87003 | 0.24907 | 7.5031 | 13.59% | 1.852% | 0.5302% | 15.97%
J | J City, G South | crakenstown | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 572 | 732.8962 | 564.1022 | 161.1483 | 6.6418 | 1.0038 | 168.7939 | 21.99% | 0.9062% | 0.137% | 23.03%
H2 | H2 & K | ballyragget | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 39.99 | 46.8207 | 30.8888 | 14.8588 | 1.0277 | 0.045356 | 15.9319 | 31.74% | 2.195% | 0.09687% | 34.03%
J | J City, G South | richardstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 36.6666 | 46.9805 | 35.264 | 10.5904 | 0.98387 | 0.14225 | 11.7165 | 22.54% | 2.094% | 0.3028% | 24.94%
K | H2 & K | butlerstown | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 40.9433 | 47.9368 | 38.1167 | 7.6105 | 0.35183 | 1.8579 | 9.8202 | 15.88% | 0.7339% | 3.876% | 20.49%
H2 | H2 & K | ballyragget | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 39.99 | 46.8207 | 38.4564 | 7.4333 | 0.34364 | 0.58734 | 8.3642 | 15.88% | 0.7339% | 1.254% | 17.86%
J | J Country | timahoe | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 478.6663 | 613.3089 | 287.3091 | 134.7479 | 5.2399 | 186.0119 | 325.9997 | 21.97% | 0.8544% | 30.33% | 53.15%
H2 | H2 & K | ballywater | 2030 | Initial | Pro-rata | IE wind priority | 42 | 118.8065 | 108.4353 | 0 | 3.3375 | 7.0337 | 10.3712 | 0% | 2.809% | 5.92% | 8.729%
J | J Country | timahoe | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 274.3331 | 351.4995 | 188.8396 | 79.2353 | 7.3611 | 76.0635 | 162.6599 | 22.54% | 2.094% | 21.64% | 46.28%
J | J City, G South | crakenstown | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 190.6665 | 244.2985 | 205.1664 | 33.1969 | 4.5242 | 1.4111 | 39.1321 | 13.59% | 1.852% | 0.5776% | 16.02%
H2 | H2 & K | ballywater | 2030 | 33% ECP | Pro-rata | IE wind priority | 42 | 118.8065 | 111.9668 | 0 | 3.7695 | 3.0701 | 6.8397 | 0% | 3.173% | 2.584% | 5.757%
J | J Country | timahoe | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 274.3331 | 351.4995 | 226.453 | 68.116 | 6.5046 | 50.4259 | 125.0465 | 19.38% | 1.851% | 14.35% | 35.58%
J | J City, G South | stephenstown | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 3.33 | 4.2667 | 3.5832 | 0.57978 | 0.079015 | 0.024644 | 0.68344 | 13.59% | 1.852% | 0.5776% | 16.02%
J | J Country | timahoe | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 274.3331 | 351.4995 | 243.8275 | 47.764 | 6.5094 | 53.3985 | 107.672 | 13.59% | 1.852% | 15.19% | 30.63%
H2 | H2 & K | ballywater | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 42 | 118.8065 | 112.854 | 0 | 4.2965 | 1.656 | 5.9525 | 0% | 3.616% | 1.394% | 5.01%
J | J Country | timahoe | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 274.3331 | 351.4995 | 231.0619 | 58.2607 | 6.5584 | 55.6184 | 120.4376 | 16.57% | 1.866% | 15.82% | 34.26%
H2 | H2 & K | ballywater | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 42 | 118.8065 | 109.2496 | 0 | 4.872 | 4.6848 | 9.5568 | 0% | 4.101% | 3.943% | 8.044%
J | J City, G South | carrickmines 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 412 | 1656.619 | 1135.222 | 474.6549 | 10.0043 | 36.7378 | 521.397 | 28.65% | 0.6039% | 2.218% | 31.47%
H2 | H2 & K | ballywater | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 42 | 118.8065 | 107.9052 | 0 | 4.94 | 5.9612 | 10.9012 | 0% | 4.158% | 5.018% | 9.176%
J | J Country | timahoe | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 274.3331 | 351.4995 | 233.0172 | 47.764 | 6.5094 | 64.2088 | 118.4822 | 13.59% | 1.852% | 18.27% | 33.71%
J | J City, G South | stephenstown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 3.33 | 4.2667 | 3.4719 | 0.7072 | 0.07961 | 0.0079578 | 0.79477 | 16.57% | 1.866% | 0.1865% | 18.63%
H2 | H2 & K | ballywater | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 42 | 118.8065 | 114.4596 | 0 | 3.7695 | 0.57732 | 4.3468 | 0% | 3.173% | 0.4859% | 3.659%
J | J Country | timahoe | 2030 | Initial | Pro-rata | IE Solar not priority | 70 | 89.6901 | 71.0161 | 7.0914 | 1.1599 | 10.4227 | 18.674 | 7.907% | 1.293% | 11.62% | 20.82%
J | J City, G South | richardstown | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 73.3333 | 93.961 | 78.7532 | 14.393 | 0.67744 | 0.13733 | 15.2078 | 15.32% | 0.721% | 0.1462% | 16.19%
J | J City, G South | crakenstown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 190.6665 | 244.2985 | 198.7923 | 40.4923 | 4.5582 | 0.45564 | 45.5061 | 16.57% | 1.866% | 0.1865% | 18.63%
J | J Country | timahoe | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 683 | 875.119 | 368.6236 | 276.1647 | 19.2805 | 211.0502 | 506.4954 | 31.56% | 2.203% | 24.12% | 57.88%
H2 | H2 & K | ballyragget | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 110.5999 | 312.8568 | 196.8336 | 96.9843 | 2.1062 | 16.9327 | 116.0232 | 31% | 0.6732% | 5.412% | 37.09%
J | J City, G South | crakenstown | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 572 | 732.8962 | 456.1884 | 231.2829 | 16.1471 | 29.2778 | 276.7078 | 31.56% | 2.203% | 3.995% | 37.76%
H2 | H2 & K | ballyragget | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 9.2 | 26.0243 | 24.1372 | 0 | 0.47858 | 1.4085 | 1.8871 | 0% | 1.839% | 5.412% | 7.251%
J | J Country | timahoe | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 478.6663 | 613.3089 | 302.1207 | 93.9471 | 4.4219 | 212.8192 | 311.1882 | 15.32% | 0.721% | 34.7% | 50.74%
J | J City, G South | richardstown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 73.3333 | 93.961 | 78.87 | 14.393 | 0.67744 | 0.020458 | 15.0909 | 15.32% | 0.721% | 0.02177% | 16.06%
H2 | H2 & K | ballyragget | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 39.99 | 46.8207 | 34.2993 | 10.5052 | 0.40298 | 1.6132 | 12.5214 | 22.44% | 0.8607% | 3.445% | 26.74%
J | J City, G South | crakenstown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 190.6665 | 244.2985 | 205.2823 | 33.1969 | 4.5242 | 1.2952 | 39.0162 | 13.59% | 1.852% | 0.5302% | 15.97%
J | J Country | timahoe | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 478.6663 | 613.3089 | 284.1765 | 93.9471 | 4.4219 | 230.7633 | 329.1323 | 15.32% | 0.721% | 37.63% | 53.67%
H2 | H2 & K | ballyragget | 2035 | 100% ECP | Pro-rata | IE wind not priority | 143.4 | 405.6392 | 309.3713 | 72.9851 | 1.4524 | 21.8304 | 96.2679 | 17.99% | 0.3581% | 5.382% | 23.73%
H2 | H2 & K | ballyragget | 2035 | 100% ECP | Pro-rata | IE wind priority | 9.2 | 26.0243 | 24.3753 | 0 | 0.24841 | 1.4006 | 1.649 | 0% | 0.9545% | 5.382% | 6.336%
J | J City, G South | crakenstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 190.6665 | 244.2985 | 183.3727 | 55.0699 | 5.1161 | 0.73973 | 60.9258 | 22.54% | 2.094% | 0.3028% | 24.94%
H2 | H2 & K | ballyragget | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 39.99 | 46.8207 | 34.2878 | 10.5438 | 0.42256 | 1.5665 | 12.5329 | 22.52% | 0.9025% | 3.346% | 26.77%
J | J Country | timahoe | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 683 | 875.119 | 386.1511 | 276.1647 | 19.2805 | 193.5226 | 488.9679 | 31.56% | 2.203% | 22.11% | 55.87%
J | J City, G South | crakenstown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 190.6665 | 244.2985 | 191.5897 | 47.3418 | 4.5208 | 0.84614 | 52.7088 | 19.38% | 1.851% | 0.3464% | 21.58%
J | J City, G South | richardstown | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 110 | 140.9416 | 108.4812 | 30.9901 | 1.2773 | 0.19304 | 32.4604 | 21.99% | 0.9062% | 0.137% | 23.03%
J | J City, G South | richardstown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 73.3333 | 93.961 | 72.4945 | 20.6438 | 0.80278 | 0.019867 | 21.4665 | 21.97% | 0.8544% | 0.02114% | 22.85%
H2 | H2 & K | ballywater | 2030 | 100% ECP | Pro-rata | IE wind priority | 42 | 118.8065 | 112.3179 | 0 | 4.5741 | 1.9145 | 6.4886 | 0% | 3.85% | 1.611% | 5.461%
H2 | H2 & K | ballyragget | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 9.2 | 26.0243 | 25.0721 | 0 | 0.8257 | 0.12646 | 0.95216 | 0% | 3.173% | 0.4859% | 3.659%
K | H2 & K | butlerstown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 40.9433 | 47.9368 | 39.3732 | 7.6105 | 0.35183 | 0.60134 | 8.5636 | 15.88% | 0.7339% | 1.254% | 17.86%
K | H2 & K | dungarvan | 2030 | Initial | Pro-rata | IE Solar not priority | 12.94 | 15.1503 | 12.6337 | 1.253 | 0.19521 | 1.0683 | 2.5166 | 8.271% | 1.289% | 7.052% | 16.61%
H2 | H2 & K | ballybeg | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 150.5 | 192.8337 | 127.5451 | 60.8533 | 4.2485 | 0.1868 | 65.2886 | 31.56% | 2.203% | 0.09687% | 33.86%
J | J City, G South | poolbeg north 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 400 | 1675.8076 | 1158.6821 | 469.9715 | 9.9907 | 37.1634 | 517.1255 | 28.04% | 0.5962% | 2.218% | 30.86%
J | J City, G South | finglas | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 110.4433 | 141.5096 | 118.8423 | 19.2292 | 2.6206 | 0.81736 | 22.6672 | 13.59% | 1.852% | 0.5776% | 16.02%
H2 | H2 & K | ballybeg | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 102.9999 | 131.9724 | 105.6905 | 20.2156 | 0.9515 | 5.1148 | 26.2819 | 15.32% | 0.721% | 3.876% | 19.91%
K | H2 & K | cullenagh | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 50 | 64.0644 | 47.2539 | 14.0864 | 0.58058 | 2.1435 | 16.8104 | 21.99% | 0.9062% | 3.346% | 26.24%
J | J City, G South | finglas | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 110.4433 | 141.5096 | 115.1502 | 23.4551 | 2.6404 | 0.26393 | 26.3594 | 16.57% | 1.866% | 0.1865% | 18.63%
H2 | H2 & K | ballybeg | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 102.9999 | 131.9724 | 109.1498 | 20.2156 | 0.9515 | 1.6555 | 22.8227 | 15.32% | 0.721% | 1.254% | 17.29%
K | H2 & K | cullenagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 33.3333 | 42.7095 | 31.4895 | 9.3836 | 0.3649 | 1.4716 | 11.22 | 21.97% | 0.8544% | 3.445% | 26.27%
H2 | H2 & K | ballybeg | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 102.9999 | 131.9724 | 97.3026 | 28.9952 | 1.1275 | 4.5471 | 34.6698 | 21.97% | 0.8544% | 3.445% | 26.27%
H2 | H2 & K | ballybeg | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 150.5 | 192.8337 | 142.2343 | 42.4 | 1.7475 | 6.4518 | 50.5994 | 21.99% | 0.9062% | 3.346% | 26.24%
K | H2 & K | cullenagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 33.3333 | 42.7095 | 35.3236 | 6.5423 | 0.30793 | 0.53576 | 7.386 | 15.32% | 0.721% | 1.254% | 17.29%
J | J City, G South | poolbeg south 220kv | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 450 | 1885.2836 | 1264.3157 | 391.7414 | 32.9498 | 196.2767 | 620.9678 | 20.78% | 1.748% | 10.41% | 32.94%
J | J City, G South | finglas | 2030 | Initial | Pro-rata | IE Solar not priority | 83.42 | 106.885 | 96.9867 | 8.451 | 1.3823 | 0.065007 | 9.8982 | 7.907% | 1.293% | 0.06082% | 9.261%
K | H2 & K | cullenagh | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 33.3333 | 42.7095 | 34.204 | 6.5423 | 0.30793 | 1.6553 | 8.5055 | 15.32% | 0.721% | 3.876% | 19.91%
H2 | H2 & K | ballybeg | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 150.5 | 192.8337 | 125.2868 | 60.8533 | 4.2485 | 2.4451 | 67.5469 | 31.56% | 2.203% | 1.268% | 35.03%
K | H2 & K | dungarvan | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 52.6066 | 61.5924 | 49.6793 | 8.5343 | 1.1449 | 2.2338 | 11.9131 | 13.86% | 1.859% | 3.627% | 19.34%
K | H2 & K | dungarvan | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 131.94 | 154.4767 | 100.1032 | 49.024 | 3.3908 | 1.9588 | 54.3735 | 31.74% | 2.195% | 1.268% | 35.2%
J | J City, G South | finglas | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 164.49 | 210.7589 | 131.1861 | 66.51 | 4.6434 | 8.4194 | 79.5728 | 31.56% | 2.203% | 3.995% | 37.76%
H2 | H2 & K | ballybeg | 2030 | Initial | Pro-rata | IE Solar not priority | 8 | 10.2503 | 8.5845 | 0.81045 | 0.13256 | 0.72281 | 1.6658 | 7.907% | 1.293% | 7.052% | 16.25%
K | H2 & K | dungarvan | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 52.6066 | 61.5924 | 51.6279 | 8.5343 | 1.1449 | 0.28523 | 9.9645 | 13.86% | 1.859% | 0.4631% | 16.18%
J | J City, G South | poolbeg north 220kv | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 400 | 1675.8076 | 1082.6166 | 455.7279 | 29.7203 | 107.7428 | 593.191 | 27.19% | 1.773% | 6.429% | 35.4%
H2 | H2 & K | ballybeg | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 55.5 | 71.1114 | 57.5524 | 9.6631 | 1.3169 | 2.579 | 13.559 | 13.59% | 1.852% | 3.627% | 19.07%
J | J City, G South | finglas | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 110.4433 | 141.5096 | 118.9095 | 19.2292 | 2.6206 | 0.75022 | 22.6001 | 13.59% | 1.852% | 0.5302% | 15.97%
K | H2 & K | dungarvan | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 52.6066 | 61.5924 | 44.0889 | 14.0196 | 1.3093 | 2.1746 | 17.5034 | 22.76% | 2.126% | 3.531% | 28.42%
K | H2 & K | dungarvan | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 52.6066 | 61.5924 | 46.2163 | 12.0545 | 1.1645 | 2.1571 | 15.3761 | 19.57% | 1.891% | 3.502% | 24.96%
H2 | H2 & K | ballybeg | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 55.5 | 71.1114 | 53.5246 | 13.7805 | 1.3159 | 2.4904 | 17.5868 | 19.38% | 1.851% | 3.502% | 24.73%
J | J City, G South | finglas | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 110.4433 | 141.5096 | 106.2184 | 31.8992 | 2.9635 | 0.42848 | 35.2912 | 22.54% | 2.094% | 0.3028% | 24.94%
J | J City, G South | poolbeg north 220kv | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 400 | 1675.8076 | 1055.473 | 490.6773 | 30.3249 | 99.3323 | 620.3346 | 29.28% | 1.81% | 5.927% | 37.02%
H2 | H2 & K | ballybeg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 55.5 | 71.1114 | 51.0815 | 16.03 | 1.4892 | 2.5106 | 20.0298 | 22.54% | 2.094% | 3.531% | 28.17%
K | H2 & K | dungarvan | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 52.6066 | 61.5924 | 48.4364 | 10.3548 | 1.1646 | 1.6365 | 13.1559 | 16.81% | 1.891% | 2.657% | 21.36%
J | J City, G South | finglas | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 110.4433 | 141.5096 | 110.9781 | 27.4227 | 2.6187 | 0.49013 | 30.5315 | 19.38% | 1.851% | 0.3464% | 21.58%
H2 | H2 & K | ballybeg | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 55.5 | 71.1114 | 59.8021 | 9.6631 | 1.3169 | 0.32932 | 11.3093 | 13.59% | 1.852% | 0.4631% | 15.9%
H2 | H2 & K | ballybeg | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 55.5 | 71.1114 | 56.1085 | 11.7866 | 1.3268 | 1.8894 | 15.0029 | 16.57% | 1.866% | 2.657% | 21.1%
J | J City, G South | dunstown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 230.5998 | 295.4645 | 231.7163 | 57.2571 | 5.4676 | 1.0234 | 63.7481 | 19.38% | 1.851% | 0.3464% | 21.58%
J | J City, G South | dunstown | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 691.8 | 886.3943 | 682.2481 | 194.8993 | 8.0329 | 1.214 | 204.1462 | 21.99% | 0.9062% | 0.137% | 23.03%
K | H2 & K | cullenagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 16.8494 | 3.5395 | 0.39845 | 0.56739 | 4.5054 | 16.57% | 1.866% | 2.657% | 21.1%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 77.8 | 220.0747 | 140.5848 | 66.6151 | 4.1968 | 8.678 | 79.4899 | 30.27% | 1.907% | 3.943% | 36.12%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 9.2 | 26.0243 | 23.9309 | 0 | 1.0672 | 1.0262 | 2.0934 | 0% | 4.101% | 3.943% | 8.044%
K | H2 & K | cullenagh | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 17.283 | 2.9018 | 0.39547 | 0.77448 | 4.0718 | 13.59% | 1.852% | 3.627% | 19.07%
J | J City, G South | dunstown | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 691.8 | 886.3943 | 551.7328 | 279.7229 | 19.529 | 35.4097 | 334.6616 | 31.56% | 2.203% | 3.995% | 37.76%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 39.99 | 46.8207 | 35.1322 | 9.1635 | 0.88525 | 1.6397 | 11.6885 | 19.57% | 1.891% | 3.502% | 24.96%
J | J City, G South | dunstown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 691.8 | 886.3943 | 545.9391 | 279.7229 | 19.529 | 41.2033 | 340.4552 | 31.56% | 2.203% | 4.648% | 38.41%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 77.8 | 220.0747 | 133.4437 | 71.3539 | 4.2348 | 11.0424 | 86.631 | 32.42% | 1.924% | 5.018% | 39.36%
K | H2 & K | butlerstown | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 59.44 | 69.5929 | 50.9644 | 15.6721 | 0.62808 | 2.3284 | 18.6286 | 22.52% | 0.9025% | 3.346% | 26.77%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 9.2 | 26.0243 | 23.6364 | 0 | 1.0821 | 1.3058 | 2.3879 | 0% | 4.158% | 5.018% | 9.176%
J | J City, G South | richardstown | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 36.6666 | 46.9805 | 39.4551 | 6.384 | 0.87003 | 0.27136 | 7.5254 | 13.59% | 1.852% | 0.5776% | 16.02%
J | J City, G South | dunstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 230.5998 | 295.4645 | 221.7784 | 66.6038 | 6.1876 | 0.89465 | 73.6861 | 22.54% | 2.094% | 0.3028% | 24.94%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 39.99 | 46.8207 | 33.5151 | 10.6573 | 0.99528 | 1.653 | 13.3056 | 22.76% | 2.126% | 3.531% | 28.42%
J | J Country | philipstown | 2035 | 100% ECP | Pro-rata | IE wind not priority | 50 | 154.1991 | 84.7544 | 31.275 | 0.58095 | 37.5887 | 69.4447 | 20.28% | 0.3768% | 24.38% | 45.04%
H2 | H2 & K | ballyragget | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 77.8 | 220.0747 | 179.113 | 35.9505 | 3.9419 | 1.0694 | 40.9618 | 16.34% | 1.791% | 0.4859% | 18.61%
J | J City, G South | richardstown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 36.6666 | 46.9805 | 38.2293 | 7.787 | 0.87658 | 0.087624 | 8.7512 | 16.57% | 1.866% | 0.1865% | 18.63%
J | J City, G South | dunstown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 230.5998 | 295.4645 | 248.2767 | 40.1496 | 5.4717 | 1.5664 | 47.1878 | 13.59% | 1.852% | 0.5302% | 15.97%
H2 | H2 & K | ballyragget | 2030 | Initial | Pro-rata | IE wind not priority | 45 | 127.2926 | 102.315 | 15.1317 | 2.3098 | 7.5361 | 24.9776 | 11.89% | 1.815% | 5.92% | 19.62%
J | J City, G South | poolbeg south 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 450 | 1885.2836 | 1303.5174 | 528.7179 | 11.2395 | 41.8088 | 581.7662 | 28.04% | 0.5962% | 2.218% | 30.86%
K | H2 & K | cullenagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 16.0734 | 4.1383 | 0.39517 | 0.74787 | 5.2813 | 19.38% | 1.851% | 3.502% | 24.73%
H2 | H2 & K | ballyragget | 2030 | Initial | Pro-rata | IE wind priority | 9.2 | 26.0243 | 23.7525 | 0 | 0.73106 | 1.5407 | 2.2718 | 0% | 2.809% | 5.92% | 8.729%
J | J City, G South | poolbeg south 220kv | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 450 | 1885.2836 | 1217.9436 | 512.6939 | 33.4354 | 121.2106 | 667.3399 | 27.19% | 1.773% | 6.429% | 35.4%
J | J City, G South | dunstown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 461.1995 | 590.929 | 455.9244 | 129.8309 | 5.0487 | 0.12494 | 135.0046 | 21.97% | 0.8544% | 0.02114% | 22.85%
H2 | H2 & K | ballyragget | 2030 | Initial | Pro-rata | IE Solar not priority | 39.99 | 46.8207 | 39.0435 | 3.8723 | 0.60329 | 3.3016 | 7.7772 | 8.271% | 1.289% | 7.052% | 16.61%
K | H2 & K | cullenagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 50 | 64.0644 | 42.3738 | 20.217 | 1.4115 | 0.06206 | 21.6906 | 31.56% | 2.203% | 0.09687% | 33.86%
H2 | H2 & K | ballyragget | 2030 | 33% ECP | Pro-rata | IE wind not priority | 77.8 | 220.0747 | 174.4953 | 35.9505 | 3.9419 | 5.6871 | 45.5794 | 16.34% | 1.791% | 2.584% | 20.71%
J | J City, G South | dunstown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 461.1995 | 590.929 | 496.0209 | 90.5189 | 4.2605 | 0.12866 | 94.9081 | 15.32% | 0.721% | 0.02177% | 16.06%
K | H2 & K | cullenagh | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 50 | 64.0644 | 41.6235 | 20.217 | 1.4115 | 0.81234 | 22.4408 | 31.56% | 2.203% | 1.268% | 35.03%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 39.99 | 46.8207 | 36.8199 | 7.8714 | 0.88533 | 1.244 | 10.0008 | 16.81% | 1.891% | 2.657% | 21.36%
J | J City, G South | poolbeg south 220kv | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 450 | 1885.2836 | 1187.4071 | 552.012 | 34.1156 | 111.7489 | 697.8764 | 29.28% | 1.81% | 5.927% | 37.02%
K | H2 & K | cullenagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 17.9586 | 2.9018 | 0.39547 | 0.098894 | 3.3962 | 13.59% | 1.852% | 0.4631% | 15.9%
H2 | H2 & K | ballyragget | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 39.99 | 46.8207 | 37.7647 | 6.4876 | 0.87033 | 1.6981 | 9.056 | 13.86% | 1.859% | 3.627% | 19.34%
J | J City, G South | dunstown | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 461.1995 | 590.929 | 495.2859 | 90.5189 | 4.2605 | 0.86366 | 95.6431 | 15.32% | 0.721% | 0.1462% | 16.19%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 77.8 | 220.0747 | 162.497 | 50.4451 | 4.0651 | 3.0676 | 57.5778 | 22.92% | 1.847% | 1.394% | 26.16%
K | H2 & K | cullenagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 15.3398 | 4.8138 | 0.44721 | 0.75394 | 6.015 | 22.54% | 2.094% | 3.531% | 28.17%
H2 | H2 & K | ballyragget | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 9.2 | 26.0243 | 24.7204 | 0 | 0.94114 | 0.36275 | 1.3039 | 0% | 3.616% | 1.394% | 5.01%
H2 | H2 & K | ballyragget | 2030 | 33% ECP | Pro-rata | IE wind priority | 9.2 | 26.0243 | 24.5261 | 0 | 0.8257 | 0.67251 | 1.4982 | 0% | 3.173% | 2.584% | 5.757%
J | J Country | blundelstown | 2030 | Initial | Pro-rata | IE Solar not priority | 60 | 76.8772 | 60.8709 | 6.0784 | 0.9942 | 8.9337 | 16.0063 | 7.907% | 1.293% | 11.62% | 20.82%
J | J Country | cushaling | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 75 | 231.2986 | 145.7014 | 42.7926 | 0.81138 | 41.9933 | 85.5972 | 18.5% | 0.3508% | 18.16% | 37.01%
I | E,F & I | rathcoursey | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 110 | 128.7891 | 87.4015 | 29.0028 | 1.1623 | 11.2224 | 41.3876 | 22.52% | 0.9025% | 8.714% | 32.14%
I | E,F & I | coolroe | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 9.3333 | 10.9275 | 7.9668 | 1.7349 | 0.080202 | 1.1456 | 2.9607 | 15.88% | 0.7339% | 10.48% | 27.09%
J | J Country | harristown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 42.3 | 54.1984 | 26.6986 | 8.3022 | 0.39076 | 18.807 | 27.4999 | 15.32% | 0.721% | 34.7% | 50.74%
J | J Country | coolnabacky | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 53.3333 | 68.3352 | 32.0122 | 15.0137 | 0.58384 | 20.7256 | 36.3231 | 21.97% | 0.8544% | 30.33% | 53.15%
H2 | H2 & K | kilvinoge | 2030 | 33% ECP | Pro-rata | IE wind not priority | 46.2 | 130.687 | 103.6205 | 21.3485 | 2.3408 | 3.3771 | 27.0664 | 16.34% | 1.791% | 2.584% | 20.71%
J | J Country | harristown | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 42.3 | 54.1984 | 25.1128 | 8.3022 | 0.39076 | 20.3927 | 29.0856 | 15.32% | 0.721% | 37.63% | 53.67%
H2 | H2 & K | kilvinoge | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 46.2 | 130.687 | 96.4956 | 29.9558 | 2.414 | 1.8216 | 34.1914 | 22.92% | 1.847% | 1.394% | 26.16%
J | J Country | coolnabacky | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 80 | 102.503 | 37.5885 | 22.5382 | 0.92893 | 41.4473 | 64.9144 | 21.99% | 0.9062% | 40.44% | 63.33%
H2 | H2 & K | kilvinoge | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 46.2 | 130.687 | 83.4835 | 39.5581 | 2.4922 | 5.1533 | 47.2035 | 30.27% | 1.907% | 3.943% | 36.12%
I | E,F & I | coolroe | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 14 | 16.3913 | 10.6916 | 5.2019 | 0.35979 | 0.13805 | 5.6997 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | kilvinoge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 46.2 | 130.687 | 79.2429 | 42.3721 | 2.5147 | 6.5573 | 51.4441 | 32.42% | 1.924% | 5.018% | 39.36%
J | J Country | harristown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 42.3 | 54.1984 | 23.9154 | 17.1036 | 1.1941 | 11.9854 | 30.2831 | 31.56% | 2.203% | 22.11% | 55.87%
H2 | H2 & K | kilvinoge | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 46.2 | 130.687 | 106.3626 | 21.3485 | 2.3408 | 0.63505 | 24.3243 | 16.34% | 1.791% | 0.4859% | 18.61%
I | E,F & I | coolroe | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 14 | 16.3913 | 10.5453 | 5.2019 | 0.35979 | 0.28441 | 5.8461 | 31.74% | 2.195% | 1.735% | 35.67%
J | J Country | harristown | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 42.3 | 54.1984 | 22.8298 | 17.1036 | 1.1941 | 13.0709 | 31.3686 | 31.56% | 2.203% | 24.12% | 57.88%
H2 | H2 & K | kilvinoge | 2030 | 100% ECP | Pro-rata | IE wind not priority | 138.6 | 392.0613 | 270.7743 | 107.804 | 7.165 | 6.318 | 121.287 | 27.5% | 1.828% | 1.611% | 30.94%
J | J Country | harristown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 42.3 | 54.1984 | 25.3897 | 11.9077 | 0.46306 | 16.438 | 28.8088 | 21.97% | 0.8544% | 30.33% | 53.15%
I | E,F & I | coolroe | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.6667 | 5.4638 | 4.4528 | 0.75707 | 0.10156 | 0.15237 | 1.011 | 13.86% | 1.859% | 2.789% | 18.5%
I | E,F & I | coolroe | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 9.3333 | 10.9275 | 8.5861 | 1.7349 | 0.080202 | 0.52642 | 2.3415 | 15.88% | 0.7339% | 4.817% | 21.43%
J | J Country | kilteel | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 15 | 19.2193 | 12.382 | 3.7244 | 0.35566 | 2.7572 | 6.8373 | 19.38% | 1.851% | 14.35% | 35.58%
J | J Country | coolnabacky | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 80 | 102.503 | 45.23 | 32.3473 | 2.2583 | 22.6674 | 57.273 | 31.56% | 2.203% | 22.11% | 55.87%
H2 | H2 & K | kilkenny | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 142.6665 | 167.0354 | 132.8171 | 26.5186 | 1.226 | 6.4737 | 34.2183 | 15.88% | 0.7339% | 3.876% | 20.49%
J | J Country | kilteel | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 15 | 19.2193 | 12.634 | 3.1856 | 0.3586 | 3.0411 | 6.5853 | 16.57% | 1.866% | 15.82% | 34.26%
H2 | H2 & K | kilkenny | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 30.8 | 87.1247 | 70.4061 | 14.1391 | 0.28635 | 2.2931 | 16.7185 | 16.23% | 0.3287% | 2.632% | 19.19%
J | J Country | kilteel | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 15 | 19.2193 | 12.7409 | 2.6116 | 0.35592 | 3.5108 | 6.4784 | 13.59% | 1.852% | 18.27% | 33.71%
H2 | H2 & K | kilkenny | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 142.6665 | 167.0354 | 137.1955 | 26.5186 | 1.226 | 2.0954 | 29.8399 | 15.88% | 0.7339% | 1.254% | 17.86%
I | E,F & I | coolroe | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 14 | 16.3913 | 11.1238 | 3.6913 | 0.14793 | 1.4283 | 5.2675 | 22.52% | 0.9025% | 8.714% | 32.14%
H2 | H2 & K | kilkenny | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 30.8 | 87.1247 | 54.8144 | 27.0083 | 0.58654 | 4.7154 | 32.3102 | 31% | 0.6732% | 5.412% | 37.09%
J | J Country | kilteel | 2030 | Initial | Pro-rata | IE Solar not priority | 15 | 19.2193 | 15.2177 | 1.5196 | 0.24855 | 2.2334 | 4.0016 | 7.907% | 1.293% | 11.62% | 20.82%
J | J Country | coolnabacky | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 53.3333 | 68.3352 | 31.6631 | 10.4676 | 0.49269 | 25.7118 | 36.6721 | 15.32% | 0.721% | 37.63% | 53.67%
H2 | H2 & K | kilkenny | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 142.6665 | 167.0354 | 122.3646 | 37.478 | 1.4377 | 5.7552 | 44.6708 | 22.44% | 0.8607% | 3.445% | 26.74%
I | E,F & I | coolroe | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 9.3333 | 10.9275 | 7.603 | 2.4518 | 0.094053 | 0.77863 | 3.3245 | 22.44% | 0.8607% | 7.125% | 30.42%
H2 | H2 & K | kilkenny | 2035 | 100% ECP | Pro-rata | IE wind not priority | 46.2 | 130.6871 | 99.6719 | 23.514 | 0.46793 | 7.0332 | 31.0152 | 17.99% | 0.3581% | 5.382% | 23.73%
J | J Country | harristown | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 42.3 | 54.1984 | 19.8749 | 11.9171 | 0.49117 | 21.9152 | 34.3235 | 21.99% | 0.9062% | 40.44% | 63.33%
H2 | H2 & K | kilkenny | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 208 | 243.5285 | 178.341 | 54.8417 | 2.1979 | 8.1479 | 65.1875 | 22.52% | 0.9025% | 3.346% | 26.77%
J | J Country | coolnabacky | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 53.3333 | 68.3352 | 33.6625 | 10.4676 | 0.49269 | 23.7124 | 34.6728 | 15.32% | 0.721% | 34.7% | 50.74%
H2 | H2 & K | kilvinoge | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 138.6 | 392.0613 | 275.4343 | 107.804 | 7.165 | 1.658 | 116.627 | 27.5% | 1.828% | 0.4229% | 29.75%
J | J Country | harristown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 42.3 | 54.1984 | 37.5963 | 7.3648 | 1.0037 | 8.2336 | 16.6022 | 13.59% | 1.852% | 15.19% | 30.63%
J | J Country | craddanstown | 2030 | 33% ECP | Pro-rata | IE wind not priority | 60.6666 | 187.0947 | 129.9118 | 34.9231 | 3.5172 | 18.7426 | 57.1829 | 18.67% | 1.88% | 10.02% | 30.56%
H2 | H2 & K | lodgewood | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 36.3333 | 42.5394 | 30.4505 | 9.6828 | 0.90427 | 1.5019 | 12.0889 | 22.76% | 2.126% | 3.531% | 28.42%
J | J Country | craddanstown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 60.6666 | 187.0947 | 135.0566 | 34.9231 | 3.5172 | 13.5978 | 52.0382 | 18.67% | 1.88% | 7.268% | 27.81%
I | E,F & I | castleview | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 3.49 | 4.0861 | 2.773 | 0.92018 | 0.036878 | 0.35606 | 1.3131 | 22.52% | 0.9025% | 8.714% | 32.14%
J | J Country | fosterstown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 55.8599 | 71.5726 | 33.5287 | 15.725 | 0.6115 | 21.7074 | 38.0439 | 21.97% | 0.8544% | 30.33% | 53.15%
H2 | H2 & K | lodgewood | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 36.3333 | 42.5394 | 35.6573 | 5.8943 | 0.79075 | 0.197 | 6.8821 | 13.86% | 1.859% | 0.4631% | 16.18%
H2 | H2 & K | lodgewood | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 109 | 127.6183 | 82.6985 | 40.5003 | 2.8012 | 1.6182 | 44.9198 | 31.74% | 2.195% | 1.268% | 35.2%
J | J Country | fosterstown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 55.8599 | 71.5726 | 35.2572 | 10.9635 | 0.51603 | 24.8358 | 36.3154 | 15.32% | 0.721% | 34.7% | 50.74%
I | E,F & I | castleview | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 2.3267 | 2.7241 | 1.8953 | 0.61121 | 0.023446 | 0.1941 | 0.82875 | 22.44% | 0.8607% | 7.125% | 30.42%
J | J Country | craddanstown | 2030 | 100% ECP | Pro-rata | IE wind not priority | 182 | 561.2847 | 304.0963 | 168.2147 | 10.3208 | 78.6529 | 257.1884 | 29.97% | 1.839% | 14.01% | 45.82%
H2 | H2 & K | lodgewood | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 109 | 127.6183 | 84.1931 | 40.5003 | 2.8012 | 0.12363 | 43.4252 | 31.74% | 2.195% | 0.09687% | 34.03%
J | J Country | fosterstown | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 55.8599 | 71.5726 | 33.1632 | 10.9635 | 0.51603 | 26.9299 | 38.4095 | 15.32% | 0.721% | 37.63% | 53.67%
I | E,F & I | castleview | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 2.3267 | 2.7241 | 2.1404 | 0.43248 | 0.019993 | 0.13123 | 0.5837 | 15.88% | 0.7339% | 4.817% | 21.43%
H2 | H2 & K | lodgewood | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 72.6666 | 85.0788 | 67.6498 | 13.5071 | 0.62443 | 3.2974 | 17.4289 | 15.88% | 0.7339% | 3.876% | 20.49%
J | J Country | craddanstown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 182 | 561.2847 | 318.9841 | 168.2147 | 10.3208 | 63.7651 | 242.3006 | 29.97% | 1.839% | 11.36% | 43.17%
I | E,F & I | castleview | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 2.3267 | 2.7241 | 1.986 | 0.43248 | 0.019993 | 0.28559 | 0.73806 | 15.88% | 0.7339% | 10.48% | 27.09%
H2 | H2 & K | lodgewood | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 72.6666 | 85.0788 | 69.8799 | 13.5071 | 0.62443 | 1.0673 | 15.1988 | 15.88% | 0.7339% | 1.254% | 17.86%
J | J Country | fosterstown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 83.79 | 107.359 | 47.3728 | 33.8797 | 2.3653 | 23.7412 | 59.9863 | 31.56% | 2.203% | 22.11% | 55.87%
J | J Country | fosterstown | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 83.79 | 107.359 | 39.3693 | 23.606 | 0.97294 | 43.4108 | 67.9898 | 21.99% | 0.9062% | 40.44% | 63.33%
H2 | H2 & K | lodgewood | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 36.3333 | 42.5394 | 31.9197 | 8.3256 | 0.8043 | 1.4898 | 10.6197 | 19.57% | 1.891% | 3.502% | 24.96%
J | J Country | harristown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 42.3 | 54.1984 | 29.1176 | 12.2174 | 1.135 | 11.7284 | 25.0809 | 22.54% | 2.094% | 21.64% | 46.28%
I | E,F & I | coolroe | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 4.6667 | 5.4638 | 3.9443 | 1.2437 | 0.11614 | 0.15962 | 1.5194 | 22.76% | 2.126% | 2.921% | 27.81%
H2 | H2 & K | kilvinoge | 2035 | 66% ECP | Pro-rata | IE wind not priority | 92.3999 | 261.374 | 207.6252 | 42.4172 | 0.85906 | 10.4725 | 53.7488 | 16.23% | 0.3287% | 4.007% | 20.56%
J | J Country | harristown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 42.3 | 54.1984 | 34.9173 | 10.5029 | 1.003 | 7.7753 | 19.2812 | 19.38% | 1.851% | 14.35% | 35.58%
H2 | H2 & K | kilvinoge | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 92.3999 | 261.374 | 211.2184 | 42.4172 | 0.85906 | 6.8792 | 50.1556 | 16.23% | 0.3287% | 2.632% | 19.19%
J | J Country | craddanstown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 60.6666 | 187.0947 | 125.3927 | 47.7433 | 3.5523 | 10.4064 | 61.7021 | 25.52% | 1.899% | 5.562% | 32.98%
I | E,F & I | coolroe | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 4.6667 | 5.4638 | 4.0757 | 1.0693 | 0.1033 | 0.21543 | 1.3881 | 19.57% | 1.891% | 3.943% | 25.4%
H2 | H2 & K | kilvinoge | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 92.3999 | 261.374 | 164.4432 | 81.0248 | 1.7596 | 14.1463 | 96.9307 | 31% | 0.6732% | 5.412% | 37.09%
H2 | H2 & K | kilkenny | 2035 | 66% ECP | Pro-rata | IE wind not priority | 30.8 | 87.1247 | 69.2084 | 14.1391 | 0.28635 | 3.4908 | 17.9163 | 16.23% | 0.3287% | 4.007% | 20.56%
J | J Country | harristown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 42.3 | 54.1984 | 35.6279 | 8.9833 | 1.0113 | 8.5759 | 18.5705 | 16.57% | 1.866% | 15.82% | 34.26%
I | E,F & I | coolroe | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 4.6667 | 5.4638 | 4.1748 | 0.91856 | 0.10331 | 0.26708 | 1.289 | 16.81% | 1.891% | 4.888% | 23.59%
J | J Country | harristown | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 42.3 | 54.1984 | 35.9294 | 7.3648 | 1.0037 | 9.9005 | 18.269 | 13.59% | 1.852% | 18.27% | 33.71%
J | J Country | craddanstown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 60.6666 | 187.0947 | 116.5181 | 60.8227 | 3.5104 | 6.2436 | 70.5767 | 32.51% | 1.876% | 3.337% | 37.72%
J | J Country | harristown | 2030 | Initial | Pro-rata | IE Solar not priority | 42.3 | 54.1984 | 42.914 | 4.2852 | 0.70091 | 6.2983 | 11.2844 | 7.907% | 1.293% | 11.62% | 20.82%
H2 | H2 & K | lodgewood | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 36.3333 | 42.5394 | 34.3115 | 5.8943 | 0.79075 | 1.5428 | 8.2279 | 13.86% | 1.859% | 3.627% | 19.34%
I | E,F & I | coolroe | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 4.6667 | 5.4638 | 4.304 | 0.75707 | 0.10156 | 0.30116 | 1.1598 | 13.86% | 1.859% | 5.512% | 21.23%
J | J Country | craddanstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 60.6666 | 187.0947 | 110.2369 | 64.9331 | 3.464 | 8.4608 | 76.8578 | 34.71% | 1.851% | 4.522% | 41.08%
H2 | H2 & K | lodgewood | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 36.3333 | 42.5394 | 33.4531 | 7.1516 | 0.80438 | 1.1303 | 9.0863 | 16.81% | 1.891% | 2.657% | 21.36%
H2 | H2 & K | kilvinoge | 2035 | 100% ECP | Pro-rata | IE wind not priority | 138.6 | 392.0613 | 299.0158 | 70.542 | 1.4038 | 21.0997 | 93.0455 | 17.99% | 0.3581% | 5.382% | 23.73%
I | E,F & I | cow cross | 2030 | Initial | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.3648 | 0.47932 | 0.074676 | 0.87675 | 1.4308 | 8.271% | 1.289% | 15.13% | 24.69%
J | J Country | kilteel | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 15 | 19.2193 | 10.3254 | 4.3324 | 0.40249 | 4.159 | 8.8939 | 22.54% | 2.094% | 21.64% | 46.28%
J | J Country | kinnegad | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 49.9999 | 64.0643 | 29.6842 | 9.8134 | 0.46189 | 24.1048 | 34.3801 | 15.32% | 0.721% | 37.63% | 53.67%
H2 | H2 & K | kellymount | 2030 | 100% ECP | Pro-rata | IE wind not priority | 50.4 | 142.5678 | 98.4634 | 39.2015 | 2.6055 | 2.2975 | 44.1044 | 27.5% | 1.828% | 1.611% | 30.94%
I | E,F & I | kilbarry | 2030 | Initial | Pro-rata | IE Solar not priority | 9.9 | 11.591 | 8.7295 | 0.95864 | 0.14935 | 1.7535 | 2.8615 | 8.271% | 1.289% | 15.13% | 24.69%
H2 | H2 & K | kellymount | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 50.4 | 142.5678 | 100.1579 | 39.2015 | 2.6055 | 0.6029 | 42.4098 | 27.5% | 1.828% | 0.4229% | 29.75%
J | J Country | clonfad | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 100 | 128.1287 | 63.1172 | 19.6268 | 0.92379 | 44.4609 | 65.0115 | 15.32% | 0.721% | 34.7% | 50.74%
J | J Country | kinnegad | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 75 | 96.0965 | 42.4031 | 30.3256 | 2.1172 | 21.2507 | 53.6934 | 31.56% | 2.203% | 22.11% | 55.87%
H2 | H2 & K | kellymount | 2035 | 66% ECP | Pro-rata | IE wind not priority | 33.6 | 95.0451 | 75.5001 | 15.4245 | 0.31239 | 3.8082 | 19.545 | 16.23% | 0.3287% | 4.007% | 20.56%
I | E,F & I | cow cross | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 12.95 | 15.162 | 10.2895 | 3.4144 | 0.13684 | 1.3212 | 4.8724 | 22.52% | 0.9025% | 8.714% | 32.14%
J | J Country | kinnegad | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 75 | 96.0965 | 40.4784 | 30.3256 | 2.1172 | 23.1753 | 55.6181 | 31.56% | 2.203% | 24.12% | 57.88%
H2 | H2 & K | kellymount | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 33.6 | 95.0451 | 76.8067 | 15.4245 | 0.31239 | 2.5015 | 18.2384 | 16.23% | 0.3287% | 2.632% | 19.19%
J | J Country | clonfad | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 100 | 128.1287 | 60.0228 | 28.1507 | 1.0947 | 38.8605 | 68.1059 | 21.97% | 0.8544% | 30.33% | 53.15%
H2 | H2 & K | kellymount | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 33.6 | 95.0451 | 59.7975 | 29.4636 | 0.63986 | 5.1441 | 35.2475 | 31% | 0.6732% | 5.412% | 37.09%
J | J Country | kinnegad | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 25 | 32.0321 | 22.22 | 4.3527 | 0.5932 | 4.8662 | 9.8121 | 13.59% | 1.852% | 15.19% | 30.63%
I | E,F & I | cow cross | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 10.2833 | 12.0398 | 8.3769 | 2.7014 | 0.10363 | 0.85788 | 3.6629 | 22.44% | 0.8607% | 7.125% | 30.42%
H2 | H2 & K | kellymount | 2035 | 100% ECP | Pro-rata | IE wind not priority | 50.4 | 142.5678 | 108.733 | 25.6517 | 0.51047 | 7.6726 | 33.8347 | 17.99% | 0.3581% | 5.382% | 23.73%
J | J Country | clonfad | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 100 | 128.1287 | 46.9857 | 28.1728 | 1.1612 | 51.8091 | 81.143 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J Country | clonfad | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 100 | 128.1287 | 59.3684 | 19.6268 | 0.92379 | 48.2097 | 68.7603 | 15.32% | 0.721% | 37.63% | 53.67%
H2 | H2 & K | kellymount | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 16.8 | 47.5225 | 38.6773 | 7.7631 | 0.8512 | 0.23093 | 8.8452 | 16.34% | 1.791% | 0.4859% | 18.61%
J | J Country | kinnegad | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 49.9999 | 64.0643 | 31.5586 | 9.8134 | 0.46189 | 22.2304 | 32.5057 | 15.32% | 0.721% | 34.7% | 50.74%
I | E,F & I | kilbarry | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 33.2 | 38.8709 | 30.6197 | 5.386 | 0.72255 | 2.1426 | 8.2511 | 13.86% | 1.859% | 5.512% | 21.23%
H2 | H2 & K | kellis | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 421.6663 | 493.6912 | 405.4961 | 78.3786 | 3.6234 | 6.1931 | 88.1951 | 15.88% | 0.7339% | 1.254% | 17.86%
I | E,F & I | kilbarry | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 33.2 | 38.8709 | 31.6783 | 5.386 | 0.72255 | 1.084 | 7.1926 | 13.86% | 1.859% | 2.789% | 18.5%
J | J Country | maynooth | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 14.0378 | 3.5395 | 0.39845 | 3.379 | 7.317 | 16.57% | 1.866% | 15.82% | 34.26%
H2 | H2 & K | kellis | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 421.6663 | 493.6912 | 361.6617 | 110.7701 | 4.2492 | 17.0101 | 132.0294 | 22.44% | 0.8607% | 3.445% | 26.74%
J | J Country | clonfad | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 100 | 128.1287 | 53.9712 | 40.4341 | 2.8229 | 30.9005 | 74.1575 | 31.56% | 2.203% | 24.12% | 57.88%
I | E,F & I | kilbarry | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 33.2 | 38.8709 | 28.0612 | 8.8478 | 0.82629 | 1.1356 | 10.8096 | 22.76% | 2.126% | 2.921% | 27.81%
H2 | H2 & K | kellis | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 592 | 693.1195 | 507.5858 | 156.088 | 6.2554 | 23.1903 | 185.5337 | 22.52% | 0.9025% | 3.346% | 26.77%
J | J Country | maynooth | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 14.1566 | 2.9018 | 0.39547 | 3.9009 | 7.1982 | 13.59% | 1.852% | 18.27% | 33.71%
J | J Country | kinnegad | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 25 | 32.0321 | 17.2089 | 7.2207 | 0.67082 | 6.9317 | 14.8232 | 22.54% | 2.094% | 21.64% | 46.28%
J | J Country | clonfad | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 100 | 128.1287 | 56.5375 | 40.4341 | 2.8229 | 28.3342 | 71.5912 | 31.56% | 2.203% | 22.11% | 55.87%
I | E,F & I | kilbarry | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 33.2 | 38.8709 | 28.9957 | 7.6076 | 0.73494 | 1.5326 | 9.8751 | 19.57% | 1.891% | 3.943% | 25.4%
H2 | H2 & K | kellymount | 2030 | 33% ECP | Pro-rata | IE wind not priority | 16.8 | 47.5225 | 37.6802 | 7.7631 | 0.8512 | 1.2281 | 9.8423 | 16.34% | 1.791% | 2.584% | 20.71%
J | J Country | kinnegad | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 75 | 96.0965 | 35.2392 | 21.1296 | 0.87087 | 38.8568 | 60.8573 | 21.99% | 0.9062% | 40.44% | 63.33%
H2 | H2 & K | kellymount | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 16.8 | 47.5225 | 35.0893 | 10.893 | 0.87782 | 0.6624 | 12.4332 | 22.92% | 1.847% | 1.394% | 26.16%
I | E,F & I | kilbarry | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 33.2 | 38.8709 | 29.7009 | 6.5349 | 0.73501 | 1.9001 | 9.17 | 16.81% | 1.891% | 4.888% | 23.59%
H2 | H2 & K | kellymount | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 16.8 | 47.5225 | 30.3576 | 14.3848 | 0.90625 | 1.8739 | 17.1649 | 30.27% | 1.907% | 3.943% | 36.12%
J | J Country | kinnegad | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 49.9999 | 64.0643 | 30.0114 | 14.0753 | 0.54735 | 19.4302 | 34.0529 | 21.97% | 0.8544% | 30.33% | 53.15%
H2 | H2 & K | kellymount | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 16.8 | 47.5225 | 28.8156 | 15.408 | 0.91445 | 2.3845 | 18.707 | 32.42% | 1.924% | 5.018% | 39.36%
H2 | H2 & K | lodgewood | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 72.6666 | 85.0788 | 62.3259 | 19.0892 | 0.73227 | 2.9314 | 22.7529 | 22.44% | 0.8607% | 3.445% | 26.74%
J | J Country | kinnegad | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 25 | 32.0321 | 20.6367 | 6.2074 | 0.59276 | 4.5953 | 11.3955 | 19.38% | 1.851% | 14.35% | 35.58%
H2 | H2 & K | kilkenny | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 15.4 | 43.5623 | 35.4542 | 7.1162 | 0.78027 | 0.21168 | 8.1081 | 16.34% | 1.791% | 0.4859% | 18.61%
J | J Country | kilteel | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 15 | 19.2193 | 8.9053 | 2.944 | 0.13857 | 7.2314 | 10.314 | 15.32% | 0.721% | 37.63% | 53.67%
I | E,F & I | cow cross | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 7.6167 | 8.9177 | 6.4377 | 2.0298 | 0.18956 | 0.26053 | 2.4799 | 22.76% | 2.126% | 2.921% | 27.81%
H2 | H2 & K | kilkenny | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 77.3333 | 90.5426 | 75.8945 | 12.5457 | 1.6831 | 0.4193 | 14.6481 | 13.86% | 1.859% | 0.4631% | 16.18%
J | J Country | coolnabacky | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 26.6666 | 34.1676 | 18.3562 | 7.7021 | 0.71554 | 7.3938 | 15.8114 | 22.54% | 2.094% | 21.64% | 46.28%
H2 | H2 & K | kilkenny | 2030 | 100% ECP | Pro-rata | IE wind not priority | 46.2 | 130.6871 | 90.2581 | 35.9347 | 2.3883 | 2.106 | 40.429 | 27.5% | 1.828% | 1.611% | 30.94%
I | E,F & I | cow cross | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 7.6167 | 8.9177 | 6.6521 | 1.7453 | 0.16861 | 0.35161 | 2.2655 | 19.57% | 1.891% | 3.943% | 25.4%
J | J Country | kilteel | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 15 | 19.2193 | 8.4806 | 6.0651 | 0.42344 | 4.2501 | 10.7387 | 31.56% | 2.203% | 22.11% | 55.87%
H2 | H2 & K | kilkenny | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 208 | 243.5285 | 157.8101 | 77.285 | 5.3455 | 3.088 | 85.7184 | 31.74% | 2.195% | 1.268% | 35.2%
J | J Country | coolnabacky | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 26.6666 | 34.1676 | 23.7013 | 4.6429 | 0.63275 | 5.1906 | 10.4663 | 13.59% | 1.852% | 15.19% | 30.63%
H2 | H2 & K | kilkenny | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 46.2 | 130.6871 | 91.8114 | 35.9347 | 2.3883 | 0.55266 | 38.8757 | 27.5% | 1.828% | 0.4229% | 29.75%
J | J Country | kilteel | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 15 | 19.2193 | 8.0957 | 6.0651 | 0.42344 | 4.6351 | 11.1236 | 31.56% | 2.203% | 24.12% | 57.88%
I | E,F & I | cow cross | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 7.6167 | 8.9177 | 6.8139 | 1.4992 | 0.16862 | 0.43592 | 2.1038 | 16.81% | 1.891% | 4.888% | 23.59%
H2 | H2 & K | kilkenny | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 208 | 243.5285 | 160.6621 | 77.285 | 5.3455 | 0.23591 | 82.8664 | 31.74% | 2.195% | 0.09687% | 34.03%
J | J Country | kilteel | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 15 | 19.2193 | 13.332 | 2.6116 | 0.35592 | 2.9197 | 5.8873 | 13.59% | 1.852% | 15.19% | 30.63%
J | J Country | coolnabacky | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 80 | 102.503 | 43.177 | 32.3473 | 2.2583 | 24.7204 | 59.326 | 31.56% | 2.203% | 24.12% | 57.88%
I | E,F & I | cow cross | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 7.6167 | 8.9177 | 7.0247 | 1.2356 | 0.16577 | 0.49154 | 1.893 | 13.86% | 1.859% | 5.512% | 21.23%
I | E,F & I | cow cross | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 7.6167 | 8.9177 | 7.2676 | 1.2356 | 0.16577 | 0.24869 | 1.6501 | 13.86% | 1.859% | 2.789% | 18.5%
H2 | H2 & K | kilkenny | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 77.3333 | 90.5426 | 64.812 | 20.6092 | 1.9247 | 3.1967 | 25.7306 | 22.76% | 2.126% | 3.531% | 28.42%
J | J Country | kilteel | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 15 | 19.2193 | 9.4676 | 2.944 | 0.13857 | 6.6691 | 9.7517 | 15.32% | 0.721% | 34.7% | 50.74%
J | J Country | coolnabacky | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 26.6666 | 34.1676 | 22.0124 | 6.6212 | 0.63228 | 4.9017 | 12.1552 | 19.38% | 1.851% | 14.35% | 35.58%
H2 | H2 & K | kilkenny | 2030 | Initial | Pro-rata | IE Solar not priority | 12 | 14.0497 | 11.716 | 1.162 | 0.18103 | 0.99073 | 2.3337 | 8.271% | 1.289% | 7.052% | 16.61%
I | E,F & I | cow cross | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 10.2833 | 12.0398 | 8.7778 | 1.9114 | 0.088366 | 1.2623 | 3.2621 | 15.88% | 0.7339% | 10.48% | 27.09%
H2 | H2 & K | kilkenny | 2030 | 33% ECP | Pro-rata | IE wind not priority | 15.4 | 43.5623 | 34.5402 | 7.1162 | 0.78027 | 1.1257 | 9.0221 | 16.34% | 1.791% | 2.584% | 20.71%
J | J Country | kinnegad | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 25 | 32.0321 | 21.0567 | 5.3093 | 0.59767 | 5.0685 | 10.9755 | 16.57% | 1.866% | 15.82% | 34.26%
H2 | H2 & K | kilkenny | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 77.3333 | 90.5426 | 73.03 | 12.5457 | 1.6831 | 3.2837 | 17.5125 | 13.86% | 1.859% | 3.627% | 19.34%
J | J Country | kinnegad | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 25 | 32.0321 | 21.2349 | 4.3527 | 0.5932 | 5.8513 | 10.7973 | 13.59% | 1.852% | 18.27% | 33.71%
H2 | H2 & K | kilkenny | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 15.4 | 43.5623 | 32.1652 | 9.9853 | 0.80467 | 0.6072 | 11.3971 | 22.92% | 1.847% | 1.394% | 26.16%
I | E,F & I | cow cross | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 10.2833 | 12.0398 | 9.46 | 1.9114 | 0.088366 | 0.58 | 2.5798 | 15.88% | 0.7339% | 4.817% | 21.43%
J | J Country | coolnabacky | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 26.6666 | 34.1676 | 22.6505 | 4.6429 | 0.63275 | 6.2414 | 11.5171 | 13.59% | 1.852% | 18.27% | 33.71%
H2 | H2 & K | kilkenny | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 77.3333 | 90.5426 | 71.2029 | 15.2219 | 1.7121 | 2.4057 | 19.3396 | 16.81% | 1.891% | 2.657% | 21.36%
I | E,F & I | cow cross | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 12.95 | 15.162 | 9.8898 | 4.8117 | 0.33281 | 0.1277 | 5.2722 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | kilkenny | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 15.4 | 43.5623 | 27.8278 | 13.186 | 0.83073 | 1.7178 | 15.7345 | 30.27% | 1.907% | 3.943% | 36.12%
J | J Country | kilteel | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 15 | 19.2193 | 7.0478 | 4.2259 | 0.17417 | 7.7714 | 12.1715 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J Country | coolnabacky | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 26.6666 | 34.1676 | 22.4604 | 5.6633 | 0.63752 | 5.4064 | 11.7072 | 16.57% | 1.866% | 15.82% | 34.26%
H2 | H2 & K | kilkenny | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 77.3333 | 90.5426 | 67.9392 | 17.7205 | 1.7119 | 3.1709 | 22.6033 | 19.57% | 1.891% | 3.502% | 24.96%
I | E,F & I | cow cross | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 12.95 | 15.162 | 9.7544 | 4.8117 | 0.33281 | 0.26308 | 5.4076 | 31.74% | 2.195% | 1.735% | 35.67%
J | J Country | kilteel | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 15 | 19.2193 | 9.0034 | 4.2226 | 0.1642 | 5.8291 | 10.2159 | 21.97% | 0.8544% | 30.33% | 53.15%
H2 | H2 & K | kilkenny | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 15.4 | 43.5623 | 26.4143 | 14.124 | 0.83825 | 2.1858 | 17.148 | 32.42% | 1.924% | 5.018% | 39.36%
J | J Country | fosterstown | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 83.79 | 107.359 | 45.2225 | 33.8797 | 2.3653 | 25.8915 | 62.1365 | 31.56% | 2.203% | 24.12% | 57.88%
J | J Country | derryiron | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 156 | 481.1012 | 273.4149 | 144.184 | 8.8464 | 54.6558 | 207.6862 | 29.97% | 1.839% | 11.36% | 43.17%
H2 | H2 & K | waterford | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 14.28 | 40.3942 | 38.6682 | 0 | 1.5552 | 0.17082 | 1.726 | 0% | 3.85% | 0.4229% | 4.273%
H2 | H2 & K | wexford | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 114.03 | 133.5075 | 97.8031 | 29.9552 | 1.1491 | 4.6 | 35.7043 | 22.44% | 0.8607% | 3.445% | 26.74%
J | J Country | cushaling | 2030 | Initial | Pro-rata | IE wind not priority | 75 | 231.2986 | 167.8798 | 31.8467 | 4.4975 | 27.0746 | 63.4188 | 13.77% | 1.944% | 11.71% | 27.42%
J | J Country | derryiron | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 132 | 169.1299 | 71.242 | 53.373 | 3.7263 | 40.7886 | 97.8878 | 31.56% | 2.203% | 24.12% | 57.88%
H2 | H2 & K | waterford | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 9.99 | 11.6964 | 7.7164 | 3.7119 | 0.25674 | 0.01133 | 3.98 | 31.74% | 2.195% | 0.09687% | 34.03%
H2 | H2 & K | wexford | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 27 | 76.3756 | 70.8374 | 0 | 1.4045 | 4.1337 | 5.5382 | 0% | 1.839% | 5.412% | 7.251%
J | J Country | derryiron | 2030 | 100% ECP | Pro-rata | IE wind not priority | 156 | 481.1012 | 260.654 | 144.184 | 8.8464 | 67.4168 | 220.4472 | 29.97% | 1.839% | 14.01% | 45.82%
J | J Country | cushaling | 2030 | 33% ECP | Pro-rata | IE wind not priority | 75 | 231.2986 | 160.6054 | 43.1743 | 4.3481 | 23.1708 | 70.6932 | 18.67% | 1.88% | 10.02% | 30.56%
J | J Country | derryiron | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 132 | 169.1299 | 117.3217 | 22.9825 | 3.1321 | 25.6936 | 51.8082 | 13.59% | 1.852% | 15.19% | 30.63%
H2 | H2 & K | wexford | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 114.03 | 133.5075 | 109.6571 | 21.1957 | 0.97987 | 1.6748 | 23.8503 | 15.88% | 0.7339% | 1.254% | 17.86%
H2 | H2 & K | waterford | 2035 | 66% ECP | Pro-rata | IE wind priority | 14.28 | 40.3942 | 38.4239 | 0 | 0.35183 | 1.6185 | 1.9703 | 0% | 0.871% | 4.007% | 4.878%
J | J Country | derryiron | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 119.3333 | 368.0218 | 265.6609 | 68.695 | 6.9184 | 26.7474 | 102.3609 | 18.67% | 1.88% | 7.268% | 27.81%
H2 | H2 & K | waterford | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 7.99 | 9.3548 | 7.4384 | 1.4852 | 0.068659 | 0.36256 | 1.9164 | 15.88% | 0.7339% | 3.876% | 20.49%
J | J Country | cushaling | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 75 | 231.2986 | 155.0185 | 59.0234 | 4.3916 | 12.8651 | 76.2801 | 25.52% | 1.899% | 5.562% | 32.98%
H2 | H2 & K | wexford | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 27 | 76.3756 | 73.7002 | 0 | 0.66522 | 2.0102 | 2.6754 | 0% | 0.871% | 2.632% | 3.503%
H2 | H2 & K | waterford | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 14.28 | 40.3942 | 38.9792 | 0 | 0.35183 | 1.0632 | 1.415 | 0% | 0.871% | 2.632% | 3.503%
H2 | H2 & K | waterford | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 9.99 | 11.6964 | 7.5794 | 3.7119 | 0.25674 | 0.14831 | 4.117 | 31.74% | 2.195% | 1.268% | 35.2%
H2 | H2 & K | wexford | 2035 | 100% ECP | Pro-rata | IE wind priority | 27 | 76.3756 | 71.5362 | 0 | 0.72902 | 4.1103 | 4.8393 | 0% | 0.9545% | 5.382% | 6.336%
J | J Country | derryiron | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 132 | 169.1299 | 74.6295 | 53.373 | 3.7263 | 37.4012 | 94.5004 | 31.56% | 2.203% | 22.11% | 55.87%
H2 | H2 & K | waterford | 2030 | 100% ECP | Pro-rata | IE wind priority | 14.28 | 40.3942 | 38.1881 | 0 | 1.5552 | 0.65095 | 2.2061 | 0% | 3.85% | 1.611% | 5.461%
J | J Country | curraghdoo | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 2.6667 | 3.4168 | 1.6831 | 0.52338 | 0.024634 | 1.1856 | 1.7336 | 15.32% | 0.721% | 34.7% | 50.74%
H2 | H2 & K | waterford | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 5.99 | 7.0131 | 5.5152 | 1.179 | 0.13261 | 0.18634 | 1.498 | 16.81% | 1.891% | 2.657% | 21.36%
I | E,F & I | barnahely | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 3.3167 | 3.8832 | 3.0589 | 0.53806 | 0.072183 | 0.21404 | 0.82429 | 13.86% | 1.859% | 5.512% | 21.23%
J | J Country | derryiron | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 137.6666 | 424.5614 | 267.443 | 78.5482 | 1.4893 | 77.0809 | 157.1184 | 18.5% | 0.3508% | 18.16% | 37.01%
H2 | H2 & K | waterford | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 14.28 | 40.3942 | 37.1449 | 0 | 1.6565 | 1.5928 | 3.2493 | 0% | 4.101% | 3.943% | 8.044%
J | J Country | derryiron | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 132 | 169.1299 | 78.3663 | 25.9074 | 1.2194 | 63.6367 | 90.7636 | 15.32% | 0.721% | 37.63% | 53.67%
H2 | H2 & K | waterford | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 5.99 | 7.0131 | 5.2624 | 1.3726 | 0.1326 | 0.24561 | 1.7508 | 19.57% | 1.891% | 3.502% | 24.96%
J | J Country | curraghdoo | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 2.6667 | 3.4168 | 1.6006 | 0.75068 | 0.029192 | 1.0363 | 1.8162 | 21.97% | 0.8544% | 30.33% | 53.15%
J | J Country | derryiron | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 132 | 169.1299 | 90.8633 | 38.1254 | 3.5419 | 36.5992 | 78.2665 | 22.54% | 2.094% | 21.64% | 46.28%
H2 | H2 & K | waterford | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 14.28 | 40.3942 | 36.6878 | 0 | 1.6796 | 2.0268 | 3.7064 | 0% | 4.158% | 5.018% | 9.176%
H2 | H2 & K | waterford | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 5.99 | 7.0131 | 5.0201 | 1.5963 | 0.14908 | 0.2476 | 1.993 | 22.76% | 2.126% | 3.531% | 28.42%
J | J Country | curraghdoo | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 4 | 5.1251 | 1.8794 | 1.1269 | 0.046446 | 2.0724 | 3.2457 | 21.99% | 0.9062% | 40.44% | 63.33%
H2 | H2 & K | waterford | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 14.28 | 40.3942 | 38.9163 | 0 | 1.2816 | 0.19629 | 1.4779 | 0% | 3.173% | 0.4859% | 3.659%
H2 | H2 & K | wexford | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 114.03 | 133.5075 | 97.7703 | 30.0654 | 1.2049 | 4.4669 | 35.7372 | 22.52% | 0.9025% | 3.346% | 26.77%
H2 | H2 & K | waterford | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 5.99 | 7.0131 | 5.8786 | 0.97175 | 0.13036 | 0.032478 | 1.1346 | 13.86% | 1.859% | 0.4631% | 16.18%
J | J Country | derryiron | 2035 | 66% ECP | Pro-rata | IE wind not priority | 137.6666 | 424.5614 | 262.5869 | 78.5482 | 1.4893 | 81.937 | 161.9745 | 18.5% | 0.3508% | 19.3% | 38.15%
J | J Country | derryiron | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 132 | 169.1299 | 83.3147 | 25.9074 | 1.2194 | 58.6884 | 85.8152 | 15.32% | 0.721% | 34.7% | 50.74%
H2 | H2 & K | waterford | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 7.99 | 9.3548 | 7.6836 | 1.4852 | 0.068659 | 0.11735 | 1.6712 | 15.88% | 0.7339% | 1.254% | 17.86%
J | J Country | derryiron | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 119.3333 | 368.0218 | 216.8398 | 127.7256 | 6.8137 | 16.6427 | 151.182 | 34.71% | 1.851% | 4.522% | 41.08%
J | J Country | derryiron | 2030 | Initial | Pro-rata | IE Solar not priority | 132 | 169.1299 | 133.916 | 13.3724 | 2.1872 | 19.6542 | 35.2139 | 7.907% | 1.293% | 11.62% | 20.82%
H2 | H2 & K | wexford | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 114.03 | 133.5075 | 107.6848 | 18.499 | 2.4817 | 4.842 | 25.8227 | 13.86% | 1.859% | 3.627% | 19.34%
J | J Country | cushaling | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 75 | 231.2986 | 131.4495 | 69.3192 | 4.2531 | 26.2768 | 99.8492 | 29.97% | 1.839% | 11.36% | 43.17%
H2 | H2 & K | wexford | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 114.03 | 133.5075 | 86.5148 | 42.3693 | 2.9305 | 1.6929 | 46.9927 | 31.74% | 2.195% | 1.268% | 35.2%
H2 | H2 & K | wexford | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 27 | 76.3756 | 72.549 | 0 | 2.762 | 1.0646 | 3.8266 | 0% | 3.616% | 1.394% | 5.01%
J | J Country | derryiron | 2030 | Initial | Pro-rata | IE wind not priority | 101 | 311.4822 | 226.0781 | 42.8869 | 6.0566 | 36.4604 | 85.404 | 13.77% | 1.944% | 11.71% | 27.42%
H2 | H2 & K | wexford | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 114.03 | 133.5075 | 104.9907 | 22.445 | 2.5245 | 3.5473 | 28.5168 | 16.81% | 1.891% | 2.657% | 21.36%
H2 | H2 & K | wexford | 2030 | 100% ECP | Pro-rata | IE wind priority | 27 | 76.3756 | 72.2043 | 0 | 2.9405 | 1.2308 | 4.1712 | 0% | 3.85% | 1.611% | 5.461%
H2 | H2 & K | wexford | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 27 | 76.3756 | 70.2319 | 0 | 3.132 | 3.0117 | 6.1437 | 0% | 4.101% | 3.943% | 8.044%
J | J Country | cushaling | 2035 | 100% ECP | Pro-rata | IE wind not priority | 75 | 231.2986 | 127.1316 | 46.9126 | 0.87142 | 56.3831 | 104.167 | 20.28% | 0.3768% | 24.38% | 45.04%
H2 | H2 & K | wexford | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 114.03 | 133.5075 | 100.1783 | 26.1293 | 2.5243 | 4.6756 | 33.3292 | 19.57% | 1.891% | 3.502% | 24.96%
H2 | H2 & K | wexford | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 114.03 | 133.5075 | 111.9085 | 18.499 | 2.4817 | 0.61827 | 21.599 | 13.86% | 1.859% | 0.4631% | 16.18%
J | J Country | cushaling | 2035 | 66% ECP | Pro-rata | IE wind not priority | 75 | 231.2986 | 143.0559 | 42.7926 | 0.81138 | 44.6388 | 88.2428 | 18.5% | 0.3508% | 19.3% | 38.15%
H2 | H2 & K | wexford | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 27 | 76.3756 | 69.3677 | 0 | 3.1757 | 3.8322 | 7.0079 | 0% | 4.158% | 5.018% | 9.176%
J | J Country | cushaling | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 75 | 231.2986 | 135.3437 | 76.2434 | 1.4931 | 18.2184 | 95.9549 | 32.96% | 0.6455% | 7.877% | 41.49%
H2 | H2 & K | wexford | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 114.03 | 133.5075 | 95.567 | 30.3889 | 2.838 | 4.7136 | 37.9404 | 22.76% | 2.126% | 3.531% | 28.42%
H2 | H2 & K | wexford | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 27 | 76.3756 | 73.5812 | 0 | 2.4233 | 0.37113 | 2.7944 | 0% | 3.173% | 0.4859% | 3.659%
H2 | H2 & K | wexford | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 27 | 76.3756 | 73.1121 | 0 | 2.9405 | 0.32298 | 3.2635 | 0% | 3.85% | 0.4229% | 4.273%
H2 | H2 & K | wexford | 2030 | 33% ECP | Pro-rata | IE wind priority | 27 | 76.3756 | 71.9787 | 0 | 2.4233 | 1.9737 | 4.3969 | 0% | 3.173% | 2.584% | 5.757%
J | J Country | derryiron | 2030 | 33% ECP | Pro-rata | IE wind not priority | 119.3333 | 368.0218 | 255.541 | 68.695 | 6.9184 | 36.8673 | 112.4808 | 18.67% | 1.88% | 10.02% | 30.56%
H2 | H2 & K | wexford | 2030 | Initial | Pro-rata | IE Solar not priority | 114.03 | 133.5075 | 111.331 | 11.0418 | 1.7203 | 9.4144 | 22.1765 | 8.271% | 1.289% | 7.052% | 16.61%
J | J Country | cushaling | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 75 | 231.2986 | 144.0472 | 75.193 | 4.3397 | 7.7187 | 87.2515 | 32.51% | 1.876% | 3.337% | 37.72%
H2 | H2 & K | waterford | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 14.28 | 40.3942 | 37.4651 | 0 | 0.74284 | 2.1862 | 2.9291 | 0% | 1.839% | 5.412% | 7.251%
J | J Country | derryiron | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 132 | 169.1299 | 108.9617 | 32.7752 | 3.1298 | 24.2633 | 60.1682 | 19.38% | 1.851% | 14.35% | 35.58%
H2 | H2 & K | waterford | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 7.99 | 9.3548 | 6.853 | 2.0989 | 0.080516 | 0.32232 | 2.5018 | 22.44% | 0.8607% | 3.445% | 26.74%
H2 | H2 & K | wexford | 2035 | 66% ECP | Pro-rata | IE wind priority | 27 | 76.3756 | 72.6502 | 0 | 0.66522 | 3.0601 | 3.7254 | 0% | 0.871% | 4.007% | 4.878%
J | J Country | cushaling | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 75 | 231.2986 | 136.282 | 80.2745 | 4.2824 | 10.4598 | 95.0166 | 34.71% | 1.851% | 4.522% | 41.08%
H2 | H2 & K | waterford | 2035 | 100% ECP | Pro-rata | IE wind priority | 14.28 | 40.3942 | 37.8347 | 0 | 0.38557 | 2.1739 | 2.5595 | 0% | 0.9545% | 5.382% | 6.336%
J | J Country | derryiron | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 119.3333 | 368.0218 | 229.195 | 119.6404 | 6.905 | 12.2814 | 138.8267 | 32.51% | 1.876% | 3.337% | 37.72%
H2 | H2 & K | wexford | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 114.03 | 133.5075 | 106.1576 | 21.1957 | 0.97987 | 5.1743 | 27.3499 | 15.88% | 0.7339% | 3.876% | 20.49%
H2 | H2 & K | waterford | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 9.99 | 11.6964 | 8.5655 | 2.634 | 0.10556 | 0.39134 | 3.1309 | 22.52% | 0.9025% | 3.346% | 26.77%
J | J Country | cushaling | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 75 | 231.2986 | 166.9657 | 43.1743 | 4.3481 | 16.8105 | 64.3329 | 18.67% | 1.88% | 7.268% | 27.81%
J | J Country | derryiron | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 119.3333 | 368.0218 | 246.6517 | 93.9128 | 6.9875 | 20.4698 | 121.3701 | 25.52% | 1.899% | 5.562% | 32.98%
H2 | H2 & K | wexford | 2030 | Initial | Pro-rata | IE wind priority | 27 | 76.3756 | 69.7084 | 0 | 2.1455 | 4.5217 | 6.6672 | 0% | 2.809% | 5.92% | 8.729%
J | J Country | derryiron | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 132 | 169.1299 | 112.1202 | 22.9825 | 3.1321 | 30.8951 | 57.0097 | 13.59% | 1.852% | 18.27% | 33.71%
H2 | H2 & K | wexford | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 114.03 | 133.5075 | 88.0784 | 42.3693 | 2.9305 | 0.12933 | 45.4291 | 31.74% | 2.195% | 0.09687% | 34.03%
J | J Country | cushaling | 2030 | 100% ECP | Pro-rata | IE wind not priority | 75 | 231.2986 | 125.3144 | 69.3192 | 4.2531 | 32.4119 | 105.9842 | 29.97% | 1.839% | 14.01% | 45.82%
J | J Country | derryiron | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 132 | 169.1299 | 111.1793 | 28.0331 | 3.1557 | 26.7618 | 57.9506 | 16.57% | 1.866% | 15.82% | 34.26%
J | J Country | maynooth | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 13.7578 | 4.1383 | 0.39517 | 3.0635 | 7.597 | 19.38% | 1.851% | 14.35% | 35.58%
H2 | H2 & K | waterford | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 14.28 | 40.3942 | 38.3703 | 0 | 1.4608 | 0.56304 | 2.0239 | 0% | 3.616% | 1.394% | 5.01%
H2 | H2 & K | waterford | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 5.99 | 7.0131 | 5.6567 | 0.97175 | 0.13036 | 0.25435 | 1.3565 | 13.86% | 1.859% | 3.627% | 19.34%
H2 | H2 & K | rosspile | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 95 | 111.227 | 73.3793 | 35.2984 | 2.4414 | 0.10775 | 37.8476 | 31.74% | 2.195% | 0.09687% | 34.03%
J | J Country | craddanstown | 2035 | 100% ECP | Pro-rata | IE wind not priority | 182 | 561.2847 | 308.506 | 113.8411 | 2.1147 | 136.8229 | 252.7787 | 20.28% | 0.3768% | 24.38% | 45.04%
J | J Country | dunfirth | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 31.5 | 40.3605 | 18.9072 | 8.8675 | 0.34483 | 12.241 | 21.4533 | 21.97% | 0.8544% | 30.33% | 53.15%
I | E,F & I | castleview | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 1.1633 | 1.362 | 1.0407 | 0.22898 | 0.025755 | 0.06658 | 0.32132 | 16.81% | 1.891% | 4.888% | 23.59%
H2 | H2 & K | rosspile | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 95 | 111.227 | 88.4414 | 17.6584 | 0.81635 | 4.3108 | 22.7855 | 15.88% | 0.7339% | 3.876% | 20.49%
J | J Country | dunfirth | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 31.5 | 40.3605 | 19.8819 | 6.1825 | 0.29099 | 14.0052 | 20.4786 | 15.32% | 0.721% | 34.7% | 50.74%
H2 | H2 & K | rosspile | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 95 | 111.227 | 91.3569 | 17.6584 | 0.81635 | 1.3953 | 19.8701 | 15.88% | 0.7339% | 1.254% | 17.86%
I | E,F & I | castleview | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 1.1633 | 1.362 | 1.0729 | 0.18873 | 0.025318 | 0.075076 | 0.28912 | 13.86% | 1.859% | 5.512% | 21.23%
J | J Country | dunfirth | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 31.5 | 40.3605 | 18.701 | 6.1825 | 0.29099 | 15.186 | 21.6595 | 15.32% | 0.721% | 37.63% | 53.67%
H2 | H2 & K | rosspile | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 95 | 111.227 | 81.4812 | 24.9561 | 0.95733 | 3.8323 | 29.7458 | 22.44% | 0.8607% | 3.445% | 26.74%
J | J Country | curraghdoo | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 1.3333 | 1.7084 | 1.1325 | 0.23215 | 0.031638 | 0.31207 | 0.57586 | 13.59% | 1.852% | 18.27% | 33.71%
H2 | H2 & K | rosspile | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 95 | 111.227 | 81.4538 | 25.0479 | 1.0038 | 3.7214 | 29.7731 | 22.52% | 0.9025% | 3.346% | 26.77%
J | J Country | dunfirth | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 31.5 | 40.3605 | 17.8093 | 12.7367 | 0.88922 | 8.9253 | 22.5512 | 31.56% | 2.203% | 22.11% | 55.87%
I | E,F & I | barnahely | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 9.95 | 11.6496 | 7.9059 | 2.6234 | 0.10514 | 1.0151 | 3.7437 | 22.52% | 0.9025% | 8.714% | 32.14%
J | J Country | dunfirth | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 31.5 | 40.3605 | 14.8005 | 8.8744 | 0.36577 | 16.3199 | 25.5601 | 21.99% | 0.9062% | 40.44% | 63.33%
I | E,F & I | castleview | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 1.1633 | 1.362 | 1.016 | 0.26657 | 0.025752 | 0.053703 | 0.34603 | 19.57% | 1.891% | 3.943% | 25.4%
H2 | H2 & K | rosspile | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 95 | 111.227 | 72.0767 | 35.2984 | 2.4414 | 1.4104 | 39.1502 | 31.74% | 2.195% | 1.268% | 35.2%
H2 | H2 & K | lodgewood | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 109 | 127.6183 | 93.4575 | 28.7392 | 1.1518 | 4.2698 | 34.1608 | 22.52% | 0.9025% | 3.346% | 26.77%
J | J Country | fosterstown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 27.93 | 35.7863 | 24.8242 | 4.8629 | 0.66273 | 5.4365 | 10.9621 | 13.59% | 1.852% | 15.19% | 30.63%
I | E,F & I | castleview | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 3.49 | 4.0861 | 2.6653 | 1.2968 | 0.089691 | 0.034414 | 1.4209 | 31.74% | 2.195% | 0.8422% | 34.77%
J | J Country | craddanstown | 2035 | 66% ECP | Pro-rata | IE wind not priority | 121.3332 | 374.1894 | 231.4324 | 69.2288 | 1.3126 | 72.2156 | 142.757 | 18.5% | 0.3508% | 19.3% | 38.15%
H2 | H2 & K | rosspile | 2030 | Initial | Pro-rata | IE Solar not priority | 95 | 111.227 | 92.7514 | 9.1991 | 1.4332 | 7.8433 | 18.4755 | 8.271% | 1.289% | 7.052% | 16.61%
J | J Country | fosterstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 27.93 | 35.7863 | 19.2258 | 8.067 | 0.74944 | 7.7441 | 16.5605 | 22.54% | 2.094% | 21.64% | 46.28%
H2 | H2 & K | rosspile | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 95 | 111.227 | 89.7137 | 15.4118 | 2.0676 | 4.0339 | 21.5133 | 13.86% | 1.859% | 3.627% | 19.34%
I | E,F & I | castleview | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 3.49 | 4.0861 | 2.6288 | 1.2968 | 0.089691 | 0.0709 | 1.4573 | 31.74% | 2.195% | 1.735% | 35.67%
H2 | H2 & K | tullabeg | 2030 | Initial | Pro-rata | IE Solar not priority | 50 | 58.5405 | 48.8165 | 4.8416 | 0.7543 | 4.128 | 9.724 | 8.271% | 1.289% | 7.052% | 16.61%
J | J Country | fosterstown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 27.93 | 35.7863 | 23.0553 | 6.9349 | 0.66223 | 5.1339 | 12.731 | 19.38% | 1.851% | 14.35% | 35.58%
J | J Country | craddanstown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 121.3332 | 374.1894 | 235.7123 | 69.2288 | 1.3126 | 67.9357 | 138.4772 | 18.5% | 0.3508% | 18.16% | 37.01%
J | J Country | fosterstown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 27.93 | 35.7863 | 23.5245 | 5.9315 | 0.66772 | 5.6625 | 12.2618 | 16.57% | 1.866% | 15.82% | 34.26%
H2 | H2 & K | rosspile | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 95 | 111.227 | 83.4599 | 21.7687 | 2.103 | 3.8953 | 27.767 | 19.57% | 1.891% | 3.502% | 24.96%
I | E,F & I | castleview | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 1.1633 | 1.362 | 1.11 | 0.18873 | 0.025318 | 0.037984 | 0.25203 | 13.86% | 1.859% | 2.789% | 18.5%
H2 | H2 & K | rosspile | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 95 | 111.227 | 79.6182 | 25.3174 | 2.3644 | 3.9269 | 31.6087 | 22.76% | 2.126% | 3.531% | 28.42%
J | J Country | fosterstown | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 27.93 | 35.7863 | 23.7236 | 4.8629 | 0.66273 | 6.5371 | 12.0627 | 13.59% | 1.852% | 18.27% | 33.71%
J | J Country | craddanstown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 121.3332 | 374.1894 | 218.9559 | 123.3447 | 2.4155 | 29.4734 | 155.2335 | 32.96% | 0.6455% | 7.877% | 41.49%
I | E,F & I | castleview | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 1.1633 | 1.362 | 0.98327 | 0.31003 | 0.028953 | 0.039792 | 0.37877 | 22.76% | 2.126% | 2.921% | 27.81%
H2 | H2 & K | rosspile | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 95 | 111.227 | 93.2325 | 15.4118 | 2.0676 | 0.51509 | 17.9944 | 13.86% | 1.859% | 0.4631% | 16.18%
H2 | H2 & K | rosspile | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 95 | 111.227 | 87.4692 | 18.6993 | 2.1032 | 2.9553 | 23.7577 | 16.81% | 1.891% | 2.657% | 21.36%
I | E,F & I | barnahely | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 3.3167 | 3.8832 | 2.9671 | 0.65283 | 0.073427 | 0.18982 | 0.91608 | 16.81% | 1.891% | 4.888% | 23.59%
J | J Country | curraghdoo | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 1.3333 | 1.7084 | 1.123 | 0.28316 | 0.031876 | 0.27032 | 0.58536 | 16.57% | 1.866% | 15.82% | 34.26%
H2 | H2 & K | tullabeg | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 95 | 111.2269 | 89.7136 | 15.4118 | 2.0675 | 4.0339 | 21.5133 | 13.86% | 1.859% | 3.627% | 19.34%
I | E,F & I | barnahely | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 9.95 | 11.6496 | 7.4947 | 3.697 | 0.25571 | 0.20214 | 4.1549 | 31.74% | 2.195% | 1.735% | 35.67%
H2 | H2 & K | tullabeg | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 139.9999 | 163.9133 | 120.0774 | 36.7774 | 1.4108 | 5.6476 | 43.8359 | 22.44% | 0.8607% | 3.445% | 26.74%
J | J Country | curraghdoo | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4 | 5.1251 | 2.2615 | 1.6174 | 0.11292 | 1.1334 | 2.8636 | 31.56% | 2.203% | 22.11% | 55.87%
H2 | H2 & K | tullabeg | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 185 | 216.5999 | 158.6206 | 48.7775 | 1.9548 | 7.247 | 57.9793 | 22.52% | 0.9025% | 3.346% | 26.77%
I | E,F & I | barnahely | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 3.3167 | 3.8832 | 3.1646 | 0.53806 | 0.072183 | 0.10829 | 0.71853 | 13.86% | 1.859% | 2.789% | 18.5%
J | J Country | derryiron | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 132 | 169.1299 | 62.0211 | 37.1881 | 1.5327 | 68.388 | 107.1088 | 21.99% | 0.9062% | 40.44% | 63.33%
I | E,F & I | barnahely | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 3.3167 | 3.8832 | 2.8033 | 0.88389 | 0.082546 | 0.11345 | 1.0799 | 22.76% | 2.126% | 2.921% | 27.81%
H2 | H2 & K | waterford | 2030 | Initial | Pro-rata | IE wind priority | 14.28 | 40.3942 | 36.868 | 0 | 1.1347 | 2.3915 | 3.5262 | 0% | 2.809% | 5.92% | 8.729%
J | J Country | derryiron | 2035 | 100% ECP | Pro-rata | IE wind not priority | 156 | 481.1012 | 264.4337 | 97.5781 | 1.8126 | 117.2767 | 216.6674 | 20.28% | 0.3768% | 24.38% | 45.04%
H2 | H2 & K | waterford | 2030 | Initial | Pro-rata | IE Solar not priority | 3.99 | 4.6715 | 3.8956 | 0.38636 | 0.060193 | 0.32942 | 0.77597 | 8.271% | 1.289% | 7.052% | 16.61%
J | J Country | derryiron | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 132 | 169.1299 | 79.2302 | 37.1589 | 1.445 | 51.2958 | 89.8997 | 21.97% | 0.8544% | 30.33% | 53.15%
I | E,F & I | barnahely | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 3.3167 | 3.8832 | 2.8967 | 0.75999 | 0.07342 | 0.15311 | 0.98652 | 19.57% | 1.891% | 3.943% | 25.4%
H2 | H2 & K | waterford | 2030 | 33% ECP | Pro-rata | IE wind priority | 14.28 | 40.3942 | 38.0687 | 0 | 1.2816 | 1.0438 | 2.3255 | 0% | 3.173% | 2.584% | 5.757%
J | J Country | curraghdoo | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 2.6667 | 3.4168 | 1.5832 | 0.52338 | 0.024634 | 1.2856 | 1.8336 | 15.32% | 0.721% | 37.63% | 53.67%
J | J Country | derryiron | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 137.6666 | 424.5614 | 248.4309 | 139.9489 | 2.7406 | 33.441 | 176.1305 | 32.96% | 0.6455% | 7.877% | 41.49%
H2 | H2 & K | tullabeg | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 139.9999 | 163.9133 | 134.6311 | 26.0229 | 1.203 | 2.0562 | 29.2822 | 15.88% | 0.7339% | 1.254% | 17.86%
J | J Country | curraghdoo | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 4 | 5.1251 | 2.1588 | 1.6174 | 0.11292 | 1.236 | 2.9663 | 31.56% | 2.203% | 24.12% | 57.88%
H2 | H2 & K | tullabeg | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 139.9999 | 163.9133 | 130.3346 | 26.0229 | 1.203 | 6.3527 | 33.5787 | 15.88% | 0.7339% | 3.876% | 20.49%
J | J Country | dunfirth | 2030 | Initial | Pro-rata | IE Solar not priority | 31.5 | 40.3605 | 31.9572 | 3.1911 | 0.52195 | 4.6902 | 8.4033 | 7.907% | 1.293% | 11.62% | 20.82%
I | E,F & I | barnahely | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 6.6333 | 7.7664 | 5.4036 | 1.7425 | 0.066845 | 0.55338 | 2.3628 | 22.44% | 0.8607% | 7.125% | 30.42%
H2 | H2 & K | tullabeg | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 95 | 111.2269 | 87.4692 | 18.6993 | 2.1032 | 2.9553 | 23.7577 | 16.81% | 1.891% | 2.657% | 21.36%
J | J Country | dunfirth | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 31.5 | 40.3605 | 27.9972 | 5.4845 | 0.74744 | 6.1314 | 12.3633 | 13.59% | 1.852% | 15.19% | 30.63%
J | J Country | curraghdoo | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 1.3333 | 1.7084 | 1.1006 | 0.33106 | 0.031614 | 0.24508 | 0.60776 | 19.38% | 1.851% | 14.35% | 35.58%
H2 | H2 & K | tullabeg | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 95 | 111.2269 | 83.4599 | 21.7687 | 2.103 | 3.8953 | 27.767 | 19.57% | 1.891% | 3.502% | 24.96%
I | E,F & I | barnahely | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 6.6333 | 7.7664 | 6.1022 | 1.233 | 0.057001 | 0.37413 | 1.6641 | 15.88% | 0.7339% | 4.817% | 21.43%
J | J Country | dunfirth | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 31.5 | 40.3605 | 21.6833 | 9.0981 | 0.84523 | 8.7339 | 18.6772 | 22.54% | 2.094% | 21.64% | 46.28%
H2 | H2 & K | tullabeg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 95 | 111.2269 | 79.6182 | 25.3174 | 2.3644 | 3.9269 | 31.6087 | 22.76% | 2.126% | 3.531% | 28.42%
J | J Country | curraghdoo | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 1.3333 | 1.7084 | 0.91781 | 0.3851 | 0.035777 | 0.36969 | 0.79057 | 22.54% | 2.094% | 21.64% | 46.28%
J | J Country | dunfirth | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 31.5 | 40.3605 | 17.0009 | 12.7367 | 0.88922 | 9.7336 | 23.3596 | 31.56% | 2.203% | 24.12% | 57.88%
J | J Country | dunfirth | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 31.5 | 40.3605 | 26.0022 | 7.8213 | 0.74688 | 5.7901 | 14.3583 | 19.38% | 1.851% | 14.35% | 35.58%
I | E,F & I | barnahely | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 6.6333 | 7.7664 | 5.6621 | 1.233 | 0.057001 | 0.81423 | 2.1042 | 15.88% | 0.7339% | 10.48% | 27.09%
H2 | H2 & K | tullabeg | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 185 | 216.5999 | 140.3599 | 68.7391 | 4.7544 | 2.7465 | 76.2399 | 31.74% | 2.195% | 1.268% | 35.2%
J | J Country | dunfirth | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 31.5 | 40.3605 | 26.5314 | 6.6897 | 0.75307 | 6.3863 | 13.8291 | 16.57% | 1.866% | 15.82% | 34.26%
H2 | H2 & K | tullabeg | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 185 | 216.5999 | 142.8966 | 68.7391 | 4.7544 | 0.20982 | 73.7033 | 31.74% | 2.195% | 0.09687% | 34.03%
J | J Country | curraghdoo | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 1.3333 | 1.7084 | 1.1851 | 0.23215 | 0.031638 | 0.25953 | 0.52331 | 13.59% | 1.852% | 15.19% | 30.63%
J | J Country | dunfirth | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 31.5 | 40.3605 | 26.7559 | 5.4845 | 0.74744 | 7.3727 | 13.6046 | 13.59% | 1.852% | 18.27% | 33.71%
I | E,F & I | barnahely | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 9.95 | 11.6496 | 7.5987 | 3.697 | 0.25571 | 0.098114 | 4.0509 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | tullabeg | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 95 | 111.2269 | 93.2325 | 15.4118 | 2.0675 | 0.51509 | 17.9944 | 13.86% | 1.859% | 0.4631% | 16.18%
H2 | H2 & K | kellis | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 421.6663 | 493.6912 | 392.5554 | 78.3786 | 3.6234 | 19.1338 | 101.1358 | 15.88% | 0.7339% | 3.876% | 20.49%
J | J Country | clonfad | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 100 | 128.1287 | 88.8801 | 17.411 | 2.3728 | 19.4648 | 39.2486 | 13.59% | 1.852% | 15.19% | 30.63%
I | E,F & I | kilbarry | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 79.8 | 93.4306 | 60.108 | 29.6507 | 2.0508 | 1.6211 | 33.3226 | 31.74% | 2.195% | 1.735% | 35.67%
H2 | H2 & K | crane | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 10.3 | 12.0593 | 7.9559 | 3.8271 | 0.2647 | 0.011682 | 4.1035 | 31.74% | 2.195% | 0.09687% | 34.03%
I | E,F & I | raffeen | 2030 | Initial | Pro-rata | IE Solar not priority | 55 | 64.3945 | 48.4973 | 5.3258 | 0.82973 | 9.7417 | 15.8972 | 8.271% | 1.289% | 15.13% | 24.69%
J | J Country | newbridge | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 12 | 15.3754 | 9.9056 | 2.9796 | 0.28453 | 2.2058 | 5.4698 | 19.38% | 1.851% | 14.35% | 35.58%
J | J Country | bracklone | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 106.9999 | 137.0976 | 88.3249 | 26.5677 | 2.537 | 19.6679 | 48.7727 | 19.38% | 1.851% | 14.35% | 35.58%
J | J Country | newbridge | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 12 | 15.3754 | 10.1072 | 2.5485 | 0.28688 | 2.4329 | 5.2682 | 16.57% | 1.866% | 15.82% | 34.26%
H2 | H2 & K | crane | 2035 | 66% ECP | Pro-rata | IE wind priority | 2.5 | 7.0718 | 6.7269 | 0 | 0.061594 | 0.28335 | 0.34494 | 0% | 0.871% | 4.007% | 4.878%
J | J Country | bracklone | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 40.8 | 125.8263 | 74.1373 | 43.6693 | 2.3296 | 5.6901 | 51.689 | 34.71% | 1.851% | 4.522% | 41.08%
J | J Country | newbridge | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 12 | 15.3754 | 10.1927 | 2.0893 | 0.28474 | 2.8086 | 5.1827 | 13.59% | 1.852% | 18.27% | 33.71%
H2 | H2 & K | crane | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 9.8667 | 11.552 | 9.1855 | 1.834 | 0.084786 | 0.44772 | 2.3665 | 15.88% | 0.7339% | 3.876% | 20.49%
I | E,F & I | midleton | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 32.55 | 38.1099 | 25.8629 | 8.5822 | 0.34394 | 3.3208 | 12.247 | 22.52% | 0.9025% | 8.714% | 32.14%
J | J Country | newbridge | 2030 | Initial | Pro-rata | IE Solar not priority | 12 | 15.3754 | 12.1742 | 1.2157 | 0.19884 | 1.7867 | 3.2013 | 7.907% | 1.293% | 11.62% | 20.82%
H2 | H2 & K | crane | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 2.5 | 7.0718 | 6.8241 | 0 | 0.061594 | 0.18613 | 0.24772 | 0% | 0.871% | 2.632% | 3.503%
J | J Country | bracklone | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 106.9999 | 137.0976 | 73.6543 | 30.9046 | 2.8711 | 29.6675 | 63.4433 | 22.54% | 2.094% | 21.64% | 46.28%
I | E,F & I | midleton | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 26.55 | 31.085 | 21.6279 | 6.9746 | 0.26755 | 2.2149 | 9.4571 | 22.44% | 0.8607% | 7.125% | 30.42%
H2 | H2 & K | crane | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 9.8667 | 11.552 | 9.4883 | 1.834 | 0.084786 | 0.14491 | 2.0637 | 15.88% | 0.7339% | 1.254% | 17.86%
J | J Country | newbridge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 12 | 15.3754 | 8.2603 | 3.4659 | 0.32199 | 3.3272 | 7.1151 | 22.54% | 2.094% | 21.64% | 46.28%
H2 | H2 & K | crane | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 2.5 | 7.0718 | 6.7696 | 0 | 0.27227 | 0.029906 | 0.30217 | 0% | 3.85% | 0.4229% | 4.273%
I | E,F & I | raffeen | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 55 | 64.3945 | 50.7255 | 8.9226 | 1.197 | 3.5494 | 13.6691 | 13.86% | 1.859% | 5.512% | 21.23%
J | J Country | bracklone | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 40.8 | 125.8263 | 78.3616 | 40.9049 | 2.3608 | 4.199 | 47.4647 | 32.51% | 1.876% | 3.337% | 37.72%
J | J Country | bracklone | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 106.9999 | 137.0976 | 90.8852 | 18.6297 | 2.5389 | 25.0438 | 46.2124 | 13.59% | 1.852% | 18.27% | 33.71%
J | J Country | newbridge | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 12 | 15.3754 | 7.5741 | 2.3552 | 0.11085 | 5.3353 | 7.8014 | 15.32% | 0.721% | 34.7% | 50.74%
I | E,F & I | raffeen | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 55 | 64.3945 | 52.4791 | 8.9226 | 1.197 | 1.7958 | 11.9154 | 13.86% | 1.859% | 2.789% | 18.5%
H2 | H2 & K | crane | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 9.4333 | 11.0446 | 8.2874 | 2.1616 | 0.20882 | 0.3868 | 2.7572 | 19.57% | 1.891% | 3.502% | 24.96%
J | J Country | newbridge | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 12 | 15.3754 | 7.1242 | 2.3552 | 0.11085 | 5.7852 | 8.2512 | 15.32% | 0.721% | 37.63% | 53.67%
H2 | H2 & K | crane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 2.5 | 7.0718 | 6.4229 | 0 | 0.29405 | 0.35483 | 0.64888 | 0% | 4.158% | 5.018% | 9.176%
I | E,F & I | raffeen | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 55 | 64.3945 | 46.487 | 14.6574 | 1.3688 | 1.8813 | 17.9076 | 22.76% | 2.126% | 2.921% | 27.81%
J | J Country | bracklone | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 40.8 | 125.8263 | 84.33 | 32.1087 | 2.389 | 6.9986 | 41.4963 | 25.52% | 1.899% | 5.562% | 32.98%
H2 | H2 & K | crane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 9.4333 | 11.0446 | 7.906 | 2.514 | 0.23478 | 0.38994 | 3.1387 | 22.76% | 2.126% | 3.531% | 28.42%
H2 | H2 & K | crane | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 2.5 | 7.0718 | 6.559 | 0 | 0.13005 | 0.38275 | 0.51279 | 0% | 1.839% | 5.412% | 7.251%
I | E,F & I | raffeen | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 55 | 64.3945 | 48.0351 | 12.6029 | 1.2175 | 2.539 | 16.3594 | 19.57% | 1.891% | 3.943% | 25.4%
J | J Country | newbridge | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 12 | 15.3754 | 6.7845 | 4.8521 | 0.33875 | 3.4001 | 8.5909 | 31.56% | 2.203% | 22.11% | 55.87%
H2 | H2 & K | crane | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 9.4333 | 11.0446 | 9.2578 | 1.5304 | 0.2053 | 0.051148 | 1.7868 | 13.86% | 1.859% | 0.4631% | 16.18%
J | J Country | bracklone | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 106.9999 | 137.0976 | 90.1225 | 22.7238 | 2.558 | 21.6932 | 46.975 | 16.57% | 1.866% | 15.82% | 34.26%
J | J Country | newbridge | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 12 | 15.3754 | 6.4765 | 4.8521 | 0.33875 | 3.7081 | 8.8989 | 31.56% | 2.203% | 24.12% | 57.88%
H2 | H2 & K | crane | 2030 | 100% ECP | Pro-rata | IE wind priority | 2.5 | 7.0718 | 6.6856 | 0 | 0.27227 | 0.11396 | 0.38623 | 0% | 3.85% | 1.611% | 5.461%
I | E,F & I | raffeen | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 55 | 64.3945 | 49.2033 | 10.8259 | 1.2176 | 3.1478 | 15.1913 | 16.81% | 1.891% | 4.888% | 23.59%
H2 | H2 & K | crane | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 10.3 | 12.0593 | 7.8146 | 3.8271 | 0.2647 | 0.15291 | 4.2447 | 31.74% | 2.195% | 1.268% | 35.2%
J | J Country | newbridge | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 12 | 15.3754 | 10.6656 | 2.0893 | 0.28474 | 2.3358 | 4.7098 | 13.59% | 1.852% | 15.19% | 30.63%
H2 | H2 & K | crane | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 2.5 | 7.0718 | 6.8131 | 0 | 0.22438 | 0.034364 | 0.25874 | 0% | 3.173% | 0.4859% | 3.659%
H2 | H2 & K | crane | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 2.5 | 7.0718 | 6.503 | 0 | 0.29 | 0.27886 | 0.56886 | 0% | 4.101% | 3.943% | 8.044%
J | J Country | mulgeeth | 2035 | 100% ECP | Pro-rata | IE wind not priority | 60 | 185.0389 | 101.7053 | 37.53 | 0.69714 | 45.1064 | 83.3336 | 20.28% | 0.3768% | 24.38% | 45.04%
H2 | H2 & K | crane | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 9.8667 | 11.552 | 8.4626 | 2.5919 | 0.099428 | 0.39802 | 3.0894 | 22.44% | 0.8607% | 3.445% | 26.74%
H2 | H2 & K | crory | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 44.012 | 124.4979 | 118.2602 | 0 | 4.5023 | 1.7353 | 6.2377 | 0% | 3.616% | 1.394% | 5.01%
J | J Country | bracklone | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 122.4 | 377.4794 | 214.5256 | 113.129 | 6.941 | 42.8838 | 162.9538 | 29.97% | 1.839% | 11.36% | 43.17%
H2 | H2 & K | crory | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 20 | 23.4162 | 18.4146 | 3.9367 | 0.44278 | 0.62216 | 5.0016 | 16.81% | 1.891% | 2.657% | 21.36%
J | J Country | mulgeeth | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 60 | 185.0389 | 109.0256 | 64.2196 | 3.4259 | 8.3678 | 76.0133 | 34.71% | 1.851% | 4.522% | 41.08%
I | E,F & I | midleton | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 20.55 | 24.0601 | 17.3692 | 5.4765 | 0.51145 | 0.70291 | 6.6909 | 22.76% | 2.126% | 2.921% | 27.81%
H2 | H2 & K | crory | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 44.012 | 124.4979 | 114.4832 | 0 | 5.1054 | 4.9092 | 10.0147 | 0% | 4.101% | 3.943% | 8.044%
J | J Country | mulgeeth | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 60 | 185.0389 | 115.2377 | 60.1544 | 3.4718 | 6.175 | 69.8012 | 32.51% | 1.876% | 3.337% | 37.72%
J | J Country | bracklone | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 321 | 411.2931 | 181.4854 | 129.7934 | 9.0616 | 90.9528 | 229.8078 | 31.56% | 2.203% | 22.11% | 55.87%
H2 | H2 & K | crory | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 20 | 23.4162 | 17.5705 | 4.5829 | 0.44274 | 0.82007 | 5.8457 | 19.57% | 1.891% | 3.502% | 24.96%
I | E,F & I | midleton | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 20.55 | 24.0601 | 17.9477 | 4.7089 | 0.45491 | 0.94865 | 6.1125 | 19.57% | 1.891% | 3.943% | 25.4%
J | J Country | mulgeeth | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 60 | 185.0389 | 124.0148 | 47.2187 | 3.5133 | 10.2921 | 61.0241 | 25.52% | 1.899% | 5.562% | 32.98%
H2 | H2 & K | crory | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 44.012 | 124.4979 | 113.0744 | 0 | 5.1767 | 6.2468 | 11.4234 | 0% | 4.158% | 5.018% | 9.176%
I | E,F & I | midleton | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 20.55 | 24.0601 | 18.3841 | 4.0449 | 0.45495 | 1.1761 | 5.676 | 16.81% | 1.891% | 4.888% | 23.59%
H2 | H2 & K | crory | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 20 | 23.4162 | 16.7617 | 5.33 | 0.49776 | 0.82672 | 6.6545 | 22.76% | 2.126% | 3.531% | 28.42%
J | J Country | mulgeeth | 2030 | 33% ECP | Pro-rata | IE wind not priority | 60 | 185.0389 | 128.4843 | 34.5394 | 3.4785 | 18.5366 | 56.5546 | 18.67% | 1.88% | 10.02% | 30.56%
H2 | H2 & K | crory | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 44.012 | 124.4979 | 119.9428 | 0 | 3.9501 | 0.60498 | 4.5551 | 0% | 3.173% | 0.4859% | 3.659%
J | J Country | mulgeeth | 2030 | Initial | Pro-rata | IE wind not priority | 60 | 185.0389 | 134.3038 | 25.4774 | 3.598 | 21.6597 | 50.7351 | 13.77% | 1.944% | 11.71% | 27.42%
I | E,F & I | midleton | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 20.55 | 24.0601 | 18.9529 | 3.3338 | 0.44724 | 1.3262 | 5.1073 | 13.86% | 1.859% | 5.512% | 21.23%
J | J Country | mulgeeth | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 60 | 185.0389 | 133.5726 | 34.5394 | 3.4785 | 13.4484 | 51.4664 | 18.67% | 1.88% | 7.268% | 27.81%
I | E,F & I | midleton | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 20.55 | 24.0601 | 19.6081 | 3.3338 | 0.44724 | 0.67097 | 4.452 | 13.86% | 1.859% | 2.789% | 18.5%
H2 | H2 & K | crory | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 20 | 23.4162 | 18.8871 | 3.2446 | 0.43527 | 0.84924 | 4.5291 | 13.86% | 1.859% | 3.627% | 19.34%
J | J Country | mulgeeth | 2030 | 100% ECP | Pro-rata | IE wind not priority | 60 | 185.0389 | 100.2515 | 55.4554 | 3.4025 | 25.9295 | 84.7874 | 29.97% | 1.839% | 14.01% | 45.82%
J | J Country | bracklone | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 40.8 | 125.8263 | 90.8292 | 23.4868 | 2.3654 | 9.1449 | 34.9971 | 18.67% | 1.88% | 7.268% | 27.81%
J | J Country | mulgeeth | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 60 | 185.0389 | 108.275 | 60.9947 | 1.1945 | 14.5748 | 76.7639 | 32.96% | 0.6455% | 7.877% | 41.49%
H2 | H2 & K | crane | 2035 | 100% ECP | Pro-rata | IE wind priority | 2.5 | 7.0718 | 6.6237 | 0 | 0.067502 | 0.38059 | 0.44809 | 0% | 0.9545% | 5.382% | 6.336%
I | E,F & I | midleton | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 26.55 | 31.085 | 22.6628 | 4.9351 | 0.22815 | 3.259 | 8.4222 | 15.88% | 0.7339% | 10.48% | 27.09%
H2 | H2 & K | crane | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 10.3 | 12.0593 | 8.8313 | 2.7157 | 0.10884 | 0.40348 | 3.228 | 22.52% | 0.9025% | 3.346% | 26.77%
J | J Country | mulgeeth | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 60 | 185.0389 | 116.5611 | 34.2341 | 0.6491 | 33.5946 | 68.4778 | 18.5% | 0.3508% | 18.16% | 37.01%
J | J Country | bracklone | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 106.9999 | 137.0976 | 95.1016 | 18.6297 | 2.5389 | 20.8274 | 41.996 | 13.59% | 1.852% | 15.19% | 30.63%
I | E,F & I | midleton | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 26.55 | 31.085 | 24.4243 | 4.9351 | 0.22815 | 1.4975 | 6.6607 | 15.88% | 0.7339% | 4.817% | 21.43%
J | J Country | mulgeeth | 2035 | 66% ECP | Pro-rata | IE wind not priority | 60 | 185.0389 | 114.4447 | 34.2341 | 0.6491 | 35.711 | 70.5942 | 18.5% | 0.3508% | 19.3% | 38.15%
J | J Country | bracklone | 2030 | 100% ECP | Pro-rata | IE wind not priority | 122.4 | 377.4794 | 204.5131 | 113.129 | 6.941 | 52.8963 | 172.9663 | 29.97% | 1.839% | 14.01% | 45.82%
H2 | H2 & K | crory | 2030 | Initial | Pro-rata | IE wind priority | 44.012 | 124.4979 | 113.6299 | 0 | 3.4973 | 7.3707 | 10.868 | 0% | 2.809% | 5.92% | 8.729%
I | E,F & I | midleton | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 32.55 | 38.1099 | 24.858 | 12.0944 | 0.83652 | 0.32097 | 13.2518 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | crory | 2030 | Initial | Pro-rata | IE Solar not priority | 20 | 23.4162 | 19.5266 | 1.9366 | 0.30172 | 1.6512 | 3.8896 | 8.271% | 1.289% | 7.052% | 16.61%
J | J Country | mulgeeth | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 60 | 185.0389 | 105.1596 | 55.4554 | 3.4025 | 21.0215 | 79.8793 | 29.97% | 1.839% | 11.36% | 43.17%
I | E,F & I | midleton | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 32.55 | 38.1099 | 24.5177 | 12.0944 | 0.83652 | 0.66126 | 13.5921 | 31.74% | 2.195% | 1.735% | 35.67%
H2 | H2 & K | crory | 2030 | 33% ECP | Pro-rata | IE wind priority | 44.012 | 124.4979 | 117.3306 | 0 | 3.9501 | 3.2172 | 7.1673 | 0% | 3.173% | 2.584% | 5.757%
J | J Country | bracklone | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 321 | 411.2931 | 173.2477 | 129.7934 | 9.0616 | 99.1905 | 238.0454 | 31.56% | 2.203% | 24.12% | 57.88%
H2 | H2 & K | crory | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 20 | 23.4162 | 19.6279 | 3.2446 | 0.43527 | 0.10844 | 3.7883 | 13.86% | 1.859% | 0.4631% | 16.18%
J | J Country | newbridge | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 12 | 15.3754 | 7.2027 | 3.3781 | 0.13136 | 4.6633 | 8.1727 | 21.97% | 0.8544% | 30.33% | 53.15%
I | E,F & I | raffeen | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 55 | 64.3945 | 41.4278 | 20.4359 | 1.4135 | 1.1173 | 22.9667 | 31.74% | 2.195% | 1.735% | 35.67%
J | J Country | blundelstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 60 | 76.8772 | 41.3015 | 17.3297 | 1.61 | 16.636 | 35.5757 | 22.54% | 2.094% | 21.64% | 46.28%
H2 | H2 & K | castledockrell | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 41.4 | 117.1092 | 106.3637 | 0 | 4.8694 | 5.876 | 10.7455 | 0% | 4.158% | 5.018% | 9.176%
I | E,F & I | rathcoursey | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 110 | 128.7891 | 82.8556 | 40.8719 | 2.8269 | 2.2347 | 45.9335 | 31.74% | 2.195% | 1.735% | 35.67%
H2 | H2 & K | castledockrell | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 12.8333 | 36.3019 | 29.5452 | 5.9301 | 0.65022 | 0.1764 | 6.7568 | 16.34% | 1.791% | 0.4859% | 18.61%
J | J Country | philipstown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 50 | 64.0644 | 28.2687 | 20.217 | 1.4115 | 14.1671 | 35.7956 | 31.56% | 2.203% | 22.11% | 55.87%
J | J Country | blundelstown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 60 | 76.8772 | 53.328 | 10.4466 | 1.4237 | 11.6789 | 23.5492 | 13.59% | 1.852% | 15.19% | 30.63%
H2 | H2 & K | castledockrell | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 41.4 | 117.1092 | 112.8245 | 0 | 3.7157 | 0.56907 | 4.2847 | 0% | 3.173% | 0.4859% | 3.659%
I | E,F & I | rathcoursey | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 36.6666 | 42.9297 | 34.9861 | 5.9484 | 0.798 | 1.1972 | 7.9436 | 13.86% | 1.859% | 2.789% | 18.5%
J | J Country | philipstown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 50 | 154.1991 | 87.633 | 46.2128 | 2.8354 | 17.5179 | 66.5661 | 29.97% | 1.839% | 11.36% | 43.17%
H2 | H2 & K | castledockrell | 2030 | 100% ECP | Pro-rata | IE wind not priority | 38.5 | 108.9059 | 75.2151 | 29.9456 | 1.9903 | 1.755 | 33.6908 | 27.5% | 1.828% | 1.611% | 30.94%
J | J Country | blundelstown | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 60 | 76.8772 | 32.3827 | 24.2604 | 1.6938 | 18.5403 | 44.4945 | 31.56% | 2.203% | 24.12% | 57.88%
H2 | H2 & K | castledockrell | 2030 | 100% ECP | Pro-rata | IE wind priority | 41.4 | 117.1092 | 110.7133 | 0 | 4.5087 | 1.8872 | 6.3959 | 0% | 3.85% | 1.611% | 5.461%
J | J Country | philipstown | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 50 | 64.0644 | 26.9856 | 20.217 | 1.4115 | 15.4502 | 37.0787 | 31.56% | 2.203% | 24.12% | 57.88%
I | E,F & I | rathcoursey | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 36.6666 | 42.9297 | 30.9913 | 9.7716 | 0.91257 | 1.2542 | 11.9384 | 22.76% | 2.126% | 2.921% | 27.81%
H2 | H2 & K | castledockrell | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 38.5 | 108.9059 | 76.5095 | 29.9456 | 1.9903 | 0.46055 | 32.3964 | 27.5% | 1.828% | 0.4229% | 29.75%
J | J Country | philipstown | 2030 | 100% ECP | Pro-rata | IE wind not priority | 50 | 154.1991 | 83.5429 | 46.2128 | 2.8354 | 21.6079 | 70.6562 | 29.97% | 1.839% | 14.01% | 45.82%
H2 | H2 & K | castledockrell | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 41.4 | 117.1092 | 112.1053 | 0 | 4.5087 | 0.49524 | 5.004 | 0% | 3.85% | 0.4229% | 4.273%
I | E,F & I | rathcoursey | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 36.6666 | 42.9297 | 32.0234 | 8.402 | 0.81168 | 1.6926 | 10.9063 | 19.57% | 1.891% | 3.943% | 25.4%
I | E,F & I | rathcoursey | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 110 | 128.7891 | 84.0056 | 40.8719 | 2.8269 | 1.0847 | 44.7835 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | castledockrell | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 12.8333 | 36.3019 | 22.0119 | 11.77 | 0.69854 | 1.8215 | 14.29 | 32.42% | 1.924% | 5.018% | 39.36%
H2 | H2 & K | castledockrell | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 41.4 | 117.1092 | 107.6889 | 0 | 4.8024 | 4.6179 | 9.4203 | 0% | 4.101% | 3.943% | 8.044%
J | J Country | philipstown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 33.3333 | 42.7095 | 20.0076 | 9.3836 | 0.3649 | 12.9535 | 22.7019 | 21.97% | 0.8544% | 30.33% | 53.15%
I | E,F & I | rathcoursey | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 73.3333 | 85.8593 | 59.7381 | 19.2644 | 0.73899 | 6.1178 | 26.1212 | 22.44% | 0.8607% | 7.125% | 30.42%
H2 | H2 & K | castledockrell | 2030 | Initial | Pro-rata | IE wind priority | 41.4 | 117.1092 | 106.8862 | 0 | 3.2898 | 6.9332 | 10.223 | 0% | 2.809% | 5.92% | 8.729%
J | J Country | philipstown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 50 | 154.1991 | 90.2292 | 50.8289 | 0.99539 | 12.1456 | 63.9699 | 32.96% | 0.6455% | 7.877% | 41.49%
J | J Country | blundelstown | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 60 | 76.8772 | 50.9637 | 10.4466 | 1.4237 | 14.0432 | 25.9135 | 13.59% | 1.852% | 18.27% | 33.71%
H2 | H2 & K | castledockrell | 2030 | 33% ECP | Pro-rata | IE wind not priority | 12.8333 | 36.3019 | 28.7835 | 5.9301 | 0.65022 | 0.9381 | 7.5185 | 16.34% | 1.791% | 2.584% | 20.71%
J | J Country | philipstown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 33.3333 | 42.7095 | 21.039 | 6.5423 | 0.30793 | 14.8203 | 21.6705 | 15.32% | 0.721% | 34.7% | 50.74%
I | E,F & I | rathcoursey | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 73.3333 | 85.8593 | 67.462 | 13.6311 | 0.63016 | 4.1361 | 18.3974 | 15.88% | 0.7339% | 4.817% | 21.43%
J | J Country | blundelstown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 60 | 76.8772 | 33.9225 | 24.2604 | 1.6938 | 17.0005 | 42.9547 | 31.56% | 2.203% | 22.11% | 55.87%
H2 | H2 & K | castledockrell | 2030 | 33% ECP | Pro-rata | IE wind priority | 41.4 | 117.1092 | 110.3673 | 0 | 3.7157 | 3.0263 | 6.7419 | 0% | 3.173% | 2.584% | 5.757%
J | J Country | philipstown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 50 | 154.1991 | 97.1343 | 28.5284 | 0.54092 | 27.9955 | 57.0648 | 18.5% | 0.3508% | 18.16% | 37.01%
H2 | H2 & K | castledockrell | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 12.8333 | 36.3019 | 26.8043 | 8.3211 | 0.67056 | 0.506 | 9.4976 | 22.92% | 1.847% | 1.394% | 26.16%
I | E,F & I | rathcoursey | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 73.3333 | 85.8593 | 62.5966 | 13.6311 | 0.63016 | 9.0015 | 23.2627 | 15.88% | 0.7339% | 10.48% | 27.09%
H2 | H2 & K | castledockrell | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 41.4 | 117.1092 | 111.2418 | 0 | 4.2351 | 1.6324 | 5.8675 | 0% | 3.616% | 1.394% | 5.01%
J | J Country | philipstown | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 33.3333 | 42.7095 | 19.7895 | 6.5423 | 0.30793 | 16.0699 | 22.9201 | 15.32% | 0.721% | 37.63% | 53.67%
J | J Country | blundelstown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 60 | 76.8772 | 49.528 | 14.8978 | 1.4226 | 11.0288 | 27.3492 | 19.38% | 1.851% | 14.35% | 35.58%
H2 | H2 & K | castledockrell | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 12.8333 | 36.3019 | 23.1899 | 10.9884 | 0.69227 | 1.4315 | 13.1121 | 30.27% | 1.907% | 3.943% | 36.12%
J | J Country | philipstown | 2035 | 66% ECP | Pro-rata | IE wind not priority | 50 | 154.1991 | 95.3706 | 28.5284 | 0.54092 | 29.7592 | 58.8285 | 18.5% | 0.3508% | 19.3% | 38.15%
J | J Country | blundelstown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 60 | 76.8772 | 50.536 | 12.7423 | 1.4344 | 12.1644 | 26.3412 | 16.57% | 1.866% | 15.82% | 34.26%
H2 | H2 & K | crane | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 9.4333 | 11.0446 | 8.6855 | 1.8568 | 0.20884 | 0.29345 | 2.3591 | 16.81% | 1.891% | 2.657% | 21.36%
J | J Country | philipstown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 14.8133 | 2.9018 | 0.39547 | 3.2441 | 6.5414 | 13.59% | 1.852% | 15.19% | 30.63%
I | E,F & I | rathcoursey | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 36.6666 | 42.9297 | 32.8021 | 7.2173 | 0.81176 | 2.0985 | 10.1275 | 16.81% | 1.891% | 4.888% | 23.59%
I | E,F & I | raffeen | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 55 | 64.3945 | 50.5965 | 10.2233 | 0.47262 | 3.1021 | 13.798 | 15.88% | 0.7339% | 4.817% | 21.43%
J | J Country | philipstown | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 14.1566 | 2.9018 | 0.39547 | 3.9009 | 7.1982 | 13.59% | 1.852% | 18.27% | 33.71%
J | J Country | blundelstown | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 60 | 76.8772 | 28.1914 | 16.9037 | 0.6967 | 31.0855 | 48.6858 | 21.99% | 0.9062% | 40.44% | 63.33%
I | E,F & I | raffeen | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 55 | 64.3945 | 46.9475 | 10.2233 | 0.47262 | 6.7512 | 17.4471 | 15.88% | 0.7339% | 10.48% | 27.09%
J | J Country | philipstown | 2030 | 33% ECP | Pro-rata | IE wind not priority | 50 | 154.1991 | 107.0703 | 28.7828 | 2.8988 | 15.4472 | 47.1288 | 18.67% | 1.88% | 10.02% | 30.56%
H2 | H2 & K | crane | 2030 | Initial | Pro-rata | IE wind priority | 2.5 | 7.0718 | 6.4545 | 0 | 0.19866 | 0.41867 | 0.61733 | 0% | 2.809% | 5.92% | 8.729%
H2 | H2 & K | crane | 2030 | Initial | Pro-rata | IE Solar not priority | 9 | 10.5373 | 8.787 | 0.87149 | 0.13577 | 0.74305 | 1.7503 | 8.271% | 1.289% | 7.052% | 16.61%
J | J Country | philipstown | 2030 | Initial | Pro-rata | IE wind not priority | 50 | 154.1991 | 111.9199 | 21.2312 | 2.9983 | 18.0497 | 42.2792 | 13.77% | 1.944% | 11.71% | 27.42%
H2 | H2 & K | crane | 2030 | 33% ECP | Pro-rata | IE wind priority | 2.5 | 7.0718 | 6.6647 | 0 | 0.22438 | 0.18275 | 0.40712 | 0% | 3.173% | 2.584% | 5.757%
H2 | H2 & K | crane | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 9.4333 | 11.0446 | 8.9084 | 1.5304 | 0.2053 | 0.40056 | 2.1362 | 13.86% | 1.859% | 3.627% | 19.34%
I | E,F & I | raffeen | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 55 | 64.3945 | 42.0028 | 20.4359 | 1.4135 | 0.54234 | 22.3917 | 31.74% | 2.195% | 0.8422% | 34.77%
J | J Country | newbridge | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 12 | 15.3754 | 5.6383 | 3.3807 | 0.13934 | 6.2171 | 9.7372 | 21.99% | 0.9062% | 40.44% | 63.33%
H2 | H2 & K | crane | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 2.5 | 7.0718 | 6.7175 | 0 | 0.25574 | 0.098572 | 0.35432 | 0% | 3.616% | 1.394% | 5.01%
J | J Country | bracklone | 2030 | 33% ECP | Pro-rata | IE wind not priority | 40.8 | 125.8263 | 87.3693 | 23.4868 | 2.3654 | 12.6049 | 38.4571 | 18.67% | 1.88% | 10.02% | 30.56%
J | J Country | philipstown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 50 | 154.1991 | 103.3457 | 39.3489 | 2.9277 | 8.5767 | 50.8534 | 25.52% | 1.899% | 5.562% | 32.98%
H2 | H2 & K | castledockrell | 2035 | 100% ECP | Pro-rata | IE wind priority | 41.4 | 117.1092 | 109.6889 | 0 | 1.1178 | 6.3025 | 7.4203 | 0% | 0.9545% | 5.382% | 6.336%
J | J Country | blundelstown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 60 | 76.8772 | 36.0137 | 16.8904 | 0.65682 | 23.3163 | 40.8635 | 21.97% | 0.8544% | 30.33% | 53.15%
I | E,F & I | raffeen | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 55 | 64.3945 | 44.8037 | 14.4483 | 0.55424 | 4.5884 | 19.5909 | 22.44% | 0.8607% | 7.125% | 30.42%
J | J Country | philipstown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 50 | 154.1991 | 111.3105 | 28.7828 | 2.8988 | 11.207 | 42.8886 | 18.67% | 1.88% | 7.268% | 27.81%
H2 | H2 & K | castledockrell | 2035 | 66% ECP | Pro-rata | IE wind not priority | 25.6666 | 72.6039 | 57.6737 | 11.7826 | 0.23863 | 2.909 | 14.9302 | 16.23% | 0.3287% | 4.007% | 20.56%
J | J Country | philipstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 11.4726 | 4.8138 | 0.44721 | 4.6211 | 9.8821 | 22.54% | 2.094% | 21.64% | 46.28%
I | E,F & I | rathcoursey | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 36.6666 | 42.9297 | 33.817 | 5.9484 | 0.798 | 2.3663 | 9.1127 | 13.86% | 1.859% | 5.512% | 21.23%
H2 | H2 & K | castledockrell | 2035 | 66% ECP | Pro-rata | IE wind priority | 41.4 | 117.1092 | 111.397 | 0 | 1.02 | 4.6922 | 5.7122 | 0% | 0.871% | 4.007% | 4.878%
J | J Country | philipstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 50 | 154.1991 | 90.8547 | 53.5163 | 2.8549 | 6.9732 | 63.3444 | 34.71% | 1.851% | 4.522% | 41.08%
H2 | H2 & K | castledockrell | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 25.6666 | 72.6039 | 58.6718 | 11.7826 | 0.23863 | 1.9109 | 13.9321 | 16.23% | 0.3287% | 2.632% | 19.19%
J | J Country | blundelstown | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 60 | 76.8772 | 35.621 | 11.7761 | 0.55427 | 28.9258 | 41.2562 | 15.32% | 0.721% | 37.63% | 53.67%
H2 | H2 & K | castledockrell | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 41.4 | 117.1092 | 113.007 | 0 | 1.02 | 3.0823 | 4.1023 | 0% | 0.871% | 2.632% | 3.503%
J | J Country | philipstown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 13.7578 | 4.1383 | 0.39517 | 3.0635 | 7.597 | 19.38% | 1.851% | 14.35% | 35.58%
H2 | H2 & K | castledockrell | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 25.6666 | 72.6039 | 45.6787 | 22.5069 | 0.48878 | 3.9295 | 26.9252 | 31% | 0.6732% | 5.412% | 37.09%
I | E,F & I | raffeen | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 55 | 64.3945 | 43.7008 | 14.5014 | 0.58116 | 5.6112 | 20.6938 | 22.52% | 0.9025% | 8.714% | 32.14%
J | J Country | philipstown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 50 | 154.1991 | 96.0315 | 50.1287 | 2.8931 | 5.1458 | 58.1676 | 32.51% | 1.876% | 3.337% | 37.72%
J | J Country | blundelstown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 60 | 76.8772 | 37.8703 | 11.7761 | 0.55427 | 26.6765 | 39.0069 | 15.32% | 0.721% | 34.7% | 50.74%
H2 | H2 & K | castledockrell | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 41.4 | 117.1092 | 108.6174 | 0 | 2.1536 | 6.3383 | 8.4919 | 0% | 1.839% | 5.412% | 7.251%
J | J Country | philipstown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 14.0378 | 3.5395 | 0.39845 | 3.379 | 7.317 | 16.57% | 1.866% | 15.82% | 34.26%
H2 | H2 & K | castledockrell | 2035 | 100% ECP | Pro-rata | IE wind not priority | 38.5 | 108.9059 | 83.06 | 19.595 | 0.38995 | 5.861 | 25.846 | 17.99% | 0.3581% | 5.382% | 23.73%
H2 | H2 & K | crory | 2030 | 100% ECP | Pro-rata | IE wind priority | 44.012 | 124.4979 | 117.6984 | 0 | 4.7932 | 2.0063 | 6.7994 | 0% | 3.85% | 1.611% | 5.461%
H2 | H2 & K | great island | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 125.3232 | 146.7297 | 115.3887 | 24.6679 | 2.7745 | 3.8986 | 31.341 | 16.81% | 1.891% | 2.657% | 21.36%
J | J Country | bracklyn | 2035 | 66% ECP | Pro-rata | IE wind not priority | 43.2 | 133.2279 | 82.4001 | 24.6485 | 0.46735 | 25.7119 | 50.8278 | 18.5% | 0.3508% | 19.3% | 38.15%
I | E,F & I | knockraha | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 201 | 235.3328 | 151.3998 | 74.6841 | 5.1656 | 4.0833 | 83.933 | 31.74% | 2.195% | 1.735% | 35.67%
H2 | H2 & K | great island | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 125.3232 | 146.7297 | 110.0996 | 28.7171 | 2.7743 | 5.1387 | 36.63 | 19.57% | 1.891% | 3.502% | 24.96%
J | J Country | monread | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 8 | 10.2503 | 4.523 | 3.2347 | 0.22583 | 2.2667 | 5.7273 | 31.56% | 2.203% | 22.11% | 55.87%
H2 | H2 & K | great island | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 125.3232 | 146.7297 | 105.0317 | 33.3985 | 3.1191 | 5.1804 | 41.6979 | 22.76% | 2.126% | 3.531% | 28.42%
J | J Country | monread | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 8 | 10.2503 | 4.3177 | 3.2347 | 0.22583 | 2.472 | 5.9326 | 31.56% | 2.203% | 24.12% | 57.88%
I | E,F & I | knockraha | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 66.9999 | 78.4442 | 63.9291 | 10.8694 | 1.4582 | 2.1876 | 14.5151 | 13.86% | 1.859% | 2.789% | 18.5%
H2 | H2 & K | great island | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 125.3232 | 146.7297 | 122.9916 | 20.3311 | 2.7275 | 0.6795 | 23.7381 | 13.86% | 1.859% | 0.4631% | 16.18%
J | J Country | bracklyn | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 43.2 | 133.2279 | 83.9239 | 24.6485 | 0.46735 | 24.1881 | 49.304 | 18.5% | 0.3508% | 18.16% | 37.01%
J | J Country | monread | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 8 | 10.2503 | 7.1104 | 1.3929 | 0.18983 | 1.5572 | 3.1399 | 13.59% | 1.852% | 15.19% | 30.63%
H2 | H2 & K | great island | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 341.99 | 400.4053 | 259.4686 | 127.0707 | 8.7889 | 5.0772 | 140.9368 | 31.74% | 2.195% | 1.268% | 35.2%
I | E,F & I | knockraha | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 66.9999 | 78.4442 | 56.6296 | 17.8554 | 1.6675 | 2.2917 | 21.8146 | 22.76% | 2.126% | 2.921% | 27.81%
H2 | H2 & K | great island | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 341.99 | 400.4053 | 264.1578 | 127.0707 | 8.7889 | 0.38788 | 136.2475 | 31.74% | 2.195% | 0.09687% | 34.03%
J | J Country | monread | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 8 | 10.2503 | 5.5069 | 2.3106 | 0.21466 | 2.2181 | 4.7434 | 22.54% | 2.094% | 21.64% | 46.28%
J | J Country | bracklyn | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 43.2 | 133.2279 | 77.9579 | 43.9161 | 0.86001 | 10.4938 | 55.27 | 32.96% | 0.6455% | 7.877% | 41.49%
I | E,F & I | knockraha | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 66.9999 | 78.4442 | 58.5154 | 15.3527 | 1.4832 | 3.0929 | 19.9287 | 19.57% | 1.891% | 3.943% | 25.4%
I | E,F & I | knockraha | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 201 | 235.3328 | 153.5012 | 74.6841 | 5.1656 | 1.982 | 81.8316 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | great island | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 125.3232 | 146.7297 | 118.3496 | 20.3311 | 2.7275 | 5.3215 | 28.3801 | 13.86% | 1.859% | 3.627% | 19.34%
J | J Country | monread | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 8 | 10.2503 | 4.7495 | 1.5701 | 0.073903 | 3.8568 | 5.5008 | 15.32% | 0.721% | 37.63% | 53.67%
H2 | H2 & K | garrintaggart | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 49.5 | 140.0219 | 98.3694 | 38.5014 | 2.5589 | 0.59214 | 41.6525 | 27.5% | 1.828% | 0.4229% | 29.75%
J | J Country | bracklyn | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 21.6 | 66.6139 | 48.0861 | 12.4342 | 1.2523 | 4.8414 | 18.5279 | 18.67% | 1.88% | 7.268% | 27.81%
J | J Country | mount lucas | 2030 | Initial | Pro-rata | IE wind not priority | 56.4 | 173.9366 | 126.2456 | 23.9487 | 3.3821 | 20.3601 | 47.691 | 13.77% | 1.944% | 11.71% | 27.42%
I | E,F & I | knockraha | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 133.9999 | 156.8884 | 109.1579 | 35.2013 | 1.3503 | 11.1789 | 47.7305 | 22.44% | 0.8607% | 7.125% | 30.42%
H2 | H2 & K | garrintaggart | 2035 | 66% ECP | Pro-rata | IE wind not priority | 33 | 93.3478 | 74.1519 | 15.149 | 0.30681 | 3.7402 | 19.196 | 16.23% | 0.3287% | 4.007% | 20.56%
J | J Country | bracklyn | 2030 | 100% ECP | Pro-rata | IE wind not priority | 64.8 | 199.842 | 108.2716 | 59.8918 | 3.6747 | 28.0039 | 91.5704 | 29.97% | 1.839% | 14.01% | 45.82%
I | E,F & I | knockraha | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 133.9999 | 156.8884 | 123.2714 | 24.9077 | 1.1515 | 7.5579 | 33.617 | 15.88% | 0.7339% | 4.817% | 21.43%
J | J Country | monread | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 8 | 10.2503 | 6.6037 | 1.9864 | 0.18968 | 1.4705 | 3.6466 | 19.38% | 1.851% | 14.35% | 35.58%
H2 | H2 & K | garrintaggart | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 33 | 93.3478 | 75.4351 | 15.149 | 0.30681 | 2.4569 | 17.9127 | 16.23% | 0.3287% | 2.632% | 19.19%
H2 | H2 & K | garrintaggart | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 33 | 93.3478 | 58.7297 | 28.9374 | 0.62844 | 5.0522 | 34.6181 | 31% | 0.6732% | 5.412% | 37.09%
I | E,F & I | knockraha | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 133.9999 | 156.8884 | 114.381 | 24.9077 | 1.1515 | 16.4482 | 42.5074 | 15.88% | 0.7339% | 10.48% | 27.09%
J | J Country | monread | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 8 | 10.2503 | 4.8018 | 2.2521 | 0.087576 | 3.1088 | 5.4485 | 21.97% | 0.8544% | 30.33% | 53.15%
H2 | H2 & K | garrintaggart | 2035 | 100% ECP | Pro-rata | IE wind not priority | 49.5 | 140.0219 | 106.7914 | 25.1936 | 0.50136 | 7.5356 | 33.2305 | 17.99% | 0.3581% | 5.382% | 23.73%
J | J Country | bracklyn | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 64.8 | 199.842 | 113.5724 | 59.8918 | 3.6747 | 22.7032 | 86.2697 | 29.97% | 1.839% | 11.36% | 43.17%
J | J Country | monread | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 8 | 10.2503 | 5.0494 | 1.5701 | 0.073903 | 3.5569 | 5.2009 | 15.32% | 0.721% | 34.7% | 50.74%
H2 | H2 & K | great island | 2030 | Initial | Pro-rata | IE Solar not priority | 16.99 | 19.8921 | 16.5879 | 1.6452 | 0.25631 | 1.4027 | 3.3042 | 8.271% | 1.289% | 7.052% | 16.61%
J | J Country | monread | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 8 | 10.2503 | 3.7589 | 2.2538 | 0.092893 | 4.1447 | 6.4914 | 21.99% | 0.9062% | 40.44% | 63.33%
J | J Country | mount lucas | 2030 | Initial | Pro-rata | IE wind priority | 79.2 | 244.2514 | 208.126 | 0 | 7.5346 | 28.5908 | 36.1253 | 0% | 3.085% | 11.71% | 14.79%
H2 | H2 & K | great island | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 233.6565 | 273.5673 | 217.5253 | 43.4316 | 2.0078 | 10.6025 | 56.042 | 15.88% | 0.7339% | 3.876% | 20.49%
J | J Country | monread | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 8 | 10.2503 | 6.7381 | 1.699 | 0.19125 | 1.6219 | 3.5122 | 16.57% | 1.866% | 15.82% | 34.26%
J | J Country | maynooth | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 33.3333 | 42.7095 | 19.7895 | 6.5423 | 0.30793 | 16.0699 | 22.9201 | 15.32% | 0.721% | 37.63% | 53.67%
J | J Country | clonfad | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 100 | 128.1287 | 84.2267 | 21.2372 | 2.3907 | 20.2741 | 43.902 | 16.57% | 1.866% | 15.82% | 34.26%
H2 | H2 & K | kellis | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 251.3332 | 294.2634 | 231.4096 | 49.4711 | 5.5642 | 7.8185 | 62.8538 | 16.81% | 1.891% | 2.657% | 21.36%
H2 | H2 & K | kellis | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 251.3332 | 294.2634 | 220.8026 | 57.5916 | 5.5637 | 10.3055 | 73.4608 | 19.57% | 1.891% | 3.502% | 24.96%
I | E,F & I | kilbarry | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 56.5 | 66.1507 | 48.2278 | 10.5021 | 0.48551 | 6.9353 | 17.9229 | 15.88% | 0.7339% | 10.48% | 27.09%
J | J Country | clonfad | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 100 | 128.1287 | 82.5467 | 24.8297 | 2.371 | 18.3813 | 45.582 | 19.38% | 1.851% | 14.35% | 35.58%
H2 | H2 & K | kellis | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 251.3332 | 294.2634 | 210.639 | 66.98 | 6.2552 | 10.3892 | 83.6244 | 22.76% | 2.126% | 3.531% | 28.42%
J | J Country | maynooth | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 50 | 64.0644 | 28.2687 | 20.217 | 1.4115 | 14.1671 | 35.7956 | 31.56% | 2.203% | 22.11% | 55.87%
H2 | H2 & K | kellis | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 251.3332 | 294.2634 | 246.6571 | 40.7736 | 5.4699 | 1.3627 | 47.6063 | 13.86% | 1.859% | 0.4631% | 16.18%
J | J Country | maynooth | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 50 | 64.0644 | 26.9856 | 20.217 | 1.4115 | 15.4502 | 37.0787 | 31.56% | 2.203% | 24.12% | 57.88%
H2 | H2 & K | kellis | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 592 | 693.1195 | 449.1517 | 219.965 | 15.214 | 8.7888 | 243.9678 | 31.74% | 2.195% | 1.268% | 35.2%
J | J Country | clonfad | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 100 | 128.1287 | 68.8359 | 28.8829 | 2.6833 | 27.7267 | 59.2928 | 22.54% | 2.094% | 21.64% | 46.28%
I | E,F & I | kilbarry | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 79.8 | 93.4306 | 60.9423 | 29.6507 | 2.0508 | 0.78688 | 32.4884 | 31.74% | 2.195% | 0.8422% | 34.77%
J | J Country | maynooth | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 14.8133 | 2.9018 | 0.39547 | 3.2441 | 6.5414 | 13.59% | 1.852% | 15.19% | 30.63%
H2 | H2 & K | kellis | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 592 | 693.1195 | 457.269 | 219.965 | 15.214 | 0.67143 | 235.8505 | 31.74% | 2.195% | 0.09687% | 34.03%
J | J Country | maynooth | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 16.6667 | 21.3548 | 11.4726 | 4.8138 | 0.44721 | 4.6211 | 9.8821 | 22.54% | 2.094% | 21.64% | 46.28%
I | E,F & I | kilbarry | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 56.5 | 66.1507 | 51.9764 | 10.5021 | 0.48551 | 3.1867 | 14.1743 | 15.88% | 0.7339% | 4.817% | 21.43%
H2 | H2 & K | kellis | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 251.3332 | 294.2634 | 237.3476 | 40.7736 | 5.4699 | 10.6722 | 56.9158 | 13.86% | 1.859% | 3.627% | 19.34%
J | J Country | maynooth | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 33.3333 | 42.7095 | 21.039 | 6.5423 | 0.30793 | 14.8203 | 21.6705 | 15.32% | 0.721% | 34.7% | 50.74%
H2 | H2 & K | kellis | 2030 | Initial | Pro-rata | IE Solar not priority | 81 | 94.8356 | 79.0828 | 7.8434 | 1.222 | 6.6874 | 15.7528 | 8.271% | 1.289% | 7.052% | 16.61%
H2 | H2 & K | great island | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 233.6565 | 273.5673 | 224.6961 | 43.4316 | 2.0078 | 3.4317 | 48.8712 | 15.88% | 0.7339% | 1.254% | 17.86%
I | E,F & I | knockraha | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 66.9999 | 78.4442 | 59.9384 | 13.1879 | 1.4833 | 3.8345 | 18.5057 | 16.81% | 1.891% | 4.888% | 23.59%
H2 | H2 & K | great island | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 233.6565 | 273.5673 | 200.4063 | 61.3807 | 2.3546 | 9.4258 | 73.161 | 22.44% | 0.8607% | 3.445% | 26.74%
J | J Country | monread | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 8 | 10.2503 | 6.7952 | 1.3929 | 0.18983 | 1.8724 | 3.4551 | 13.59% | 1.852% | 18.27% | 33.71%
I | E,F & I | knockraha | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 66.9999 | 78.4442 | 61.7928 | 10.8694 | 1.4582 | 4.3239 | 16.6514 | 13.86% | 1.859% | 5.512% | 21.23%
H2 | H2 & K | great island | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 341.99 | 400.4053 | 293.2251 | 90.1698 | 3.6137 | 13.3967 | 107.1802 | 22.52% | 0.9025% | 3.346% | 26.77%
J | J Country | monread | 2030 | Initial | Pro-rata | IE Solar not priority | 8 | 10.2503 | 8.1161 | 0.81045 | 0.13256 | 1.1912 | 2.1342 | 7.907% | 1.293% | 11.62% | 20.82%
J | J Country | bracklyn | 2035 | 100% ECP | Pro-rata | IE wind not priority | 64.8 | 199.842 | 109.8417 | 40.5325 | 0.75291 | 48.715 | 90.0003 | 20.28% | 0.3768% | 24.38% | 45.04%
J | J Country | clonfad | 2030 | Initial | Pro-rata | IE Solar not priority | 100 | 128.1287 | 101.4515 | 10.1306 | 1.657 | 14.8896 | 26.6772 | 7.907% | 1.293% | 11.62% | 20.82%
H2 | H2 & K | great island 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 450 | 1809.414 | 1182.1228 | 518.4337 | 10.927 | 97.9304 | 627.2912 | 28.65% | 0.6039% | 5.412% | 34.67%
J | J Country | maynooth | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 50 | 64.0644 | 23.4928 | 14.0864 | 0.58058 | 25.9046 | 40.5715 | 21.99% | 0.9062% | 40.44% | 63.33%
I | E,F & I | kilbarry | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 79.8 | 93.4306 | 63.4058 | 21.0402 | 0.84322 | 8.1414 | 30.0248 | 22.52% | 0.9025% | 8.714% | 32.14%
J | J Country | maynooth | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 33.3333 | 42.7095 | 20.0076 | 9.3836 | 0.3649 | 12.9535 | 22.7019 | 21.97% | 0.8544% | 30.33% | 53.15%
J | J Country | clonfad | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 100 | 128.1287 | 84.9395 | 17.411 | 2.3728 | 23.4054 | 43.1892 | 13.59% | 1.852% | 18.27% | 33.71%
I | E,F & I | kilbarry | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 56.5 | 66.1507 | 46.0255 | 14.8423 | 0.56936 | 4.7135 | 20.1252 | 22.44% | 0.8607% | 7.125% | 30.42%
I | E,F & I | knockraha | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 201 | 235.3328 | 159.7064 | 52.9961 | 2.1239 | 20.5064 | 75.6264 | 22.52% | 0.9025% | 8.714% | 32.14%
J | J Country | mount lucas | 2030 | 33% ECP | Pro-rata | IE wind not priority | 56.4 | 173.9366 | 120.7753 | 32.467 | 3.2698 | 17.4244 | 53.1613 | 18.67% | 1.88% | 10.02% | 30.56%
J | J Country | mount lucas | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 56.4 | 173.9366 | 109.5675 | 32.18 | 0.61016 | 31.5789 | 64.3691 | 18.5% | 0.3508% | 18.16% | 37.01%
I | E,F & I | lysaghtstown | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 166.3333 | 194.7446 | 141.9805 | 30.9177 | 1.4293 | 20.4171 | 52.7642 | 15.88% | 0.7339% | 10.48% | 27.09%
H2 | H2 & K | crory | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 44.012 | 124.4979 | 115.4702 | 0 | 2.2895 | 6.7382 | 9.0276 | 0% | 1.839% | 5.412% | 7.251%
J | J Country | mount lucas | 2035 | 66% ECP | Pro-rata | IE wind priority | 79.2 | 244.2514 | 194.7291 | 0 | 2.3837 | 47.1386 | 49.5223 | 0% | 0.9759% | 19.3% | 20.28%
H2 | H2 & K | crory | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 20 | 23.4162 | 17.1539 | 5.2539 | 0.20154 | 0.80681 | 6.2623 | 22.44% | 0.8607% | 3.445% | 26.74%
J | J Country | bracklone | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 81.5999 | 251.6527 | 147.2538 | 82.9527 | 1.6245 | 19.8216 | 104.3988 | 32.96% | 0.6455% | 7.877% | 41.49%
J | J Country | mount lucas | 2035 | 66% ECP | Pro-rata | IE wind not priority | 56.4 | 173.9366 | 107.578 | 32.18 | 0.61016 | 33.5684 | 66.3586 | 18.5% | 0.3508% | 19.3% | 38.15%
H2 | H2 & K | crory | 2035 | 100% ECP | Pro-rata | IE wind priority | 44.012 | 124.4979 | 116.6094 | 0 | 1.1884 | 6.7001 | 7.8885 | 0% | 0.9545% | 5.382% | 6.336%
I | E,F & I | lysaghtstown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 206 | 241.1869 | 157.3196 | 76.5419 | 5.2941 | 2.0313 | 83.8672 | 31.74% | 2.195% | 0.8422% | 34.77%
H2 | H2 & K | crory | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 20 | 23.4162 | 17.1482 | 5.2732 | 0.21133 | 0.78346 | 6.268 | 22.52% | 0.9025% | 3.346% | 26.77%
J | J Country | bracklone | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 213.9998 | 274.1951 | 128.4488 | 60.2424 | 2.3426 | 83.1613 | 145.7464 | 21.97% | 0.8544% | 30.33% | 53.15%
I | E,F & I | lysaghtstown | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 206 | 241.1869 | 155.166 | 76.5419 | 5.2941 | 4.1849 | 86.0209 | 31.74% | 2.195% | 1.735% | 35.67%
J | J Country | mount lucas | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 79.2 | 244.2514 | 206.6095 | 0 | 9.8935 | 27.7483 | 37.6419 | 0% | 4.051% | 11.36% | 15.41%
H2 | H2 & K | effernoge | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 17 | 19.9038 | 16.054 | 2.7579 | 0.36998 | 0.72186 | 3.8497 | 13.86% | 1.859% | 3.627% | 19.34%
H2 | H2 & K | crory | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 20 | 23.4162 | 19.233 | 3.7176 | 0.17186 | 0.29374 | 4.1832 | 15.88% | 0.7339% | 1.254% | 17.86%
J | J Country | bracklone | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 213.9998 | 274.1951 | 135.0706 | 42.0014 | 1.9769 | 95.1462 | 139.1245 | 15.32% | 0.721% | 34.7% | 50.74%
H2 | H2 & K | crory | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 44.012 | 124.4979 | 120.1368 | 0 | 1.0844 | 3.2767 | 4.3611 | 0% | 0.871% | 2.632% | 3.503%
J | J Country | mount lucas | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 79.2 | 244.2514 | 197.5228 | 0 | 2.3837 | 44.3449 | 46.7286 | 0% | 0.9759% | 18.16% | 19.13%
I | E,F & I | midleton | 2030 | Initial | Pro-rata | IE Solar not priority | 14.55 | 17.0353 | 12.8297 | 1.4089 | 0.2195 | 2.5771 | 4.2055 | 8.271% | 1.289% | 15.13% | 24.69%
H2 | H2 & K | crory | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 20 | 23.4162 | 15.174 | 7.4312 | 0.51399 | 0.29692 | 8.2422 | 31.74% | 2.195% | 1.268% | 35.2%
J | J Country | bracklone | 2035 | 66% ECP | Pro-rata | IE wind not priority | 81.5999 | 251.6527 | 155.6446 | 46.5583 | 0.88278 | 48.567 | 96.008 | 18.5% | 0.3508% | 19.3% | 38.15%
H2 | H2 & K | crory | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 44.012 | 124.4979 | 119.1782 | 0 | 4.7932 | 0.52649 | 5.3197 | 0% | 3.85% | 0.4229% | 4.273%
J | J Country | mount lucas | 2035 | 100% ECP | Pro-rata | IE wind priority | 79.2 | 244.2514 | 182.0308 | 0 | 2.68 | 59.5405 | 62.2205 | 0% | 1.097% | 24.38% | 25.47%
H2 | H2 & K | crory | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 20 | 23.4162 | 15.4483 | 7.4312 | 0.51399 | 0.022684 | 7.9679 | 31.74% | 2.195% | 0.09687% | 34.03%
J | J Country | mount lucas | 2035 | 100% ECP | Pro-rata | IE wind not priority | 56.4 | 173.9366 | 95.603 | 35.2782 | 0.65531 | 42.4001 | 78.3336 | 20.28% | 0.3768% | 24.38% | 45.04%
J | J Country | bracklone | 2035 | 100% ECP | Pro-rata | IE wind not priority | 122.4 | 377.4794 | 207.4788 | 76.5613 | 1.4222 | 92.0171 | 170.0006 | 20.28% | 0.3768% | 24.38% | 45.04%
J | J Country | bracklone | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 213.9998 | 274.1951 | 127.0483 | 42.0014 | 1.9769 | 103.1686 | 147.1469 | 15.32% | 0.721% | 37.63% | 53.67%
J | J Country | mount lucas | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 79.2 | 244.2514 | 220.3361 | 0 | 4.6765 | 19.2387 | 23.9152 | 0% | 1.915% | 7.877% | 9.791%
I | E,F & I | lysaghtstown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 166.3333 | 194.7446 | 135.4971 | 43.6951 | 1.6762 | 13.8763 | 59.2476 | 22.44% | 0.8607% | 7.125% | 30.42%
H2 | H2 & K | crory | 2035 | 66% ECP | Pro-rata | IE wind priority | 44.012 | 124.4979 | 118.4252 | 0 | 1.0844 | 4.9883 | 6.0726 | 0% | 0.871% | 4.007% | 4.878%
J | J Country | mount lucas | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 56.4 | 173.9366 | 101.7785 | 57.335 | 1.1228 | 13.7003 | 72.1581 | 32.96% | 0.6455% | 7.877% | 41.49%
J | J Country | bracklone | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 81.5999 | 251.6527 | 158.523 | 46.5583 | 0.88278 | 45.6886 | 93.1297 | 18.5% | 0.3508% | 18.16% | 37.01%
H2 | H2 & K | crory | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 20 | 23.4162 | 18.6192 | 3.7176 | 0.17186 | 0.90753 | 4.797 | 15.88% | 0.7339% | 3.876% | 20.49%
I | E,F & I | lysaghtstown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 166.3333 | 194.7446 | 153.0161 | 30.9177 | 1.4293 | 9.3815 | 41.7286 | 15.88% | 0.7339% | 4.817% | 21.43%
I | E,F & I | lysaghtstown | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 206 | 241.1869 | 163.6792 | 54.3144 | 2.1767 | 21.0165 | 77.5077 | 22.52% | 0.9025% | 8.714% | 32.14%
H2 | H2 & K | garrintaggart | 2030 | 100% ECP | Pro-rata | IE wind not priority | 49.5 | 140.0219 | 96.7051 | 38.5014 | 2.5589 | 2.2564 | 43.3168 | 27.5% | 1.828% | 1.611% | 30.94%
I | E,F & I | lysaghtstown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 126.6666 | 148.3026 | 120.861 | 20.5491 | 2.7567 | 4.1357 | 27.4415 | 13.86% | 1.859% | 2.789% | 18.5%
J | J Country | mount lucas | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 56.4 | 173.9366 | 98.85 | 52.1281 | 3.1983 | 19.7602 | 75.0866 | 29.97% | 1.839% | 11.36% | 43.17%
J | J Country | mount lucas | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 79.2 | 244.2514 | 225.7147 | 0 | 10.3857 | 8.151 | 18.5367 | 0% | 4.252% | 3.337% | 7.589%
H2 | H2 & K | effernoge | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 51 | 59.7113 | 43.7278 | 13.4468 | 0.5389 | 1.9978 | 15.9835 | 22.52% | 0.9025% | 3.346% | 26.77%
J | J Country | mount lucas | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 56.4 | 173.9366 | 108.3235 | 56.5451 | 3.2635 | 5.8045 | 65.6131 | 32.51% | 1.876% | 3.337% | 37.72%
J | J Country | bracklyn | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 21.6 | 66.6139 | 44.6453 | 16.9987 | 1.2648 | 3.7051 | 21.9686 | 25.52% | 1.899% | 5.562% | 32.98%
I | E,F & I | knockraha 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 450 | 1912.6962 | 1262.3496 | 513.6734 | 11.2285 | 125.4447 | 650.3466 | 26.86% | 0.587% | 6.559% | 34%
H2 | H2 & K | garrintaggart | 2030 | 33% ECP | Pro-rata | IE wind not priority | 16.5 | 46.6739 | 37.0073 | 7.6245 | 0.836 | 1.2061 | 9.6666 | 16.34% | 1.791% | 2.584% | 20.71%
J | J Country | mount lucas | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 79.2 | 244.2514 | 221.2138 | 0 | 9.452 | 13.5856 | 23.0375 | 0% | 3.87% | 5.562% | 9.432%
H2 | H2 & K | garrintaggart | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 16.5 | 46.6739 | 34.4627 | 10.6985 | 0.86214 | 0.65058 | 12.2112 | 22.92% | 1.847% | 1.394% | 26.16%
J | J Country | bracklyn | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 21.6 | 66.6139 | 41.4855 | 21.6556 | 1.2498 | 2.223 | 25.1284 | 32.51% | 1.876% | 3.337% | 37.72%
J | J Country | mount lucas | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 56.4 | 173.9366 | 116.5739 | 44.3856 | 3.3025 | 9.6746 | 57.3626 | 25.52% | 1.899% | 5.562% | 32.98%
H2 | H2 & K | garrintaggart | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 16.5 | 46.6739 | 29.8155 | 14.1279 | 0.89007 | 1.8405 | 16.8584 | 30.27% | 1.907% | 3.943% | 36.12%
J | J Country | mount lucas | 2030 | 33% ECP | Pro-rata | IE wind priority | 79.2 | 244.2514 | 211.3825 | 0 | 8.4005 | 24.4684 | 32.8689 | 0% | 3.439% | 10.02% | 13.46%
H2 | H2 & K | garrintaggart | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 16.5 | 46.6739 | 28.301 | 15.1329 | 0.89812 | 2.3419 | 18.3729 | 32.42% | 1.924% | 5.018% | 39.36%
J | J Country | bracklyn | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 21.6 | 66.6139 | 39.2492 | 23.119 | 1.2333 | 3.0124 | 27.3648 | 34.71% | 1.851% | 4.522% | 41.08%
H2 | H2 & K | garrintaggart | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 16.5 | 46.6739 | 37.9867 | 7.6245 | 0.836 | 0.2268 | 8.6873 | 16.34% | 1.791% | 0.4859% | 18.61%
H2 | H2 & K | effernoge | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 34 | 39.8075 | 29.1617 | 8.9317 | 0.34262 | 1.3716 | 10.6458 | 22.44% | 0.8607% | 3.445% | 26.74%
J | J Country | bracklyn | 2030 | 33% ECP | Pro-rata | IE wind not priority | 21.6 | 66.6139 | 46.2543 | 12.4342 | 1.2523 | 6.6732 | 20.3596 | 18.67% | 1.88% | 10.02% | 30.56%
I | E,F & I | lysaghtstown | 2030 | Initial | Pro-rata | IE Solar not priority | 87 | 101.8605 | 76.7139 | 8.4244 | 1.3125 | 15.4096 | 25.1465 | 8.271% | 1.289% | 15.13% | 24.69%
J | J Country | mount lucas | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 56.4 | 173.9366 | 102.4841 | 60.3664 | 3.2203 | 7.8657 | 71.4525 | 34.71% | 1.851% | 4.522% | 41.08%
H2 | H2 & K | effernoge | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 17 | 19.9038 | 14.9349 | 3.8955 | 0.37632 | 0.69706 | 4.9688 | 19.57% | 1.891% | 3.502% | 24.96%
I | E,F & I | lysaghtstown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 126.6666 | 148.3026 | 107.0609 | 33.7565 | 3.1525 | 4.3326 | 41.2416 | 22.76% | 2.126% | 2.921% | 27.81%
J | J Country | mount lucas | 2030 | 100% ECP | Pro-rata | IE wind priority | 79.2 | 244.2514 | 200.1309 | 0 | 9.8935 | 34.227 | 44.1205 | 0% | 4.051% | 14.01% | 18.06%
J | J Country | bracklone | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 321 | 411.2931 | 150.824 | 90.4346 | 3.7273 | 166.3072 | 260.4692 | 21.99% | 0.9062% | 40.44% | 63.33%
H2 | H2 & K | effernoge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 17 | 19.9038 | 14.2475 | 4.5305 | 0.4231 | 0.70271 | 5.6563 | 22.76% | 2.126% | 3.531% | 28.42%
J | J Country | mount lucas | 2030 | 100% ECP | Pro-rata | IE wind not priority | 56.4 | 173.9366 | 94.2364 | 52.1281 | 3.1983 | 24.3738 | 79.7001 | 29.97% | 1.839% | 14.01% | 45.82%
H2 | H2 & K | effernoge | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 17 | 19.9038 | 16.6837 | 2.7579 | 0.36998 | 0.092174 | 3.2201 | 13.86% | 1.859% | 0.4631% | 16.18%
I | E,F & I | lysaghtstown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 126.6666 | 148.3026 | 110.6263 | 29.025 | 2.804 | 5.8473 | 37.6763 | 19.57% | 1.891% | 3.943% | 25.4%
H2 | H2 & K | effernoge | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 17 | 19.9038 | 15.6524 | 3.3462 | 0.37636 | 0.52884 | 4.2514 | 16.81% | 1.891% | 2.657% | 21.36%
H2 | H2 & K | effernoge | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 51 | 59.7113 | 38.6938 | 18.9497 | 1.3107 | 0.75714 | 21.0175 | 31.74% | 2.195% | 1.268% | 35.2%
I | E,F & I | lysaghtstown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 126.6666 | 148.3026 | 113.3165 | 24.9324 | 2.8043 | 7.2494 | 34.986 | 16.81% | 1.891% | 4.888% | 23.59%
H2 | H2 & K | effernoge | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 51 | 59.7113 | 39.3931 | 18.9497 | 1.3107 | 0.057843 | 20.3182 | 31.74% | 2.195% | 0.09687% | 34.03%
J | J Country | mount lucas | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 56.4 | 173.9366 | 125.5582 | 32.467 | 3.2698 | 12.6415 | 48.3784 | 18.67% | 1.88% | 7.268% | 27.81%
I | E,F & I | lysaghtstown | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 126.6666 | 148.3026 | 116.8223 | 20.5491 | 2.7567 | 8.1745 | 31.4803 | 13.86% | 1.859% | 5.512% | 21.23%
J | J Country | mount lucas | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 79.2 | 244.2514 | 222.7839 | 0 | 10.422 | 11.0455 | 21.4675 | 0% | 4.267% | 4.522% | 8.789%
H2 | H2 & K | effernoge | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 34 | 39.8075 | 31.6527 | 6.3199 | 0.29217 | 1.5428 | 8.1548 | 15.88% | 0.7339% | 3.876% | 20.49%
H2 | H2 & K | effernoge | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 34 | 39.8075 | 32.6961 | 6.3199 | 0.29217 | 0.49936 | 7.1114 | 15.88% | 0.7339% | 1.254% | 17.86%
J | J Country | mount lucas | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 79.2 | 244.2514 | 218.0989 | 0 | 8.4005 | 17.7519 | 26.1524 | 0% | 3.439% | 7.268% | 10.71%
J | J City, G South | grange | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 39.99 | 51.2387 | 43.0312 | 6.9626 | 0.94889 | 0.29595 | 8.2075 | 13.59% | 1.852% | 0.5776% | 16.02%
F | E,F & I | macroom | 2035 | 66% ECP | Pro-rata | IE wind priority | 24 | 77.6717 | 66.0849 | 0 | 0.62619 | 10.9606 | 11.5868 | 0% | 0.8062% | 14.11% | 14.92%
H1 | H1 | timoney | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 171.56 | 200.8642 | 115.7258 | 63.7453 | 4.409 | 16.9841 | 85.1384 | 31.74% | 2.195% | 8.456% | 42.39%
C | C | richmond | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 31 | 39.7199 | 27.3383 | 8.7336 | 0.35996 | 3.288 | 12.3815 | 21.99% | 0.9062% | 8.278% | 31.17%
C | C | richmond | 2035 | 100% ECP | Pro-rata | IE wind not priority | 18.5 | 59.3731 | 47.181 | 10.182 | 0.19831 | 1.8118 | 12.1921 | 17.15% | 0.334% | 3.052% | 20.53%
C | C | richmond | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 24.6667 | 31.6051 | 23.098 | 6.9438 | 0.27003 | 1.2932 | 8.507 | 21.97% | 0.8544% | 4.092% | 26.92%
C | C | richmond | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 12.3333 | 39.5821 | 27.716 | 11.3702 | 0.23644 | 0.25932 | 11.866 | 28.73% | 0.5973% | 0.6551% | 29.98%
C | C | richmond | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 24.6667 | 31.6051 | 25.8991 | 4.8413 | 0.22787 | 0.63684 | 5.706 | 15.32% | 0.721% | 2.015% | 18.05%
C | C | richmond | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 12.3333 | 39.5821 | 33.2453 | 6.1363 | 0.12121 | 0.079326 | 6.3368 | 15.5% | 0.3062% | 0.2004% | 16.01%
C | C | richmond | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 24.6667 | 31.6051 | 24.5007 | 4.8413 | 0.22787 | 2.0353 | 7.1044 | 15.32% | 0.721% | 6.44% | 22.48%
C | C | richmond | 2035 | 66% ECP | Pro-rata | IE wind not priority | 12.3333 | 39.5821 | 32.5218 | 6.1363 | 0.12121 | 0.80278 | 7.0603 | 15.5% | 0.3062% | 2.028% | 17.84%
C | C | richmond | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 31 | 39.7199 | 24.0405 | 12.5346 | 0.87511 | 2.2697 | 15.6794 | 31.56% | 2.203% | 5.714% | 39.47%
C | C | richmond | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 18.5 | 59.3731 | 41.8082 | 15.4114 | 1.014 | 1.1395 | 17.5649 | 25.96% | 1.708% | 1.919% | 29.58%
C | C | richmond | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 31 | 39.7199 | 23.8962 | 12.5346 | 0.87511 | 2.414 | 15.8237 | 31.56% | 2.203% | 6.078% | 39.84%
C | C | richmond | 2030 | 100% ECP | Pro-rata | IE wind not priority | 18.5 | 59.3731 | 40.7995 | 15.4114 | 1.014 | 2.1483 | 18.5736 | 25.96% | 1.708% | 3.618% | 31.28%
C | C | richmond | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 18.3333 | 23.4903 | 19.2057 | 3.192 | 0.43502 | 0.65757 | 4.2846 | 13.59% | 1.852% | 2.799% | 18.24%
C | C | shannonbridge | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 21.6666 | 27.7612 | 22.5843 | 3.7724 | 0.51411 | 0.89043 | 5.1769 | 13.59% | 1.852% | 3.207% | 18.65%
C | C | shannonbridge | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 21.6666 | 27.7612 | 21.7962 | 4.6014 | 0.51798 | 0.84566 | 5.965 | 16.57% | 1.866% | 3.046% | 21.49%
C | C | sliabh bawn | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 58 | 186.1428 | 162.4618 | 0 | 7.252 | 16.429 | 23.681 | 0% | 3.896% | 8.826% | 12.72%
C | C | sliabh bawn | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 58 | 186.1428 | 163.209 | 0 | 7.104 | 15.8298 | 22.9338 | 0% | 3.816% | 8.504% | 12.32%
C | C | sliabh bawn | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 58 | 186.1428 | 165.0182 | 0 | 6.3921 | 14.7325 | 21.1246 | 0% | 3.434% | 7.915% | 11.35%
C | C | sliabh bawn | 2030 | 33% ECP | Pro-rata | IE wind priority | 58 | 186.1428 | 165.1725 | 0 | 5.636 | 15.3343 | 20.9703 | 0% | 3.028% | 8.238% | 11.27%
C | C | sliabh bawn | 2030 | Initial | Pro-rata | IE wind priority | 58 | 186.1428 | 151.0481 | 0 | 5.0615 | 30.0332 | 35.0947 | 0% | 2.719% | 16.13% | 18.85%
C | C | shannonbridge | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 65 | 83.2837 | 57.3223 | 18.3123 | 0.75475 | 6.8943 | 25.9613 | 21.99% | 0.9062% | 8.278% | 31.17%
C | C | richmond | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 6.1667 | 19.791 | 15.0058 | 3.0942 | 0.34079 | 1.3503 | 4.7853 | 15.63% | 1.722% | 6.823% | 24.18%
C | C | shannonbridge | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 43.3333 | 55.5224 | 40.5776 | 12.1986 | 0.47437 | 2.2718 | 14.9448 | 21.97% | 0.8544% | 4.092% | 26.92%
C | C | shannonbridge | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 43.3333 | 55.5224 | 43.0417 | 8.505 | 0.40031 | 3.5754 | 12.4807 | 15.32% | 0.721% | 6.44% | 22.48%
C | C | shannonbridge | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 65 | 83.2837 | 50.4075 | 26.2821 | 1.8349 | 4.7591 | 32.8762 | 31.56% | 2.203% | 5.714% | 39.47%
C | C | shannonbridge | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 65 | 83.2837 | 50.105 | 26.2821 | 1.8349 | 5.0616 | 33.1786 | 31.56% | 2.203% | 6.078% | 39.84%
C | C | shannonbridge | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 21.6666 | 27.7612 | 22.6976 | 3.7724 | 0.51411 | 0.77713 | 5.0636 | 13.59% | 1.852% | 2.799% | 18.24%
C | C | shannonbridge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 21.6666 | 27.7612 | 20.139 | 6.2579 | 0.58138 | 0.78282 | 7.6221 | 22.54% | 2.094% | 2.82% | 27.46%
C | C | shannonbridge | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 21.6666 | 27.7612 | 21.0617 | 5.3798 | 0.51373 | 0.80598 | 6.6995 | 19.38% | 1.851% | 2.903% | 24.13%
C | C | shannonbridge | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 43.3333 | 55.5224 | 45.4984 | 8.505 | 0.40031 | 1.1188 | 10.024 | 15.32% | 0.721% | 2.015% | 18.05%
C | C | richmond | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 18.3333 | 23.4903 | 17.0407 | 5.2952 | 0.49193 | 0.66239 | 6.4495 | 22.54% | 2.094% | 2.82% | 27.46%
C | C | richmond | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 6.1667 | 19.791 | 11.686 | 6.0043 | 0.35398 | 1.7468 | 8.105 | 30.34% | 1.789% | 8.826% | 40.95%
C | C | richmond | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 18.3333 | 23.4903 | 17.8215 | 4.5521 | 0.43469 | 0.68199 | 5.6688 | 19.38% | 1.851% | 2.903% | 24.13%
C | C | lanesboro | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 215.6 | 276.2455 | 166.1945 | 87.1759 | 6.0862 | 16.7889 | 110.051 | 31.56% | 2.203% | 6.078% | 39.84%
C | C | lanesboro | 2030 | 100% ECP | Pro-rata | IE wind not priority | 99.45 | 319.1707 | 219.3249 | 82.8468 | 5.4507 | 11.5483 | 99.8459 | 25.96% | 1.708% | 3.618% | 31.28%
C | C | lanesboro | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 112.2666 | 143.8458 | 117.6084 | 19.5467 | 2.6639 | 4.0267 | 26.2373 | 13.59% | 1.852% | 2.799% | 18.24%
C | C | lanesboro | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 33.15 | 106.3901 | 80.6661 | 16.6335 | 1.832 | 7.2585 | 25.724 | 15.63% | 1.722% | 6.823% | 24.18%
C | C | lanesboro | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 112.2666 | 143.8458 | 104.3513 | 32.4258 | 3.0124 | 4.0562 | 39.4945 | 22.54% | 2.094% | 2.82% | 27.46%
C | C | lanesboro | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 33.15 | 106.3901 | 62.8201 | 32.2771 | 1.9029 | 9.39 | 43.57 | 30.34% | 1.789% | 8.826% | 40.95%
C | C | lanesboro | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 112.2666 | 143.8458 | 109.1322 | 27.8754 | 2.6619 | 4.1762 | 34.7136 | 19.38% | 1.851% | 2.903% | 24.13%
C | C | lanesboro | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 99.45 | 319.1707 | 224.7475 | 82.8468 | 5.4507 | 6.1257 | 94.4232 | 25.96% | 1.708% | 1.919% | 29.58%
C | C | lanesboro | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 33.15 | 106.3901 | 65.3419 | 30.1186 | 1.8821 | 9.0475 | 41.0482 | 28.31% | 1.769% | 8.504% | 38.58%
C | C | lanesboro | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 33.15 | 106.3901 | 72.8766 | 23.2221 | 1.871 | 8.4204 | 33.5135 | 21.83% | 1.759% | 7.915% | 31.5%
C | C | lanesboro | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 112.2666 | 143.8458 | 117.0214 | 19.5467 | 2.6639 | 4.6138 | 26.8244 | 13.59% | 1.852% | 3.207% | 18.65%
C | C | lanesboro | 2030 | 33% ECP | Pro-rata | IE wind not priority | 33.15 | 106.3901 | 79.1603 | 16.6335 | 1.832 | 8.7643 | 27.2299 | 15.63% | 1.722% | 8.238% | 25.59%
C | C | lanesboro | 2030 | Initial | Pro-rata | IE Solar not priority | 60.6 | 77.646 | 70.0824 | 6.1392 | 1.0041 | 0.4203 | 7.5636 | 7.907% | 1.293% | 0.5413% | 9.741%
C | C | derrycarney | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 444.25 | 569.2117 | 391.7762 | 125.1576 | 5.1585 | 47.1196 | 177.4356 | 21.99% | 0.9062% | 8.278% | 31.17%
C | C | lanesboro | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 112.2666 | 143.8458 | 112.9377 | 23.8423 | 2.6839 | 4.3818 | 30.9081 | 16.57% | 1.866% | 3.046% | 21.49%
C | C | sliabh bawn | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 58 | 186.1428 | 167.8071 | 0 | 5.636 | 12.6997 | 18.3357 | 0% | 3.028% | 6.823% | 9.85%
C | C | lanesboro | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 215.6 | 276.2455 | 167.1978 | 87.1759 | 6.0862 | 15.7856 | 109.0477 | 31.56% | 2.203% | 5.714% | 39.47%
C | C | richmond | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 6.1667 | 19.791 | 12.1551 | 5.6028 | 0.35011 | 1.6831 | 7.6359 | 28.31% | 1.769% | 8.504% | 38.58%
C | C | richmond | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 18.3333 | 23.4903 | 18.4429 | 3.8935 | 0.43829 | 0.71556 | 5.0473 | 16.57% | 1.866% | 3.046% | 21.49%
C | C | richmond | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 6.1667 | 19.791 | 13.5567 | 4.3199 | 0.34805 | 1.5664 | 6.2343 | 21.83% | 1.759% | 7.915% | 31.5%
C | C | richmond | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 18.3333 | 23.4903 | 19.1098 | 3.192 | 0.43502 | 0.75344 | 4.3805 | 13.59% | 1.852% | 3.207% | 18.65%
C | C | richmond | 2030 | 33% ECP | Pro-rata | IE wind not priority | 6.1667 | 19.791 | 14.7256 | 3.0942 | 0.34079 | 1.6304 | 5.0654 | 15.63% | 1.722% | 8.238% | 25.59%
C | C | richmond | 2030 | Initial | Pro-rata | IE Solar not priority | 12 | 15.3754 | 13.8777 | 1.2157 | 0.19884 | 0.083228 | 1.4977 | 7.907% | 1.293% | 0.5413% | 9.741%
C | C | lanesboro | 2035 | 100% ECP | Pro-rata | IE wind not priority | 99.45 | 319.1707 | 253.6298 | 54.7354 | 1.0661 | 9.7396 | 65.541 | 17.15% | 0.334% | 3.052% | 20.53%
C | C | lanesboro | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 163.9332 | 210.0455 | 153.5082 | 46.1484 | 1.7946 | 8.5944 | 56.5373 | 21.97% | 0.8544% | 4.092% | 26.92%
C | C | lanesboro | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 66.2999 | 212.7803 | 148.9925 | 61.1228 | 1.271 | 1.394 | 63.7878 | 28.73% | 0.5973% | 0.6551% | 29.98%
C | C | lanesboro | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 163.9332 | 210.0455 | 172.1238 | 32.1749 | 1.5144 | 4.2324 | 37.9217 | 15.32% | 0.721% | 2.015% | 18.05%
C | C | lanesboro | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 66.2999 | 212.7803 | 178.7157 | 32.9866 | 0.65157 | 0.42643 | 34.0646 | 15.5% | 0.3062% | 0.2004% | 16.01%
C | C | lanesboro | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 163.9332 | 210.0455 | 162.83 | 32.1749 | 1.5144 | 13.5262 | 47.2155 | 15.32% | 0.721% | 6.44% | 22.48%
C | C | lanesboro | 2035 | 66% ECP | Pro-rata | IE wind not priority | 66.2999 | 212.7803 | 174.8266 | 32.9866 | 0.65157 | 4.3155 | 37.9537 | 15.5% | 0.3062% | 2.028% | 17.84%
C | C | lanesboro | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 215.6 | 276.2455 | 190.1338 | 60.7405 | 2.5035 | 22.8677 | 86.1117 | 21.99% | 0.9062% | 8.278% | 31.17%
C | C | derrycarney | 2035 | 100% ECP | Pro-rata | IE wind not priority | 34 | 109.1182 | 86.711 | 18.7129 | 0.36446 | 3.3298 | 22.4072 | 17.15% | 0.334% | 3.052% | 20.53%
C | C | sliabh bawn | 2030 | 100% ECP | Pro-rata | IE wind priority | 58 | 186.1428 | 172.7243 | 0 | 6.6834 | 6.7351 | 13.4185 | 0% | 3.59% | 3.618% | 7.209%
C | J Country | mullingar | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 23.2333 | 29.7686 | 14.6642 | 4.56 | 0.21463 | 10.3297 | 15.1043 | 15.32% | 0.721% | 34.7% | 50.74%
C | J Country | mullingar | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 68.1666 | 218.7711 | 144.467 | 33.9153 | 0.66991 | 39.7188 | 74.3041 | 15.5% | 0.3062% | 18.16% | 33.96%
C | J Country | mullingar | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 23.2333 | 29.7686 | 13.7933 | 4.56 | 0.21463 | 11.2007 | 15.9753 | 15.32% | 0.721% | 37.63% | 53.67%
C | J Country | mullingar | 2035 | 66% ECP | Pro-rata | IE wind not priority | 68.1666 | 218.7711 | 141.9648 | 33.9153 | 0.66991 | 42.2211 | 76.8063 | 15.5% | 0.3062% | 19.3% | 35.11%
C | J Country | mullingar | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 28.85 | 36.9651 | 16.3111 | 11.6652 | 0.81441 | 8.1744 | 20.6541 | 31.56% | 2.203% | 22.11% | 55.87%
C | J Country | mullingar | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 97.5 | 312.9125 | 190.7977 | 81.2223 | 5.3438 | 35.5486 | 122.1148 | 25.96% | 1.708% | 11.36% | 39.03%
C | J Country | mullingar | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 28.85 | 36.9651 | 15.5707 | 11.6652 | 0.81441 | 8.9148 | 21.3944 | 31.56% | 2.203% | 24.12% | 57.88%
C | J Country | mullingar | 2030 | 100% ECP | Pro-rata | IE wind not priority | 97.5 | 312.9125 | 182.4978 | 81.2223 | 5.3438 | 43.8485 | 130.4147 | 25.96% | 1.708% | 14.01% | 41.68%
C | J Country | mullingar | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 17.6167 | 22.572 | 15.6577 | 3.0672 | 0.41801 | 3.4291 | 6.9143 | 13.59% | 1.852% | 15.19% | 30.63%
C | J Country | mullingar | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 38.8333 | 124.63 | 93.9407 | 19.4852 | 2.1461 | 9.058 | 30.6893 | 15.63% | 1.722% | 7.268% | 24.62%
C | J Country | mullingar | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 17.6167 | 22.572 | 12.1266 | 5.0882 | 0.4727 | 4.8845 | 10.4454 | 22.54% | 2.094% | 21.64% | 46.28%
C | J Country | mullingar | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 38.8333 | 124.63 | 78.9541 | 37.8108 | 2.2291 | 5.636 | 45.6759 | 30.34% | 1.789% | 4.522% | 36.65%
C | J Country | mullingar | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 17.6167 | 22.572 | 14.542 | 4.3742 | 0.4177 | 3.2382 | 8.03 | 19.38% | 1.851% | 14.35% | 35.58%
C | J Country | mullingar | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 68.1666 | 218.7711 | 137.3889 | 62.8437 | 1.3068 | 17.2317 | 81.3822 | 28.73% | 0.5973% | 7.877% | 37.2%
C | J Country | mullingar | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 23.2333 | 29.7686 | 13.9453 | 6.5403 | 0.25433 | 9.0286 | 15.8233 | 21.97% | 0.8544% | 30.33% | 53.15%
C | J Country | mullingar | 2035 | 100% ECP | Pro-rata | IE wind not priority | 97.5 | 312.9125 | 181.9274 | 53.6621 | 1.0452 | 76.2778 | 130.9851 | 17.15% | 0.334% | 24.38% | 41.86%
C | J Country | mullingar | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 28.85 | 36.9651 | 13.5554 | 8.1278 | 0.335 | 14.9469 | 23.4098 | 21.99% | 0.9062% | 40.44% | 63.33%
D | D and E North | ardnacrusha | 2030 | Initial | Pro-rata | IE wind priority | 7.5 | 23.298 | 22.5337 | 0 | 0.63545 | 0.1289 | 0.76436 | 0% | 2.727% | 0.5533% | 3.281%
C | J Country | shanonagh | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 200 | 256.2574 | 93.9713 | 56.3456 | 2.3223 | 103.6182 | 162.2861 | 21.99% | 0.9062% | 40.44% | 63.33%
C | J Country | shanonagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 133.3332 | 170.8381 | 80.0304 | 37.5342 | 1.4596 | 51.8139 | 90.8077 | 21.97% | 0.8544% | 30.33% | 53.15%
C | J Country | shanonagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 133.3332 | 170.8381 | 84.1562 | 26.1691 | 1.2317 | 59.2811 | 86.6819 | 15.32% | 0.721% | 34.7% | 50.74%
C | J Country | shanonagh | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 133.3332 | 170.8381 | 79.1578 | 26.1691 | 1.2317 | 64.2795 | 91.6803 | 15.32% | 0.721% | 37.63% | 53.67%
C | J Country | mullingar | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 38.8333 | 124.63 | 82.9839 | 35.2822 | 2.2048 | 4.1591 | 41.6461 | 28.31% | 1.769% | 3.337% | 33.42%
C | J Country | shanonagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 200 | 256.2574 | 113.075 | 80.8681 | 5.6458 | 56.6684 | 143.1824 | 31.56% | 2.203% | 22.11% | 55.87%
C | J Country | shanonagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 66.6666 | 85.419 | 59.2533 | 11.6073 | 1.5819 | 12.9766 | 26.1657 | 13.59% | 1.852% | 15.19% | 30.63%
C | J Country | shanonagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 66.6666 | 85.419 | 45.8905 | 19.2552 | 1.7889 | 18.4844 | 39.5285 | 22.54% | 2.094% | 21.64% | 46.28%
C | J Country | shanonagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 66.6666 | 85.419 | 55.0311 | 16.5531 | 1.5807 | 12.2542 | 30.388 | 19.38% | 1.851% | 14.35% | 35.58%
C | J Country | shanonagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 66.6666 | 85.419 | 56.1511 | 14.1581 | 1.5938 | 13.516 | 29.2679 | 16.57% | 1.866% | 15.82% | 34.26%
C | J Country | shanonagh | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 66.6666 | 85.419 | 56.6263 | 11.6073 | 1.5819 | 15.6036 | 28.7928 | 13.59% | 1.852% | 18.27% | 33.71%
C | J Country | shanonagh | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 200 | 256.2574 | 107.9425 | 80.8681 | 5.6458 | 61.8009 | 148.3149 | 31.56% | 2.203% | 24.12% | 57.88%
C | J Country | mullingar | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 17.6167 | 22.572 | 14.8379 | 3.7413 | 0.42116 | 3.5716 | 7.7341 | 16.57% | 1.866% | 15.82% | 34.26%
C | J Country | mullingar | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 38.8333 | 124.63 | 88.3028 | 27.2034 | 2.1918 | 6.9321 | 36.3272 | 21.83% | 1.759% | 5.562% | 29.15%
C | J Country | mullingar | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 17.6167 | 22.572 | 14.9635 | 3.0672 | 0.41801 | 4.1233 | 7.6085 | 13.59% | 1.852% | 18.27% | 33.71%
C | C | somerset | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 66.6666 | 85.4191 | 69.9975 | 13.0846 | 0.61586 | 1.7212 | 15.4216 | 15.32% | 0.721% | 2.015% | 18.05%
C | C | somerset | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 66.6666 | 85.4191 | 66.218 | 13.0846 | 0.61586 | 5.5007 | 19.2011 | 15.32% | 0.721% | 6.44% | 22.48%
C | C | somerset | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 98 | 125.5661 | 75.999 | 39.6254 | 2.7665 | 7.1753 | 49.5671 | 31.56% | 2.203% | 5.714% | 39.47%
C | C | somerset | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 98 | 125.5661 | 75.543 | 39.6254 | 2.7665 | 7.6313 | 50.0232 | 31.56% | 2.203% | 6.078% | 39.84%
C | C | somerset | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 35.3333 | 45.2721 | 37.0145 | 6.1519 | 0.8384 | 1.2673 | 8.2576 | 13.59% | 1.852% | 2.799% | 18.24%
C | C | somerset | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 35.3333 | 45.2721 | 32.8421 | 10.2053 | 0.94809 | 1.2766 | 12.43 | 22.54% | 2.094% | 2.82% | 27.46%
C | C | somerset | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 66.6666 | 85.4191 | 62.4271 | 18.7671 | 0.7298 | 3.4951 | 22.992 | 21.97% | 0.8544% | 4.092% | 26.92%
C | C | somerset | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 35.3333 | 45.2721 | 34.3468 | 8.7731 | 0.83777 | 1.3144 | 10.9253 | 19.38% | 1.851% | 2.903% | 24.13%
C | C | somerset | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 35.3333 | 45.2721 | 36.8298 | 6.1519 | 0.8384 | 1.4521 | 8.4423 | 13.59% | 1.852% | 3.207% | 18.65%
C | C | somerset | 2030 | Initial | Pro-rata | IE Solar not priority | 4 | 5.1251 | 4.6259 | 0.40522 | 0.06628 | 0.027743 | 0.49925 | 7.907% | 1.293% | 0.5413% | 9.741%
C | C | sliabh bawn | 2035 | 100% ECP | Pro-rata | IE wind priority | 58 | 186.1428 | 178.7131 | 0 | 1.7495 | 5.6802 | 7.4297 | 0% | 0.9399% | 3.052% | 3.991%
C | C | sliabh bawn | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 58 | 186.1428 | 181.7638 | 0 | 3.1595 | 1.2195 | 4.379 | 0% | 1.697% | 0.6551% | 2.352%
C | C | sliabh bawn | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 58 | 186.1428 | 184.2254 | 0 | 1.5444 | 0.37305 | 1.9175 | 0% | 0.8297% | 0.2004% | 1.03%
C | C | sliabh bawn | 2035 | 66% ECP | Pro-rata | IE wind priority | 58 | 186.1428 | 180.8232 | 0 | 1.5444 | 3.7753 | 5.3197 | 0% | 0.8297% | 2.028% | 2.858%
C | C | somerset | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 35.3333 | 45.2721 | 35.5445 | 7.5038 | 0.84471 | 1.3791 | 9.7276 | 16.57% | 1.866% | 3.046% | 21.49%
C | C | sliabh bawn | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 58 | 186.1428 | 175.8869 | 0 | 6.6834 | 3.5726 | 10.256 | 0% | 3.59% | 1.919% | 5.51%
C | C | somerset | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 98 | 125.5661 | 86.4245 | 27.6093 | 1.1379 | 10.3944 | 39.1417 | 21.99% | 0.9062% | 8.278% | 31.17%
C | C | stonestown | 2030 | Initial | Pro-rata | IE wind not priority | 105 | 336.9827 | 238.4701 | 38.1861 | 5.956 | 54.3705 | 98.5126 | 11.33% | 1.767% | 16.13% | 29.23%
C | J Country | mullingar | 2030 | 33% ECP | Pro-rata | IE wind not priority | 38.8333 | 124.63 | 90.5136 | 19.4852 | 2.1461 | 12.4851 | 34.1164 | 15.63% | 1.722% | 10.02% | 27.37%
C | J Country | mullingar | 2030 | Initial | Pro-rata | IE Solar not priority | 12 | 15.3754 | 12.1742 | 1.2157 | 0.19884 | 1.7867 | 3.2013 | 7.907% | 1.293% | 11.62% | 20.82%
C | J Country | mullingar | 2030 | Initial | Pro-rata | IE wind not priority | 9.5 | 30.4889 | 22.9262 | 3.4549 | 0.53888 | 3.5689 | 7.5627 | 11.33% | 1.767% | 11.71% | 24.8%
C | C | stonestown | 2035 | 100% ECP | Pro-rata | IE wind not priority | 105 | 336.9827 | 267.7841 | 57.79 | 1.1256 | 10.2831 | 69.1986 | 17.15% | 0.334% | 3.052% | 20.53%
C | C | stonestown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 105 | 336.9827 | 235.9612 | 96.8009 | 2.0129 | 2.2077 | 101.0215 | 28.73% | 0.5973% | 0.6551% | 29.98%
C | C | stonestown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 105 | 336.9827 | 283.0342 | 52.2413 | 1.0319 | 0.67535 | 53.9485 | 15.5% | 0.3062% | 0.2004% | 16.01%
C | C | stonestown | 2035 | 66% ECP | Pro-rata | IE wind not priority | 105 | 336.9827 | 276.875 | 52.2413 | 1.0319 | 6.8345 | 60.1077 | 15.5% | 0.3062% | 2.028% | 17.84%
C | C | stonestown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 105 | 336.9827 | 237.29 | 87.4702 | 5.7549 | 6.4676 | 99.6927 | 25.96% | 1.708% | 1.919% | 29.58%
C | C | stonestown | 2030 | 100% ECP | Pro-rata | IE wind not priority | 105 | 336.9827 | 231.5647 | 87.4702 | 5.7549 | 12.1928 | 105.4179 | 25.96% | 1.708% | 3.618% | 31.28%
C | C | stonestown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 105 | 336.9827 | 255.5037 | 52.6854 | 5.8027 | 22.9908 | 81.4789 | 15.63% | 1.722% | 6.823% | 24.18%
C | C | stonestown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 105 | 336.9827 | 198.978 | 102.2354 | 6.0271 | 29.7421 | 138.0047 | 30.34% | 1.789% | 8.826% | 40.95%
C | C | stonestown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 105 | 336.9827 | 206.9655 | 95.3984 | 5.9614 | 28.6574 | 130.0172 | 28.31% | 1.769% | 8.504% | 38.58%
C | C | stonestown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 105 | 336.9827 | 230.8312 | 73.5544 | 5.9262 | 26.6709 | 106.1515 | 21.83% | 1.759% | 7.915% | 31.5%
C | C | stonestown | 2030 | 33% ECP | Pro-rata | IE wind not priority | 105 | 336.9827 | 250.7342 | 52.6854 | 5.8027 | 27.7604 | 86.2485 | 15.63% | 1.722% | 8.238% | 25.59%
D | D and E North | ardnacrusha | 2030 | 33% ECP | Pro-rata | IE wind not priority | 98.7332 | 306.7052 | 248.5631 | 51.4559 | 5.1786 | 1.5075 | 58.142 | 16.78% | 1.688% | 0.4915% | 18.96%
C | C | derrycarney | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 296.1664 | 379.4741 | 277.3322 | 83.3729 | 3.2421 | 15.5269 | 102.1419 | 21.97% | 0.8544% | 4.092% | 26.92%
C | C | derrycarney | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 296.1664 | 379.4741 | 310.9637 | 58.1281 | 2.736 | 7.6463 | 68.5104 | 15.32% | 0.721% | 2.015% | 18.05%
C | C | athlone | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 127.39 | 408.8402 | 287.8892 | 106.1222 | 6.9821 | 7.8467 | 120.951 | 25.96% | 1.708% | 1.919% | 29.58%
C | C | athlone | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 132.99 | 170.3984 | 102.5149 | 53.7733 | 3.7542 | 10.356 | 67.8835 | 31.56% | 2.203% | 6.078% | 39.84%
C | C | athlone | 2030 | 100% ECP | Pro-rata | IE wind not priority | 127.39 | 408.8402 | 280.9432 | 106.1222 | 6.9821 | 14.7928 | 127.8971 | 25.96% | 1.708% | 3.618% | 31.28%
C | C | athlone | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 46.9966 | 60.2162 | 49.2328 | 8.1826 | 1.1151 | 1.6857 | 10.9834 | 13.59% | 1.852% | 2.799% | 18.24%
C | C | athlone | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 42.4633 | 136.2799 | 103.3289 | 21.3066 | 2.3467 | 9.2978 | 32.9511 | 15.63% | 1.722% | 6.823% | 24.18%
C | C | athlone | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 46.9966 | 60.2162 | 43.6831 | 13.574 | 1.2611 | 1.698 | 16.533 | 22.54% | 2.094% | 2.82% | 27.46%
C | C | athlone | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 42.4633 | 136.2799 | 80.4692 | 41.3452 | 2.4375 | 12.0281 | 55.8108 | 30.34% | 1.789% | 8.826% | 40.95%
C | C | athlone | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 46.9966 | 60.2162 | 45.6845 | 11.6691 | 1.1143 | 1.7482 | 14.5317 | 19.38% | 1.851% | 2.903% | 24.13%
C | C | athlone | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 42.4633 | 136.2799 | 83.6994 | 38.5803 | 2.4109 | 11.5894 | 52.5805 | 28.31% | 1.769% | 8.504% | 38.58%
C | C | athlone | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 46.9966 | 60.2162 | 47.2775 | 9.9808 | 1.1235 | 1.8343 | 12.9386 | 16.57% | 1.866% | 3.046% | 21.49%
C | C | athlone | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 42.4633 | 136.2799 | 93.351 | 29.7463 | 2.3966 | 10.786 | 42.929 | 21.83% | 1.759% | 7.915% | 31.5%
C | C | athlone | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 46.9966 | 60.2162 | 48.987 | 8.1826 | 1.1151 | 1.9314 | 11.2291 | 13.59% | 1.852% | 3.207% | 18.65%
C | C | athlone | 2030 | 33% ECP | Pro-rata | IE wind not priority | 42.4633 | 136.2799 | 101.4 | 21.3066 | 2.3467 | 11.2266 | 34.88 | 15.63% | 1.722% | 8.238% | 25.59%
C | C | athlone | 2030 | Initial | Pro-rata | IE Solar not priority | 4 | 5.1251 | 4.6259 | 0.40522 | 0.06628 | 0.027743 | 0.49925 | 7.907% | 1.293% | 0.5413% | 9.741%
C | C | athlone | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 132.99 | 170.3984 | 103.1337 | 53.7733 | 3.7542 | 9.7371 | 67.2646 | 31.56% | 2.203% | 5.714% | 39.47%
C | C | athlone | 2035 | 66% ECP | Pro-rata | IE wind not priority | 84.9266 | 272.5599 | 223.9433 | 42.254 | 0.83462 | 5.5279 | 48.6166 | 15.5% | 0.3062% | 2.028% | 17.84%
C | C | carrick on shannon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 2.3 | 7.3815 | 4.3586 | 2.2394 | 0.13202 | 0.65149 | 3.023 | 30.34% | 1.789% | 8.826% | 40.95%
C | C | carrick on shannon | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 6.6567 | 8.5291 | 6.4708 | 1.6528 | 0.15783 | 0.24762 | 2.0583 | 19.38% | 1.851% | 2.903% | 24.13%
C | C | carrick on shannon | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 2.3 | 7.3815 | 4.5335 | 2.0897 | 0.13058 | 0.62773 | 2.848 | 28.31% | 1.769% | 8.504% | 38.58%
C | C | carrick on shannon | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 6.6567 | 8.5291 | 6.6964 | 1.4137 | 0.15914 | 0.25981 | 1.8326 | 16.57% | 1.866% | 3.046% | 21.49%
C | C | carrick on shannon | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 2.3 | 7.3815 | 5.0563 | 1.6112 | 0.12981 | 0.58422 | 2.3252 | 21.83% | 1.759% | 7.915% | 31.5%
C | C | carrick on shannon | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 6.6567 | 8.5291 | 6.9386 | 1.159 | 0.15795 | 0.27357 | 1.5905 | 13.59% | 1.852% | 3.207% | 18.65%
C | C | carrick on shannon | 2030 | 33% ECP | Pro-rata | IE wind not priority | 2.3 | 7.3815 | 5.4923 | 1.1541 | 0.12711 | 0.60808 | 1.8893 | 15.63% | 1.722% | 8.238% | 25.59%
B | C | shantallow | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 35 | 44.845 | 30.8659 | 9.8605 | 0.40641 | 3.7123 | 13.9792 | 21.99% | 0.9062% | 8.278% | 31.17%
C | C | athlone | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 132.99 | 170.3984 | 117.2815 | 37.467 | 1.5442 | 14.1056 | 53.1168 | 21.99% | 0.9062% | 8.278% | 31.17%
C | C | athlone | 2035 | 100% ECP | Pro-rata | IE wind not priority | 127.39 | 408.8402 | 324.8858 | 70.113 | 1.3656 | 12.4759 | 83.9544 | 17.15% | 0.334% | 3.052% | 20.53%
C | C | athlone | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 89.9932 | 115.3072 | 84.2703 | 25.3337 | 0.98515 | 4.718 | 31.0369 | 21.97% | 0.8544% | 4.092% | 26.92%
C | C | athlone | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 84.9266 | 272.5599 | 190.8512 | 78.2949 | 1.6281 | 1.7857 | 81.7087 | 28.73% | 0.5973% | 0.6551% | 29.98%
C | C | athlone | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 89.9932 | 115.3072 | 94.4896 | 17.6628 | 0.83135 | 2.3234 | 20.8176 | 15.32% | 0.721% | 2.015% | 18.05%
C | C | athlone | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 84.9266 | 272.5599 | 228.925 | 42.254 | 0.83462 | 0.54624 | 43.6349 | 15.5% | 0.3062% | 0.2004% | 16.01%
C | C | athlone | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 89.9932 | 115.3072 | 89.3876 | 17.6628 | 0.83135 | 7.4254 | 25.9196 | 15.32% | 0.721% | 6.44% | 22.48%
B | C | shantallow | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 23.3333 | 29.8967 | 21.8495 | 6.5685 | 0.25543 | 1.2233 | 8.0472 | 21.97% | 0.8544% | 4.092% | 26.92%
B | C | shantallow | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 23.3333 | 29.8967 | 24.4991 | 4.5796 | 0.21555 | 0.60241 | 5.3976 | 15.32% | 0.721% | 2.015% | 18.05%
B | C | shantallow | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 23.3333 | 29.8967 | 23.1763 | 4.5796 | 0.21555 | 1.9252 | 6.7204 | 15.32% | 0.721% | 6.44% | 22.48%
B | C | cloon | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 103.98 | 133.2282 | 80.6365 | 42.0434 | 2.9353 | 7.6131 | 52.5917 | 31.56% | 2.203% | 5.714% | 39.47%
B | C | cloon | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 78.79 | 239.636 | 161.1732 | 69.6922 | 4.1713 | 4.5992 | 78.4628 | 29.08% | 1.741% | 1.919% | 32.74%
B | C | cloon | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 103.98 | 133.2282 | 80.1526 | 42.0434 | 2.9353 | 8.097 | 53.0756 | 31.56% | 2.203% | 6.078% | 39.84%
B | C | cloon | 2030 | 100% ECP | Pro-rata | IE wind not priority | 78.79 | 239.636 | 157.1019 | 69.6922 | 4.1713 | 8.6706 | 82.5341 | 29.08% | 1.741% | 3.618% | 34.44%
B | C | cloon | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 47.9933 | 61.4932 | 50.2769 | 8.3561 | 1.1388 | 1.7214 | 11.2163 | 13.59% | 1.852% | 2.799% | 18.24%
B | C | cloon | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 26.2633 | 79.8786 | 58.735 | 14.3099 | 1.3839 | 5.4498 | 21.1436 | 17.91% | 1.733% | 6.823% | 26.47%
B | C | cloon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 47.9933 | 61.4932 | 44.6095 | 13.8618 | 1.2878 | 1.734 | 16.8837 | 22.54% | 2.094% | 2.82% | 27.46%
B | C | cloon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 26.2633 | 79.8786 | 45.3014 | 26.1536 | 1.3735 | 7.0501 | 34.5772 | 32.74% | 1.72% | 8.826% | 43.29%
B | C | cloon | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 26.2633 | 79.8786 | 47.1044 | 24.5989 | 1.3823 | 6.793 | 32.7742 | 30.8% | 1.731% | 8.504% | 41.03%
B | C | cloon | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 47.9933 | 61.4932 | 48.2802 | 10.1924 | 1.1474 | 1.8732 | 13.213 | 16.57% | 1.866% | 3.046% | 21.49%
B | C | cloon | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 26.2633 | 79.8786 | 52.7558 | 19.394 | 1.4067 | 6.3221 | 27.1228 | 24.28% | 1.761% | 7.915% | 33.96%
B | C | cloon | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 47.9933 | 61.4932 | 50.0259 | 8.3561 | 1.1388 | 1.9724 | 11.4673 | 13.59% | 1.852% | 3.207% | 18.65%
B | C | cloon | 2030 | 33% ECP | Pro-rata | IE wind not priority | 26.2633 | 79.8786 | 57.6044 | 14.3099 | 1.3839 | 6.5803 | 22.2741 | 17.91% | 1.733% | 8.238% | 27.89%
B | C | cloon | 2030 | Initial | Pro-rata | IE Solar not priority | 20 | 25.6257 | 23.1295 | 2.0261 | 0.3314 | 0.13871 | 2.4962 | 7.907% | 1.293% | 0.5413% | 9.741%
B | C | cloon | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 47.9933 | 61.4932 | 46.6534 | 11.9166 | 1.1379 | 1.7853 | 14.8398 | 19.38% | 1.851% | 2.903% | 24.13%
C | C | carrick on shannon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 6.6567 | 8.5291 | 6.1873 | 1.9226 | 0.17862 | 0.24051 | 2.3418 | 22.54% | 2.094% | 2.82% | 27.46%
B | C | cloon | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 75.9866 | 97.3607 | 75.4752 | 14.9138 | 0.70196 | 6.2697 | 21.8854 | 15.32% | 0.721% | 6.44% | 22.48%
B | C | shantallow | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 35 | 44.845 | 27.1425 | 14.1519 | 0.98802 | 2.5626 | 17.7025 | 31.56% | 2.203% | 5.714% | 39.47%
B | C | shantallow | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 35 | 44.845 | 26.9796 | 14.1519 | 0.98802 | 2.7255 | 17.8654 | 31.56% | 2.203% | 6.078% | 39.84%
B | C | shantallow | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 11.6667 | 14.9483 | 12.2218 | 2.0313 | 0.27683 | 0.41846 | 2.7266 | 13.59% | 1.852% | 2.799% | 18.24%
B | C | shantallow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 11.6667 | 14.9483 | 10.8441 | 3.3697 | 0.31305 | 0.42152 | 4.1042 | 22.54% | 2.094% | 2.82% | 27.46%
B | C | shantallow | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 11.6667 | 14.9483 | 11.3409 | 2.8968 | 0.27662 | 0.43399 | 3.6074 | 19.38% | 1.851% | 2.903% | 24.13%
B | C | shantallow | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 11.6667 | 14.9483 | 11.7364 | 2.4777 | 0.27891 | 0.45536 | 3.2119 | 16.57% | 1.866% | 3.046% | 21.49%
B | C | cloon | 2035 | 66% ECP | Pro-rata | IE wind not priority | 52.5266 | 159.7572 | 128.1686 | 27.8561 | 0.49228 | 3.2401 | 31.5885 | 17.44% | 0.3081% | 2.028% | 19.77%
B | C | shantallow | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 11.6667 | 14.9483 | 12.1608 | 2.0313 | 0.27683 | 0.47946 | 2.7876 | 13.59% | 1.852% | 3.207% | 18.65%
B | C | cloon | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 103.98 | 133.2282 | 91.6981 | 29.2941 | 1.2074 | 11.0287 | 41.5301 | 21.99% | 0.9062% | 8.278% | 31.17%
B | C | cloon | 2035 | 100% ECP | Pro-rata | IE wind not priority | 78.79 | 239.636 | 185.1403 | 46.3697 | 0.81344 | 7.3126 | 54.4957 | 19.35% | 0.3394% | 3.052% | 22.74%
B | C | cloon | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 75.9866 | 97.3607 | 71.1544 | 21.3908 | 0.83182 | 3.9837 | 26.2063 | 21.97% | 0.8544% | 4.092% | 26.92%
B | C | cloon | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 52.5266 | 159.7572 | 108.7745 | 49.0085 | 0.92753 | 1.0466 | 50.9827 | 30.68% | 0.5806% | 0.6551% | 31.91%
B | C | cloon | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 75.9866 | 97.3607 | 79.7831 | 14.9138 | 0.70196 | 1.9618 | 17.5775 | 15.32% | 0.721% | 2.015% | 18.05%
B | C | cloon | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 52.5266 | 159.7572 | 131.0886 | 27.8561 | 0.49228 | 0.32017 | 28.6686 | 17.44% | 0.3081% | 0.2004% | 17.95%
C | C | derrycarney | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 34 | 109.1182 | 76.4065 | 31.345 | 0.65181 | 0.71488 | 32.7117 | 28.73% | 0.5973% | 0.6551% | 29.98%
C | C | carrick on shannon | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 2.3 | 7.3815 | 5.5967 | 1.1541 | 0.12711 | 0.50361 | 1.7848 | 15.63% | 1.722% | 6.823% | 24.18%
C | C | carrick on shannon | 2030 | 100% ECP | Pro-rata | IE wind not priority | 6.9 | 22.1446 | 15.2171 | 5.748 | 0.37818 | 0.80124 | 6.9275 | 25.96% | 1.708% | 3.618% | 31.28%
C | C | dallow | 2035 | 100% ECP | Pro-rata | IE wind priority | 9.99 | 32.0615 | 30.7818 | 0 | 0.30134 | 0.97836 | 1.2797 | 0% | 0.9399% | 3.052% | 3.991%
C | C | dallow | 2035 | 100% ECP | Pro-rata | IE wind not priority | 67.09 | 215.3159 | 171.1013 | 36.925 | 0.71917 | 6.5704 | 44.2146 | 17.15% | 0.334% | 3.052% | 20.53%
C | C | dallow | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 9.99 | 32.0615 | 31.3073 | 0 | 0.54419 | 0.21005 | 0.75424 | 0% | 1.697% | 0.6551% | 2.352%
C | C | dallow | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 44.7266 | 143.5438 | 100.5119 | 41.234 | 0.85745 | 0.94042 | 43.0319 | 28.73% | 0.5973% | 0.6551% | 29.98%
C | C | dallow | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 9.99 | 32.0615 | 31.7312 | 0 | 0.26601 | 0.064254 | 0.33027 | 0% | 0.8297% | 0.2004% | 1.03%
C | C | dallow | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 44.7266 | 143.5438 | 120.5635 | 22.2531 | 0.43955 | 0.28768 | 22.9803 | 15.5% | 0.3062% | 0.2004% | 16.01%
C | C | dallow | 2035 | 66% ECP | Pro-rata | IE wind priority | 9.99 | 32.0615 | 31.1452 | 0 | 0.26601 | 0.65025 | 0.91627 | 0% | 0.8297% | 2.028% | 2.858%
C | C | dallow | 2035 | 66% ECP | Pro-rata | IE wind not priority | 44.7266 | 143.5438 | 117.9398 | 22.2531 | 0.43955 | 2.9113 | 25.6039 | 15.5% | 0.3062% | 2.028% | 17.84%
C | C | dallow | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 9.99 | 32.0615 | 30.295 | 0 | 1.1512 | 0.61534 | 1.7665 | 0% | 3.59% | 1.919% | 5.51%
C | C | dallow | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 67.09 | 215.3159 | 151.617 | 55.8893 | 3.6771 | 4.1325 | 63.6989 | 25.96% | 1.708% | 1.919% | 29.58%
C | C | dallow | 2030 | 100% ECP | Pro-rata | IE wind priority | 9.99 | 32.0615 | 29.7503 | 0 | 1.1512 | 1.1601 | 2.3112 | 0% | 3.59% | 3.618% | 7.209%
C | C | derrycarney | 2030 | Initial | Pro-rata | IE wind not priority | 34 | 109.1182 | 77.2189 | 12.365 | 1.9286 | 17.6057 | 31.8993 | 11.33% | 1.767% | 16.13% | 29.23%
C | C | derrycarney | 2030 | 33% ECP | Pro-rata | IE wind not priority | 34 | 109.1182 | 81.1901 | 17.06 | 1.879 | 8.9891 | 27.9281 | 15.63% | 1.722% | 8.238% | 25.59%
C | C | derrycarney | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 148.0832 | 189.7371 | 154.3549 | 25.7827 | 3.5137 | 6.0857 | 35.3822 | 13.59% | 1.852% | 3.207% | 18.65%
C | C | derrycarney | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 34 | 109.1182 | 74.7453 | 23.8176 | 1.919 | 8.6363 | 34.3729 | 21.83% | 1.759% | 7.915% | 31.5%
C | C | derrycarney | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 34 | 109.1182 | 91.6492 | 16.9162 | 0.33414 | 0.21868 | 17.469 | 15.5% | 0.3062% | 0.2004% | 16.01%
C | C | derrycarney | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 296.1664 | 379.4741 | 294.1733 | 58.1281 | 2.736 | 24.4368 | 85.3008 | 15.32% | 0.721% | 6.44% | 22.48%
C | C | derrycarney | 2035 | 66% ECP | Pro-rata | IE wind not priority | 34 | 109.1182 | 89.6548 | 16.9162 | 0.33414 | 2.2131 | 19.4634 | 15.5% | 0.3062% | 2.028% | 17.84%
C | C | derrycarney | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 444.25 | 569.2117 | 344.5158 | 179.6284 | 12.5408 | 32.5267 | 224.6959 | 31.56% | 2.203% | 5.714% | 39.47%
C | C | derrycarney | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 34 | 109.1182 | 76.8368 | 28.3237 | 1.8635 | 2.0943 | 32.2814 | 25.96% | 1.708% | 1.919% | 29.58%
C | C | dallow | 2030 | 100% ECP | Pro-rata | IE wind not priority | 67.09 | 215.3159 | 147.9588 | 55.8893 | 3.6771 | 7.7906 | 67.357 | 25.96% | 1.708% | 3.618% | 31.28%
C | C | derrycarney | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 444.25 | 569.2117 | 342.4485 | 179.6284 | 12.5408 | 34.594 | 226.7632 | 31.56% | 2.203% | 6.078% | 39.84%
C | C | derrycarney | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 148.0832 | 189.7371 | 155.1292 | 25.7827 | 3.5137 | 5.3114 | 34.6079 | 13.59% | 1.852% | 2.799% | 18.24%
C | C | derrycarney | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 34 | 109.1182 | 82.7345 | 17.06 | 1.879 | 7.4446 | 26.3837 | 15.63% | 1.722% | 6.823% | 24.18%
C | C | derrycarney | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 148.0832 | 189.7371 | 137.6426 | 42.7707 | 3.9735 | 5.3503 | 52.0944 | 22.54% | 2.094% | 2.82% | 27.46%
C | C | derrycarney | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 34 | 109.1182 | 64.431 | 33.1048 | 1.9516 | 9.6308 | 44.6872 | 30.34% | 1.789% | 8.826% | 40.95%
C | C | derrycarney | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 148.0832 | 189.7371 | 143.9488 | 36.7686 | 3.5111 | 5.5086 | 45.7883 | 19.38% | 1.851% | 2.903% | 24.13%
C | C | derrycarney | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 34 | 109.1182 | 67.0174 | 30.8909 | 1.9304 | 9.2795 | 42.1008 | 28.31% | 1.769% | 8.504% | 38.58%
C | C | derrycarney | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 148.0832 | 189.7371 | 148.9683 | 31.4487 | 3.5402 | 5.7798 | 40.7687 | 16.57% | 1.866% | 3.046% | 21.49%
C | C | derrycarney | 2030 | 100% ECP | Pro-rata | IE wind not priority | 34 | 109.1182 | 74.9829 | 28.3237 | 1.8635 | 3.9481 | 34.1353 | 25.96% | 1.708% | 3.618% | 31.28%
C | C | dallow | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 9.99 | 32.0615 | 28.9033 | 0 | 0.97075 | 2.1874 | 3.1582 | 0% | 3.028% | 6.823% | 9.85%
C | C | dallow | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 22.3633 | 71.7719 | 54.4182 | 11.2211 | 1.2359 | 4.8967 | 17.3537 | 15.63% | 1.722% | 6.823% | 24.18%
C | C | dallow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 9.99 | 32.0615 | 27.9827 | 0 | 1.2491 | 2.8298 | 4.0788 | 0% | 3.896% | 8.826% | 12.72%
C | C | cregg | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 25 | 32.0321 | 26.0588 | 4.3527 | 0.5932 | 1.0274 | 5.9734 | 13.59% | 1.852% | 3.207% | 18.65%
C | C | carrick on shannon | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 19.97 | 25.5873 | 17.6112 | 5.6261 | 0.23188 | 2.1181 | 7.9761 | 21.99% | 0.9062% | 8.278% | 31.17%
C | C | carrick on shannon | 2035 | 100% ECP | Pro-rata | IE wind not priority | 6.9 | 22.1446 | 17.5972 | 3.7976 | 0.073965 | 0.67575 | 4.5473 | 17.15% | 0.334% | 3.052% | 20.53%
C | C | carrick on shannon | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 13.3133 | 17.0582 | 12.4667 | 3.7478 | 0.14574 | 0.69797 | 4.5915 | 21.97% | 0.8544% | 4.092% | 26.92%
C | C | carrick on shannon | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 4.6 | 14.763 | 10.3373 | 4.2408 | 0.088186 | 0.096719 | 4.4257 | 28.73% | 0.5973% | 0.6551% | 29.98%
C | C | cregg | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 25 | 32.0321 | 25.1494 | 5.3093 | 0.59767 | 0.97576 | 6.8827 | 16.57% | 1.866% | 3.046% | 21.49%
C | C | carrick on shannon | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 13.3133 | 17.0582 | 13.9785 | 2.613 | 0.12299 | 0.34372 | 3.0797 | 15.32% | 0.721% | 2.015% | 18.05%
C | C | carrick on shannon | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 13.3133 | 17.0582 | 13.2237 | 2.613 | 0.12299 | 1.0985 | 3.8345 | 15.32% | 0.721% | 6.44% | 22.48%
C | C | carrick on shannon | 2035 | 66% ECP | Pro-rata | IE wind not priority | 4.6 | 14.763 | 12.1297 | 2.2887 | 0.045207 | 0.29942 | 2.6333 | 15.5% | 0.3062% | 2.028% | 17.84%
C | C | carrick on shannon | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 19.97 | 25.5873 | 15.4867 | 8.0747 | 0.56374 | 1.4621 | 10.1006 | 31.56% | 2.203% | 5.714% | 39.47%
C | C | carrick on shannon | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 6.9 | 22.1446 | 15.5933 | 5.748 | 0.37818 | 0.42501 | 6.5512 | 25.96% | 1.708% | 1.919% | 29.58%
C | C | carrick on shannon | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 19.97 | 25.5873 | 15.3938 | 8.0747 | 0.56374 | 1.5551 | 10.1935 | 31.56% | 2.203% | 6.078% | 39.84%
C | C | carrick on shannon | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 4.6 | 14.763 | 12.3996 | 2.2887 | 0.045207 | 0.029587 | 2.3635 | 15.5% | 0.3062% | 0.2004% | 16.01%
C | C | carrick on shannon | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 6.6567 | 8.5291 | 6.9734 | 1.159 | 0.15795 | 0.23876 | 1.5557 | 13.59% | 1.852% | 2.799% | 18.24%
C | C | cregg | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 25 | 32.0321 | 24.302 | 6.2074 | 0.59276 | 0.92998 | 7.7302 | 19.38% | 1.851% | 2.903% | 24.13%
C | C | cregg | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 25 | 32.0321 | 26.1895 | 4.3527 | 0.5932 | 0.89669 | 5.8426 | 13.59% | 1.852% | 2.799% | 18.24%
C | C | dallow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 22.3633 | 71.7719 | 42.3791 | 21.7745 | 1.2837 | 6.3346 | 29.3928 | 30.34% | 1.789% | 8.826% | 40.95%
C | C | dallow | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 9.99 | 32.0615 | 28.1114 | 0 | 1.2236 | 2.7265 | 3.9501 | 0% | 3.816% | 8.504% | 12.32%
C | C | dallow | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 22.3633 | 71.7719 | 44.0803 | 20.3183 | 1.2697 | 6.1036 | 27.6916 | 28.31% | 1.769% | 8.504% | 38.58%
C | C | dallow | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 9.99 | 32.0615 | 28.423 | 0 | 1.101 | 2.5375 | 3.6385 | 0% | 3.434% | 7.915% | 11.35%
C | C | dallow | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 22.3633 | 71.7719 | 49.1633 | 15.6659 | 1.2622 | 5.6805 | 22.6086 | 21.83% | 1.759% | 7.915% | 31.5%
C | C | dallow | 2030 | 33% ECP | Pro-rata | IE wind priority | 9.99 | 32.0615 | 28.4495 | 0 | 0.97075 | 2.6412 | 3.612 | 0% | 3.028% | 8.238% | 11.27%
C | C | dallow | 2030 | 33% ECP | Pro-rata | IE wind not priority | 22.3633 | 71.7719 | 53.4023 | 11.2211 | 1.2359 | 5.9125 | 18.3695 | 15.63% | 1.722% | 8.238% | 25.59%
C | C | cregg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 25 | 32.0321 | 23.2374 | 7.2207 | 0.67082 | 0.90326 | 8.7948 | 22.54% | 2.094% | 2.82% | 27.46%
C | C | dallow | 2030 | Initial | Pro-rata | IE wind priority | 9.99 | 32.0615 | 26.0167 | 0 | 0.8718 | 5.173 | 6.0448 | 0% | 2.719% | 16.13% | 18.85%
C | C | cregg | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 75 | 96.0965 | 66.1412 | 21.1296 | 0.87087 | 7.9549 | 29.9554 | 21.99% | 0.9062% | 8.278% | 31.17%
C | C | cregg | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 49.9999 | 64.0643 | 46.8203 | 14.0753 | 0.54735 | 2.6213 | 17.244 | 21.97% | 0.8544% | 4.092% | 26.92%
C | C | cregg | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 49.9999 | 64.0643 | 52.4981 | 9.8134 | 0.46189 | 1.2909 | 11.5662 | 15.32% | 0.721% | 2.015% | 18.05%
C | C | cregg | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 49.9999 | 64.0643 | 49.6635 | 9.8134 | 0.46189 | 4.1255 | 14.4008 | 15.32% | 0.721% | 6.44% | 22.48%
C | C | cregg | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 75 | 96.0965 | 58.1625 | 30.3256 | 2.1172 | 5.4913 | 37.934 | 31.56% | 2.203% | 5.714% | 39.47%
C | C | cregg | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 75 | 96.0965 | 57.8135 | 30.3256 | 2.1172 | 5.8403 | 38.283 | 31.56% | 2.203% | 6.078% | 39.84%
B | C | cashla | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 311 | 398.4803 | 274.2654 | 87.6173 | 3.6112 | 32.9863 | 124.2149 | 21.99% | 0.9062% | 8.278% | 31.17%
D | D and E North | ardnacrusha | 2030 | 33% ECP | Pro-rata | IE wind priority | 7.5 | 23.298 | 22.4654 | 0 | 0.71812 | 0.11451 | 0.83263 | 0% | 3.082% | 0.4915% | 3.574%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 98.7332 | 306.7052 | 229.8841 | 70.5784 | 5.3476 | 0.8951 | 76.8211 | 23.01% | 1.744% | 0.2918% | 25.05%
E | D and E North | rathkeale | 2030 | Initial | Pro-rata | IE wind priority | 27.5 | 89.0367 | 86.1682 | 0 | 2.3759 | 0.49262 | 2.8685 | 0% | 2.668% | 0.5533% | 3.222%
E | D and E North | prospect | 2035 | 100% ECP | Pro-rata | IE wind not priority | 63 | 203.975 | 158.4778 | 36.0439 | 0.68028 | 8.773 | 45.4972 | 17.67% | 0.3335% | 4.301% | 22.31%
E | D and E North | prospect | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 42 | 135.9832 | 94.0321 | 39.7717 | 0.82141 | 1.3579 | 41.9511 | 29.25% | 0.604% | 0.9986% | 30.85%
E | D and E North | prospect | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 42 | 135.9832 | 112.4994 | 21.7112 | 0.41679 | 1.3558 | 23.4838 | 15.97% | 0.3065% | 0.997% | 17.27%
E | D and E North | prospect | 2035 | 66% ECP | Pro-rata | IE wind not priority | 42 | 135.9832 | 109.7064 | 21.7112 | 0.41679 | 4.1488 | 26.2768 | 15.97% | 0.3065% | 3.051% | 19.32%
E | D and E North | prospect | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 63 | 203.975 | 145.2022 | 54.4176 | 3.4565 | 0.89873 | 58.7727 | 26.68% | 1.695% | 0.4406% | 28.81%
E | D and E North | prospect | 2030 | 100% ECP | Pro-rata | IE wind not priority | 63 | 203.975 | 144.8688 | 54.4176 | 3.4565 | 1.2321 | 59.1062 | 26.68% | 1.695% | 0.6041% | 28.98%
E | D and E North | prospect | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 21 | 67.9916 | 55.7643 | 11.0304 | 1.1168 | 0.080033 | 12.2273 | 16.22% | 1.643% | 0.1177% | 17.98%
E | D and E North | prospect | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 21 | 67.9916 | 45.4741 | 21.0961 | 1.1729 | 0.24843 | 22.5174 | 31.03% | 1.725% | 0.3654% | 33.12%
E | D and E North | prospect | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 21 | 67.9916 | 46.9936 | 19.7038 | 1.1806 | 0.11365 | 20.998 | 28.98% | 1.736% | 0.1671% | 30.88%
E | D and E North | prospect | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 21 | 67.9916 | 51.4254 | 15.1958 | 1.172 | 0.19843 | 16.5662 | 22.35% | 1.724% | 0.2918% | 24.37%
E | D and E North | prospect | 2030 | 33% ECP | Pro-rata | IE wind not priority | 21 | 67.9916 | 55.5101 | 11.0304 | 1.1168 | 0.33419 | 12.4814 | 16.22% | 1.643% | 0.4915% | 18.36%
E | D and E North | rathkeale | 2030 | 33% ECP | Pro-rata | IE wind priority | 27.5 | 89.0367 | 85.9321 | 0 | 2.6669 | 0.43763 | 3.1046 | 0% | 2.995% | 0.4915% | 3.487%
E | D and E North | rathkeale | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 18 | 21.0746 | 17.6465 | 2.9201 | 0.39175 | 0.11615 | 3.428 | 13.86% | 1.859% | 0.5511% | 16.27%
E | D and E North | rathkeale | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 27.5 | 89.0367 | 85.7025 | 0 | 3.0744 | 0.25985 | 3.3342 | 0% | 3.453% | 0.2918% | 3.745%
E | D and E North | rathkeale | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 18 | 21.0746 | 17.0543 | 3.543 | 0.3985 | 0.078738 | 4.0203 | 16.81% | 1.891% | 0.3736% | 19.08%
E | D and E North | rathkeale | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 36 | 42.1491 | 35.1477 | 6.6916 | 0.30935 | 0.00043271 | 7.0014 | 15.88% | 0.7339% | 0.001027% | 16.61%
E | D and E North | rathkeale | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 27.5 | 89.0367 | 87.3892 | 0 | 0.75982 | 0.88773 | 1.6475 | 0% | 0.8534% | 0.997% | 1.85%
E | D and E North | rathkeale | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 36 | 42.1491 | 34.5721 | 6.6916 | 0.30935 | 0.5761 | 7.5771 | 15.88% | 0.7339% | 1.367% | 17.98%
E | D and E North | rathkeale | 2035 | 66% ECP | Pro-rata | IE wind priority | 27.5 | 89.0367 | 85.5604 | 0 | 0.75982 | 2.7164 | 3.4763 | 0% | 0.8534% | 3.051% | 3.904%
E | D and E North | rathkeale | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 54 | 63.2237 | 41.6518 | 20.0644 | 1.3878 | 0.11977 | 21.5719 | 31.74% | 2.195% | 0.1894% | 34.12%
E | D and E North | moneypoint | 2035 | 100% ECP | Pro-rata | IE wind priority | 17.25 | 55.8503 | 52.9023 | 0 | 0.5458 | 2.4021 | 2.9479 | 0% | 0.9773% | 4.301% | 5.278%
E | D and E North | rathkeale | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 27.5 | 89.0367 | 85.3796 | 0 | 3.2648 | 0.3923 | 3.6571 | 0% | 3.667% | 0.4406% | 4.107%
E | D and E North | rathkeale | 2030 | 100% ECP | Pro-rata | IE wind priority | 27.5 | 89.0367 | 85.2341 | 0 | 3.2648 | 0.53784 | 3.8026 | 0% | 3.667% | 0.6041% | 4.271%
E | D and E North | rathkeale | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 18 | 21.0746 | 17.7581 | 2.9201 | 0.39175 | 0.0046249 | 3.3165 | 13.86% | 1.859% | 0.02195% | 15.74%
E | D and E North | rathkeale | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 27.5 | 89.0367 | 86.265 | 0 | 2.6669 | 0.1048 | 2.7717 | 0% | 2.995% | 0.1177% | 3.113%
E | D and E North | rathkeale | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 18 | 21.0746 | 15.8052 | 4.797 | 0.44799 | 0.024425 | 5.2694 | 22.76% | 2.126% | 0.1159% | 25%
E | D and E North | rathkeale | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 27.5 | 89.0367 | 85.2527 | 0 | 3.4587 | 0.32533 | 3.784 | 0% | 3.885% | 0.3654% | 4.25%
E | D and E North | rathkeale | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 18 | 21.0746 | 16.4999 | 4.1246 | 0.39846 | 0.051601 | 4.5747 | 19.57% | 1.891% | 0.2448% | 21.71%
E | D and E North | rathkeale | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 27.5 | 89.0367 | 85.4713 | 0 | 3.4166 | 0.14882 | 3.5654 | 0% | 3.837% | 0.1671% | 4.004%
E | D and E North | rathkeale | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 54 | 63.2237 | 41.433 | 20.0644 | 1.3878 | 0.33858 | 21.7907 | 31.74% | 2.195% | 0.5355% | 34.47%
E | D and E North | moneypoint | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 17.25 | 55.8503 | 54.3258 | 0 | 0.96679 | 0.55773 | 1.5245 | 0% | 1.731% | 0.9986% | 2.73%
E | D and E North | moneypoint | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 17.25 | 55.8503 | 54.8168 | 0 | 0.47661 | 0.55685 | 1.0335 | 0% | 0.8534% | 0.997% | 1.85%
E | D and E North | moneypoint | 2035 | 66% ECP | Pro-rata | IE wind priority | 17.25 | 55.8503 | 53.6697 | 0 | 0.47661 | 1.704 | 2.1806 | 0% | 0.8534% | 3.051% | 3.904%
E | D and E North | limerick | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 1.65 | 1.9318 | 1.5633 | 0.32478 | 0.036529 | 0.0072177 | 0.36852 | 16.81% | 1.891% | 0.3736% | 19.08%
E | D and E North | limerick | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 1.65 | 1.9318 | 1.6176 | 0.26768 | 0.03591 | 0.010647 | 0.31424 | 13.86% | 1.859% | 0.5511% | 16.27%
E | D and E North | ballinknockane | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 50 | 58.5405 | 44.0335 | 13.1831 | 0.52833 | 0.79558 | 14.507 | 22.52% | 0.9025% | 1.359% | 24.78%
E | D and E North | ballinknockane | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 50 | 58.5405 | 44.3892 | 13.1348 | 0.50386 | 0.51266 | 14.1513 | 22.44% | 0.8607% | 0.8757% | 24.17%
E | D and E North | ballinknockane | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 50 | 58.5405 | 48.8163 | 9.2939 | 0.42966 | 0.00060098 | 9.7242 | 15.88% | 0.7339% | 0.001027% | 16.61%
E | D and E North | ballinknockane | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 50 | 58.5405 | 48.0168 | 9.2939 | 0.42966 | 0.80014 | 10.5237 | 15.88% | 0.7339% | 1.367% | 17.98%
E | D and E North | limerick | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 1.65 | 1.9318 | 1.5125 | 0.37809 | 0.036526 | 0.0047301 | 0.41934 | 19.57% | 1.891% | 0.2448% | 21.71%
E | D and E North | ballinknockane | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 50 | 58.5405 | 38.3639 | 18.5781 | 1.285 | 0.3135 | 20.1766 | 31.74% | 2.195% | 0.5355% | 34.47%
E | D and E North | ballinknockane | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 50 | 58.5405 | 49.328 | 8.1115 | 1.0882 | 0.012847 | 9.2125 | 13.86% | 1.859% | 0.02195% | 15.74%
E | D and E North | ballinknockane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 50 | 58.5405 | 43.9033 | 13.3249 | 1.2444 | 0.067847 | 14.6372 | 22.76% | 2.126% | 0.1159% | 25%
E | D and E North | ballinknockane | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 50 | 58.5405 | 45.8331 | 11.4572 | 1.1068 | 0.14334 | 12.7074 | 19.57% | 1.891% | 0.2448% | 21.71%
E | D and E North | ballinknockane | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 50 | 58.5405 | 47.3731 | 9.8417 | 1.1069 | 0.21872 | 11.1674 | 16.81% | 1.891% | 0.3736% | 19.08%
E | D and E North | ballinknockane | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 50 | 58.5405 | 49.0182 | 8.1115 | 1.0882 | 0.32264 | 9.5223 | 13.86% | 1.859% | 0.5511% | 16.27%
E | D and E North | ballinknockane | 2030 | Initial | Pro-rata | IE Solar not priority | 50 | 58.5405 | 52.2481 | 4.8416 | 0.7543 | 0.69646 | 6.2924 | 8.271% | 1.289% | 1.19% | 10.75%
E | D and E North | ballinknockane | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 50 | 58.5405 | 38.5665 | 18.5781 | 1.285 | 0.1109 | 19.974 | 31.74% | 2.195% | 0.1894% | 34.12%
E | D and E North | rathkeale | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 27.5 | 89.0367 | 86.6063 | 0 | 1.5413 | 0.88913 | 2.4304 | 0% | 1.731% | 0.9986% | 2.73%
E | D and E North | limerick | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 1.65 | 1.9318 | 1.4488 | 0.43972 | 0.041065 | 0.002239 | 0.48303 | 22.76% | 2.126% | 0.1159% | 25%
E | D and E North | limerick | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 3.798 | 1.8392 | 0.12721 | 0.031037 | 1.9975 | 31.74% | 2.195% | 0.5355% | 34.47%
E | D and E North | moneypoint | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 17.25 | 55.8503 | 53.5563 | 0 | 2.0479 | 0.24608 | 2.294 | 0% | 3.667% | 0.4406% | 4.107%
E | D and E North | moneypoint | 2030 | 100% ECP | Pro-rata | IE wind priority | 17.25 | 55.8503 | 53.465 | 0 | 2.0479 | 0.33737 | 2.3853 | 0% | 3.667% | 0.6041% | 4.271%
E | D and E North | moneypoint | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 17.25 | 55.8503 | 54.1117 | 0 | 1.6729 | 0.065741 | 1.7386 | 0% | 2.995% | 0.1177% | 3.113%
E | D and E North | moneypoint | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 17.25 | 55.8503 | 53.4767 | 0 | 2.1695 | 0.20407 | 2.3736 | 0% | 3.885% | 0.3654% | 4.25%
E | D and E North | moneypoint | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 17.25 | 55.8503 | 53.6138 | 0 | 2.1431 | 0.093353 | 2.2365 | 0% | 3.837% | 0.1671% | 4.004%
E | D and E North | moneypoint | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 17.25 | 55.8503 | 53.7588 | 0 | 1.9285 | 0.163 | 2.0915 | 0% | 3.453% | 0.2918% | 3.745%
E | D and E North | limerick | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 1.65 | 1.9318 | 1.6278 | 0.26768 | 0.03591 | 0.00042395 | 0.30401 | 13.86% | 1.859% | 0.02195% | 15.74%
E | D and E North | moneypoint | 2030 | 33% ECP | Pro-rata | IE wind priority | 17.25 | 55.8503 | 53.9029 | 0 | 1.6729 | 0.27451 | 1.9474 | 0% | 2.995% | 0.4915% | 3.487%
E | D and E North | limerick | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.3593 | 1.3051 | 0.052305 | 0.078762 | 1.4362 | 22.52% | 0.9025% | 1.359% | 24.78%
E | D and E North | limerick | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 3.3 | 3.8637 | 2.9297 | 0.8669 | 0.033254 | 0.033835 | 0.93399 | 22.44% | 0.8607% | 0.8757% | 24.17%
E | D and E North | limerick | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 3.3 | 3.8637 | 3.2219 | 0.6134 | 0.028357 | 3.9665e-05 | 0.64179 | 15.88% | 0.7339% | 0.001027% | 16.61%
E | D and E North | limerick | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 3.3 | 3.8637 | 3.1691 | 0.6134 | 0.028357 | 0.052809 | 0.69456 | 15.88% | 0.7339% | 1.367% | 17.98%
E | D and E North | limerick | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 3.8181 | 1.8392 | 0.12721 | 0.010979 | 1.9774 | 31.74% | 2.195% | 0.1894% | 34.12%
E | D and E North | moneypoint | 2030 | Initial | Pro-rata | IE wind priority | 17.25 | 55.8503 | 54.051 | 0 | 1.4903 | 0.30901 | 1.7993 | 0% | 2.668% | 0.5533% | 3.222%
E | D and E North | rathkeale | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 36 | 42.1491 | 31.9602 | 9.4571 | 0.36278 | 0.36911 | 10.1889 | 22.44% | 0.8607% | 0.8757% | 24.17%
E | D and E North | rathkeale | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 54 | 63.2237 | 47.5562 | 14.2378 | 0.5706 | 0.85922 | 15.6676 | 22.52% | 0.9025% | 1.359% | 24.78%
E | E,F & I | ballyvouskil 220 | 2035 | 100% ECP | Pro-rata | IE wind not priority | 164.4 | 532.2776 | 358.5795 | 94.0575 | 1.7752 | 77.8654 | 173.698 | 17.67% | 0.3335% | 14.63% | 32.63%
E | E,F & I | ballyvouskil 220 | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 12.5 | 14.6351 | 10.1826 | 3.2837 | 0.12596 | 1.0428 | 4.4525 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | ballyvouskil 220 | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 123.5999 | 400.1792 | 254.4736 | 117.0425 | 2.4173 | 26.2459 | 145.7057 | 29.25% | 0.604% | 6.559% | 36.41%
E | E,F & I | ballyvouskil 220 | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 12.5 | 14.6351 | 11.4992 | 2.3235 | 0.10741 | 0.70502 | 3.1359 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | ballyvouskil 220 | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 123.5999 | 400.1792 | 296.0002 | 63.893 | 1.2265 | 39.0595 | 104.179 | 15.97% | 0.3065% | 9.76% | 26.03%
E | E,F & I | ballyvouskil 220 | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 12.5 | 14.6351 | 10.6699 | 2.3235 | 0.10741 | 1.5344 | 3.9652 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | ballyvouskil 220 | 2035 | 66% ECP | Pro-rata | IE wind not priority | 123.5999 | 400.1792 | 278.5886 | 63.893 | 1.2265 | 56.4711 | 121.5906 | 15.97% | 0.3065% | 14.11% | 30.38%
E | E,F & I | ballyvouskil 220 | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 12.5 | 14.6351 | 9.5461 | 4.6445 | 0.32124 | 0.12326 | 5.089 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | ballyvouskil 220 | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 164.4 | 532.2776 | 362.7184 | 142.0039 | 9.0197 | 18.5356 | 169.5592 | 26.68% | 1.695% | 3.482% | 31.86%
E | E,F & I | ballyvouskil 220 | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 12.5 | 14.6351 | 9.4154 | 4.6445 | 0.32124 | 0.25394 | 5.2197 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | ballyvouskil 220 | 2030 | 100% ECP | Pro-rata | IE wind not priority | 164.4 | 532.2776 | 355.5962 | 142.0039 | 9.0197 | 25.6578 | 176.6814 | 26.68% | 1.695% | 4.82% | 33.19%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 12.5 | 14.6351 | 11.9271 | 2.0279 | 0.27205 | 0.40813 | 2.708 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 82.8 | 268.0813 | 211.042 | 43.4915 | 4.4034 | 9.1444 | 57.0393 | 16.22% | 1.643% | 3.411% | 21.28%
E | E,F & I | ballyvouskil 220 | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 12.5 | 14.6351 | 9.932 | 3.2958 | 0.13208 | 1.2753 | 4.7031 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | boggeragh | 2030 | Initial | Pro-rata | IE wind not priority | 23.35 | 75.6003 | 58.3818 | 9.0242 | 1.2691 | 6.9251 | 17.2184 | 11.94% | 1.679% | 9.16% | 22.78%
E | E,F & I | boggeragh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 8.0667 | 9.4445 | 7.6969 | 1.3086 | 0.17556 | 0.26338 | 1.7476 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | boggeragh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 142.7 | 462.0195 | 432.4209 | 0 | 13.839 | 15.7597 | 29.5986 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | boggeragh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 23.35 | 75.6003 | 59.5149 | 12.2648 | 1.2418 | 2.5788 | 16.0854 | 16.22% | 1.643% | 3.411% | 21.28%
E | E,F & I | boggeragh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 8.0667 | 9.4445 | 6.8181 | 2.1498 | 0.20076 | 0.27592 | 2.6264 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | boggeragh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 142.7 | 462.0195 | 421.467 | 0 | 17.9474 | 22.6051 | 40.5525 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | boggeragh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 23.35 | 75.6003 | 47.1403 | 23.4569 | 1.3042 | 3.6989 | 28.4599 | 31.03% | 1.725% | 4.893% | 37.65%
E | E,F & I | boggeragh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 8.0667 | 9.4445 | 7.0451 | 1.8484 | 0.17857 | 0.37238 | 2.3994 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 12.5 | 14.6351 | 10.5652 | 3.3312 | 0.3111 | 0.42756 | 4.0699 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | boggeragh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 142.7 | 462.0195 | 427.1995 | 0 | 17.7291 | 17.0909 | 34.82 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | boggeragh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 8.0667 | 9.4445 | 7.2165 | 1.5878 | 0.17859 | 0.46167 | 2.2281 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | boggeragh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 142.7 | 462.0195 | 424.3934 | 0 | 15.9532 | 21.673 | 37.6261 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | boggeragh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 23.35 | 75.6003 | 53.8545 | 16.8963 | 1.3031 | 3.5463 | 21.7458 | 22.35% | 1.724% | 4.691% | 28.76%
E | E,F & I | boggeragh | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 8.0667 | 9.4445 | 7.4397 | 1.3086 | 0.17556 | 0.52058 | 2.0048 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | boggeragh | 2030 | 33% ECP | Pro-rata | IE wind priority | 142.7 | 462.0195 | 421.615 | 0 | 13.839 | 26.5656 | 40.4046 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | boggeragh | 2030 | 33% ECP | Pro-rata | IE wind not priority | 23.35 | 75.6003 | 57.7467 | 12.2648 | 1.2418 | 4.3469 | 17.8535 | 16.22% | 1.643% | 5.75% | 23.62%
E | E,F & I | boggeragh | 2030 | Initial | Pro-rata | IE wind priority | 142.7 | 462.0195 | 407.3691 | 0 | 12.3286 | 42.3218 | 54.6504 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | boggeragh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 23.35 | 75.6003 | 49.5822 | 21.9088 | 1.3127 | 2.7966 | 26.018 | 28.98% | 1.736% | 3.699% | 34.42%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 82.8 | 268.0813 | 167.1613 | 83.179 | 4.6246 | 13.1164 | 100.9199 | 31.03% | 1.725% | 4.893% | 37.65%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 12.5 | 14.6351 | 10.9171 | 2.8643 | 0.27671 | 0.57704 | 3.7181 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 82.8 | 268.0813 | 175.8203 | 77.6893 | 4.6549 | 9.9168 | 92.2609 | 28.98% | 1.736% | 3.699% | 34.42%
E | E,F & I | athea | 2030 | 100% ECP | Pro-rata | IE wind priority | 34.35 | 111.2149 | 101.7759 | 0 | 4.078 | 5.361 | 9.439 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | athea | 2030 | 100% ECP | Pro-rata | IE wind not priority | 23.15 | 74.9527 | 50.0733 | 19.9963 | 1.2701 | 3.613 | 24.8794 | 26.68% | 1.695% | 4.82% | 33.19%
E | E,F & I | athea | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 34.35 | 111.2149 | 104.0901 | 0 | 3.3312 | 3.7936 | 7.1248 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | athea | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 23.15 | 74.9527 | 59.0051 | 12.1598 | 1.2312 | 2.5567 | 15.9476 | 16.22% | 1.643% | 3.411% | 21.28%
E | E,F & I | athea | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 34.35 | 111.2149 | 101.4533 | 0 | 4.3202 | 5.4414 | 9.7616 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | athea | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 23.15 | 74.9527 | 46.7366 | 23.256 | 1.293 | 3.6672 | 28.2162 | 31.03% | 1.725% | 4.893% | 37.65%
E | E,F & I | athea | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 34.35 | 111.2149 | 102.8332 | 0 | 4.2676 | 4.114 | 8.3817 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | athea | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 23.15 | 74.9527 | 51.0762 | 19.9963 | 1.2701 | 2.6101 | 23.8765 | 26.68% | 1.695% | 3.482% | 31.86%
E | E,F & I | athea | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 23.15 | 74.9527 | 49.1575 | 21.7211 | 1.3015 | 2.7726 | 25.7952 | 28.98% | 1.736% | 3.699% | 34.42%
E | E,F & I | athea | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 23.15 | 74.9527 | 53.3932 | 16.7516 | 1.292 | 3.516 | 21.5595 | 22.35% | 1.724% | 4.691% | 28.76%
E | E,F & I | athea | 2030 | 33% ECP | Pro-rata | IE wind priority | 34.35 | 111.2149 | 101.489 | 0 | 3.3312 | 6.3947 | 9.726 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | athea | 2030 | 33% ECP | Pro-rata | IE wind not priority | 23.15 | 74.9527 | 57.2521 | 12.1598 | 1.2312 | 4.3097 | 17.7006 | 16.22% | 1.643% | 5.75% | 23.62%
E | E,F & I | athea | 2030 | Initial | Pro-rata | IE wind priority | 34.35 | 111.2149 | 98.0598 | 0 | 2.9677 | 10.1875 | 13.1552 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | athea | 2030 | Initial | Pro-rata | IE wind not priority | 23.15 | 74.9527 | 57.8818 | 8.9469 | 1.2582 | 6.8658 | 17.0709 | 11.94% | 1.679% | 9.16% | 22.78%
E | E,F & I | athea | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 34.35 | 111.2149 | 102.1578 | 0 | 3.8402 | 5.217 | 9.0572 | 0% | 3.453% | 4.691% | 8.144%
E | D and E North | rathkeale | 2035 | 100% ECP | Pro-rata | IE wind priority | 27.5 | 89.0367 | 84.3371 | 0 | 0.87012 | 3.8295 | 4.6996 | 0% | 0.9773% | 4.301% | 5.278%
E | E,F & I | athea | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 34.35 | 111.2149 | 103.264 | 0 | 4.078 | 3.8729 | 7.9509 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 12.5 | 14.6351 | 11.1826 | 2.4604 | 0.27674 | 0.7154 | 3.4526 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 82.8 | 268.0813 | 190.9699 | 59.915 | 4.6209 | 12.5755 | 77.1114 | 22.35% | 1.724% | 4.691% | 28.76%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 12.5 | 14.6351 | 11.5285 | 2.0279 | 0.27205 | 0.80669 | 3.1066 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | ballyvouskil 220 | 2030 | 33% ECP | Pro-rata | IE wind not priority | 82.8 | 268.0813 | 204.772 | 43.4915 | 4.4034 | 15.4144 | 63.3093 | 16.22% | 1.643% | 5.75% | 23.62%
E | E,F & I | ballyvouskil 220 | 2030 | Initial | Pro-rata | IE Solar not priority | 12.5 | 14.6351 | 11.0221 | 1.2104 | 0.18857 | 2.214 | 3.613 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | ballyvouskil 220 | 2030 | Initial | Pro-rata | IE wind not priority | 42 | 135.9833 | 105.0123 | 16.232 | 2.2827 | 12.4563 | 30.971 | 11.94% | 1.679% | 9.16% | 22.78%
E | E,F & I | athea | 2035 | 100% ECP | Pro-rata | IE wind not priority | 23.15 | 74.9527 | 50.4934 | 13.2447 | 0.24998 | 10.9646 | 24.4593 | 17.67% | 0.3335% | 14.63% | 32.63%
E | E,F & I | athea | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 34.35 | 111.2149 | 101.9957 | 0 | 1.9252 | 7.2941 | 9.2192 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | athea | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 23.15 | 74.9527 | 47.6624 | 21.9218 | 0.45275 | 4.9158 | 27.2904 | 29.25% | 0.604% | 6.559% | 36.41%
E | E,F & I | athea | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 34.35 | 111.2149 | 99.4107 | 0 | 0.94908 | 10.8551 | 11.8042 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | athea | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 23.15 | 74.9527 | 55.4402 | 11.967 | 0.22973 | 7.3158 | 19.5125 | 15.97% | 0.3065% | 9.76% | 26.03%
E | E,F & I | athea | 2035 | 66% ECP | Pro-rata | IE wind priority | 34.35 | 111.2149 | 94.5718 | 0 | 0.94908 | 15.694 | 16.6431 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | athea | 2035 | 66% ECP | Pro-rata | IE wind not priority | 23.15 | 74.9527 | 52.179 | 11.967 | 0.22973 | 10.5769 | 22.7737 | 15.97% | 0.3065% | 14.11% | 30.38%
E | E,F & I | athea | 2035 | 100% ECP | Pro-rata | IE wind priority | 34.35 | 111.2149 | 93.8588 | 0 | 1.0869 | 16.2693 | 17.3562 | 0% | 0.9773% | 14.63% | 15.61%
D | D and E North | ardnacrusha | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 39.673 | 46.4495 | 38.8939 | 6.4361 | 0.86343 | 0.256 | 7.5556 | 13.86% | 1.859% | 0.5511% | 16.27%
D | D and E North | tullabrack | 2035 | 100% ECP | Pro-rata | IE wind not priority | 31.5 | 97.8517 | 75.2819 | 18.0265 | 0.33469 | 4.2086 | 22.5698 | 18.42% | 0.342% | 4.301% | 23.07%
D | D and E North | booltiagh | 2035 | 66% ECP | Pro-rata | IE wind priority | 31.45 | 97.6964 | 93.8606 | 0 | 0.85512 | 2.9806 | 3.8358 | 0% | 0.8753% | 3.051% | 3.926%
D | D and E North | booltiagh | 2035 | 66% ECP | Pro-rata | IE wind not priority | 148.579 | 461.5461 | 369.3154 | 76.6659 | 1.4833 | 14.0815 | 92.2307 | 16.61% | 0.3214% | 3.051% | 19.98%
D | D and E North | booltiagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 31.45 | 97.6964 | 93.6338 | 0 | 3.6321 | 0.43046 | 4.0626 | 0% | 3.718% | 0.4406% | 4.158%
D | D and E North | booltiagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 164.579 | 511.2486 | 358.8507 | 141.4739 | 8.6714 | 2.2526 | 152.3979 | 27.67% | 1.696% | 0.4406% | 29.81%
D | D and E North | booltiagh | 2030 | 100% ECP | Pro-rata | IE wind priority | 31.45 | 97.6964 | 93.4741 | 0 | 3.6321 | 0.59015 | 4.2223 | 0% | 3.718% | 0.6041% | 4.322%
D | D and E North | booltiagh | 2030 | 100% ECP | Pro-rata | IE wind not priority | 164.579 | 511.2486 | 358.015 | 141.4739 | 8.6714 | 3.0883 | 153.2336 | 27.67% | 1.696% | 0.6041% | 29.97%
D | D and E North | booltiagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 31.45 | 97.6964 | 94.5701 | 0 | 3.0113 | 0.115 | 3.1263 | 0% | 3.082% | 0.1177% | 3.2%
D | D and E North | booltiagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 132.579 | 411.8437 | 335.3101 | 69.095 | 6.9538 | 0.48478 | 76.5336 | 16.78% | 1.688% | 0.1177% | 18.58%
D | D and E North | booltiagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 31.45 | 97.6964 | 93.5119 | 0 | 3.8275 | 0.35697 | 4.1845 | 0% | 3.918% | 0.3654% | 4.283%
D | D and E North | booltiagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 132.579 | 411.8437 | 273.7235 | 129.4813 | 7.1341 | 1.5048 | 138.1202 | 31.44% | 1.732% | 0.3654% | 33.54%
D | D and E North | booltiagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 31.45 | 97.6964 | 93.7528 | 0 | 3.7803 | 0.1633 | 3.9436 | 0% | 3.869% | 0.1671% | 4.037%
D | D and E North | booltiagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 132.579 | 411.8437 | 282.7145 | 121.2819 | 7.1589 | 0.68839 | 129.1292 | 29.45% | 1.738% | 0.1671% | 31.35%
D | D and E North | booltiagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 31.45 | 97.6964 | 93.9677 | 0 | 3.4436 | 0.28512 | 3.7287 | 0% | 3.525% | 0.2918% | 3.817%
D | D and E North | booltiagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 148.579 | 461.5461 | 378.7951 | 76.6659 | 1.4833 | 4.6018 | 82.751 | 16.61% | 0.3214% | 0.997% | 17.93%
D | D and E North | booltiagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 31.45 | 97.6964 | 95.8672 | 0 | 0.85512 | 0.97407 | 1.8292 | 0% | 0.8753% | 0.997% | 1.872%
D | D and E North | booltiagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 148.579 | 461.5461 | 316.8569 | 137.33 | 2.7502 | 4.6091 | 144.6893 | 29.75% | 0.5959% | 0.9986% | 31.35%
D | D and E North | booltiagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 31.45 | 97.6964 | 95.0541 | 0 | 1.6667 | 0.97561 | 2.6423 | 0% | 1.706% | 0.9986% | 2.705%
D | D and E North | coolshamroge | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 60 | 70.2486 | 52.8402 | 15.8197 | 0.634 | 0.95469 | 17.4084 | 22.52% | 0.9025% | 1.359% | 24.78%
D | D and E North | coolshamroge | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 40 | 46.8324 | 35.5113 | 10.5078 | 0.40308 | 0.41012 | 11.321 | 22.44% | 0.8607% | 0.8757% | 24.17%
D | D and E North | coolshamroge | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 40 | 46.8324 | 39.053 | 7.4351 | 0.34372 | 0.00048078 | 7.7793 | 15.88% | 0.7339% | 0.001027% | 16.61%
D | D and E North | coolshamroge | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 40 | 46.8324 | 38.4134 | 7.4351 | 0.34372 | 0.64011 | 8.419 | 15.88% | 0.7339% | 1.367% | 17.98%
D | D and E North | coolshamroge | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 60 | 70.2486 | 46.2798 | 22.2937 | 1.542 | 0.13308 | 23.9688 | 31.74% | 2.195% | 0.1894% | 34.12%
D | D and E North | coolshamroge | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 60 | 70.2486 | 46.0367 | 22.2937 | 1.542 | 0.3762 | 24.2119 | 31.74% | 2.195% | 0.5355% | 34.47%
D | D and E North | booltiagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 132.579 | 411.8437 | 308.6883 | 94.7727 | 7.1808 | 1.2019 | 103.1554 | 23.01% | 1.744% | 0.2918% | 25.05%
D | D and E North | coolshamroge | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 20 | 23.4162 | 19.7312 | 3.2446 | 0.43527 | 0.0051388 | 3.685 | 13.86% | 1.859% | 0.02195% | 15.74%
D | D and E North | coolshamroge | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 20 | 23.4162 | 18.3332 | 4.5829 | 0.44274 | 0.057334 | 5.083 | 19.57% | 1.891% | 0.2448% | 21.71%
D | D and E North | coolshamroge | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 20 | 23.4162 | 18.9492 | 3.9367 | 0.44278 | 0.087487 | 4.467 | 16.81% | 1.891% | 0.3736% | 19.08%
D | D and E North | coolshamroge | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 20 | 23.4162 | 19.6073 | 3.2446 | 0.43527 | 0.12906 | 3.8089 | 13.86% | 1.859% | 0.5511% | 16.27%
D | D and E North | booltiagh | 2035 | 100% ECP | Pro-rata | IE wind priority | 31.45 | 97.6964 | 92.5328 | 0 | 0.96161 | 4.202 | 5.1636 | 0% | 0.9843% | 4.301% | 5.285%
D | D and E North | booltiagh | 2035 | 100% ECP | Pro-rata | IE wind not priority | 164.579 | 511.2486 | 393.3274 | 94.1836 | 1.7487 | 21.989 | 117.9212 | 18.42% | 0.342% | 4.301% | 23.07%
D | D and E North | coolshamroge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 20 | 23.4162 | 17.5613 | 5.33 | 0.49776 | 0.027139 | 5.8549 | 22.76% | 2.126% | 0.1159% | 25%
D | D and E North | booltiagh | 2030 | 33% ECP | Pro-rata | IE wind priority | 31.45 | 97.6964 | 94.2049 | 0 | 3.0113 | 0.48019 | 3.4915 | 0% | 3.082% | 0.4915% | 3.574%
D | D and E North | booltiagh | 2030 | 33% ECP | Pro-rata | IE wind not priority | 132.579 | 411.8437 | 333.7706 | 69.095 | 6.9538 | 2.0243 | 78.0731 | 16.78% | 1.688% | 0.4915% | 18.96%
D | D and E North | booltiagh | 2030 | Initial | Pro-rata | IE wind priority | 31.45 | 97.6964 | 94.4912 | 0 | 2.6647 | 0.54053 | 3.2052 | 0% | 2.727% | 0.5533% | 3.281%
D | D and E North | ardnacrusha | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 7.5 | 23.298 | 22.3292 | 0 | 0.86617 | 0.10265 | 0.96882 | 0% | 3.718% | 0.4406% | 4.158%
D | D and E North | ardnacrusha | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 296.2 | 920.1165 | 645.8393 | 254.6168 | 15.6063 | 4.0541 | 274.2772 | 27.67% | 1.696% | 0.4406% | 29.81%
D | D and E North | ardnacrusha | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 119.019 | 139.3486 | 91.3207 | 44.223 | 3.0587 | 0.74626 | 48.028 | 31.74% | 2.195% | 0.5355% | 34.47%
D | D and E North | ardnacrusha | 2030 | 100% ECP | Pro-rata | IE wind priority | 7.5 | 23.298 | 22.2911 | 0 | 0.86617 | 0.14074 | 1.0069 | 0% | 3.718% | 0.6041% | 4.322%
D | D and E North | ardnacrusha | 2030 | 100% ECP | Pro-rata | IE wind not priority | 296.2 | 920.1165 | 644.3353 | 254.6168 | 15.6063 | 5.5581 | 275.7812 | 27.67% | 1.696% | 0.6041% | 29.97%
D | D and E North | ardnacrusha | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 39.673 | 46.4495 | 39.1398 | 6.4361 | 0.86343 | 0.010194 | 7.3097 | 13.86% | 1.859% | 0.02195% | 15.74%
D | D and E North | ardnacrusha | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 7.5 | 23.298 | 22.5525 | 0 | 0.71812 | 0.027424 | 0.74554 | 0% | 3.082% | 0.1177% | 3.2%
D | D and E North | ardnacrusha | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 119.019 | 139.3486 | 91.8029 | 44.223 | 3.0587 | 0.26398 | 47.5457 | 31.74% | 2.195% | 0.1894% | 34.12%
D | D and E North | ardnacrusha | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 98.7332 | 306.7052 | 249.7096 | 51.4559 | 5.1786 | 0.36102 | 56.9956 | 16.78% | 1.688% | 0.1177% | 18.58%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 7.5 | 23.298 | 22.3001 | 0 | 0.91275 | 0.085129 | 0.99788 | 0% | 3.918% | 0.3654% | 4.283%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 98.7332 | 306.7052 | 203.8453 | 96.4263 | 5.3129 | 1.1207 | 102.8599 | 31.44% | 1.732% | 0.3654% | 33.54%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 39.673 | 46.4495 | 36.3667 | 9.0908 | 0.87823 | 0.11373 | 10.0828 | 19.57% | 1.891% | 0.2448% | 21.71%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 7.5 | 23.298 | 22.3576 | 0 | 0.90151 | 0.038942 | 0.94045 | 0% | 3.869% | 0.1671% | 4.037%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 98.7332 | 306.7052 | 210.541 | 90.3202 | 5.3314 | 0.51265 | 96.1642 | 29.45% | 1.738% | 0.1671% | 31.35%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 39.673 | 46.4495 | 37.5886 | 7.809 | 0.87831 | 0.17354 | 8.8609 | 16.81% | 1.891% | 0.3736% | 19.08%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 7.5 | 23.298 | 22.4088 | 0 | 0.8212 | 0.067994 | 0.88919 | 0% | 3.525% | 0.2918% | 3.817%
D | D and E North | ardnacrusha | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 39.673 | 46.4495 | 34.8355 | 10.5728 | 0.98739 | 0.053834 | 11.614 | 22.76% | 2.126% | 0.1159% | 25%
D | D and E North | booltiagh | 2030 | Initial | Pro-rata | IE wind not priority | 116.579 | 362.1413 | 310.1624 | 43.7428 | 6.2324 | 2.0037 | 51.9789 | 12.08% | 1.721% | 0.5533% | 14.35%
D | D and E North | ardnacrusha | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 119.019 | 139.3486 | 104.8164 | 31.3808 | 1.2576 | 1.8938 | 34.5322 | 22.52% | 0.9025% | 1.359% | 24.78%
D | D and E North | ardnacrusha | 2035 | 100% ECP | Pro-rata | IE wind priority | 7.5 | 23.298 | 22.0666 | 0 | 0.22932 | 1.0021 | 1.2314 | 0% | 0.9843% | 4.301% | 5.285%
D | D and E North | ardnacrusha | 2035 | 100% ECP | Pro-rata | IE wind not priority | 296.2 | 920.1165 | 707.8885 | 169.5063 | 3.1472 | 39.5745 | 212.228 | 18.42% | 0.342% | 4.301% | 23.07%
D | D and E North | ardnacrusha | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 79.3459 | 92.899 | 70.442 | 20.8439 | 0.79958 | 0.81354 | 22.457 | 22.44% | 0.8607% | 0.8757% | 24.17%
D | D and E North | ardnacrusha | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 197.4665 | 613.4104 | 421.1135 | 182.5162 | 3.6551 | 6.1256 | 192.2969 | 29.75% | 0.5959% | 0.9986% | 31.35%
D | D and E North | ardnacrusha | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 79.3459 | 92.899 | 77.4675 | 14.7487 | 0.68183 | 0.00095371 | 15.4315 | 15.88% | 0.7339% | 0.001027% | 16.61%
D | D and E North | ardnacrusha | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 7.5 | 23.298 | 22.8618 | 0 | 0.20392 | 0.23229 | 0.43621 | 0% | 0.8753% | 0.997% | 1.872%
D | D and E North | ardnacrusha | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 197.4665 | 613.4104 | 503.4315 | 101.8916 | 1.9714 | 6.1159 | 109.9789 | 16.61% | 0.3214% | 0.997% | 17.93%
D | D and E North | ardnacrusha | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 79.3459 | 92.899 | 76.1987 | 14.7487 | 0.68183 | 1.2698 | 16.7003 | 15.88% | 0.7339% | 1.367% | 17.98%
D | D and E North | ardnacrusha | 2035 | 66% ECP | Pro-rata | IE wind priority | 7.5 | 23.298 | 22.3833 | 0 | 0.20392 | 0.71081 | 0.91473 | 0% | 0.8753% | 3.051% | 3.926%
D | D and E North | ardnacrusha | 2035 | 66% ECP | Pro-rata | IE wind not priority | 197.4665 | 613.4104 | 490.8327 | 101.8916 | 1.9714 | 18.7147 | 122.5777 | 16.61% | 0.3214% | 3.051% | 19.98%
D | D and E North | ardnacrusha | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 7.5 | 23.298 | 22.6679 | 0 | 0.39745 | 0.23266 | 0.63011 | 0% | 1.706% | 0.9986% | 2.705%
D | D and E North | tullabrack | 2035 | 100% ECP | Pro-rata | IE wind priority | 13.8 | 42.8684 | 40.6026 | 0 | 0.42195 | 1.8438 | 2.2657 | 0% | 0.9843% | 4.301% | 5.285%
D | D and E North | derrybrien | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 23.3333 | 29.8967 | 25.1157 | 4.0626 | 0.55366 | 0.16477 | 4.781 | 13.59% | 1.852% | 0.5511% | 15.99%
D | D and E North | derrybrien | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 23.3333 | 29.8967 | 23.4766 | 5.7936 | 0.55324 | 0.073202 | 6.42 | 19.38% | 1.851% | 0.2448% | 21.47%
D | D and E North | tullabrack | 2030 | 33% ECP | Pro-rata | IE wind priority | 13.8 | 42.8684 | 41.3363 | 0 | 1.3213 | 0.2107 | 1.532 | 0% | 3.082% | 0.4915% | 3.574%
D | D and E North | tullabrack | 2030 | 33% ECP | Pro-rata | IE wind not priority | 10.5 | 32.6172 | 26.434 | 5.4722 | 0.55073 | 0.16032 | 6.1832 | 16.78% | 1.688% | 0.4915% | 18.96%
D | D and E North | tullabrack | 2030 | Initial | Pro-rata | IE wind priority | 13.8 | 42.8684 | 41.4619 | 0 | 1.1692 | 0.23718 | 1.4064 | 0% | 2.727% | 0.5533% | 3.281%
D | D and E North | slievecallan | 2035 | 100% ECP | Pro-rata | IE wind priority | 71.875 | 223.2727 | 211.472 | 0 | 2.1976 | 9.603 | 11.8007 | 0% | 0.9843% | 4.301% | 5.285%
D | D and E North | slievecallan | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 71.875 | 223.2727 | 217.2341 | 0 | 3.8089 | 2.2296 | 6.0386 | 0% | 1.706% | 0.9986% | 2.705%
D | D and E North | slievecallan | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 71.875 | 223.2727 | 219.0923 | 0 | 1.9543 | 2.2261 | 4.1804 | 0% | 0.8753% | 0.997% | 1.872%
D | D and E North | slievecallan | 2035 | 66% ECP | Pro-rata | IE wind priority | 71.875 | 223.2727 | 214.5065 | 0 | 1.9543 | 6.8119 | 8.7662 | 0% | 0.8753% | 3.051% | 3.926%
D | D and E North | slievecallan | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 71.875 | 223.2727 | 213.9882 | 0 | 8.3008 | 0.98376 | 9.2845 | 0% | 3.718% | 0.4406% | 4.158%
D | D and E North | slievecallan | 2030 | 100% ECP | Pro-rata | IE wind priority | 71.875 | 223.2727 | 213.6232 | 0 | 8.3008 | 1.3487 | 9.6495 | 0% | 3.718% | 0.6041% | 4.322%
D | D and E North | slievecallan | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 71.875 | 223.2727 | 216.1279 | 0 | 6.882 | 0.26281 | 7.1448 | 0% | 3.082% | 0.1177% | 3.2%
D | D and E North | slievecallan | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 71.875 | 223.2727 | 213.7096 | 0 | 8.7472 | 0.81581 | 9.563 | 0% | 3.918% | 0.3654% | 4.283%
D | D and E North | slievecallan | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 71.875 | 223.2727 | 214.2601 | 0 | 8.6394 | 0.3732 | 9.0126 | 0% | 3.869% | 0.1671% | 4.037%
D | D and E North | slievecallan | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 71.875 | 223.2727 | 214.7513 | 0 | 7.8698 | 0.65161 | 8.5214 | 0% | 3.525% | 0.2918% | 3.817%
D | D and E North | tullabrack | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 10.5 | 32.6172 | 24.4475 | 7.5058 | 0.56871 | 0.095191 | 8.1697 | 23.01% | 1.744% | 0.2918% | 25.05%
D | D and E North | tullabrack | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 13.8 | 42.8684 | 41.2322 | 0 | 1.511 | 0.12511 | 1.6361 | 0% | 3.525% | 0.2918% | 3.817%
D | D and E North | tullabrack | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 10.5 | 32.6172 | 22.3904 | 9.6053 | 0.56697 | 0.054519 | 10.2268 | 29.45% | 1.738% | 0.1671% | 31.35%
D | D and E North | tullabrack | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 13.8 | 42.8684 | 41.1379 | 0 | 1.6588 | 0.071654 | 1.7304 | 0% | 3.869% | 0.1671% | 4.037%
D | D and E North | tullabrack | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 13.8 | 42.8684 | 41.709 | 0 | 0.73131 | 0.42809 | 1.1594 | 0% | 1.706% | 0.9986% | 2.705%
D | D and E North | tullabrack | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 21 | 65.2344 | 44.7842 | 19.4101 | 0.38871 | 0.65144 | 20.4502 | 29.75% | 0.5959% | 0.9986% | 31.35%
D | D and E North | tullabrack | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 13.8 | 42.8684 | 42.0657 | 0 | 0.37522 | 0.42741 | 0.80263 | 0% | 0.8753% | 0.997% | 1.872%
D | D and E North | tullabrack | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 21 | 65.2344 | 53.5385 | 10.8359 | 0.20965 | 0.65041 | 11.6959 | 16.61% | 0.3214% | 0.997% | 17.93%
D | D and E North | tullabrack | 2035 | 66% ECP | Pro-rata | IE wind priority | 13.8 | 42.8684 | 41.1853 | 0 | 0.37522 | 1.3079 | 1.6831 | 0% | 0.8753% | 3.051% | 3.926%
D | D and E North | tullabrack | 2035 | 66% ECP | Pro-rata | IE wind not priority | 21 | 65.2344 | 52.1986 | 10.8359 | 0.20965 | 1.9903 | 13.0358 | 16.61% | 0.3214% | 3.051% | 19.98%
D | D and E North | slievecallan | 2030 | 33% ECP | Pro-rata | IE wind priority | 71.875 | 223.2727 | 215.2933 | 0 | 6.882 | 1.0974 | 7.9794 | 0% | 3.082% | 0.4915% | 3.574%
D | D and E North | tullabrack | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 31.5 | 97.8517 | 68.6831 | 27.0778 | 1.6597 | 0.43114 | 29.1686 | 27.67% | 1.696% | 0.4406% | 29.81%
D | D and E North | tullabrack | 2030 | 100% ECP | Pro-rata | IE wind priority | 13.8 | 42.8684 | 41.0157 | 0 | 1.5937 | 0.25895 | 1.8527 | 0% | 3.718% | 0.6041% | 4.322%
D | D and E North | tullabrack | 2030 | 100% ECP | Pro-rata | IE wind not priority | 31.5 | 97.8517 | 68.5232 | 27.0778 | 1.6597 | 0.59109 | 29.3285 | 27.67% | 1.696% | 0.6041% | 29.97%
D | D and E North | tullabrack | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 13.8 | 42.8684 | 41.4966 | 0 | 1.3213 | 0.05046 | 1.3718 | 0% | 3.082% | 0.1177% | 3.2%
D | D and E North | tullabrack | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 10.5 | 32.6172 | 26.5559 | 5.4722 | 0.55073 | 0.038394 | 6.0613 | 16.78% | 1.688% | 0.1177% | 18.58%
D | D and E North | tullabrack | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 13.8 | 42.8684 | 41.0323 | 0 | 1.6795 | 0.15664 | 1.8361 | 0% | 3.918% | 0.3654% | 4.283%
D | D and E North | tullabrack | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 10.5 | 32.6172 | 21.6784 | 10.2547 | 0.56501 | 0.11918 | 10.9388 | 31.44% | 1.732% | 0.3654% | 33.54%
D | D and E North | tullabrack | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 13.8 | 42.8684 | 41.0857 | 0 | 1.5937 | 0.18888 | 1.7826 | 0% | 3.718% | 0.4406% | 4.158%
D | D and E North | slievecallan | 2030 | Initial | Pro-rata | IE wind priority | 71.875 | 223.2727 | 215.9476 | 0 | 6.0898 | 1.2353 | 7.3251 | 0% | 2.727% | 0.5533% | 3.281%
D | D and E North | ennis | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 92.09 | 107.8199 | 81.1009 | 24.2806 | 0.97308 | 1.4653 | 26.719 | 22.52% | 0.9025% | 1.359% | 24.78%
D | D and E North | drumline | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 39.3966 | 46.126 | 38.8671 | 6.3913 | 0.85742 | 0.010123 | 7.2588 | 13.86% | 1.859% | 0.02195% | 15.74%
D | D and E North | drumline | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 39.3966 | 46.126 | 34.5928 | 10.4992 | 0.98051 | 0.053459 | 11.5331 | 22.76% | 2.126% | 0.1159% | 25%
D | D and E North | drumline | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 39.3966 | 46.126 | 36.1134 | 9.0275 | 0.87211 | 0.11294 | 10.0126 | 19.57% | 1.891% | 0.2448% | 21.71%
D | D and E North | drumline | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 39.3966 | 46.126 | 37.3268 | 7.7546 | 0.8722 | 0.17233 | 8.7991 | 16.81% | 1.891% | 0.3736% | 19.08%
D | D and E North | drumline | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 39.3966 | 46.126 | 38.623 | 6.3913 | 0.85742 | 0.25422 | 7.5029 | 13.86% | 1.859% | 0.5511% | 16.27%
D | D and E North | drumline | 2030 | Initial | Pro-rata | IE Solar not priority | 4 | 4.6832 | 4.1798 | 0.38733 | 0.060344 | 0.055717 | 0.50339 | 8.271% | 1.289% | 1.19% | 10.75%
D | D and E North | drumline | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 110.19 | 129.0116 | 84.5464 | 40.9425 | 2.8318 | 0.6909 | 44.4652 | 31.74% | 2.195% | 0.5355% | 34.47%
D | D and E North | derrybrien | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 70 | 89.6901 | 67.9374 | 19.7209 | 0.81281 | 1.2189 | 21.7527 | 21.99% | 0.9062% | 1.359% | 24.25%
D | D and E North | derrybrien | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 46.6666 | 59.7933 | 50.2024 | 9.1592 | 0.4311 | 0.00061384 | 9.5909 | 15.32% | 0.721% | 0.001027% | 16.04%
D | D and E North | derrybrien | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 46.6666 | 59.7933 | 49.3858 | 9.1592 | 0.4311 | 0.81726 | 10.4076 | 15.32% | 0.721% | 1.367% | 17.41%
D | D and E North | derrybrien | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 70 | 89.6901 | 59.2403 | 28.3039 | 1.976 | 0.1699 | 30.4498 | 31.56% | 2.203% | 0.1894% | 33.95%
D | D and E North | derrybrien | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 70 | 89.6901 | 58.9299 | 28.3039 | 1.976 | 0.48032 | 30.7602 | 31.56% | 2.203% | 0.5355% | 34.3%
D | D and E North | derrybrien | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 23.3333 | 29.8967 | 25.2739 | 4.0626 | 0.55366 | 0.0065609 | 4.6228 | 13.59% | 1.852% | 0.02195% | 15.46%
D | D and E North | derrybrien | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 23.3333 | 29.8967 | 22.4966 | 6.7393 | 0.6261 | 0.03465 | 7.4001 | 22.54% | 2.094% | 0.1159% | 24.75%
D | D and E North | derrybrien | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 46.6666 | 59.7933 | 45.6219 | 13.137 | 0.51086 | 0.52363 | 14.1715 | 21.97% | 0.8544% | 0.8757% | 23.7%
D | D and E North | derrybrien | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 23.3333 | 29.8967 | 24.2718 | 4.9553 | 0.55783 | 0.1117 | 5.6249 | 16.57% | 1.866% | 0.3736% | 18.81%
D | D and E North | drumline | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 110.19 | 129.0116 | 84.9929 | 40.9425 | 2.8318 | 0.24439 | 44.0187 | 31.74% | 2.195% | 0.1894% | 34.12%
D | D and E North | drumline | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 74.7933 | 87.5687 | 71.8267 | 13.9024 | 0.64271 | 1.1969 | 15.742 | 15.88% | 0.7339% | 1.367% | 17.98%
D | D and E North | ennis | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 67.4933 | 79.0218 | 59.9194 | 17.7302 | 0.68014 | 0.69202 | 19.1024 | 22.44% | 0.8607% | 0.8757% | 24.17%
D | D and E North | ennis | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 67.4933 | 79.0218 | 65.8955 | 12.5455 | 0.57998 | 0.00081124 | 13.1263 | 15.88% | 0.7339% | 0.001027% | 16.61%
D | D and E North | ennis | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 67.4933 | 79.0218 | 64.8162 | 12.5455 | 0.57998 | 1.0801 | 14.2056 | 15.88% | 0.7339% | 1.367% | 17.98%
D | D and E North | ennis | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 92.09 | 107.8199 | 71.0318 | 34.2172 | 2.3667 | 0.20425 | 36.7881 | 31.74% | 2.195% | 0.1894% | 34.12%
D | D and E North | ennis | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 92.09 | 107.8199 | 70.6586 | 34.2172 | 2.3667 | 0.57741 | 37.1613 | 31.74% | 2.195% | 0.5355% | 34.47%
D | D and E North | ennis | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 42.8966 | 50.2238 | 42.3201 | 6.9591 | 0.93359 | 0.011022 | 7.9037 | 13.86% | 1.859% | 0.02195% | 15.74%
D | D and E North | ennis | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 42.8966 | 50.2238 | 37.6661 | 11.4319 | 1.0676 | 0.058208 | 12.5577 | 22.76% | 2.126% | 0.1159% | 25%
D | D and E North | ennis | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 42.8966 | 50.2238 | 40.6429 | 8.4435 | 0.94968 | 0.18764 | 9.5809 | 16.81% | 1.891% | 0.3736% | 19.08%
D | D and E North | ennis | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 42.8966 | 50.2238 | 42.0543 | 6.9591 | 0.93359 | 0.2768 | 8.1695 | 13.86% | 1.859% | 0.5511% | 16.27%
D | D and E North | ennis | 2030 | Initial | Pro-rata | IE Solar not priority | 18.3 | 21.4258 | 19.1228 | 1.772 | 0.27607 | 0.2549 | 2.303 | 8.271% | 1.289% | 1.19% | 10.75%
D | D and E North | drumline | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 110.19 | 129.0116 | 97.041 | 29.0529 | 1.1643 | 1.7533 | 31.9706 | 22.52% | 0.9025% | 1.359% | 24.78%
D | D and E North | drumline | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 74.7933 | 87.5687 | 66.4002 | 19.6479 | 0.7537 | 0.76686 | 21.1685 | 22.44% | 0.8607% | 0.8757% | 24.17%
D | D and E North | drumline | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 74.7933 | 87.5687 | 73.0227 | 13.9024 | 0.64271 | 0.00089899 | 14.546 | 15.88% | 0.7339% | 0.001027% | 16.61%
D | D and E North | ennis | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 42.8966 | 50.2238 | 39.3217 | 9.8295 | 0.94959 | 0.12297 | 10.9021 | 19.57% | 1.891% | 0.2448% | 21.71%
E | E,F & I | boggeragh | 2030 | 100% ECP | Pro-rata | IE wind not priority | 23.35 | 75.6003 | 50.5059 | 20.169 | 1.2811 | 3.6442 | 25.0943 | 26.68% | 1.695% | 4.82% | 33.19%
B | C | cashla | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 207.3331 | 265.6532 | 194.1481 | 58.3657 | 2.2697 | 10.8697 | 71.5051 | 21.97% | 0.8544% | 4.092% | 26.92%
B | C | cashla | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 207.3331 | 265.6532 | 205.9378 | 40.693 | 1.9153 | 17.1071 | 59.7154 | 15.32% | 0.721% | 6.44% | 22.48%
A | A, B North | meentycat | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 84.96 | 245.7654 | 197.7728 | 0 | 9.8024 | 38.1901 | 47.9925 | 0% | 3.989% | 15.54% | 19.53%
A | A, B North | meentycat | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 84.96 | 245.7654 | 199.7477 | 0 | 9.6375 | 36.3802 | 46.0176 | 0% | 3.921% | 14.8% | 18.72%
A | A, B North | meentycat | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 84.96 | 245.7654 | 195.2613 | 0 | 8.79 | 41.714 | 50.504 | 0% | 3.577% | 16.97% | 20.55%
A | A, B North | meentycat | 2030 | 33% ECP | Pro-rata | IE wind priority | 84.96 | 245.7654 | 189.8989 | 0 | 7.8745 | 47.9919 | 55.8664 | 0% | 3.204% | 19.53% | 22.73%
A | A, B North | meentycat | 2030 | Initial | Pro-rata | IE wind priority | 84.96 | 245.7654 | 190.4497 | 0 | 6.9926 | 48.323 | 55.3156 | 0% | 2.845% | 19.66% | 22.51%
A | A, B North | letterkenny | 2035 | 100% ECP | Pro-rata | IE wind not priority | 170.4 | 492.9192 | 310.261 | 91.7971 | 1.7387 | 89.1224 | 182.6582 | 18.62% | 0.3527% | 18.08% | 37.06%
A | A, B North | letterkenny | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 120.2666 | 347.8973 | 210.9932 | 102.8082 | 2.014 | 32.0819 | 136.9041 | 29.55% | 0.5789% | 9.222% | 39.35%
A | A, B North | letterkenny | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 120.2666 | 347.8973 | 243.0983 | 58.5779 | 1.1044 | 45.1166 | 104.799 | 16.84% | 0.3175% | 12.97% | 30.12%
A | A, B North | letterkenny | 2035 | 66% ECP | Pro-rata | IE wind not priority | 120.2666 | 347.8973 | 237.6109 | 58.5779 | 1.1044 | 50.604 | 110.2864 | 16.84% | 0.3175% | 14.55% | 31.7%
A | A, B North | letterkenny | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 170.4 | 492.9192 | 250.5148 | 136.0683 | 8.4693 | 97.8668 | 242.4044 | 27.6% | 1.718% | 19.85% | 49.18%
A | A, B North | letterkenny | 2030 | 100% ECP | Pro-rata | IE wind not priority | 170.4 | 492.9192 | 243.4492 | 136.0683 | 8.4693 | 104.9324 | 249.47 | 27.6% | 1.718% | 21.29% | 50.61%
A | A, B North | letterkenny | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 70.1333 | 202.8758 | 129.8363 | 34.3844 | 3.5935 | 35.0616 | 73.0395 | 16.95% | 1.771% | 17.28% | 36%
A | A, B North | letterkenny | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 70.1333 | 202.8758 | 103.9052 | 63.8181 | 3.6271 | 31.5254 | 98.9706 | 31.46% | 1.788% | 15.54% | 48.78%
A | A, B North | meentycat | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 84.96 | 245.7654 | 195.4169 | 0 | 7.8745 | 42.474 | 50.3484 | 0% | 3.204% | 17.28% | 20.49%
A | A, B North | meentycat | 2030 | 100% ECP | Pro-rata | IE wind priority | 84.96 | 245.7654 | 184.2785 | 0 | 9.1685 | 52.3184 | 61.4869 | 0% | 3.731% | 21.29% | 25.02%
A | A, B North | meentycat | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 84.96 | 245.7654 | 187.8013 | 0 | 9.1685 | 48.7956 | 57.964 | 0% | 3.731% | 19.85% | 23.59%
A | A, B North | mulreavy | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 95.25 | 275.5314 | 237.347 | 0 | 2.4525 | 35.7319 | 38.1844 | 0% | 0.8901% | 12.97% | 13.86%
A | A, B North | mulreavy | 2035 | 66% ECP | Pro-rata | IE wind priority | 95.25 | 275.5314 | 233.001 | 0 | 2.4525 | 40.0779 | 42.5304 | 0% | 0.8901% | 14.55% | 15.44%
A | A, B North | mulreavy | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 95.25 | 275.5314 | 210.547 | 0 | 10.2789 | 54.7055 | 64.9844 | 0% | 3.731% | 19.85% | 23.59%
A | A, B North | mulreavy | 2030 | 100% ECP | Pro-rata | IE wind priority | 95.25 | 275.5314 | 206.5975 | 0 | 10.2789 | 58.655 | 68.9339 | 0% | 3.731% | 21.29% | 25.02%
A | A, B North | mulreavy | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 95.25 | 275.5314 | 219.085 | 0 | 8.8282 | 47.6182 | 56.4464 | 0% | 3.204% | 17.28% | 20.49%
A | A, B North | mulreavy | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 95.25 | 275.5314 | 221.7263 | 0 | 10.9896 | 42.8155 | 53.8052 | 0% | 3.989% | 15.54% | 19.53%
A | A, B North | letterkenny | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 70.1333 | 202.8758 | 109.669 | 59.5723 | 3.6032 | 30.0313 | 93.2068 | 29.36% | 1.776% | 14.8% | 45.94%
A | A, B North | mulreavy | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 95.25 | 275.5314 | 223.9403 | 0 | 10.8047 | 40.7864 | 51.5911 | 0% | 3.921% | 14.8% | 18.72%
A | A, B North | mulreavy | 2030 | 33% ECP | Pro-rata | IE wind priority | 95.25 | 275.5314 | 212.8987 | 0 | 8.8282 | 53.8045 | 62.6327 | 0% | 3.204% | 19.53% | 22.73%
A | A, B North | mulreavy | 2030 | Initial | Pro-rata | IE wind priority | 95.25 | 275.5314 | 213.5162 | 0 | 7.8395 | 54.1757 | 62.0152 | 0% | 2.845% | 19.66% | 22.51%
A | A, B North | meentycat | 2035 | 100% ECP | Pro-rata | IE wind priority | 84.96 | 245.7654 | 198.8441 | 0 | 2.4856 | 44.4357 | 46.9212 | 0% | 1.011% | 18.08% | 19.09%
A | A, B North | meentycat | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 84.96 | 245.7654 | 218.864 | 0 | 4.2377 | 22.6637 | 26.9014 | 0% | 1.724% | 9.222% | 10.95%
A | A, B North | meentycat | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 84.96 | 245.7654 | 211.706 | 0 | 2.1876 | 31.8718 | 34.0593 | 0% | 0.8901% | 12.97% | 13.86%
A | A, B North | meentycat | 2035 | 66% ECP | Pro-rata | IE wind priority | 84.96 | 245.7654 | 207.8295 | 0 | 2.1876 | 35.7483 | 37.9358 | 0% | 0.8901% | 14.55% | 15.44%
A | A, B North | mulreavy | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 95.25 | 275.5314 | 218.9106 | 0 | 9.8546 | 46.7663 | 56.6209 | 0% | 3.577% | 16.97% | 20.55%
A | A, B North | letterkenny | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 70.1333 | 202.8758 | 117.8576 | 46.9689 | 3.6149 | 34.4344 | 85.0182 | 23.15% | 1.782% | 16.97% | 41.91%
A | A, B North | letterkenny | 2030 | 33% ECP | Pro-rata | IE wind not priority | 70.1333 | 202.8758 | 125.2813 | 34.3844 | 3.5935 | 39.6167 | 77.5946 | 16.95% | 1.771% | 19.53% | 38.25%
A | A, B North | letterkenny | 2030 | Initial | Pro-rata | IE wind not priority | 20 | 57.8544 | 38.241 | 7.1975 | 1.0405 | 11.3755 | 19.6134 | 12.44% | 1.798% | 19.66% | 33.9%
A | A, B North | golagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 48 | 138.8505 | 70.5675 | 38.3291 | 2.3857 | 27.5681 | 68.2829 | 27.6% | 1.718% | 19.85% | 49.18%
A | A, B North | golagh | 2030 | 100% ECP | Pro-rata | IE wind not priority | 48 | 138.8505 | 68.5773 | 38.3291 | 2.3857 | 29.5584 | 70.2732 | 27.6% | 1.718% | 21.29% | 50.61%
A | A, B North | golagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 48 | 138.8505 | 88.8614 | 23.533 | 2.4595 | 23.9966 | 49.9891 | 16.95% | 1.771% | 17.28% | 36%
A | A, B North | golagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 48 | 138.8505 | 71.1139 | 43.6778 | 2.4824 | 21.5763 | 67.7366 | 31.46% | 1.788% | 15.54% | 48.78%
A | A, B North | golagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 48 | 138.8505 | 75.0587 | 40.7719 | 2.4661 | 20.5538 | 63.7918 | 29.36% | 1.776% | 14.8% | 45.94%
A | A, B North | golagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 48 | 138.8505 | 80.6631 | 32.1461 | 2.4741 | 23.5673 | 58.1874 | 23.15% | 1.782% | 16.97% | 41.91%
A | A, B North | golagh | 2030 | 33% ECP | Pro-rata | IE wind not priority | 48 | 138.8505 | 85.7439 | 23.533 | 2.4595 | 27.1141 | 53.1066 | 16.95% | 1.771% | 19.53% | 38.25%
A | A, B North | golagh | 2030 | Initial | Pro-rata | IE wind not priority | 48 | 138.8505 | 91.7784 | 17.2739 | 2.4971 | 27.3011 | 47.0721 | 12.44% | 1.798% | 19.66% | 33.9%
A | A, B North | garvagh | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 40 | 42.117 | 30.6196 | 9.2339 | 0.38692 | 1.8766 | 11.4974 | 21.92% | 0.9187% | 4.456% | 27.3%
A | A, B North | garvagh | 2035 | 100% ECP | Pro-rata | IE wind priority | 48 | 138.8505 | 112.3413 | 0 | 1.4043 | 25.1049 | 26.5092 | 0% | 1.011% | 18.08% | 19.09%
A | A, B North | garvagh | 2035 | 100% ECP | Pro-rata | IE wind not priority | 82 | 237.2029 | 149.304 | 44.1747 | 0.83669 | 42.8875 | 87.8989 | 18.62% | 0.3527% | 18.08% | 37.06%
A | A, B North | garvagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 40 | 42.117 | 31.2795 | 9.0849 | 0.36185 | 1.3907 | 10.8375 | 21.57% | 0.8592% | 3.302% | 25.73%
A | A, B North | garvagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 48 | 138.8505 | 123.652 | 0 | 2.3942 | 12.8043 | 15.1985 | 0% | 1.724% | 9.222% | 10.95%
A | A, B North | mulreavy | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 95.25 | 275.5314 | 245.3719 | 0 | 4.751 | 25.4086 | 30.1596 | 0% | 1.724% | 9.222% | 10.95%
A | A, B North | golagh | 2035 | 66% ECP | Pro-rata | IE wind not priority | 48 | 138.8505 | 94.8337 | 23.3792 | 0.44079 | 20.1968 | 44.0168 | 16.84% | 0.3175% | 14.55% | 31.7%
A | A, B North | golagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 48 | 138.8505 | 84.2102 | 41.0321 | 0.80381 | 12.8043 | 54.6403 | 29.55% | 0.5789% | 9.222% | 39.35%
A | A, B North | lenalea | 2035 | 100% ECP | Pro-rata | IE wind not priority | 102.1 | 295.3465 | 185.9017 | 55.0028 | 1.0418 | 53.4002 | 109.4448 | 18.62% | 0.3527% | 18.08% | 37.06%
A | A, B North | lenalea | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 78.1 | 225.9212 | 137.0169 | 66.7627 | 1.3079 | 20.8337 | 88.9042 | 29.55% | 0.5789% | 9.222% | 39.35%
A | A, B North | lenalea | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 78.1 | 225.9212 | 157.8657 | 38.0399 | 0.7172 | 29.2983 | 68.0554 | 16.84% | 0.3175% | 12.97% | 30.12%
A | A, B North | lenalea | 2035 | 66% ECP | Pro-rata | IE wind not priority | 78.1 | 225.9212 | 154.3022 | 38.0399 | 0.7172 | 32.8618 | 71.6189 | 16.84% | 0.3175% | 14.55% | 31.7%
A | A, B North | lenalea | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 102.1 | 295.3465 | 150.1031 | 81.5292 | 5.0746 | 58.6397 | 145.2435 | 27.6% | 1.718% | 19.85% | 49.18%
A | A, B North | golagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 48 | 138.8505 | 97.0238 | 23.3792 | 0.44079 | 18.0066 | 41.8267 | 16.84% | 0.3175% | 12.97% | 30.12%
A | A, B North | lenalea | 2030 | 100% ECP | Pro-rata | IE wind not priority | 102.1 | 295.3465 | 145.8695 | 81.5292 | 5.0746 | 62.8732 | 149.477 | 27.6% | 1.718% | 21.29% | 50.61%
A | A, B North | lenalea | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 54.1 | 156.496 | 80.1512 | 49.2285 | 2.7979 | 24.3183 | 76.3447 | 31.46% | 1.788% | 15.54% | 48.78%
A | A, B North | lenalea | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 54.1 | 156.496 | 84.5974 | 45.9533 | 2.7795 | 23.1658 | 71.8986 | 29.36% | 1.776% | 14.8% | 45.94%
A | A, B North | lenalea | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 54.1 | 156.496 | 90.914 | 36.2313 | 2.7885 | 26.5622 | 65.582 | 23.15% | 1.782% | 16.97% | 41.91%
A | A, B North | lenalea | 2030 | 33% ECP | Pro-rata | IE wind not priority | 54.1 | 156.496 | 96.6405 | 26.5237 | 2.772 | 30.5598 | 59.8555 | 16.95% | 1.771% | 19.53% | 38.25%
A | A, B North | lenalea | 2030 | Initial | Pro-rata | IE wind not priority | 30.1 | 87.0708 | 57.5527 | 10.8322 | 1.5659 | 17.1201 | 29.5181 | 12.44% | 1.798% | 19.66% | 33.9%
A | A, B North | golagh | 2035 | 100% ECP | Pro-rata | IE wind not priority | 48 | 138.8505 | 87.3975 | 25.8583 | 0.48977 | 25.1049 | 51.453 | 18.62% | 0.3527% | 18.08% | 37.06%
A | A, B North | lenalea | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 54.1 | 156.496 | 100.1542 | 26.5237 | 2.772 | 27.0461 | 56.3418 | 16.95% | 1.771% | 17.28% | 36%
A | A, B North | garvagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 66 | 190.9193 | 115.789 | 56.4192 | 1.1052 | 17.6059 | 75.1303 | 29.55% | 0.5789% | 9.222% | 39.35%
A | A, B North | mulreavy | 2035 | 100% ECP | Pro-rata | IE wind priority | 95.25 | 275.5314 | 222.9273 | 0 | 2.7866 | 49.8175 | 52.6041 | 0% | 1.011% | 18.08% | 19.09%
A | A, B North | sorne hill | 2030 | Initial | Pro-rata | IE wind priority | 48.1 | 139.1398 | 107.8229 | 0 | 3.9588 | 27.358 | 31.3169 | 0% | 2.845% | 19.66% | 22.51%
A | G North | gortawee | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 5 | 5.2646 | 3.497 | 1.6451 | 0.11558 | 0.0069198 | 1.7676 | 31.25% | 2.195% | 0.1314% | 33.58%
A | G North | gortawee | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 4.2 | 12.1494 | 8.565 | 3.3538 | 0.20875 | 0.021895 | 3.5844 | 27.6% | 1.718% | 0.1802% | 29.5%
A | G North | gortawee | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 5 | 5.2646 | 3.4267 | 1.6451 | 0.11558 | 0.077227 | 1.8379 | 31.25% | 2.195% | 1.467% | 34.91%
A | G North | gortawee | 2030 | 100% ECP | Pro-rata | IE wind not priority | 4.2 | 12.1494 | 8.2934 | 3.3538 | 0.20875 | 0.29351 | 3.8561 | 27.6% | 1.718% | 2.416% | 31.74%
A | G North | gortawee | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 1.6667 | 1.7549 | 1.4907 | 0.23138 | 0.032372 | 0.00043816 | 0.26419 | 13.19% | 1.845% | 0.02497% | 15.05%
A | G North | gortawee | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 1.4 | 4.0498 | 3.2831 | 0.68638 | 0.071734 | 0.0086199 | 0.76673 | 16.95% | 1.771% | 0.2128% | 18.93%
A | G North | gortawee | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 1.6667 | 1.7549 | 1.319 | 0.38621 | 0.036676 | 0.012955 | 0.43584 | 22.01% | 2.09% | 0.7382% | 24.84%
A | G North | gortawee | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 1.4 | 4.0498 | 2.6617 | 1.2739 | 0.072404 | 0.041739 | 1.3881 | 31.46% | 1.788% | 1.031% | 34.28%
A | G North | gortawee | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 1.6667 | 1.7549 | 1.3786 | 0.32901 | 0.032668 | 0.014615 | 0.37629 | 18.75% | 1.862% | 0.8328% | 21.44%
A | G North | gortawee | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 1.4 | 4.0498 | 2.7492 | 1.1892 | 0.071928 | 0.039484 | 1.3006 | 29.36% | 1.776% | 0.975% | 32.11%
A | G North | gortawee | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 1.6667 | 1.7549 | 1.431 | 0.28122 | 0.032911 | 0.0097404 | 0.32387 | 16.02% | 1.875% | 0.555% | 18.46%
A | G North | gortawee | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 1.4 | 4.0498 | 2.9833 | 0.93759 | 0.072161 | 0.056762 | 1.0665 | 23.15% | 1.782% | 1.402% | 26.34%
A | G North | gortawee | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 1.6667 | 1.7549 | 1.4733 | 0.23138 | 0.032372 | 0.01786 | 0.28162 | 13.19% | 1.845% | 1.018% | 16.05%
A | G North | gortawee | 2030 | 33% ECP | Pro-rata | IE wind not priority | 1.4 | 4.0498 | 3.1897 | 0.68638 | 0.071734 | 0.10195 | 0.86007 | 16.95% | 1.771% | 2.518% | 21.24%
A | G North | gortawee | 2035 | 66% ECP | Pro-rata | IE wind not priority | 2.8 | 8.0996 | 6.6454 | 1.3638 | 0.025713 | 0.064707 | 1.4542 | 16.84% | 0.3175% | 0.7989% | 17.95%
A | G North | gortawee | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 3.3333 | 3.5097 | 2.899 | 0.53238 | 0.025665 | 0.052716 | 0.61076 | 15.17% | 0.7313% | 1.502% | 17.4%
A | G North | gortawee | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 2.8 | 8.0996 | 6.6951 | 1.3638 | 0.025713 | 0.014994 | 1.4045 | 16.84% | 0.3175% | 0.1851% | 17.34%
B | A, B North | bellacorick | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 6.45 | 19.6174 | 15.5765 | 0 | 0.71117 | 3.3297 | 4.0409 | 0% | 3.625% | 16.97% | 20.6%
B | A, B North | bellacorick | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 197.2333 | 599.8755 | 341.848 | 145.6461 | 10.5639 | 101.8176 | 258.0275 | 24.28% | 1.761% | 16.97% | 43.01%
B | A, B North | bellacorick | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 94.3 | 286.8089 | 163.4423 | 69.6354 | 5.0507 | 48.6804 | 123.3666 | 24.28% | 1.761% | 16.97% | 43.01%
B | A, B North | bellacorick | 2030 | 33% ECP | Pro-rata | IE wind priority | 6.45 | 19.6174 | 15.1542 | 0 | 0.6324 | 3.8308 | 4.4632 | 0% | 3.224% | 19.53% | 22.75%
B | A, B North | bellacorick | 2030 | 33% ECP | Pro-rata | IE wind not priority | 197.2333 | 599.8755 | 364.8766 | 107.4649 | 10.3931 | 117.1409 | 234.9989 | 17.91% | 1.733% | 19.53% | 39.17%
B | A, B North | bellacorick | 2030 | 33% ECP | Pro-rata | IE wind not priority | 94.3 | 286.8089 | 174.4526 | 51.3805 | 4.9691 | 56.0067 | 112.3563 | 17.91% | 1.733% | 19.53% | 39.17%
B | A, B North | bellacorick | 2030 | Initial | Pro-rata | IE wind priority | 6.45 | 19.6174 | 15.1928 | 0 | 0.56731 | 3.8572 | 4.4245 | 0% | 2.892% | 19.66% | 22.55%
B | A, B North | bellacorick | 2030 | Initial | Pro-rata | IE wind not priority | 123.2 | 374.7069 | 245.1597 | 49.1688 | 6.7025 | 73.6759 | 129.5471 | 13.12% | 1.789% | 19.66% | 34.57%
A | G North | gortawee | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 5 | 5.2646 | 3.9876 | 1.1542 | 0.048365 | 0.074451 | 1.2771 | 21.92% | 0.9187% | 1.414% | 24.26%
A | G North | gortawee | 2035 | 100% ECP | Pro-rata | IE wind not priority | 4.2 | 12.1494 | 9.742 | 2.2626 | 0.042855 | 0.10196 | 2.4074 | 18.62% | 0.3527% | 0.8392% | 19.82%
A | G North | gortawee | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 3.3333 | 3.5097 | 2.6874 | 0.75708 | 0.030154 | 0.035075 | 0.8223 | 21.57% | 0.8592% | 0.9994% | 23.43%
A | G North | gortawee | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 2.8 | 8.0996 | 5.6467 | 2.3935 | 0.046889 | 0.012512 | 2.4529 | 29.55% | 0.5789% | 0.1545% | 30.28%
A | G North | gortawee | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 3.3333 | 3.5097 | 2.9053 | 0.53238 | 0.025665 | 0.046391 | 0.60444 | 15.17% | 0.7313% | 1.322% | 17.22%
B | A, B North | bellacorick | 2030 | Initial | Pro-rata | IE wind not priority | 83 | 252.4405 | 165.1644 | 33.1251 | 4.5155 | 49.6355 | 87.2761 | 13.12% | 1.789% | 19.66% | 34.57%
A | A, B North | trillick | 2035 | 100% ECP | Pro-rata | IE wind priority | 30.89 | 89.3561 | 72.2963 | 0 | 0.9037 | 16.1561 | 17.0598 | 0% | 1.011% | 18.08% | 19.09%
A | A, B North | trillick | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 30.89 | 89.3561 | 79.5752 | 0 | 1.5408 | 8.2401 | 9.7809 | 0% | 1.724% | 9.222% | 10.95%
A | A, B North | trillick | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 30.89 | 89.3561 | 76.9727 | 0 | 0.79536 | 11.588 | 12.3834 | 0% | 0.8901% | 12.97% | 13.86%
A | A, B North | tievebrack | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 9.9667 | 28.8307 | 15.5851 | 8.4658 | 0.51206 | 4.2678 | 13.2456 | 29.36% | 1.776% | 14.8% | 45.94%
A | A, B North | tievebrack | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 9.9667 | 28.8307 | 16.7488 | 6.6748 | 0.51371 | 4.8935 | 12.082 | 23.15% | 1.782% | 16.97% | 41.91%
A | A, B North | tievebrack | 2030 | 33% ECP | Pro-rata | IE wind not priority | 9.9667 | 28.8307 | 17.8038 | 4.8864 | 0.51068 | 5.6299 | 11.027 | 16.95% | 1.771% | 19.53% | 38.25%
A | A, B North | sorne hill | 2035 | 100% ECP | Pro-rata | IE wind priority | 48.1 | 139.1398 | 112.5754 | 0 | 1.4072 | 25.1572 | 26.5644 | 0% | 1.011% | 18.08% | 19.09%
A | A, B North | sorne hill | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 48.1 | 139.1398 | 123.9096 | 0 | 2.3992 | 12.831 | 15.2302 | 0% | 1.724% | 9.222% | 10.95%
A | A, B North | sorne hill | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 48.1 | 139.1398 | 119.8571 | 0 | 1.2385 | 18.0442 | 19.2826 | 0% | 0.8901% | 12.97% | 13.86%
A | A, B North | tievebrack | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 9.9667 | 28.8307 | 14.766 | 9.0692 | 0.51545 | 4.4801 | 14.0647 | 31.46% | 1.788% | 15.54% | 48.78%
A | A, B North | sorne hill | 2035 | 66% ECP | Pro-rata | IE wind priority | 48.1 | 139.1398 | 117.6624 | 0 | 1.2385 | 20.2388 | 21.4773 | 0% | 0.8901% | 14.55% | 15.44%
A | A, B North | sorne hill | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 48.1 | 139.1398 | 106.3235 | 0 | 5.1907 | 27.6255 | 32.8163 | 0% | 3.731% | 19.85% | 23.59%
A | A, B North | sorne hill | 2030 | 100% ECP | Pro-rata | IE wind priority | 48.1 | 139.1398 | 104.329 | 0 | 5.1907 | 29.62 | 34.8107 | 0% | 3.731% | 21.29% | 25.02%
A | A, B North | sorne hill | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 48.1 | 139.1398 | 110.635 | 0 | 4.4581 | 24.0466 | 28.5047 | 0% | 3.204% | 17.28% | 20.49%
A | A, B North | sorne hill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 48.1 | 139.1398 | 111.9689 | 0 | 5.5496 | 21.6213 | 27.1709 | 0% | 3.989% | 15.54% | 19.53%
A | A, B North | sorne hill | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 48.1 | 139.1398 | 113.0869 | 0 | 5.4562 | 20.5966 | 26.0528 | 0% | 3.921% | 14.8% | 18.72%
A | A, B North | sorne hill | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 48.1 | 139.1398 | 110.547 | 0 | 4.9764 | 23.6164 | 28.5928 | 0% | 3.577% | 16.97% | 20.55%
A | A, B North | sorne hill | 2030 | 33% ECP | Pro-rata | IE wind priority | 48.1 | 139.1398 | 107.5111 | 0 | 4.4581 | 27.1706 | 31.6287 | 0% | 3.204% | 19.53% | 22.73%
A | A, B North | tievebrack | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 9.9667 | 28.8307 | 18.4511 | 4.8864 | 0.51068 | 4.9826 | 10.3797 | 16.95% | 1.771% | 17.28% | 36%
A | A, B North | tievebrack | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 29.9 | 86.4923 | 43.9577 | 23.8758 | 1.4861 | 17.1726 | 42.5346 | 27.6% | 1.718% | 19.85% | 49.18%
A | A, B North | trillick | 2035 | 66% ECP | Pro-rata | IE wind priority | 30.89 | 89.3561 | 75.5633 | 0 | 0.79536 | 12.9975 | 13.7928 | 0% | 0.8901% | 14.55% | 15.44%
A | A, B North | trillick | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 30.89 | 89.3561 | 68.2813 | 0 | 3.3335 | 17.7412 | 21.0747 | 0% | 3.731% | 19.85% | 23.59%
A | A, B North | trillick | 2030 | 100% ECP | Pro-rata | IE wind priority | 30.89 | 89.3561 | 67.0005 | 0 | 3.3335 | 19.0221 | 22.3556 | 0% | 3.731% | 21.29% | 25.02%
A | A, B North | trillick | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 30.89 | 89.3561 | 71.0502 | 0 | 2.863 | 15.4428 | 18.3058 | 0% | 3.204% | 17.28% | 20.49%
A | A, B North | trillick | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 30.89 | 89.3561 | 71.9068 | 0 | 3.564 | 13.8853 | 17.4493 | 0% | 3.989% | 15.54% | 19.53%
A | A, B North | trillick | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 30.89 | 89.3561 | 72.6248 | 0 | 3.504 | 13.2272 | 16.7312 | 0% | 3.921% | 14.8% | 18.72%
A | A, B North | tievebrack | 2030 | 100% ECP | Pro-rata | IE wind not priority | 29.9 | 86.4923 | 42.7179 | 23.8758 | 1.4861 | 18.4124 | 43.7744 | 27.6% | 1.718% | 21.29% | 50.61%
A | A, B North | trillick | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 30.89 | 89.3561 | 70.9937 | 0 | 3.1959 | 15.1665 | 18.3624 | 0% | 3.577% | 16.97% | 20.55%
A | A, B North | trillick | 2030 | Initial | Pro-rata | IE wind priority | 30.89 | 89.3561 | 69.2443 | 0 | 2.5424 | 17.5694 | 20.1118 | 0% | 2.845% | 19.66% | 22.51%
A | A, B North | tievebrack | 2035 | 100% ECP | Pro-rata | IE wind not priority | 29.9 | 86.4923 | 54.4413 | 16.1076 | 0.30509 | 15.6383 | 32.0509 | 18.62% | 0.3527% | 18.08% | 37.06%
A | A, B North | tievebrack | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 19.9333 | 57.6615 | 34.9706 | 17.0397 | 0.3338 | 5.3173 | 22.6909 | 29.55% | 0.5789% | 9.222% | 39.35%
A | A, B North | tievebrack | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 19.9333 | 57.6615 | 40.2918 | 9.7089 | 0.18305 | 7.4778 | 17.3697 | 16.84% | 0.3175% | 12.97% | 30.12%
A | A, B North | tievebrack | 2035 | 66% ECP | Pro-rata | IE wind not priority | 19.9333 | 57.6615 | 39.3823 | 9.7089 | 0.18305 | 8.3873 | 18.2792 | 16.84% | 0.3175% | 14.55% | 31.7%
A | A, B North | trillick | 2030 | 33% ECP | Pro-rata | IE wind priority | 30.89 | 89.3561 | 69.044 | 0 | 2.863 | 17.449 | 20.3121 | 0% | 3.204% | 19.53% | 22.73%
B | A, B North | bellacorick | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 94.3 | 286.8089 | 151.0661 | 88.3238 | 4.9633 | 42.4558 | 135.7428 | 30.8% | 1.731% | 14.8% | 47.33%
A | A, B North | garvagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 40 | 42.117 | 33.9227 | 6.3886 | 0.30798 | 1.4977 | 8.1943 | 15.17% | 0.7313% | 3.556% | 19.46%
A | A, B North | garvagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 66 | 190.9193 | 133.4077 | 32.1464 | 0.60609 | 24.7591 | 57.5116 | 16.84% | 0.3175% | 12.97% | 30.12%
A | A, B North | binbane | 2035 | 100% ECP | Pro-rata | IE wind priority | 35.54 | 102.8072 | 83.1794 | 0 | 1.0397 | 18.5881 | 19.6278 | 0% | 1.011% | 18.08% | 19.09%
A | A, B North | binbane | 2035 | 100% ECP | Pro-rata | IE wind not priority | 43.2 | 124.9654 | 78.6577 | 23.2725 | 0.44079 | 22.5944 | 46.3077 | 18.62% | 0.3527% | 18.08% | 37.06%
A | A, B North | binbane | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 35.54 | 102.8072 | 91.554 | 0 | 1.7727 | 9.4805 | 11.2532 | 0% | 1.724% | 9.222% | 10.95%
A | A, B North | binbane | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 36.6667 | 106.0663 | 64.3272 | 31.344 | 0.61402 | 9.7811 | 41.7391 | 29.55% | 0.5789% | 9.222% | 39.35%
A | A, B North | binbane | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 35.54 | 102.8072 | 88.5597 | 0 | 0.91508 | 13.3324 | 14.2475 | 0% | 0.8901% | 12.97% | 13.86%
A | A, B North | binbane | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 36.6667 | 106.0663 | 74.1154 | 17.8591 | 0.33672 | 13.7551 | 31.9509 | 16.84% | 0.3175% | 12.97% | 30.12%
A | A, B North | binbane | 2035 | 66% ECP | Pro-rata | IE wind priority | 35.54 | 102.8072 | 86.9381 | 0 | 0.91508 | 14.954 | 15.8691 | 0% | 0.8901% | 14.55% | 15.44%
A | A, B North | binbane | 2035 | 66% ECP | Pro-rata | IE wind not priority | 36.6667 | 106.0663 | 72.4424 | 17.8591 | 0.33672 | 15.4281 | 33.6239 | 16.84% | 0.3175% | 14.55% | 31.7%
A | A, B North | binbane | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 35.54 | 102.8072 | 78.56 | 0 | 3.8353 | 20.4119 | 24.2472 | 0% | 3.731% | 19.85% | 23.59%
A | A, B North | binbane | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 43.2 | 124.9654 | 63.5108 | 34.4962 | 2.1472 | 24.8113 | 61.4546 | 27.6% | 1.718% | 19.85% | 49.18%
A | A, B North | binbane | 2030 | 100% ECP | Pro-rata | IE wind priority | 35.54 | 102.8072 | 77.0864 | 0 | 3.8353 | 21.8855 | 25.7208 | 0% | 3.731% | 21.29% | 25.02%
A | A, B North | cathaleen's fall | 2030 | Initial | Pro-rata | IE wind priority | 17.5 | 50.6226 | 39.2287 | 0 | 1.4403 | 9.9535 | 11.3939 | 0% | 2.845% | 19.66% | 22.51%
A | A, B North | cathaleen's fall | 2030 | 33% ECP | Pro-rata | IE wind not priority | 12.5 | 36.1589 | 22.3291 | 6.1284 | 0.64048 | 7.061 | 13.8298 | 16.95% | 1.771% | 19.53% | 38.25%
A | A, B North | cathaleen's fall | 2030 | 33% ECP | Pro-rata | IE wind priority | 17.5 | 50.6226 | 39.1152 | 0 | 1.622 | 9.8853 | 11.5073 | 0% | 3.204% | 19.53% | 22.73%
A | A, B North | cathaleen's fall | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 12.5 | 36.1589 | 21.006 | 8.3714 | 0.64429 | 6.1373 | 15.153 | 23.15% | 1.782% | 16.97% | 41.91%
A | A, B North | cathaleen's fall | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 25 | 72.3179 | 50.5332 | 12.1767 | 0.22958 | 9.3785 | 21.7847 | 16.84% | 0.3175% | 12.97% | 30.12%
A | A, B North | cathaleen's fall | 2035 | 66% ECP | Pro-rata | IE wind priority | 17.5 | 50.6226 | 42.8086 | 0 | 0.45059 | 7.3634 | 7.814 | 0% | 0.8901% | 14.55% | 15.44%
A | A, B North | cathaleen's fall | 2035 | 66% ECP | Pro-rata | IE wind not priority | 25 | 72.3179 | 49.3925 | 12.1767 | 0.22958 | 10.5191 | 22.9254 | 16.84% | 0.3175% | 14.55% | 31.7%
A | A, B North | cathaleen's fall | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 17.5 | 50.6226 | 38.6832 | 0 | 1.8885 | 10.0509 | 11.9394 | 0% | 3.731% | 19.85% | 23.59%
A | A, B North | cathaleen's fall | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 37.5 | 108.4769 | 55.1309 | 29.9446 | 1.8638 | 21.5376 | 53.346 | 27.6% | 1.718% | 19.85% | 49.18%
A | A, B North | binbane | 2030 | 100% ECP | Pro-rata | IE wind not priority | 43.2 | 124.9654 | 61.7195 | 34.4962 | 2.1472 | 26.6026 | 63.2459 | 27.6% | 1.718% | 21.29% | 50.61%
A | A, B North | cathaleen's fall | 2030 | 100% ECP | Pro-rata | IE wind priority | 17.5 | 50.6226 | 37.9576 | 0 | 1.8885 | 10.7765 | 12.665 | 0% | 3.731% | 21.29% | 25.02%
A | A, B North | cathaleen's fall | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 17.5 | 50.6226 | 40.2518 | 0 | 1.622 | 8.7488 | 10.3707 | 0% | 3.204% | 17.28% | 20.49%
A | A, B North | cathaleen's fall | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 12.5 | 36.1589 | 23.141 | 6.1284 | 0.64048 | 6.2491 | 13.018 | 16.95% | 1.771% | 17.28% | 36%
A | A, B North | cathaleen's fall | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 17.5 | 50.6226 | 40.7371 | 0 | 2.0191 | 7.8664 | 9.8855 | 0% | 3.989% | 15.54% | 19.53%
A | A, B North | cathaleen's fall | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 12.5 | 36.1589 | 18.5192 | 11.3744 | 0.64646 | 5.6188 | 17.6397 | 31.46% | 1.788% | 15.54% | 48.78%
A | A, B North | cathaleen's fall | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 17.5 | 50.6226 | 41.1439 | 0 | 1.9851 | 7.4936 | 9.4787 | 0% | 3.921% | 14.8% | 18.72%
A | A, B North | cathaleen's fall | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 12.5 | 36.1589 | 19.5465 | 10.6177 | 0.64221 | 5.3525 | 16.6124 | 29.36% | 1.776% | 14.8% | 45.94%
A | A, B North | cathaleen's fall | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 17.5 | 50.6226 | 40.2198 | 0 | 1.8106 | 8.5922 | 10.4028 | 0% | 3.577% | 16.97% | 20.55%
A | A, B North | cathaleen's fall | 2030 | 100% ECP | Pro-rata | IE wind not priority | 37.5 | 108.4769 | 53.576 | 29.9446 | 1.8638 | 23.0925 | 54.901 | 27.6% | 1.718% | 21.29% | 50.61%
A | A, B North | binbane | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 35.54 | 102.8072 | 81.7457 | 0 | 3.294 | 17.7675 | 21.0615 | 0% | 3.204% | 17.28% | 20.49%
A | A, B North | binbane | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 30.1333 | 87.1672 | 55.7852 | 14.7735 | 1.544 | 15.0645 | 31.382 | 16.95% | 1.771% | 17.28% | 36%
A | A, B North | binbane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 35.54 | 102.8072 | 82.7312 | 0 | 4.1005 | 15.9755 | 20.076 | 0% | 3.989% | 15.54% | 19.53%
A | A, B North | arigna | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 0.5 | 1.4464 | 0.84024 | 0.33485 | 0.025772 | 0.24549 | 0.60612 | 23.15% | 1.782% | 16.97% | 41.91%
A | A, B North | arigna | 2030 | 33% ECP | Pro-rata | IE wind not priority | 0.5 | 1.4464 | 0.89316 | 0.24514 | 0.025619 | 0.28244 | 0.55319 | 16.95% | 1.771% | 19.53% | 38.25%
A | A, B North | ardnagappary | 2035 | 100% ECP | Pro-rata | IE wind not priority | 26.96 | 77.9877 | 49.0882 | 14.5238 | 0.27509 | 14.1006 | 28.8994 | 18.62% | 0.3527% | 18.08% | 37.06%
A | A, B North | ardnagappary | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 23.96 | 69.3095 | 42.0349 | 20.4819 | 0.40124 | 6.3915 | 27.2746 | 29.55% | 0.5789% | 9.222% | 39.35%
A | A, B North | ardnagappary | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 23.96 | 69.3095 | 48.431 | 11.6701 | 0.22003 | 8.9883 | 20.8785 | 16.84% | 0.3175% | 12.97% | 30.12%
A | A, B North | ardnagappary | 2035 | 66% ECP | Pro-rata | IE wind not priority | 23.96 | 69.3095 | 47.3378 | 11.6701 | 0.22003 | 10.0815 | 21.9717 | 16.84% | 0.3175% | 14.55% | 31.7%
A | A, B North | arigna | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 0.5 | 1.4464 | 0.78186 | 0.42471 | 0.025688 | 0.2141 | 0.6645 | 29.36% | 1.776% | 14.8% | 45.94%
A | A, B North | ardnagappary | 2030 | 100% ECP | Pro-rata | IE wind not priority | 26.96 | 77.9877 | 38.5176 | 21.5282 | 1.34 | 16.602 | 39.4701 | 27.6% | 1.718% | 21.29% | 50.61%
A | A, B North | ardnagappary | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 20.96 | 60.6314 | 38.8028 | 10.2761 | 1.074 | 10.4785 | 21.8286 | 16.95% | 1.771% | 17.28% | 36%
A | A, B North | ardnagappary | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 20.96 | 60.6314 | 31.0531 | 19.0727 | 1.084 | 9.4217 | 29.5783 | 31.46% | 1.788% | 15.54% | 48.78%
A | A, B North | ardnagappary | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 20.96 | 60.6314 | 32.7756 | 17.8037 | 1.0769 | 8.9751 | 27.8557 | 29.36% | 1.776% | 14.8% | 45.94%
A | A, B North | ardnagappary | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 20.96 | 60.6314 | 35.2229 | 14.0371 | 1.0803 | 10.291 | 25.4085 | 23.15% | 1.782% | 16.97% | 41.91%
A | A, B North | ardnagappary | 2030 | 33% ECP | Pro-rata | IE wind not priority | 20.96 | 60.6314 | 37.4415 | 10.2761 | 1.074 | 11.8398 | 23.1899 | 16.95% | 1.771% | 19.53% | 38.25%
A | A, B North | ardnagappary | 2030 | Initial | Pro-rata | IE wind not priority | 17.96 | 51.9532 | 34.3404 | 6.4633 | 0.93433 | 10.2152 | 17.6128 | 12.44% | 1.798% | 19.66% | 33.9%
A | A, B North | ardnagappary | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 26.96 | 77.9877 | 39.6354 | 21.5282 | 1.34 | 15.4841 | 38.3522 | 27.6% | 1.718% | 19.85% | 49.18%
A | A, B North | cathaleen's fall | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 17.5 | 50.6226 | 43.6071 | 0 | 0.45059 | 6.5649 | 7.0155 | 0% | 0.8901% | 12.97% | 13.86%
A | A, B North | arigna | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 0.5 | 1.4464 | 0.74077 | 0.45498 | 0.025859 | 0.22475 | 0.70559 | 31.46% | 1.788% | 15.54% | 48.78%
A | A, B North | arigna | 2030 | 100% ECP | Pro-rata | IE wind not priority | 1.5 | 4.3391 | 2.143 | 1.1978 | 0.074554 | 0.9237 | 2.196 | 27.6% | 1.718% | 21.29% | 50.61%
A | A, B North | binbane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 30.1333 | 87.1672 | 44.6437 | 27.42 | 1.5584 | 13.5451 | 42.5235 | 31.46% | 1.788% | 15.54% | 48.78%
A | A, B North | binbane | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 35.54 | 102.8072 | 83.5574 | 0 | 4.0315 | 15.2184 | 19.2498 | 0% | 3.921% | 14.8% | 18.72%
A | A, B North | binbane | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 30.1333 | 87.1672 | 47.1202 | 25.5957 | 1.5482 | 12.9032 | 40.0471 | 29.36% | 1.776% | 14.8% | 45.94%
A | A, B North | binbane | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 35.54 | 102.8072 | 81.6806 | 0 | 3.677 | 17.4496 | 21.1266 | 0% | 3.577% | 16.97% | 20.55%
A | A, B North | binbane | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 30.1333 | 87.1672 | 50.6385 | 20.1806 | 1.5532 | 14.795 | 36.5288 | 23.15% | 1.782% | 16.97% | 41.91%
A | A, B North | binbane | 2030 | 33% ECP | Pro-rata | IE wind priority | 35.54 | 102.8072 | 79.4375 | 0 | 3.294 | 20.0757 | 23.3697 | 0% | 3.204% | 19.53% | 22.73%
A | A, B North | binbane | 2030 | 33% ECP | Pro-rata | IE wind not priority | 30.1333 | 87.1672 | 53.8281 | 14.7735 | 1.544 | 17.0216 | 33.3391 | 16.95% | 1.771% | 19.53% | 38.25%
A | A, B North | arigna | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 0.5 | 1.4464 | 0.92564 | 0.24514 | 0.025619 | 0.24996 | 0.52072 | 16.95% | 1.771% | 17.28% | 36%
A | A, B North | binbane | 2030 | Initial | Pro-rata | IE wind priority | 35.54 | 102.8072 | 79.6679 | 0 | 2.9251 | 20.2142 | 23.1393 | 0% | 2.845% | 19.66% | 22.51%
A | A, B North | arigna | 2035 | 100% ECP | Pro-rata | IE wind not priority | 1.5 | 4.3391 | 2.7312 | 0.80807 | 0.015305 | 0.78453 | 1.6079 | 18.62% | 0.3527% | 18.08% | 37.06%
A | A, B North | arigna | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 1 | 2.8927 | 1.7544 | 0.85484 | 0.016746 | 0.26676 | 1.1383 | 29.55% | 0.5789% | 9.222% | 39.35%
A | A, B North | arigna | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 1 | 2.8927 | 2.0213 | 0.48707 | 0.0091832 | 0.37514 | 0.87139 | 16.84% | 0.3175% | 12.97% | 30.12%
A | A, B North | arigna | 2035 | 66% ECP | Pro-rata | IE wind not priority | 1 | 2.8927 | 1.9757 | 0.48707 | 0.0091832 | 0.42077 | 0.91702 | 16.84% | 0.3175% | 14.55% | 31.7%
A | A, B North | arigna | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 1.5 | 4.3391 | 2.2052 | 1.1978 | 0.074554 | 0.8615 | 2.1338 | 27.6% | 1.718% | 19.85% | 49.18%
A | A, B North | binbane | 2030 | Initial | Pro-rata | IE wind not priority | 23.6 | 68.2682 | 45.1244 | 8.493 | 1.2277 | 13.4231 | 23.1438 | 12.44% | 1.798% | 19.66% | 33.9%
A | A, B North | garvagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 48 | 138.8505 | 119.6079 | 0 | 1.2359 | 18.0066 | 19.2425 | 0% | 0.8901% | 12.97% | 13.86%
A | A, B North | cathaleen's fall | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 25 | 72.3179 | 43.8594 | 21.3709 | 0.41865 | 6.6689 | 28.4584 | 29.55% | 0.5789% | 9.222% | 39.35%
A | A, B North | cathaleen's fall | 2035 | 100% ECP | Pro-rata | IE wind not priority | 37.5 | 108.4769 | 68.2793 | 20.2018 | 0.38263 | 19.6132 | 40.1977 | 18.62% | 0.3527% | 18.08% | 37.06%
A | A, B North | garvagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 50 | 144.6359 | 78.1861 | 42.4707 | 2.5688 | 21.4102 | 66.4497 | 29.36% | 1.776% | 14.8% | 45.94%
A | A, B North | garvagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 40 | 42.117 | 31.1379 | 6.7492 | 0.78987 | 3.44 | 10.9791 | 16.02% | 1.875% | 8.168% | 26.07%
A | A, B North | garvagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 48 | 138.8505 | 110.3171 | 0 | 4.9661 | 23.5673 | 28.5333 | 0% | 3.577% | 16.97% | 20.55%
A | A, B North | garvagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 50 | 144.6359 | 84.024 | 33.4855 | 2.5772 | 24.5492 | 60.6119 | 23.15% | 1.782% | 16.97% | 41.91%
A | A, B North | garvagh | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 40 | 42.117 | 31.8276 | 5.5532 | 0.77694 | 3.9593 | 10.2894 | 13.19% | 1.845% | 9.401% | 24.43%
A | A, B North | garvagh | 2030 | 33% ECP | Pro-rata | IE wind priority | 48 | 138.8505 | 107.2875 | 0 | 4.4489 | 27.1141 | 31.5629 | 0% | 3.204% | 19.53% | 22.73%
A | A, B North | garvagh | 2030 | 33% ECP | Pro-rata | IE wind not priority | 50 | 144.6359 | 89.3165 | 24.5136 | 2.5619 | 28.2438 | 55.3193 | 16.95% | 1.771% | 19.53% | 38.25%
A | A, B North | garvagh | 2030 | Initial | Pro-rata | IE Solar not priority | 40 | 42.117 | 32.1704 | 3.1666 | 0.53912 | 6.2408 | 9.9466 | 7.519% | 1.28% | 14.82% | 23.62%
A | A, B North | garvagh | 2030 | Initial | Pro-rata | IE wind priority | 48 | 138.8505 | 107.5987 | 0 | 3.9506 | 27.3011 | 31.2518 | 0% | 2.845% | 19.66% | 22.51%
A | A, B North | garvagh | 2030 | Initial | Pro-rata | IE wind not priority | 34 | 98.3524 | 65.0097 | 12.2357 | 1.7688 | 19.3383 | 33.3428 | 12.44% | 1.798% | 19.66% | 33.9%
A | A, B North | croaghonagh | 2035 | 100% ECP | Pro-rata | IE wind not priority | 138.1 | 399.4844 | 251.4498 | 74.3966 | 1.4091 | 72.2289 | 148.0346 | 18.62% | 0.3527% | 18.08% | 37.06%
A | A, B North | croaghonagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 138.1 | 399.4844 | 242.2798 | 118.0529 | 2.3126 | 36.8391 | 157.2046 | 29.55% | 0.5789% | 9.222% | 39.35%
A | A, B North | croaghonagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 138.1 | 399.4844 | 279.1456 | 67.264 | 1.2682 | 51.8066 | 120.3388 | 16.84% | 0.3175% | 12.97% | 30.12%
A | A, B North | croaghonagh | 2035 | 66% ECP | Pro-rata | IE wind not priority | 138.1 | 399.4844 | 272.8445 | 67.264 | 1.2682 | 58.1077 | 126.6399 | 16.84% | 0.3175% | 14.55% | 31.7%
A | A, B North | garvagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 48 | 138.8505 | 112.8518 | 0 | 5.4449 | 20.5538 | 25.9987 | 0% | 3.921% | 14.8% | 18.72%
A | A, B North | garvagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 40 | 42.117 | 30.3247 | 7.8962 | 0.78404 | 3.112 | 11.7923 | 18.75% | 1.862% | 7.389% | 28%
A | A, B North | garvagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 50 | 144.6359 | 74.0769 | 45.4977 | 2.5859 | 22.4753 | 70.5589 | 31.46% | 1.788% | 15.54% | 48.78%
A | A, B North | garvagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 48 | 138.8505 | 111.7361 | 0 | 5.5381 | 21.5763 | 27.1144 | 0% | 3.989% | 15.54% | 19.53%
A | A, B North | garvagh | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 40 | 42.117 | 33.0549 | 6.3886 | 0.30798 | 2.3655 | 9.0621 | 15.17% | 0.7313% | 5.617% | 21.52%
A | A, B North | garvagh | 2035 | 66% ECP | Pro-rata | IE wind priority | 48 | 138.8505 | 117.4178 | 0 | 1.2359 | 20.1968 | 21.4327 | 0% | 0.8901% | 14.55% | 15.44%
A | A, B North | garvagh | 2035 | 66% ECP | Pro-rata | IE wind not priority | 66 | 190.9193 | 130.3963 | 32.1464 | 0.60609 | 27.7705 | 60.523 | 16.84% | 0.3175% | 14.55% | 31.7%
A | A, B North | garvagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 40 | 42.117 | 26.293 | 13.1608 | 0.92465 | 1.7386 | 15.824 | 31.25% | 2.195% | 4.128% | 37.57%
A | A, B North | garvagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 48 | 138.8505 | 106.1024 | 0 | 5.1799 | 27.5681 | 32.748 | 0% | 3.731% | 19.85% | 23.59%
A | A, B North | garvagh | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 40 | 42.117 | 26.1871 | 13.1608 | 0.92465 | 1.8444 | 15.9299 | 31.25% | 2.195% | 4.379% | 37.82%
A | A, B North | garvagh | 2030 | 100% ECP | Pro-rata | IE wind priority | 48 | 138.8505 | 104.1121 | 0 | 5.1799 | 29.5584 | 34.7383 | 0% | 3.731% | 21.29% | 25.02%
A | A, B North | garvagh | 2030 | 100% ECP | Pro-rata | IE wind not priority | 82 | 237.2029 | 117.1528 | 65.4789 | 4.0756 | 50.4956 | 120.0501 | 27.6% | 1.718% | 21.29% | 50.61%
A | A, B North | garvagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 40 | 42.117 | 32.1066 | 5.5532 | 0.77694 | 3.6802 | 10.0104 | 13.19% | 1.845% | 8.738% | 23.77%
A | A, B North | garvagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 48 | 138.8505 | 110.405 | 0 | 4.4489 | 23.9966 | 28.4454 | 0% | 3.204% | 17.28% | 20.49%
A | A, B North | garvagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 50 | 144.6359 | 92.5639 | 24.5136 | 2.5619 | 24.9964 | 52.0719 | 16.95% | 1.771% | 17.28% | 36%
A | A, B North | garvagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 40 | 42.117 | 28.8438 | 9.2691 | 0.88022 | 3.1239 | 13.2732 | 22.01% | 2.09% | 7.417% | 31.52%
A | A, B North | garvagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 82 | 237.2029 | 120.5529 | 65.4789 | 4.0756 | 47.0955 | 116.65 | 27.6% | 1.718% | 19.85% | 49.18%
A | A, B North | croaghonagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 138.1 | 399.4844 | 203.0287 | 110.276 | 6.8639 | 79.3158 | 196.4557 | 27.6% | 1.718% | 19.85% | 49.18%
A | A, B North | croaghonagh | 2030 | 100% ECP | Pro-rata | IE wind not priority | 138.1 | 399.4844 | 197.3025 | 110.276 | 6.8639 | 85.042 | 202.1819 | 27.6% | 1.718% | 21.29% | 50.61%
A | A, B North | croaghonagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 138.1 | 399.4844 | 255.6617 | 67.7065 | 7.0761 | 69.0402 | 143.8227 | 16.95% | 1.771% | 17.28% | 36%
A | A, B North | corderry | 2030 | 100% ECP | Pro-rata | IE wind not priority | 36.55 | 105.7289 | 52.2187 | 29.186 | 1.8166 | 22.5075 | 53.5101 | 27.6% | 1.718% | 21.29% | 50.61%
A | A, B North | corderry | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 45.655 | 132.0671 | 105.0113 | 0 | 4.2315 | 22.8242 | 27.0558 | 0% | 3.204% | 17.28% | 20.49%
A | A, B North | corderry | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 23.0833 | 66.7736 | 42.7337 | 11.3171 | 1.1828 | 11.54 | 24.0399 | 16.95% | 1.771% | 17.28% | 36%
A | A, B North | corderry | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 45.655 | 132.0671 | 106.2773 | 0 | 5.2675 | 20.5222 | 25.7898 | 0% | 3.989% | 15.54% | 19.53%
A | A, B North | corderry | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 23.0833 | 66.7736 | 34.1989 | 21.0048 | 1.1938 | 10.3761 | 32.5747 | 31.46% | 1.788% | 15.54% | 48.78%
A | A, B North | corderry | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 45.655 | 132.0671 | 107.3385 | 0 | 5.1789 | 19.5496 | 24.7285 | 0% | 3.921% | 14.8% | 18.72%
A | A, B North | corderry | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 23.0833 | 66.7736 | 36.0959 | 19.6073 | 1.186 | 9.8844 | 30.6776 | 29.36% | 1.776% | 14.8% | 45.94%
A | A, B North | corderry | 2030 | 100% ECP | Pro-rata | IE wind priority | 45.655 | 132.0671 | 99.0258 | 0 | 4.9269 | 28.1144 | 33.0412 | 0% | 3.731% | 21.29% | 25.02%
A | A, B North | corderry | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 45.655 | 132.0671 | 104.9277 | 0 | 4.7235 | 22.4159 | 27.1394 | 0% | 3.577% | 16.97% | 20.55%
A | A, B North | corderry | 2030 | 33% ECP | Pro-rata | IE wind priority | 45.655 | 132.0671 | 102.0461 | 0 | 4.2315 | 25.7894 | 30.021 | 0% | 3.204% | 19.53% | 22.73%
A | A, B North | corderry | 2030 | 33% ECP | Pro-rata | IE wind not priority | 23.0833 | 66.7736 | 41.2345 | 11.3171 | 1.1828 | 13.0392 | 25.5391 | 16.95% | 1.771% | 19.53% | 38.25%
A | A, B North | corderry | 2030 | Initial | Pro-rata | IE wind priority | 45.655 | 132.0671 | 102.3421 | 0 | 3.7576 | 25.9674 | 29.725 | 0% | 2.845% | 19.66% | 22.51%
A | A, B North | corderry | 2030 | Initial | Pro-rata | IE wind not priority | 16.35 | 47.2959 | 31.262 | 5.8839 | 0.85057 | 9.2995 | 16.0339 | 12.44% | 1.798% | 19.66% | 33.9%
A | A, B North | cathaleen's fall | 2035 | 100% ECP | Pro-rata | IE wind priority | 17.5 | 50.6226 | 40.9578 | 0 | 0.51197 | 9.1528 | 9.6648 | 0% | 1.011% | 18.08% | 19.09%
A | A, B North | corderry | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 23.0833 | 66.7736 | 38.7911 | 15.4591 | 1.1898 | 11.3336 | 27.9825 | 23.15% | 1.782% | 16.97% | 41.91%
A | A, B North | cathaleen's fall | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 17.5 | 50.6226 | 45.0814 | 0 | 0.87288 | 4.6682 | 5.5411 | 0% | 1.724% | 9.222% | 10.95%
A | A, B North | corderry | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 36.55 | 105.7289 | 53.7342 | 29.186 | 1.8166 | 20.992 | 51.9946 | 27.6% | 1.718% | 19.85% | 49.18%
A | A, B North | croaghonagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 138.1 | 399.4844 | 204.6006 | 125.6648 | 7.1421 | 62.0769 | 194.8838 | 31.46% | 1.788% | 15.54% | 48.78%
A | A, B North | croaghonagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 138.1 | 399.4844 | 215.9501 | 117.3042 | 7.0952 | 59.1349 | 183.5343 | 29.36% | 1.776% | 14.8% | 45.94%
A | A, B North | croaghonagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 138.1 | 399.4844 | 232.0744 | 92.4869 | 7.1181 | 67.805 | 167.41 | 23.15% | 1.782% | 16.97% | 41.91%
A | A, B North | croaghonagh | 2030 | 33% ECP | Pro-rata | IE wind not priority | 138.1 | 399.4844 | 246.6924 | 67.7065 | 7.0761 | 78.0095 | 152.792 | 16.95% | 1.771% | 19.53% | 38.25%
A | A, B North | croaghonagh | 2030 | Initial | Pro-rata | IE wind not priority | 138.1 | 399.4844 | 264.054 | 49.6984 | 7.1843 | 78.5477 | 135.4304 | 12.44% | 1.798% | 19.66% | 33.9%
A | A, B North | corderry | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 45.655 | 132.0671 | 100.9189 | 0 | 4.9269 | 26.2213 | 31.1482 | 0% | 3.731% | 19.85% | 23.59%
A | A, B North | corderry | 2035 | 100% ECP | Pro-rata | IE wind priority | 45.655 | 132.0671 | 106.853 | 0 | 1.3357 | 23.8784 | 25.2141 | 0% | 1.011% | 18.08% | 19.09%
A | A, B North | corderry | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 45.655 | 132.0671 | 117.6111 | 0 | 2.2772 | 12.1788 | 14.456 | 0% | 1.724% | 9.222% | 10.95%
A | A, B North | corderry | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 29.8167 | 86.2512 | 52.3097 | 25.4884 | 0.49931 | 7.9538 | 33.9415 | 29.55% | 0.5789% | 9.222% | 39.35%
A | A, B North | corderry | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 45.655 | 132.0671 | 113.7646 | 0 | 1.1755 | 17.1269 | 18.3025 | 0% | 0.8901% | 12.97% | 13.86%
A | A, B North | corderry | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 29.8167 | 86.2512 | 60.2693 | 14.5227 | 0.27381 | 11.1854 | 25.9819 | 16.84% | 0.3175% | 12.97% | 30.12%
A | A, B North | corderry | 2035 | 66% ECP | Pro-rata | IE wind priority | 45.655 | 132.0671 | 111.6815 | 0 | 1.1755 | 19.2101 | 20.3856 | 0% | 0.8901% | 14.55% | 15.44%
A | A, B North | corderry | 2035 | 66% ECP | Pro-rata | IE wind not priority | 29.8167 | 86.2512 | 58.9088 | 14.5227 | 0.27381 | 12.5458 | 27.3424 | 16.84% | 0.3175% | 14.55% | 31.7%
A | A, B North | corderry | 2035 | 100% ECP | Pro-rata | IE wind not priority | 36.55 | 105.7289 | 66.5495 | 19.69 | 0.37294 | 19.1163 | 39.1793 | 18.62% | 0.3527% | 18.08% | 37.06%
B | C | cashla | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 207.3331 | 265.6532 | 217.6921 | 40.693 | 1.9153 | 5.3529 | 47.9611 | 15.32% | 0.721% | 2.015% | 18.05%
B | A, B North | bellacorick | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 197.2333 | 599.8755 | 315.9624 | 184.7337 | 10.3809 | 88.7984 | 283.913 | 30.8% | 1.731% | 14.8% | 47.33%
B | A, B North | bellacorick | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 94.3 | 286.8089 | 143.4031 | 93.9061 | 4.9317 | 44.568 | 143.4058 | 32.74% | 1.72% | 15.54% | 50%
B | A, B North | tawnaghmore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 19.2 | 58.3959 | 46.9863 | 0 | 2.3353 | 9.0743 | 11.4096 | 0% | 3.999% | 15.54% | 19.54%
B | A, B North | tawnaghmore | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 19.2 | 58.3959 | 47.4462 | 0 | 2.3054 | 8.6442 | 10.9497 | 0% | 3.948% | 14.8% | 18.75%
B | A, B North | tawnaghmore | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 19.2 | 58.3959 | 46.3673 | 0 | 2.117 | 9.9116 | 12.0286 | 0% | 3.625% | 16.97% | 20.6%
B | A, B North | tawnaghmore | 2030 | 33% ECP | Pro-rata | IE wind priority | 19.2 | 58.3959 | 45.1101 | 0 | 1.8825 | 11.4033 | 13.2858 | 0% | 3.224% | 19.53% | 22.75%
B | A, B North | tawnaghmore | 2030 | Initial | Pro-rata | IE wind priority | 19.2 | 58.3959 | 45.2252 | 0 | 1.6887 | 11.482 | 13.1707 | 0% | 2.892% | 19.66% | 22.55%
B | A, B North | sligo | 2035 | 100% ECP | Pro-rata | IE wind priority | 13.65 | 41.5158 | 33.5817 | 0 | 0.42785 | 7.5063 | 7.9341 | 0% | 1.031% | 18.08% | 19.11%
B | A, B North | sligo | 2035 | 100% ECP | Pro-rata | IE wind not priority | 4.08 | 12.4091 | 7.7222 | 2.4012 | 0.042122 | 2.2436 | 4.6869 | 19.35% | 0.3394% | 18.08% | 37.77%
B | A, B North | sligo | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 13.65 | 41.5158 | 36.9665 | 0 | 0.72089 | 3.8284 | 4.5493 | 0% | 1.736% | 9.222% | 10.96%
B | A, B North | sligo | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 2.72 | 8.2727 | 4.924 | 2.5378 | 0.04803 | 0.76288 | 3.3487 | 30.68% | 0.5806% | 9.222% | 40.48%
B | A, B North | sligo | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 13.65 | 41.5158 | 35.7611 | 0 | 0.37076 | 5.3839 | 5.7547 | 0% | 0.8931% | 12.97% | 13.86%
B | A, B North | sligo | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 2.72 | 8.2727 | 5.7319 | 1.4425 | 0.025492 | 1.0728 | 2.5408 | 17.44% | 0.3081% | 12.97% | 30.71%
B | A, B North | sligo | 2035 | 66% ECP | Pro-rata | IE wind priority | 13.65 | 41.5158 | 35.1063 | 0 | 0.37076 | 6.0388 | 6.4095 | 0% | 0.8931% | 14.55% | 15.44%
B | A, B North | sligo | 2035 | 66% ECP | Pro-rata | IE wind not priority | 2.72 | 8.2727 | 5.6014 | 1.4425 | 0.025492 | 1.2033 | 2.6713 | 17.44% | 0.3081% | 14.55% | 32.29%
B | A, B North | tawnaghmore | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 19.2 | 58.3959 | 46.4212 | 0 | 1.8825 | 10.0922 | 11.9747 | 0% | 3.224% | 17.28% | 20.51%
B | A, B North | tawnaghmore | 2030 | 100% ECP | Pro-rata | IE wind priority | 19.2 | 58.3959 | 43.7162 | 0 | 2.2484 | 12.4313 | 14.6797 | 0% | 3.85% | 21.29% | 25.14%
B | A, B North | tawnaghmore | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 19.2 | 58.3959 | 44.5533 | 0 | 2.2484 | 11.5942 | 13.8426 | 0% | 3.85% | 19.85% | 23.7%
B | A, B North | tonroe | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 3.3267 | 10.1179 | 6.0223 | 3.1039 | 0.058743 | 0.93304 | 4.0956 | 30.68% | 0.5806% | 9.222% | 40.48%
B | A, B North | tonroe | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 3.3267 | 10.1179 | 7.0104 | 1.7642 | 0.031178 | 1.3121 | 3.1075 | 17.44% | 0.3081% | 12.97% | 30.71%
B | A, B North | tonroe | 2035 | 66% ECP | Pro-rata | IE wind not priority | 3.3267 | 10.1179 | 6.8508 | 1.7642 | 0.031178 | 1.4717 | 3.2671 | 17.44% | 0.3081% | 14.55% | 32.29%
B | A, B North | tonroe | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 4.99 | 15.1768 | 7.4856 | 4.4138 | 0.26418 | 3.0133 | 7.6913 | 29.08% | 1.741% | 19.85% | 50.68%
B | A, B North | tonroe | 2030 | 100% ECP | Pro-rata | IE wind not priority | 4.99 | 15.1768 | 7.268 | 4.4138 | 0.26418 | 3.2308 | 7.9088 | 29.08% | 1.741% | 21.29% | 52.11%
B | A, B North | tonroe | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 1.6633 | 5.0589 | 3.1907 | 0.90629 | 0.087648 | 0.8743 | 1.8682 | 17.91% | 1.733% | 17.28% | 36.93%
B | A, B North | tonroe | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 1.6633 | 5.0589 | 2.5294 | 1.6564 | 0.086989 | 0.78612 | 2.5295 | 32.74% | 1.72% | 15.54% | 50%
B | A, B North | tonroe | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 1.6633 | 5.0589 | 2.8829 | 1.2283 | 0.089088 | 0.85866 | 2.176 | 24.28% | 1.761% | 16.97% | 43.01%
B | A, B North | tonroe | 2030 | 33% ECP | Pro-rata | IE wind not priority | 1.6633 | 5.0589 | 3.0771 | 0.90629 | 0.087648 | 0.98789 | 1.9818 | 17.91% | 1.733% | 19.53% | 39.17%
B | A, B North | tawnaghmore | 2035 | 100% ECP | Pro-rata | IE wind priority | 19.2 | 58.3959 | 47.2358 | 0 | 0.60181 | 10.5583 | 11.1601 | 0% | 1.031% | 18.08% | 19.11%
B | A, B North | tawnaghmore | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 19.2 | 58.3959 | 51.9968 | 0 | 1.014 | 5.3851 | 6.3991 | 0% | 1.736% | 9.222% | 10.96%
B | A, B North | tawnaghmore | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 19.2 | 58.3959 | 50.3014 | 0 | 0.52151 | 7.573 | 8.0945 | 0% | 0.8931% | 12.97% | 13.86%
B | A, B North | tawnaghmore | 2035 | 66% ECP | Pro-rata | IE wind priority | 19.2 | 58.3959 | 49.3803 | 0 | 0.52151 | 8.4941 | 9.0156 | 0% | 0.8931% | 14.55% | 15.44%
B | A, B North | tonroe | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 1.6633 | 5.0589 | 2.6646 | 1.5579 | 0.087546 | 0.74887 | 2.3943 | 30.8% | 1.731% | 14.8% | 47.33%
B | A, B North | sligo | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 13.65 | 41.5158 | 31.6746 | 0 | 1.5985 | 8.2428 | 9.8412 | 0% | 3.85% | 19.85% | 23.7%
B | A, B North | sligo | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 4.08 | 12.4091 | 6.1205 | 3.6089 | 0.216 | 2.4638 | 6.2887 | 29.08% | 1.741% | 19.85% | 50.68%
B | A, B North | moy | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 6 | 18.2487 | 15.7192 | 0 | 0.16297 | 2.3666 | 2.5295 | 0% | 0.8931% | 12.97% | 13.86%
B | A, B North | moy | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 2.6667 | 2.8078 | 2.2037 | 0.42591 | 0.020532 | 0.1577 | 0.60414 | 15.17% | 0.7313% | 5.617% | 21.52%
B | A, B North | moy | 2035 | 66% ECP | Pro-rata | IE wind priority | 6 | 18.2487 | 15.4313 | 0 | 0.16297 | 2.6544 | 2.8174 | 0% | 0.8931% | 14.55% | 15.44%
B | A, B North | moy | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4 | 4.2117 | 2.6293 | 1.3161 | 0.092465 | 0.17386 | 1.5824 | 31.25% | 2.195% | 4.128% | 37.57%
B | A, B North | moy | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 6 | 18.2487 | 13.9229 | 0 | 0.70262 | 3.6232 | 4.3258 | 0% | 3.85% | 19.85% | 23.7%
B | A, B North | moy | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 2.6667 | 2.8078 | 2.2615 | 0.42591 | 0.020532 | 0.09985 | 0.54629 | 15.17% | 0.7313% | 3.556% | 19.46%
B | A, B North | moy | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 4 | 4.2117 | 2.6187 | 1.3161 | 0.092465 | 0.18444 | 1.593 | 31.25% | 2.195% | 4.379% | 37.82%
B | A, B North | moy | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 1.3333 | 1.4039 | 1.0702 | 0.18511 | 0.025898 | 0.12267 | 0.33368 | 13.19% | 1.845% | 8.738% | 23.77%
B | A, B North | moy | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 6 | 18.2487 | 14.5066 | 0 | 0.58828 | 3.1538 | 3.7421 | 0% | 3.224% | 17.28% | 20.51%
B | A, B North | moy | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 1.3333 | 1.4039 | 0.96146 | 0.30897 | 0.029341 | 0.10413 | 0.44244 | 22.01% | 2.09% | 7.417% | 31.52%
B | A, B North | moy | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 6 | 18.2487 | 14.6832 | 0 | 0.72978 | 2.8357 | 3.5655 | 0% | 3.999% | 15.54% | 19.54%
B | A, B North | moy | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 1.3333 | 1.4039 | 1.0108 | 0.26321 | 0.026135 | 0.10373 | 0.39307 | 18.75% | 1.862% | 7.389% | 28%
B | A, B North | moy | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 6 | 18.2487 | 14.8269 | 0 | 0.72044 | 2.7013 | 3.4218 | 0% | 3.948% | 14.8% | 18.75%
B | A, B North | moy | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 1.3333 | 1.4039 | 1.0379 | 0.22497 | 0.026329 | 0.11467 | 0.36597 | 16.02% | 1.875% | 8.168% | 26.07%
B | A, B North | moy | 2030 | 100% ECP | Pro-rata | IE wind priority | 6 | 18.2487 | 13.6613 | 0 | 0.70262 | 3.8848 | 4.5874 | 0% | 3.85% | 21.29% | 25.14%
B | A, B North | tonroe | 2035 | 100% ECP | Pro-rata | IE wind not priority | 4.99 | 15.1768 | 9.4445 | 2.9367 | 0.051517 | 2.7441 | 5.7323 | 19.35% | 0.3394% | 18.08% | 37.77%
B | A, B North | moy | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 6 | 18.2487 | 16.249 | 0 | 0.31688 | 1.6828 | 1.9997 | 0% | 1.736% | 9.222% | 10.96%
B | A, B North | moy | 2035 | 100% ECP | Pro-rata | IE wind priority | 6 | 18.2487 | 14.7612 | 0 | 0.18807 | 3.2995 | 3.4875 | 0% | 1.031% | 18.08% | 19.11%
B | A, B North | sligo | 2030 | 100% ECP | Pro-rata | IE wind priority | 13.65 | 41.5158 | 31.0795 | 0 | 1.5985 | 8.8379 | 10.4363 | 0% | 3.85% | 21.29% | 25.14%
B | A, B North | sligo | 2030 | 100% ECP | Pro-rata | IE wind not priority | 4.08 | 12.4091 | 5.9426 | 3.6089 | 0.216 | 2.6416 | 6.4665 | 29.08% | 1.741% | 21.29% | 52.11%
B | A, B North | sligo | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 13.65 | 41.5158 | 33.0026 | 0 | 1.3383 | 7.1749 | 8.5132 | 0% | 3.224% | 17.28% | 20.51%
B | A, B North | sligo | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 1.36 | 4.1364 | 2.6088 | 0.74101 | 0.071664 | 0.71486 | 1.5275 | 17.91% | 1.733% | 17.28% | 36.93%
B | A, B North | sligo | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 13.65 | 41.5158 | 33.4043 | 0 | 1.6603 | 6.4512 | 8.1115 | 0% | 3.999% | 15.54% | 19.54%
B | A, B North | sligo | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 1.36 | 4.1364 | 2.0682 | 1.3543 | 0.071125 | 0.64276 | 2.0682 | 32.74% | 1.72% | 15.54% | 50%
B | A, B North | sligo | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 13.65 | 41.5158 | 33.7313 | 0 | 1.639 | 6.1455 | 7.7845 | 0% | 3.948% | 14.8% | 18.75%
B | A, B North | moy | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 2.6667 | 2.8078 | 2.0853 | 0.60566 | 0.024124 | 0.092716 | 0.7225 | 21.57% | 0.8592% | 3.302% | 25.73%
B | A, B North | sligo | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 1.36 | 4.1364 | 2.1787 | 1.2738 | 0.07158 | 0.6123 | 1.9577 | 30.8% | 1.731% | 14.8% | 47.33%
B | A, B North | sligo | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 1.36 | 4.1364 | 2.3572 | 1.0043 | 0.072842 | 0.70207 | 1.7792 | 24.28% | 1.761% | 16.97% | 43.01%
B | A, B North | sligo | 2030 | 33% ECP | Pro-rata | IE wind priority | 13.65 | 41.5158 | 32.0705 | 0 | 1.3383 | 8.107 | 9.4454 | 0% | 3.224% | 19.53% | 22.75%
B | A, B North | sligo | 2030 | 33% ECP | Pro-rata | IE wind not priority | 1.36 | 4.1364 | 2.516 | 0.74101 | 0.071664 | 0.80773 | 1.6204 | 17.91% | 1.733% | 19.53% | 39.17%
B | A, B North | sligo | 2030 | Initial | Pro-rata | IE wind priority | 13.65 | 41.5158 | 32.1523 | 0 | 1.2006 | 8.1629 | 9.3635 | 0% | 2.892% | 19.66% | 22.55%
B | A, B North | moy | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 4 | 4.2117 | 3.062 | 0.92339 | 0.038692 | 0.18766 | 1.1497 | 21.92% | 0.9187% | 4.456% | 27.3%
B | A, B North | sligo | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 13.65 | 41.5158 | 32.9642 | 0 | 1.505 | 7.0465 | 8.5516 | 0% | 3.625% | 16.97% | 20.6%
B | A, B North | moy | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 6 | 18.2487 | 14.4898 | 0 | 0.66156 | 3.0974 | 3.7589 | 0% | 3.625% | 16.97% | 20.6%
B | B South | galway | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 0.4 | 0.51251 | 0.41794 | 0.084949 | 0.0095627 | 6.56e-05 | 0.094577 | 16.57% | 1.866% | 0.0128% | 18.45%
B | B South | uggool | 2030 | 33% ECP | Pro-rata | IE wind priority | 169 | 747.4128 | 651.8386 | 0 | 19.9265 | 75.6478 | 95.5742 | 0% | 2.666% | 10.12% | 12.79%
B | B South | uggool | 2030 | Initial | Pro-rata | IE wind priority | 169 | 747.4128 | 656.1533 | 0 | 17.4991 | 73.7604 | 91.2595 | 0% | 2.341% | 9.869% | 12.21%
B | B South | salthill | 2035 | 100% ECP | Pro-rata | IE wind priority | 40.9 | 124.3954 | 103.431 | 0 | 1.282 | 19.6824 | 20.9644 | 0% | 1.031% | 15.82% | 16.85%
B | B South | salthill | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 40.9 | 124.3954 | 110.2052 | 0 | 2.16 | 12.0301 | 14.1901 | 0% | 1.736% | 9.671% | 11.41%
B | B South | salthill | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 40.9 | 124.3954 | 109.0731 | 0 | 1.1109 | 14.2114 | 15.3223 | 0% | 0.8931% | 11.42% | 12.32%
B | B South | salthill | 2035 | 66% ECP | Pro-rata | IE wind priority | 40.9 | 124.3954 | 105.3756 | 0 | 1.1109 | 17.9089 | 19.0198 | 0% | 0.8931% | 14.4% | 15.29%
B | B South | salthill | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 40.9 | 124.3954 | 109.8201 | 0 | 4.7895 | 9.7858 | 14.5753 | 0% | 3.85% | 7.867% | 11.72%
B | B South | salthill | 2030 | 100% ECP | Pro-rata | IE wind priority | 40.9 | 124.3954 | 107.0502 | 0 | 4.7895 | 12.5556 | 17.3452 | 0% | 3.85% | 10.09% | 13.94%
B | B South | salthill | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 40.9 | 124.3954 | 110.7243 | 0 | 4.0101 | 9.6609 | 13.6711 | 0% | 3.224% | 7.766% | 10.99%
B | B South | salthill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 40.9 | 124.3954 | 109.9794 | 0 | 4.9747 | 9.4413 | 14.416 | 0% | 3.999% | 7.59% | 11.59%
B | B South | salthill | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 40.9 | 124.3954 | 110.4243 | 0 | 4.911 | 9.06 | 13.971 | 0% | 3.948% | 7.283% | 11.23%
B | B South | salthill | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 40.9 | 124.3954 | 108.9989 | 0 | 4.5096 | 10.8869 | 15.3965 | 0% | 3.625% | 8.752% | 12.38%
B | B South | salthill | 2030 | 33% ECP | Pro-rata | IE wind priority | 40.9 | 124.3954 | 107.7948 | 0 | 4.0101 | 12.5904 | 16.6005 | 0% | 3.224% | 10.12% | 13.34%
B | B South | uggool | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 169 | 747.4128 | 659.1516 | 0 | 22.8488 | 65.4125 | 88.2612 | 0% | 3.057% | 8.752% | 11.81%
B | B South | uggool | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 169 | 747.4128 | 667.481 | 0 | 25.496 | 54.4359 | 79.9319 | 0% | 3.411% | 7.283% | 10.69%
B | B South | uggool | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 169 | 747.4128 | 664.5421 | 0 | 26.1438 | 56.7269 | 82.8707 | 0% | 3.498% | 7.59% | 11.09%
B | B South | uggool | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 169 | 747.4128 | 669.4399 | 0 | 19.9265 | 58.0465 | 77.9729 | 0% | 2.666% | 7.766% | 10.43%
B | C | cashla | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 311 | 398.4803 | 241.1805 | 125.75 | 8.7793 | 22.7705 | 157.2998 | 31.56% | 2.203% | 5.714% | 39.47%
B | C | cashla | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 311 | 398.4803 | 239.7332 | 125.75 | 8.7793 | 24.2178 | 158.747 | 31.56% | 2.203% | 6.078% | 39.84%
B | C | cashla | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 103.6666 | 132.8266 | 108.5992 | 18.0493 | 2.4598 | 3.7183 | 24.2275 | 13.59% | 1.852% | 2.799% | 18.24%
B | C | cashla | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 103.6666 | 132.8266 | 96.3576 | 29.9419 | 2.7817 | 3.7455 | 36.469 | 22.54% | 2.094% | 2.82% | 27.46%
B | C | cashla | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 103.6666 | 132.8266 | 100.7723 | 25.7401 | 2.458 | 3.8563 | 32.0544 | 19.38% | 1.851% | 2.903% | 24.13%
B | C | cashla | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 103.6666 | 132.8266 | 104.2862 | 22.0159 | 2.4783 | 4.0462 | 28.5404 | 16.57% | 1.866% | 3.046% | 21.49%
B | B South | salthill | 2030 | Initial | Pro-rata | IE wind priority | 40.9 | 124.3954 | 108.5217 | 0 | 3.5974 | 12.2763 | 15.8736 | 0% | 2.892% | 9.869% | 12.76%
B | C | cashla | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 103.6666 | 132.8266 | 108.0571 | 18.0493 | 2.4598 | 4.2603 | 24.7695 | 13.59% | 1.852% | 3.207% | 18.65%
B | B South | uggool | 2035 | 100% ECP | Pro-rata | IE wind priority | 169 | 747.4128 | 622.9457 | 0 | 6.2083 | 118.2589 | 124.4672 | 0% | 0.8306% | 15.82% | 16.65%
B | B South | uggool | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 169 | 747.4128 | 664.0472 | 0 | 11.0843 | 72.2813 | 83.3656 | 0% | 1.483% | 9.671% | 11.15%
B | B South | uggool | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 169 | 747.4128 | 656.5694 | 0 | 5.4563 | 85.3871 | 90.8434 | 0% | 0.73% | 11.42% | 12.15%
B | B South | uggool | 2035 | 66% ECP | Pro-rata | IE wind priority | 169 | 747.4128 | 634.3534 | 0 | 5.4563 | 107.6031 | 113.0594 | 0% | 0.73% | 14.4% | 15.13%
B | B South | uggool | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 169 | 747.4128 | 664.5332 | 0 | 24.0829 | 58.7967 | 82.8796 | 0% | 3.222% | 7.867% | 11.09%
B | B South | uggool | 2030 | 100% ECP | Pro-rata | IE wind priority | 169 | 747.4128 | 647.891 | 0 | 24.0829 | 75.4389 | 99.5218 | 0% | 3.222% | 10.09% | 13.32%
B | B South | knockranny | 2035 | 100% ECP | Pro-rata | IE wind priority | 33.6 | 148.598 | 123.8519 | 0 | 1.2343 | 23.5118 | 24.7461 | 0% | 0.8306% | 15.82% | 16.65%
B | B South | knockranny | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 124.9667 | 552.6726 | 390.528 | 105.0169 | 8.7586 | 48.3691 | 162.1447 | 19% | 1.585% | 8.752% | 29.34%
B | B South | knockranny | 2030 | 33% ECP | Pro-rata | IE wind priority | 33.6 | 148.598 | 129.5963 | 0 | 3.9617 | 15.04 | 19.0017 | 0% | 2.666% | 10.12% | 12.79%
B | B South | knockranny | 2030 | 33% ECP | Pro-rata | IE wind not priority | 124.9667 | 552.6726 | 413.1152 | 75.1819 | 8.438 | 55.9376 | 139.5575 | 13.6% | 1.527% | 10.12% | 25.25%
B | B South | knockranny | 2030 | Initial | Pro-rata | IE wind priority | 33.6 | 148.598 | 130.4541 | 0 | 3.4791 | 14.6648 | 18.1439 | 0% | 2.341% | 9.869% | 12.21%
B | B South | knockranny | 2030 | Initial | Pro-rata | IE wind not priority | 109.2 | 482.9437 | 381.0298 | 46.8655 | 7.3878 | 47.6606 | 101.9139 | 9.704% | 1.53% | 9.869% | 21.1%
B | B South | galway | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 1.2 | 1.5375 | 1.1617 | 0.33807 | 0.013934 | 0.023811 | 0.37582 | 21.99% | 0.9062% | 1.549% | 24.44%
B | B South | knockranny | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 33.6 | 148.598 | 131.0503 | 0 | 4.5427 | 13.0051 | 17.5478 | 0% | 3.057% | 8.752% | 11.81%
B | B South | galway | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 0.8 | 1.025 | 0.78746 | 0.22521 | 0.0087576 | 0.0036073 | 0.23757 | 21.97% | 0.8544% | 0.3519% | 23.18%
B | B South | galway | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 0.8 | 1.025 | 0.84864 | 0.15701 | 0.0073903 | 0.011987 | 0.17639 | 15.32% | 0.721% | 1.169% | 17.21%
B | B South | galway | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 1.2 | 1.5375 | 1.0185 | 0.48521 | 0.033875 | 0 | 0.51908 | 31.56% | 2.203% | 0% | 33.76%
B | B South | galway | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 1.2 | 1.5375 | 1.0167 | 0.48521 | 0.033875 | 0.0017877 | 0.52087 | 31.56% | 2.203% | 0.1163% | 33.88%
B | B South | galway | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 0.4 | 0.51251 | 0.43338 | 0.069644 | 0.0094913 | 0 | 0.079135 | 13.59% | 1.852% | 0% | 15.44%
B | B South | galway | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 0.4 | 0.51251 | 0.38625 | 0.11553 | 0.010733 | 0 | 0.12626 | 22.54% | 2.094% | 0% | 24.64%
B | B South | galway | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 0.4 | 0.51251 | 0.40371 | 0.099319 | 0.0094842 | 0 | 0.1088 | 19.38% | 1.851% | 0% | 21.23%
B | B South | galway | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 0.8 | 1.025 | 0.85918 | 0.15701 | 0.0073903 | 0.0014434 | 0.16585 | 15.32% | 0.721% | 0.1408% | 16.18%
B | B South | galway | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 0.4 | 0.51251 | 0.43338 | 0.069644 | 0.0094913 | 0 | 0.079135 | 13.59% | 1.852% | 0% | 15.44%
B | B South | knockranny | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 124.9667 | 552.6726 | 366.0403 | 137.4212 | 8.9587 | 40.2525 | 186.6323 | 24.86% | 1.621% | 7.283% | 33.77%
B | B South | knockranny | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 124.9667 | 552.6726 | 353.8891 | 147.7561 | 9.0809 | 41.9466 | 198.7836 | 26.73% | 1.643% | 7.59% | 35.97%
B | B South | knockranny | 2035 | 100% ECP | Pro-rata | IE wind not priority | 156.5 | 692.1308 | 475.6721 | 104.8706 | 2.0761 | 109.5119 | 216.4587 | 15.15% | 0.3% | 15.82% | 31.27%
B | B South | knockranny | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 33.6 | 148.598 | 132.0236 | 0 | 2.2037 | 14.3707 | 16.5745 | 0% | 1.483% | 9.671% | 11.15%
B | B South | knockranny | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 140.7333 | 622.4016 | 401.0009 | 157.8386 | 3.3705 | 60.1916 | 221.4007 | 25.36% | 0.5415% | 9.671% | 35.57%
B | B South | knockranny | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 33.6 | 148.598 | 130.5369 | 0 | 1.0848 | 16.9764 | 18.0612 | 0% | 0.73% | 11.42% | 12.15%
B | B South | knockranny | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 140.7333 | 622.4016 | 465.0284 | 84.5541 | 1.7138 | 71.1054 | 157.3732 | 13.59% | 0.2754% | 11.42% | 25.28%
B | B South | knockranny | 2035 | 66% ECP | Pro-rata | IE wind priority | 33.6 | 148.598 | 126.12 | 0 | 1.0848 | 21.3933 | 22.4781 | 0% | 0.73% | 14.4% | 15.13%
B | B South | knockranny | 2035 | 66% ECP | Pro-rata | IE wind not priority | 140.7333 | 622.4016 | 446.5282 | 84.5541 | 1.7138 | 89.6056 | 175.8735 | 13.59% | 0.2754% | 14.4% | 28.26%
B | B South | knockranny | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 33.6 | 148.598 | 132.7063 | 0 | 5.069 | 10.8227 | 15.8918 | 0% | 3.411% | 7.283% | 10.69%
B | B South | knockranny | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 33.6 | 148.598 | 132.1202 | 0 | 4.7881 | 11.6898 | 16.4778 | 0% | 3.222% | 7.867% | 11.09%
B | B South | knockranny | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 156.5 | 692.1308 | 467.8999 | 159.0534 | 10.7296 | 54.4478 | 224.2309 | 22.98% | 1.55% | 7.867% | 32.4%
B | B South | knockranny | 2030 | 100% ECP | Pro-rata | IE wind priority | 33.6 | 148.598 | 128.8115 | 0 | 4.7881 | 14.9985 | 19.7866 | 0% | 3.222% | 10.09% | 13.32%
B | B South | knockranny | 2030 | 100% ECP | Pro-rata | IE wind not priority | 156.5 | 692.1308 | 452.4886 | 159.0534 | 10.7296 | 69.8591 | 239.6422 | 22.98% | 1.55% | 10.09% | 34.62%
B | B South | knockranny | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 33.6 | 148.598 | 133.0957 | 0 | 3.9617 | 11.5406 | 15.5023 | 0% | 2.666% | 7.766% | 10.43%
B | B South | knockranny | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 124.9667 | 552.6726 | 426.1304 | 75.1819 | 8.438 | 42.9223 | 126.5422 | 13.6% | 1.527% | 7.766% | 22.9%
B | B South | knockranny | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 33.6 | 148.598 | 132.122 | 0 | 5.1978 | 11.2782 | 16.4761 | 0% | 3.498% | 7.59% | 11.09%
B | A, B North | bellacorick | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 6.45 | 19.6174 | 15.939 | 0 | 0.77448 | 2.9039 | 3.6784 | 0% | 3.948% | 14.8% | 18.75%
B | A, B North | moy | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 1.3333 | 1.4039 | 1.0609 | 0.18511 | 0.025898 | 0.13197 | 0.34298 | 13.19% | 1.845% | 9.401% | 24.43%
B | A, B North | moy | 2030 | Initial | Pro-rata | IE wind priority | 6 | 18.2487 | 14.1329 | 0 | 0.52773 | 3.5881 | 4.1158 | 0% | 2.892% | 19.66% | 22.55%
B | A, B North | castlebar | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 3.9712 | 2.0177 | 0.14086 | 0.26393 | 2.4224 | 31.56% | 2.203% | 4.128% | 37.89%
B | A, B North | castlebar | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 8.5 | 25.8523 | 19.7241 | 0 | 0.99538 | 5.1329 | 6.1282 | 0% | 3.85% | 19.85% | 23.7%
B | A, B North | castlebar | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 6.8 | 20.6819 | 10.2008 | 6.0148 | 0.36001 | 4.1063 | 10.4811 | 29.08% | 1.741% | 19.85% | 50.68%
B | A, B North | castlebar | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 3.9551 | 2.0177 | 0.14086 | 0.27999 | 2.4385 | 31.56% | 2.203% | 4.379% | 38.14%
B | A, B North | castlebar | 2030 | 100% ECP | Pro-rata | IE wind priority | 8.5 | 25.8523 | 19.3535 | 0 | 0.99538 | 5.5034 | 6.4988 | 0% | 3.85% | 21.29% | 25.14%
B | A, B North | castlebar | 2030 | 100% ECP | Pro-rata | IE wind not priority | 6.8 | 20.6819 | 9.9043 | 6.0148 | 0.36001 | 4.4027 | 10.7776 | 29.08% | 1.741% | 21.29% | 52.11%
B | A, B North | castlebar | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 1.6633 | 2.1312 | 1.6159 | 0.2896 | 0.039468 | 0.18623 | 0.5153 | 13.59% | 1.852% | 8.738% | 24.18%
B | A, B North | castlebar | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 8.5 | 25.8523 | 20.5511 | 0 | 0.8334 | 4.4679 | 5.3013 | 0% | 3.224% | 17.28% | 20.51%
B | A, B North | castlebar | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 6.8 | 20.6819 | 13.0442 | 3.7051 | 0.35832 | 3.5743 | 7.6377 | 17.91% | 1.733% | 17.28% | 36.93%
B | A, B North | castlebar | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 1.6633 | 2.1312 | 1.4481 | 0.48042 | 0.044632 | 0.15807 | 0.68312 | 22.54% | 2.094% | 7.417% | 32.05%
B | A, B North | castlebar | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 8.5 | 25.8523 | 20.8012 | 0 | 1.0339 | 4.0173 | 5.0511 | 0% | 3.999% | 15.54% | 19.54%
B | A, B North | castlebar | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 6.8 | 20.6819 | 10.3408 | 6.7716 | 0.35563 | 3.2138 | 10.341 | 32.74% | 1.72% | 15.54% | 50%
B | A, B North | castlebar | 2035 | 66% ECP | Pro-rata | IE wind not priority | 6.8 | 20.6819 | 14.0036 | 3.6062 | 0.06373 | 3.0083 | 6.6783 | 17.44% | 0.3081% | 14.55% | 32.29%
B | A, B North | castlebar | 2035 | 66% ECP | Pro-rata | IE wind priority | 8.5 | 25.8523 | 21.8611 | 0 | 0.23088 | 3.7604 | 3.9913 | 0% | 0.8931% | 14.55% | 15.44%
B | A, B North | castlebar | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 3.3267 | 4.2624 | 3.3394 | 0.65292 | 0.030731 | 0.2394 | 0.92305 | 15.32% | 0.721% | 5.617% | 21.66%
B | A, B North | castlebar | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 6.8 | 20.6819 | 14.3298 | 3.6062 | 0.06373 | 2.6821 | 6.352 | 17.44% | 0.3081% | 12.97% | 30.71%
B | A, B North | cunghill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 34.8 | 105.8425 | 85.1627 | 0 | 4.2327 | 16.4471 | 20.6799 | 0% | 3.999% | 15.54% | 19.54%
B | A, B North | cunghill | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 34.8 | 105.8425 | 85.9963 | 0 | 4.1786 | 15.6677 | 19.8462 | 0% | 3.948% | 14.8% | 18.75%
B | A, B North | cunghill | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 34.8 | 105.8425 | 84.0407 | 0 | 3.837 | 17.9648 | 21.8018 | 0% | 3.625% | 16.97% | 20.6%
B | A, B North | cunghill | 2030 | 33% ECP | Pro-rata | IE wind priority | 34.8 | 105.8425 | 81.762 | 0 | 3.412 | 20.6684 | 24.0805 | 0% | 3.224% | 19.53% | 22.75%
B | A, B North | cunghill | 2030 | Initial | Pro-rata | IE wind priority | 34.8 | 105.8425 | 81.9707 | 0 | 3.0608 | 20.811 | 23.8719 | 0% | 2.892% | 19.66% | 22.55%
B | A, B North | castlebar | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 1.6633 | 2.1312 | 1.5213 | 0.413 | 0.039438 | 0.15748 | 0.60991 | 19.38% | 1.851% | 7.389% | 28.62%
B | A, B North | castlebar | 2035 | 100% ECP | Pro-rata | IE wind priority | 8.5 | 25.8523 | 20.9117 | 0 | 0.26643 | 4.6742 | 4.9407 | 0% | 1.031% | 18.08% | 19.11%
B | A, B North | castlebar | 2035 | 100% ECP | Pro-rata | IE wind not priority | 6.8 | 20.6819 | 12.8703 | 4.002 | 0.070204 | 3.7394 | 7.8115 | 19.35% | 0.3394% | 18.08% | 37.77%
B | A, B North | castlebar | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 3.3267 | 4.2624 | 3.1488 | 0.93648 | 0.036417 | 0.14075 | 1.1136 | 21.97% | 0.8544% | 3.302% | 26.13%
B | A, B North | castlebar | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 8.5 | 25.8523 | 23.0194 | 0 | 0.44891 | 2.384 | 2.8329 | 0% | 1.736% | 9.222% | 10.96%
B | A, B North | castlebar | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 6.8 | 20.6819 | 12.31 | 6.3446 | 0.12008 | 1.9072 | 8.3718 | 30.68% | 0.5806% | 9.222% | 40.48%
B | A, B North | castlebar | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 3.3267 | 4.2624 | 3.4272 | 0.65292 | 0.030731 | 0.15158 | 0.83523 | 15.32% | 0.721% | 3.556% | 19.6%
B | A, B North | castlebar | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 8.5 | 25.8523 | 22.2688 | 0 | 0.23088 | 3.3526 | 3.5835 | 0% | 0.8931% | 12.97% | 13.86%
B | A, B North | castlebar | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 4.99 | 6.3936 | 4.645 | 1.4058 | 0.057942 | 0.28488 | 1.7486 | 21.99% | 0.9062% | 4.456% | 27.35%
B | A, B North | castlebar | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 8.5 | 25.8523 | 21.0048 | 0 | 1.0206 | 3.8269 | 4.8475 | 0% | 3.948% | 14.8% | 18.75%
B | A, B North | castlebar | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 6.8 | 20.6819 | 10.8934 | 6.3691 | 0.3579 | 3.0615 | 9.7885 | 30.8% | 1.731% | 14.8% | 47.33%
B | A, B North | castlebar | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 1.6633 | 2.1312 | 1.5641 | 0.35325 | 0.039765 | 0.17407 | 0.56708 | 16.57% | 1.866% | 8.168% | 26.61%
B | A, B North | bellacorick | 2035 | 66% ECP | Pro-rata | IE wind not priority | 271.2665 | 825.044 | 558.6342 | 143.8592 | 2.5423 | 120.0083 | 266.4098 | 17.44% | 0.3081% | 14.55% | 32.29%
B | A, B North | bellacorick | 2035 | 66% ECP | Pro-rata | IE wind not priority | 105.6 | 321.1772 | 217.4679 | 56.0022 | 0.98969 | 46.7174 | 103.7093 | 17.44% | 0.3081% | 14.55% | 32.29%
B | A, B North | bellacorick | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 6.45 | 19.6174 | 14.9671 | 0 | 0.75531 | 3.8949 | 4.6503 | 0% | 3.85% | 19.85% | 23.7%
B | A, B North | bellacorick | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 345.3 | 1050.2133 | 517.9889 | 305.4286 | 18.2809 | 208.515 | 532.2244 | 29.08% | 1.741% | 19.85% | 50.68%
B | A, B North | bellacorick | 2035 | 66% ECP | Pro-rata | IE wind priority | 6.45 | 19.6174 | 16.5887 | 0 | 0.1752 | 2.8535 | 3.0287 | 0% | 0.8931% | 14.55% | 15.44%
B | A, B North | bellacorick | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 116.9 | 355.5457 | 175.3632 | 103.4017 | 6.1889 | 70.5919 | 180.1826 | 29.08% | 1.741% | 19.85% | 50.68%
B | A, B North | bellacorick | 2030 | 100% ECP | Pro-rata | IE wind not priority | 345.3 | 1050.2133 | 502.935 | 305.4286 | 18.2809 | 223.5688 | 547.2783 | 29.08% | 1.741% | 21.29% | 52.11%
B | A, B North | bellacorick | 2030 | 100% ECP | Pro-rata | IE wind not priority | 116.9 | 355.5457 | 170.2667 | 103.4017 | 6.1889 | 75.6884 | 185.279 | 29.08% | 1.741% | 21.29% | 52.11%
B | A, B North | bellacorick | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 6.45 | 19.6174 | 15.5946 | 0 | 0.6324 | 3.3903 | 4.0227 | 0% | 3.224% | 17.28% | 20.51%
B | A, B North | bellacorick | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 197.2333 | 599.8755 | 378.3451 | 107.4649 | 10.3931 | 103.6724 | 221.5303 | 17.91% | 1.733% | 17.28% | 36.93%
B | A, B North | bellacorick | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 94.3 | 286.8089 | 180.8921 | 51.3805 | 4.9691 | 49.5672 | 105.9168 | 17.91% | 1.733% | 17.28% | 36.93%
B | A, B North | bellacorick | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 6.45 | 19.6174 | 15.7845 | 0 | 0.78451 | 3.0484 | 3.8329 | 0% | 3.999% | 15.54% | 19.54%
B | A, B North | bellacorick | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 197.2333 | 599.8755 | 299.935 | 196.4094 | 10.3149 | 93.2162 | 299.9405 | 32.74% | 1.72% | 15.54% | 50%
B | A, B North | bellacorick | 2030 | 100% ECP | Pro-rata | IE wind priority | 6.45 | 19.6174 | 14.6859 | 0 | 0.75531 | 4.1761 | 4.9314 | 0% | 3.85% | 21.29% | 25.14%
B | A, B North | cunghill | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 34.8 | 105.8425 | 84.1384 | 0 | 3.412 | 18.292 | 21.7041 | 0% | 3.224% | 17.28% | 20.51%
B | A, B North | bellacorick | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 105.6 | 321.1772 | 222.5339 | 56.0022 | 0.98969 | 41.6515 | 98.6434 | 17.44% | 0.3081% | 12.97% | 30.71%
B | A, B North | bellacorick | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 6.45 | 19.6174 | 16.8981 | 0 | 0.1752 | 2.5441 | 2.7192 | 0% | 0.8931% | 12.97% | 13.86%
B | A, B North | castlebar | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 8.5 | 25.8523 | 20.5272 | 0 | 0.93721 | 4.3879 | 5.3252 | 0% | 3.625% | 16.97% | 20.6%
B | A, B North | castlebar | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 6.8 | 20.6819 | 11.7859 | 5.0214 | 0.36421 | 3.5104 | 8.896 | 24.28% | 1.761% | 16.97% | 43.01%
B | A, B North | castlebar | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 1.6633 | 2.1312 | 1.6018 | 0.2896 | 0.039468 | 0.20035 | 0.52942 | 13.59% | 1.852% | 9.401% | 24.84%
B | A, B North | castlebar | 2030 | 33% ECP | Pro-rata | IE wind priority | 8.5 | 25.8523 | 19.9706 | 0 | 0.8334 | 5.0483 | 5.8817 | 0% | 3.224% | 19.53% | 22.75%
B | A, B North | castlebar | 2030 | 33% ECP | Pro-rata | IE wind not priority | 6.8 | 20.6819 | 12.5798 | 3.7051 | 0.35832 | 4.0387 | 8.102 | 17.91% | 1.733% | 19.53% | 39.17%
B | A, B North | castlebar | 2030 | Initial | Pro-rata | IE wind priority | 8.5 | 25.8523 | 20.0216 | 0 | 0.74762 | 5.0832 | 5.8308 | 0% | 2.892% | 19.66% | 22.55%
B | A, B North | castlebar | 2030 | Initial | Pro-rata | IE wind not priority | 6.8 | 20.6819 | 13.5315 | 2.7139 | 0.36995 | 4.0665 | 7.1503 | 13.12% | 1.789% | 19.66% | 34.57%
B | A, B North | bellacorick | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 271.2665 | 825.044 | 571.6478 | 143.8592 | 2.5423 | 106.9948 | 253.3963 | 17.44% | 0.3081% | 12.97% | 30.71%
B | A, B North | bellacorick | 2035 | 100% ECP | Pro-rata | IE wind priority | 6.45 | 19.6174 | 15.8683 | 0 | 0.20217 | 3.5469 | 3.7491 | 0% | 1.031% | 18.08% | 19.11%
B | A, B North | bellacorick | 2035 | 100% ECP | Pro-rata | IE wind not priority | 345.3 | 1050.2133 | 653.5475 | 203.2168 | 3.5649 | 189.8841 | 396.6659 | 19.35% | 0.3394% | 18.08% | 37.77%
B | A, B North | bellacorick | 2035 | 100% ECP | Pro-rata | IE wind not priority | 116.9 | 355.5457 | 221.256 | 68.7983 | 1.2069 | 64.2846 | 134.2897 | 19.35% | 0.3394% | 18.08% | 37.77%
B | A, B North | bellacorick | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 6.45 | 19.6174 | 17.4677 | 0 | 0.34064 | 1.809 | 2.1497 | 0% | 1.736% | 9.222% | 10.96%
B | A, B North | bellacorick | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 271.2665 | 825.044 | 491.0734 | 253.0978 | 4.7901 | 76.0828 | 333.9707 | 30.68% | 0.5806% | 9.222% | 40.48%
B | A, B North | bellacorick | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 105.6 | 321.1772 | 191.1675 | 98.5272 | 1.8647 | 29.6179 | 130.0098 | 30.68% | 0.5806% | 9.222% | 40.48%
B | A, B North | moy | 2030 | 33% ECP | Pro-rata | IE wind priority | 6 | 18.2487 | 14.0969 | 0 | 0.58828 | 3.5635 | 4.1518 | 0% | 3.224% | 19.53% | 22.75%
B | A, B North | cunghill | 2030 | 100% ECP | Pro-rata | IE wind priority | 34.8 | 105.8425 | 79.2356 | 0 | 4.0752 | 22.5317 | 26.6069 | 0% | 3.85% | 21.29% | 25.14%
B | A, B North | glenree | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 34.15 | 103.8656 | 84.39 | 0 | 4.1005 | 15.375 | 19.4756 | 0% | 3.948% | 14.8% | 18.75%
B | A, B North | glenree | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 44.8 | 136.257 | 71.7684 | 41.9608 | 2.3579 | 20.1699 | 64.4886 | 30.8% | 1.731% | 14.8% | 47.33%
B | A, B North | glenree | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 34.15 | 103.8656 | 82.471 | 0 | 3.7654 | 17.6292 | 21.3946 | 0% | 3.625% | 16.97% | 20.6%
B | A, B North | glenree | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 44.8 | 136.257 | 77.6481 | 33.0824 | 2.3995 | 23.1271 | 58.6089 | 24.28% | 1.761% | 16.97% | 43.01%
B | A, B North | glenree | 2030 | 33% ECP | Pro-rata | IE wind priority | 34.15 | 103.8656 | 80.2349 | 0 | 3.3483 | 20.2824 | 23.6307 | 0% | 3.224% | 19.53% | 22.75%
B | A, B North | glenree | 2030 | 33% ECP | Pro-rata | IE wind not priority | 44.8 | 136.257 | 82.8789 | 24.4098 | 2.3607 | 26.6076 | 53.3782 | 17.91% | 1.733% | 19.53% | 39.17%
B | A, B North | glenree | 2030 | Initial | Pro-rata | IE wind priority | 34.15 | 103.8656 | 80.4396 | 0 | 3.0037 | 20.4223 | 23.426 | 0% | 2.892% | 19.66% | 22.55%
B | A, B North | glenree | 2030 | Initial | Pro-rata | IE wind not priority | 43.15 | 131.2386 | 85.8656 | 17.221 | 2.3475 | 25.8045 | 45.373 | 13.12% | 1.789% | 19.66% | 34.57%
B | A, B North | firlough | 2035 | 100% ECP | Pro-rata | IE wind not priority | 75.6 | 229.9338 | 143.0877 | 44.4923 | 0.7805 | 41.5732 | 86.846 | 19.35% | 0.3394% | 18.08% | 37.77%
B | A, B North | firlough | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 59.5 | 180.9663 | 107.7127 | 55.5148 | 1.0507 | 16.6881 | 73.2536 | 30.68% | 0.5806% | 9.222% | 40.48%
B | A, B North | firlough | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 59.5 | 180.9663 | 125.386 | 31.5543 | 0.55764 | 23.4684 | 55.5803 | 17.44% | 0.3081% | 12.97% | 30.71%
B | A, B North | firlough | 2035 | 66% ECP | Pro-rata | IE wind not priority | 59.5 | 180.9663 | 122.5316 | 31.5543 | 0.55764 | 26.3228 | 58.4347 | 17.44% | 0.3081% | 14.55% | 32.29%
B | A, B North | firlough | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 75.6 | 229.9338 | 113.4085 | 66.8706 | 4.0024 | 45.6523 | 116.5252 | 29.08% | 1.741% | 19.85% | 50.68%
B | A, B North | glenree | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 44.8 | 136.257 | 68.1279 | 44.6129 | 2.343 | 21.1733 | 68.1291 | 32.74% | 1.72% | 15.54% | 50%
B | A, B North | glenree | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 34.15 | 103.8656 | 83.572 | 0 | 4.1537 | 16.1399 | 20.2936 | 0% | 3.999% | 15.54% | 19.54%
B | A, B North | glenree | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 44.8 | 136.257 | 85.9381 | 24.4098 | 2.3607 | 23.5484 | 50.3189 | 17.91% | 1.733% | 17.28% | 36.93%
B | A, B North | glenree | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 34.15 | 103.8656 | 82.5669 | 0 | 3.3483 | 17.9504 | 21.2987 | 0% | 3.224% | 17.28% | 20.51%
B | A, B North | glenree | 2035 | 100% ECP | Pro-rata | IE wind priority | 34.15 | 103.8656 | 84.0157 | 0 | 1.0704 | 18.7794 | 19.8499 | 0% | 1.031% | 18.08% | 19.11%
B | A, B North | glenree | 2035 | 100% ECP | Pro-rata | IE wind not priority | 48.1 | 146.2938 | 91.0386 | 28.3079 | 0.49659 | 26.4507 | 55.2552 | 19.35% | 0.3394% | 18.08% | 37.77%
B | A, B North | glenree | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 34.15 | 103.8656 | 92.4839 | 0 | 1.8035 | 9.5781 | 11.3817 | 0% | 1.736% | 9.222% | 10.96%
B | A, B North | glenree | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 46.45 | 141.2754 | 84.0884 | 43.3389 | 0.82023 | 13.0279 | 57.1871 | 30.68% | 0.5806% | 9.222% | 40.48%
B | A, B North | glenree | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 34.15 | 103.8656 | 89.4683 | 0 | 0.92759 | 13.4697 | 14.3973 | 0% | 0.8931% | 12.97% | 13.86%
B | A, B North | firlough | 2030 | 100% ECP | Pro-rata | IE wind not priority | 75.6 | 229.9338 | 110.1126 | 66.8706 | 4.0024 | 48.9482 | 119.8211 | 29.08% | 1.741% | 21.29% | 52.11%
B | A, B North | glenree | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 46.45 | 141.2754 | 97.8854 | 24.6336 | 0.43533 | 18.3211 | 43.39 | 17.44% | 0.3081% | 12.97% | 30.71%
B | A, B North | glenree | 2035 | 66% ECP | Pro-rata | IE wind not priority | 46.45 | 141.2754 | 95.6571 | 24.6336 | 0.43533 | 20.5495 | 45.6184 | 17.44% | 0.3081% | 14.55% | 32.29%
B | A, B North | glenree | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 34.15 | 103.8656 | 79.2445 | 0 | 3.9991 | 20.622 | 24.6211 | 0% | 3.85% | 19.85% | 23.7%
B | A, B North | glenree | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 48.1 | 146.2938 | 72.1554 | 42.5459 | 2.5465 | 29.046 | 74.1384 | 29.08% | 1.741% | 19.85% | 50.68%
B | A, B North | glenree | 2030 | 100% ECP | Pro-rata | IE wind priority | 34.15 | 103.8656 | 77.7557 | 0 | 3.9991 | 22.1108 | 26.1099 | 0% | 3.85% | 21.29% | 25.14%
B | A, B North | glenree | 2030 | 100% ECP | Pro-rata | IE wind not priority | 48.1 | 146.2938 | 70.0584 | 42.5459 | 2.5465 | 31.1429 | 76.2354 | 29.08% | 1.741% | 21.29% | 52.11%
B | A, B North | glenree | 2035 | 66% ECP | Pro-rata | IE wind priority | 34.15 | 103.8656 | 87.83 | 0 | 0.92759 | 15.108 | 16.0355 | 0% | 0.8931% | 14.55% | 15.44%
B | A, B North | firlough | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 43.4 | 131.999 | 83.2526 | 23.647 | 2.2869 | 22.8125 | 48.7464 | 17.91% | 1.733% | 17.28% | 36.93%
B | A, B North | firlough | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 43.4 | 131.999 | 65.9989 | 43.2187 | 2.2697 | 20.5117 | 66.0001 | 32.74% | 1.72% | 15.54% | 50%
B | A, B North | firlough | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 43.4 | 131.999 | 69.5256 | 40.6495 | 2.2843 | 19.5396 | 62.4733 | 30.8% | 1.731% | 14.8% | 47.33%
B | A, B North | dalton | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 40.8 | 124.0912 | 98.6451 | 0 | 4.0003 | 21.4458 | 25.4462 | 0% | 3.224% | 17.28% | 20.51%
B | A, B North | dalton | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 10.6667 | 13.6671 | 9.2863 | 3.0808 | 0.28622 | 1.0137 | 4.3808 | 22.54% | 2.094% | 7.417% | 32.05%
B | A, B North | dalton | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 40.8 | 124.0912 | 99.8459 | 0 | 4.9625 | 19.2828 | 24.2454 | 0% | 3.999% | 15.54% | 19.54%
B | A, B North | dalton | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 10.6667 | 13.6671 | 9.7558 | 2.6485 | 0.25291 | 1.0099 | 3.9113 | 19.38% | 1.851% | 7.389% | 28.62%
B | A, B North | dalton | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 40.8 | 124.0912 | 100.8232 | 0 | 4.899 | 18.369 | 23.268 | 0% | 3.948% | 14.8% | 18.75%
B | A, B North | dalton | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 10.6667 | 13.6671 | 10.0305 | 2.2653 | 0.25501 | 1.1163 | 3.6366 | 16.57% | 1.866% | 8.168% | 26.61%
B | A, B North | dalton | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 40.8 | 124.0912 | 98.5305 | 0 | 4.4986 | 21.0622 | 25.5607 | 0% | 3.625% | 16.97% | 20.6%
B | A, B North | dalton | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 10.6667 | 13.6671 | 10.3626 | 1.8572 | 0.2531 | 1.1942 | 3.3045 | 13.59% | 1.852% | 8.738% | 24.18%
B | A, B North | dalton | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 10.6667 | 13.6671 | 10.272 | 1.8572 | 0.2531 | 1.2848 | 3.3951 | 13.59% | 1.852% | 9.401% | 24.84%
B | A, B North | dalton | 2030 | Initial | Pro-rata | IE Solar not priority | 4 | 5.1251 | 3.8942 | 0.40522 | 0.06628 | 0.75943 | 1.2309 | 7.907% | 1.293% | 14.82% | 24.02%
B | A, B North | dalton | 2030 | Initial | Pro-rata | IE wind priority | 40.8 | 124.0912 | 96.1035 | 0 | 3.5886 | 24.3991 | 27.9877 | 0% | 2.892% | 19.66% | 22.55%
B | A, B North | cunghill | 2035 | 100% ECP | Pro-rata | IE wind priority | 34.8 | 105.8425 | 85.6148 | 0 | 1.0908 | 19.1369 | 20.2277 | 0% | 1.031% | 18.08% | 19.11%
B | A, B North | cunghill | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 34.8 | 105.8425 | 94.2442 | 0 | 1.8379 | 9.7604 | 11.5983 | 0% | 1.736% | 9.222% | 10.96%
B | A, B North | cunghill | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 34.8 | 105.8425 | 91.1712 | 0 | 0.94524 | 13.726 | 14.6713 | 0% | 0.8931% | 12.97% | 13.86%
B | A, B North | cunghill | 2035 | 66% ECP | Pro-rata | IE wind priority | 34.8 | 105.8425 | 89.5018 | 0 | 0.94524 | 15.3955 | 16.3408 | 0% | 0.8931% | 14.55% | 15.44%
B | A, B North | dalton | 2030 | 33% ECP | Pro-rata | IE wind priority | 40.8 | 124.0912 | 95.8589 | 0 | 4.0003 | 24.232 | 28.2323 | 0% | 3.224% | 19.53% | 22.75%
B | A, B North | cunghill | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 34.8 | 105.8425 | 80.7528 | 0 | 4.0752 | 21.0145 | 25.0897 | 0% | 3.85% | 19.85% | 23.7%
B | A, B North | dalton | 2030 | 100% ECP | Pro-rata | IE wind priority | 40.8 | 124.0912 | 92.897 | 0 | 4.7778 | 26.4165 | 31.1943 | 0% | 3.85% | 21.29% | 25.14%
B | A, B North | dalton | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 40.8 | 124.0912 | 94.6757 | 0 | 4.7778 | 24.6377 | 29.4155 | 0% | 3.85% | 19.85% | 23.7%
B | A, B North | firlough | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 43.4 | 131.999 | 75.2216 | 32.0485 | 2.3245 | 22.4043 | 56.7774 | 24.28% | 1.761% | 16.97% | 43.01%
B | A, B North | firlough | 2030 | 33% ECP | Pro-rata | IE wind not priority | 43.4 | 131.999 | 80.2889 | 23.647 | 2.2869 | 25.7761 | 51.7101 | 17.91% | 1.733% | 19.53% | 39.17%
B | A, B North | firlough | 2030 | Initial | Pro-rata | IE wind not priority | 27.3 | 83.0316 | 54.3252 | 10.8954 | 1.4852 | 16.3259 | 28.7065 | 13.12% | 1.789% | 19.66% | 34.57%
B | A, B North | dalton | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 24 | 30.7509 | 22.3406 | 6.7615 | 0.27868 | 1.3702 | 8.4103 | 21.99% | 0.9062% | 4.456% | 27.35%
B | A, B North | dalton | 2035 | 100% ECP | Pro-rata | IE wind priority | 40.8 | 124.0912 | 100.376 | 0 | 1.2789 | 22.4364 | 23.7152 | 0% | 1.031% | 18.08% | 19.11%
B | A, B North | dalton | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 24 | 30.7509 | 19.0226 | 9.7042 | 0.6775 | 1.3466 | 11.7283 | 31.56% | 2.203% | 4.379% | 38.14%
B | A, B North | dalton | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 17.3333 | 22.209 | 16.4064 | 4.8795 | 0.18975 | 0.73336 | 5.8026 | 21.97% | 0.8544% | 3.302% | 26.13%
B | A, B North | dalton | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 17.3333 | 22.209 | 17.8571 | 3.402 | 0.16012 | 0.78979 | 4.3519 | 15.32% | 0.721% | 3.556% | 19.6%
B | A, B North | dalton | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 40.8 | 124.0912 | 106.8904 | 0 | 1.1082 | 16.0926 | 17.2008 | 0% | 0.8931% | 12.97% | 13.86%
B | A, B North | dalton | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 17.3333 | 22.209 | 17.3995 | 3.402 | 0.16012 | 1.2474 | 4.8095 | 15.32% | 0.721% | 5.617% | 21.66%
B | A, B North | dalton | 2035 | 66% ECP | Pro-rata | IE wind priority | 40.8 | 124.0912 | 104.9331 | 0 | 1.1082 | 18.0499 | 19.1581 | 0% | 0.8931% | 14.55% | 15.44%
B | A, B North | dalton | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 24 | 30.7509 | 19.0998 | 9.7042 | 0.6775 | 1.2694 | 11.6511 | 31.56% | 2.203% | 4.128% | 37.89%
B | A, B North | dalton | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 40.8 | 124.0912 | 110.4932 | 0 | 2.1548 | 11.4433 | 13.598 | 0% | 1.736% | 9.222% | 10.96%
E | E,F & I | boggeragh | 2030 | 100% ECP | Pro-rata | IE wind priority | 142.7 | 462.0195 | 422.8071 | 0 | 16.9414 | 22.2711 | 39.2124 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | boggeragh | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 24.2 | 28.3336 | 18.2282 | 8.9918 | 0.62193 | 0.49163 | 10.1054 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | boggeragh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 23.35 | 75.6003 | 51.5175 | 20.169 | 1.2811 | 2.6326 | 24.0828 | 26.68% | 1.695% | 3.482% | 31.86%
G | G North | shankill | 2035 | 66% ECP | Pro-rata | IE wind priority | 22 | 68.7311 | 67.5745 | 0 | 0.60751 | 0.54909 | 1.1566 | 0% | 0.8839% | 0.7989% | 1.683%
G | G North | shankill | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 11 | 14.0942 | 9.3174 | 4.4477 | 0.31052 | 0.018525 | 4.7768 | 31.56% | 2.203% | 0.1314% | 33.89%
G | G North | shankill | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 22 | 68.7311 | 66.0229 | 0 | 2.5843 | 0.12387 | 2.7082 | 0% | 3.76% | 0.1802% | 3.94%
G | G North | shankill | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 11 | 14.0942 | 9.1291 | 4.4477 | 0.31052 | 0.20675 | 4.965 | 31.56% | 2.203% | 1.467% | 35.23%
G | G North | shankill | 2030 | 100% ECP | Pro-rata | IE wind priority | 22 | 68.7311 | 64.4863 | 0 | 2.5843 | 1.6604 | 4.2448 | 0% | 3.76% | 2.416% | 6.176%
G | G North | shankill | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 3.6667 | 4.698 | 3.9715 | 0.6384 | 0.087003 | 0.001173 | 0.72658 | 13.59% | 1.852% | 0.02497% | 15.47%
G | G North | shankill | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 22 | 68.7311 | 66.3444 | 0 | 2.2404 | 0.14629 | 2.3867 | 0% | 3.26% | 0.2128% | 3.472%
G | G North | shankill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 3.6667 | 4.698 | 3.5059 | 1.059 | 0.098387 | 0.034683 | 1.1921 | 22.54% | 2.094% | 0.7382% | 25.37%
G | G North | shankill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 22 | 68.7311 | 65.2651 | 0 | 2.7576 | 0.70837 | 3.466 | 0% | 4.012% | 1.031% | 5.043%
G | G North | shankill | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 3.6667 | 4.698 | 3.6616 | 0.91042 | 0.086938 | 0.039126 | 1.0365 | 19.38% | 1.851% | 0.8328% | 22.06%
G | G North | shankill | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 22 | 68.7311 | 65.3521 | 0 | 2.7089 | 0.67009 | 3.379 | 0% | 3.941% | 0.975% | 4.916%
G | G North | shankill | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 3.6667 | 4.698 | 3.8056 | 0.7787 | 0.087658 | 0.026076 | 0.89243 | 16.57% | 1.866% | 0.555% | 19%
G | G North | shankill | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 22 | 68.7311 | 65.2874 | 0 | 2.4803 | 0.96333 | 3.4437 | 0% | 3.609% | 1.402% | 5.01%
G | G North | shankill | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 7.3333 | 9.3961 | 7.7479 | 1.4393 | 0.067744 | 0.14113 | 1.6482 | 15.32% | 0.721% | 1.502% | 17.54%
G | G North | shankill | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 22 | 68.7311 | 67.9963 | 0 | 0.60751 | 0.12723 | 0.73474 | 0% | 0.8839% | 0.1851% | 1.069%
G | G North | shankill | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 7.3333 | 9.3961 | 7.7649 | 1.4393 | 0.067744 | 0.1242 | 1.6312 | 15.32% | 0.721% | 1.322% | 17.36%
G | G North | shankill | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 22 | 68.7311 | 67.4005 | 0 | 1.2244 | 0.10618 | 1.3305 | 0% | 1.781% | 0.1545% | 1.936%
G | J City, G South | baltrasna | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 17.13 | 21.9484 | 18.4233 | 3.3621 | 0.15825 | 0.0047787 | 3.5251 | 15.32% | 0.721% | 0.02177% | 16.06%
G | J City, G South | baltrasna | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 17.13 | 21.9484 | 18.396 | 3.3621 | 0.15825 | 0.032078 | 3.5524 | 15.32% | 0.721% | 0.1462% | 16.19%
G | J City, G South | baltrasna | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 17.13 | 21.9484 | 13.5183 | 6.9264 | 0.48357 | 1.0203 | 8.4302 | 31.56% | 2.203% | 4.648% | 38.41%
G | J City, G South | baltrasna | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 17.13 | 21.9484 | 13.6617 | 6.9264 | 0.48357 | 0.8768 | 8.2867 | 31.56% | 2.203% | 3.995% | 37.76%
G | J City, G South | baltrasna | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 17.13 | 21.9484 | 18.4431 | 2.9825 | 0.40646 | 0.11636 | 3.5053 | 13.59% | 1.852% | 0.5302% | 15.97%
G | J City, G South | baltrasna | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 17.13 | 21.9484 | 16.4747 | 4.9476 | 0.45965 | 0.066459 | 5.4737 | 22.54% | 2.094% | 0.3028% | 24.94%
G | G North | shankill | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 3.6667 | 4.698 | 3.9248 | 0.6384 | 0.087003 | 0.047813 | 0.77322 | 13.59% | 1.852% | 1.018% | 16.46%
G | J City, G South | baltrasna | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 17.13 | 21.9484 | 17.2129 | 4.2533 | 0.40616 | 0.07602 | 4.7355 | 19.38% | 1.851% | 0.3464% | 21.58%
G | J City, G South | baltrasna | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 17.13 | 21.9484 | 18.4327 | 2.9825 | 0.40646 | 0.12677 | 3.5157 | 13.59% | 1.852% | 0.5776% | 16.02%
G | J City, G South | baltrasna | 2030 | Initial | Pro-rata | IE Solar not priority | 17.13 | 21.9484 | 19.9159 | 1.7354 | 0.28384 | 0.013349 | 2.0326 | 7.907% | 1.293% | 0.06082% | 9.261%
G | G North | shankill | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 11 | 14.0942 | 10.6681 | 3.099 | 0.12773 | 0.19932 | 3.4261 | 21.99% | 0.9062% | 1.414% | 24.31%
G | G North | shankill | 2035 | 100% ECP | Pro-rata | IE wind priority | 22 | 68.7311 | 67.4669 | 0 | 0.68738 | 0.57681 | 1.2642 | 0% | 1% | 0.8392% | 1.839%
G | G North | shankill | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 7.3333 | 9.3961 | 7.1575 | 2.0644 | 0.080278 | 0.0939 | 2.2386 | 21.97% | 0.8544% | 0.9994% | 23.82%
G | J City, G South | baltrasna | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 17.13 | 21.9484 | 17.8601 | 3.6379 | 0.40952 | 0.040936 | 4.0884 | 16.57% | 1.866% | 0.1865% | 18.63%
G | G North | shankill | 2030 | 33% ECP | Pro-rata | IE wind priority | 22 | 68.7311 | 64.7604 | 0 | 2.2404 | 1.7303 | 3.9707 | 0% | 3.26% | 2.518% | 5.777%
G | G North | shankill | 2030 | Initial | Pro-rata | IE wind priority | 22 | 68.7311 | 64.898 | 0 | 2.0085 | 1.8245 | 3.8331 | 0% | 2.922% | 2.655% | 5.577%
G | G North | ratrussan | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 78.62 | 245.6199 | 237.0908 | 0 | 8.0062 | 0.52279 | 8.529 | 0% | 3.26% | 0.2128% | 3.472%
G | G North | ratrussan | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 78.62 | 245.6199 | 233.2336 | 0 | 9.8548 | 2.5315 | 12.3863 | 0% | 4.012% | 1.031% | 5.043%
G | G North | ratrussan | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 78.62 | 245.6199 | 233.5445 | 0 | 9.6807 | 2.3947 | 12.0753 | 0% | 3.941% | 0.975% | 4.916%
G | G North | ratrussan | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 78.62 | 245.6199 | 233.3135 | 0 | 8.8638 | 3.4426 | 12.3064 | 0% | 3.609% | 1.402% | 5.01%
G | G North | ratrussan | 2030 | 33% ECP | Pro-rata | IE wind priority | 78.62 | 245.6199 | 231.4301 | 0 | 8.0062 | 6.1835 | 14.1897 | 0% | 3.26% | 2.518% | 5.777%
G | G North | ratrussan | 2030 | Initial | Pro-rata | IE wind priority | 78.62 | 245.6199 | 231.9219 | 0 | 7.1777 | 6.5202 | 13.6979 | 0% | 2.922% | 2.655% | 5.577%
G | G North | ratrussan | 2030 | 100% ECP | Pro-rata | IE wind priority | 78.62 | 245.6199 | 230.4506 | 0 | 9.2355 | 5.9338 | 15.1693 | 0% | 3.76% | 2.416% | 6.176%
G | G North | oriel 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 165 | 691.2706 | 492.2184 | 193.8632 | 4.1211 | 1.0679 | 199.0523 | 28.04% | 0.5962% | 0.1545% | 28.8%
G | G North | oriel 220kv | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 210 | 879.799 | 597.2052 | 257.6056 | 15.9206 | 9.0676 | 282.5938 | 29.28% | 1.81% | 1.031% | 32.12%
G | G North | oriel 220kv | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 165 | 691.2706 | 469.2327 | 202.4044 | 12.509 | 7.1245 | 222.038 | 29.28% | 1.81% | 1.031% | 32.12%
G | G North | oriel 220kv | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 210 | 879.799 | 616.361 | 239.2572 | 15.6032 | 8.5776 | 263.438 | 27.19% | 1.773% | 0.975% | 29.94%
G | G North | oriel 220kv | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 165 | 691.2706 | 484.2837 | 187.9878 | 12.2596 | 6.7396 | 206.987 | 27.19% | 1.773% | 0.975% | 29.94%
G | G North | oriel 220kv | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 210 | 879.799 | 626.4597 | 246.735 | 5.2451 | 1.3591 | 253.3393 | 28.04% | 0.5962% | 0.1545% | 28.8%
G | J City, G South | baltrasna | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 17.13 | 21.9484 | 16.9341 | 4.8222 | 0.18752 | 0.0046407 | 5.0144 | 21.97% | 0.8544% | 0.02114% | 22.85%
G | G North | ratrussan | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 78.62 | 245.6199 | 235.9417 | 0 | 9.2355 | 0.44265 | 9.6781 | 0% | 3.76% | 0.1802% | 3.94%
G | G North | ratrussan | 2035 | 66% ECP | Pro-rata | IE wind priority | 78.62 | 245.6199 | 241.4866 | 0 | 2.171 | 1.9622 | 4.1332 | 0% | 0.8839% | 0.7989% | 1.683%
G | G North | ricetown | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 63 | 80.7211 | 61.0992 | 17.7488 | 0.73153 | 1.1415 | 19.6219 | 21.99% | 0.9062% | 1.414% | 24.31%
G | G North | ricetown | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 42 | 53.814 | 40.9932 | 11.8233 | 0.45977 | 0.53779 | 12.8208 | 21.97% | 0.8544% | 0.9994% | 23.82%
G | G North | ricetown | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 42 | 53.814 | 44.4714 | 8.2433 | 0.38799 | 0.7113 | 9.3426 | 15.32% | 0.721% | 1.322% | 17.36%
G | G North | ricetown | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 42 | 53.814 | 44.3745 | 8.2433 | 0.38799 | 0.80828 | 9.4395 | 15.32% | 0.721% | 1.502% | 17.54%
G | G North | ricetown | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 63 | 80.7211 | 53.3631 | 25.4735 | 1.7784 | 0.1061 | 27.358 | 31.56% | 2.203% | 0.1314% | 33.89%
G | G North | ricetown | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 63 | 80.7211 | 52.2851 | 25.4735 | 1.7784 | 1.1841 | 28.436 | 31.56% | 2.203% | 1.467% | 35.23%
G | G North | ricetown | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 21 | 26.907 | 22.7457 | 3.6563 | 0.49829 | 0.0067182 | 4.1613 | 13.59% | 1.852% | 0.02497% | 15.47%
G | G North | ricetown | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 21 | 26.907 | 20.9708 | 5.2142 | 0.49792 | 0.22409 | 5.9362 | 19.38% | 1.851% | 0.8328% | 22.06%
G | G North | ricetown | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 21 | 26.907 | 21.7958 | 4.4598 | 0.50204 | 0.14935 | 5.1112 | 16.57% | 1.866% | 0.555% | 19%
G | G North | ricetown | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 21 | 26.907 | 22.4786 | 3.6563 | 0.49829 | 0.27384 | 4.4284 | 13.59% | 1.852% | 1.018% | 16.46%
G | G North | ratrussan | 2035 | 100% ECP | Pro-rata | IE wind priority | 78.62 | 245.6199 | 241.1021 | 0 | 2.4564 | 2.0613 | 4.5177 | 0% | 1% | 0.8392% | 1.839%
G | G North | ratrussan | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 78.62 | 245.6199 | 240.865 | 0 | 4.3754 | 0.37944 | 4.7548 | 0% | 1.781% | 0.1545% | 1.936%
G | G North | ratrussan | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 78.62 | 245.6199 | 242.9942 | 0 | 2.171 | 0.45468 | 2.6257 | 0% | 0.8839% | 0.1851% | 1.069%
G | G North | ricetown | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 21 | 26.907 | 20.0795 | 6.0654 | 0.56349 | 0.19864 | 6.8275 | 22.54% | 2.094% | 0.7382% | 25.37%
G | J City, G South | baltrasna | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 17.13 | 21.9484 | 16.8935 | 4.826 | 0.19891 | 0.030061 | 5.055 | 21.99% | 0.9062% | 0.137% | 23.03%
G | J City, G South | deenes | 2030 | Initial | Pro-rata | IE Solar not priority | 85 | 108.9094 | 98.8237 | 8.611 | 1.4084 | 0.066239 | 10.0857 | 7.907% | 1.293% | 0.06082% | 9.261%
G | J City, G South | gorman | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 196 | 251.1323 | 156.3163 | 79.2508 | 5.5329 | 10.0322 | 94.8159 | 31.56% | 2.203% | 3.995% | 37.76%
G | J City, G South | gorman | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 65.3333 | 83.7107 | 70.3415 | 11.3752 | 1.5502 | 0.44379 | 13.3692 | 13.59% | 1.852% | 0.5302% | 15.97%
G | J City, G South | gorman | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 65.3333 | 83.7107 | 62.834 | 18.8701 | 1.7531 | 0.25347 | 20.8767 | 22.54% | 2.094% | 0.3028% | 24.94%
G | J City, G South | gorman | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 65.3333 | 83.7107 | 65.6496 | 16.222 | 1.5491 | 0.28994 | 18.0611 | 19.38% | 1.851% | 0.3464% | 21.58%
G | J City, G South | gorman | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 65.3333 | 83.7107 | 68.1177 | 13.875 | 1.5619 | 0.15613 | 15.593 | 16.57% | 1.866% | 0.1865% | 18.63%
G | J City, G South | gorman | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 65.3333 | 83.7107 | 70.3018 | 11.3752 | 1.5502 | 0.48351 | 13.4089 | 13.59% | 1.852% | 0.5776% | 16.02%
G | J City, G South | garballagh | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 215 | 275.4767 | 212.0314 | 60.5715 | 2.4965 | 0.3773 | 63.4453 | 21.99% | 0.9062% | 0.137% | 23.03%
G | J City, G South | garballagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 191 | 244.7258 | 188.8153 | 53.7678 | 2.0909 | 0.051744 | 55.9104 | 21.97% | 0.8544% | 0.02114% | 22.85%
G | J City, G South | garballagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 191 | 244.7258 | 205.4208 | 37.4873 | 1.7644 | 0.053283 | 39.305 | 15.32% | 0.721% | 0.02177% | 16.06%
G | J City, G South | garballagh | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 191 | 244.7258 | 205.1164 | 37.4873 | 1.7644 | 0.35768 | 39.6094 | 15.32% | 0.721% | 0.1462% | 16.19%
G | J City, G South | garballagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 215 | 275.4767 | 169.6689 | 86.9333 | 6.0693 | 12.8053 | 105.8078 | 31.56% | 2.203% | 4.648% | 38.41%
G | J City, G South | garballagh | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 215 | 275.4767 | 171.4694 | 86.9333 | 6.0693 | 11.0048 | 104.0073 | 31.56% | 2.203% | 3.995% | 37.76%
G | J City, G South | garballagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 167 | 213.9749 | 179.8016 | 29.0763 | 3.9626 | 1.1344 | 34.1733 | 13.59% | 1.852% | 0.5302% | 15.97%
G | J City, G South | gorman | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 196 | 251.1323 | 154.6749 | 79.2508 | 5.5329 | 11.6737 | 96.4574 | 31.56% | 2.203% | 4.648% | 38.41%
G | J City, G South | gorman | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 130.6665 | 167.4213 | 140.3238 | 25.6457 | 1.2071 | 0.24469 | 27.0975 | 15.32% | 0.721% | 0.1462% | 16.19%
G | J City, G South | gorman | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 130.6665 | 167.4213 | 140.5321 | 25.6457 | 1.2071 | 0.036452 | 26.8893 | 15.32% | 0.721% | 0.02177% | 16.06%
H1 | H1 | ahane | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 4 | 4.6832 | 2.8583 | 1.0546 | 0.042266 | 0.72805 | 1.825 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | ahane | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 2.6667 | 3.1222 | 2.0662 | 0.70052 | 0.026872 | 0.32859 | 1.056 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | ahane | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 2.6667 | 3.1222 | 2.2519 | 0.49567 | 0.022915 | 0.35165 | 0.87024 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | ahane | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 2.6667 | 3.1222 | 2.1481 | 0.49567 | 0.022915 | 0.45551 | 0.9741 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | ahane | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4 | 4.6832 | 2.6982 | 1.4862 | 0.1028 | 0.39599 | 1.985 | 31.74% | 2.195% | 8.456% | 42.39%
G | J City, G South | garballagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 167 | 213.9749 | 160.6115 | 48.2344 | 4.4811 | 0.64791 | 53.3634 | 22.54% | 2.094% | 0.3028% | 24.94%
H1 | H1 | ahane | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 4 | 4.6832 | 2.67 | 1.4862 | 0.1028 | 0.42419 | 2.0132 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | ahane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 1.3333 | 1.5611 | 1.0773 | 0.35533 | 0.033184 | 0.095218 | 0.48373 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | ahane | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 1.3333 | 1.5611 | 1.1329 | 0.30553 | 0.029516 | 0.093127 | 0.42817 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | ahane | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 1.3333 | 1.5611 | 1.1688 | 0.26245 | 0.029518 | 0.10031 | 0.39227 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | ahane | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 1.3333 | 1.5611 | 1.212 | 0.21631 | 0.029018 | 0.10373 | 0.34906 | 13.86% | 1.859% | 6.645% | 22.36%
G | J City, G South | gorman | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 196 | 251.1323 | 193.2938 | 55.2186 | 2.2759 | 0.34396 | 57.8385 | 21.99% | 0.9062% | 0.137% | 23.03%
G | J City, G South | gorman | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 130.6665 | 167.4213 | 129.172 | 36.7835 | 1.4304 | 0.035399 | 38.2493 | 21.97% | 0.8544% | 0.02114% | 22.85%
H1 | H1 | ahane | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 1.3333 | 1.5611 | 1.232 | 0.21631 | 0.029018 | 0.083721 | 0.32904 | 13.86% | 1.859% | 5.363% | 21.08%
G | J City, G South | garballagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 167 | 213.9749 | 167.8086 | 41.4655 | 3.9597 | 0.74111 | 46.1663 | 19.38% | 1.851% | 0.3464% | 21.58%
G | J City, G South | garballagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 167 | 213.9749 | 174.1172 | 35.4661 | 3.9924 | 0.39909 | 39.8577 | 16.57% | 1.866% | 0.1865% | 18.63%
G | J City, G South | garballagh | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 167 | 213.9749 | 179.7001 | 29.0763 | 3.9626 | 1.2359 | 34.2748 | 13.59% | 1.852% | 0.5776% | 16.02%
G | J City, G South | deenes | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 85 | 108.9094 | 91.4176 | 16.6828 | 0.78522 | 0.023712 | 17.4918 | 15.32% | 0.721% | 0.02177% | 16.06%
G | J City, G South | deenes | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 56.6666 | 72.6062 | 60.8547 | 11.1219 | 0.52348 | 0.10612 | 11.7515 | 15.32% | 0.721% | 0.1462% | 16.19%
G | J City, G South | deenes | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 85 | 108.9094 | 91.2822 | 16.6828 | 0.78522 | 0.15918 | 17.6272 | 15.32% | 0.721% | 0.1462% | 16.19%
G | J City, G South | deenes | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 85 | 108.9094 | 67.0784 | 34.369 | 2.3995 | 5.0626 | 41.831 | 31.56% | 2.203% | 4.648% | 38.41%
G | J City, G South | deenes | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 85 | 108.9094 | 67.7902 | 34.369 | 2.3995 | 4.3507 | 41.1192 | 31.56% | 2.203% | 3.995% | 37.76%
G | J City, G South | deenes | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 28.3333 | 36.3031 | 30.5052 | 4.9331 | 0.6723 | 0.19246 | 5.7979 | 13.59% | 1.852% | 0.5302% | 15.97%
G | J City, G South | deenes | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 56.6666 | 72.6062 | 60.945 | 11.1219 | 0.52348 | 0.015808 | 11.6612 | 15.32% | 0.721% | 0.02177% | 16.06%
G | J City, G South | deenes | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 85 | 108.9094 | 91.5158 | 14.7993 | 2.0169 | 0.57738 | 17.3936 | 13.59% | 1.852% | 0.5302% | 15.97%
G | J City, G South | deenes | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 85 | 108.9094 | 81.7484 | 24.5504 | 2.2808 | 0.32977 | 27.161 | 22.54% | 2.094% | 0.3028% | 24.94%
G | J City, G South | deenes | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 28.3333 | 36.3031 | 28.4705 | 7.0351 | 0.6718 | 0.12574 | 7.8326 | 19.38% | 1.851% | 0.3464% | 21.58%
G | J City, G South | deenes | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 85 | 108.9094 | 85.4116 | 21.1052 | 2.0154 | 0.37721 | 23.4978 | 19.38% | 1.851% | 0.3464% | 21.58%
G | J City, G South | deenes | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 28.3333 | 36.3031 | 29.5408 | 6.0172 | 0.67736 | 0.067709 | 6.7623 | 16.57% | 1.866% | 0.1865% | 18.63%
G | J City, G South | deenes | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 85 | 108.9094 | 88.6225 | 18.0516 | 2.0321 | 0.20313 | 20.2868 | 16.57% | 1.866% | 0.1865% | 18.63%
G | J City, G South | deenes | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 28.3333 | 36.3031 | 30.488 | 4.9331 | 0.6723 | 0.20969 | 5.8151 | 13.59% | 1.852% | 0.5776% | 16.02%
G | J City, G South | deenes | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 85 | 108.9094 | 91.4641 | 14.7993 | 2.0169 | 0.62906 | 17.4453 | 13.59% | 1.852% | 0.5776% | 16.02%
G | J City, G South | deenes | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 28.3333 | 36.3031 | 27.2494 | 8.1835 | 0.76026 | 0.10992 | 9.0537 | 22.54% | 2.094% | 0.3028% | 24.94%
G | J City, G South | deenes | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 85 | 108.9094 | 84.0278 | 23.9281 | 0.93049 | 0.023027 | 24.8816 | 21.97% | 0.8544% | 0.02114% | 22.85%
G | J City, G South | deenes | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 85 | 108.9094 | 83.8264 | 23.9469 | 0.98699 | 0.14916 | 25.083 | 21.99% | 0.9062% | 0.137% | 23.03%
G | J City, G South | garballagh | 2030 | Initial | Pro-rata | IE Solar not priority | 143 | 183.224 | 166.2563 | 14.4868 | 2.3695 | 0.11144 | 16.9677 | 7.907% | 1.293% | 0.06082% | 9.261%
G | J City, G South | drybridge | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 16.97 | 21.7434 | 16.7357 | 4.7809 | 0.19705 | 0.02978 | 5.0077 | 21.99% | 0.9062% | 0.137% | 23.03%
G | J City, G South | drybridge | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 16.64 | 21.3206 | 16.4497 | 4.6843 | 0.18216 | 0.0045079 | 4.8709 | 21.97% | 0.8544% | 0.02114% | 22.85%
G | J City, G South | drybridge | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 16.64 | 21.3206 | 17.8963 | 3.2659 | 0.15372 | 0.004642 | 3.4243 | 15.32% | 0.721% | 0.02177% | 16.06%
G | J City, G South | drybridge | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 16.64 | 21.3206 | 17.8698 | 3.2659 | 0.15372 | 0.031161 | 3.4508 | 15.32% | 0.721% | 0.1462% | 16.19%
G | J City, G South | deenes | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 56.6666 | 72.6062 | 56.0185 | 15.952 | 0.62033 | 0.015352 | 16.5877 | 21.97% | 0.8544% | 0.02114% | 22.85%
G | J City, G South | drybridge | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 16.97 | 21.7434 | 13.392 | 6.8617 | 0.47905 | 1.0107 | 8.3514 | 31.56% | 2.203% | 4.648% | 38.41%
G | J City, G South | drybridge | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 16.31 | 20.8978 | 17.5603 | 2.8397 | 0.38701 | 0.11079 | 3.3375 | 13.59% | 1.852% | 0.5302% | 15.97%
G | J City, G South | drybridge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 16.31 | 20.8978 | 15.6861 | 4.7108 | 0.43764 | 0.063278 | 5.2117 | 22.54% | 2.094% | 0.3028% | 24.94%
G | J City, G South | drybridge | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 16.31 | 20.8978 | 16.389 | 4.0497 | 0.38672 | 0.072381 | 4.5088 | 19.38% | 1.851% | 0.3464% | 21.58%
G | J City, G South | drybridge | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 16.31 | 20.8978 | 17.0051 | 3.4638 | 0.38992 | 0.038977 | 3.8927 | 16.57% | 1.866% | 0.1865% | 18.63%
G | J City, G South | drybridge | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 16.31 | 20.8978 | 17.5503 | 2.8397 | 0.38701 | 0.12071 | 3.3474 | 13.59% | 1.852% | 0.5776% | 16.02%
G | J City, G South | drybridge | 2030 | Initial | Pro-rata | IE Solar not priority | 15.98 | 20.475 | 18.5789 | 1.6189 | 0.26479 | 0.012453 | 1.8961 | 7.907% | 1.293% | 0.06082% | 9.261%
G | J City, G South | drybridge | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 16.97 | 21.7434 | 13.5341 | 6.8617 | 0.47905 | 0.86861 | 8.2093 | 31.56% | 2.203% | 3.995% | 37.76%
H1 | H1 | ballydine | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 5.9333 | 6.9468 | 5.3935 | 0.96256 | 0.12913 | 0.46161 | 1.5533 | 13.86% | 1.859% | 6.645% | 22.36%
G | G North | navan | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 116.449 | 149.2046 | 112.9355 | 32.8069 | 1.3522 | 2.11 | 36.2691 | 21.99% | 0.9062% | 1.414% | 24.31%
G | G North | navan | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 81.9656 | 105.0215 | 86.7889 | 16.0873 | 0.75719 | 1.3881 | 18.2326 | 15.32% | 0.721% | 1.322% | 17.36%
G | G North | dundalk | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 37.9166 | 48.5821 | 40.1478 | 7.4418 | 0.35027 | 0.64215 | 8.4343 | 15.32% | 0.721% | 1.322% | 17.36%
G | G North | dundalk | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 16.1 | 50.2987 | 49.761 | 0 | 0.44458 | 0.093111 | 0.5377 | 0% | 0.8839% | 0.1851% | 1.069%
G | G North | dundalk | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 37.9166 | 48.5821 | 40.0603 | 7.4418 | 0.35027 | 0.72969 | 8.5218 | 15.32% | 0.721% | 1.502% | 17.54%
G | G North | dundalk | 2035 | 66% ECP | Pro-rata | IE wind priority | 16.1 | 50.2987 | 49.4522 | 0 | 0.44458 | 0.40183 | 0.84642 | 0% | 0.8839% | 0.7989% | 1.683%
G | G North | dundalk | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 54.88 | 70.317 | 46.4852 | 22.1902 | 1.5492 | 0.092425 | 23.8319 | 31.56% | 2.203% | 0.1314% | 33.89%
G | G North | dundalk | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 16.1 | 50.2987 | 48.3167 | 0 | 1.8913 | 0.090647 | 1.9819 | 0% | 3.76% | 0.1802% | 3.94%
G | G North | dundalk | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 54.88 | 70.317 | 45.5461 | 22.1902 | 1.5492 | 1.0315 | 24.7709 | 31.56% | 2.203% | 1.467% | 35.23%
G | G North | dundalk | 2030 | 100% ECP | Pro-rata | IE wind priority | 16.1 | 50.2987 | 47.1922 | 0 | 1.8913 | 1.2151 | 3.1064 | 0% | 3.76% | 2.416% | 6.176%
G | G North | dundalk | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 20.9533 | 26.8472 | 22.6951 | 3.6482 | 0.49718 | 0.0067033 | 4.1521 | 13.59% | 1.852% | 0.02497% | 15.47%
G | G North | dundalk | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 16.1 | 50.2987 | 48.5521 | 0 | 1.6395 | 0.10706 | 1.7466 | 0% | 3.26% | 0.2128% | 3.472%
G | G North | dundalk | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 20.9533 | 26.8472 | 20.0349 | 6.0519 | 0.56224 | 0.1982 | 6.8123 | 22.54% | 2.094% | 0.7382% | 25.37%
G | G North | dundalk | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 16.1 | 50.2987 | 47.7622 | 0 | 2.0181 | 0.5184 | 2.5365 | 0% | 4.012% | 1.031% | 5.043%
G | G North | dundalk | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 20.9533 | 26.8472 | 20.9242 | 5.2026 | 0.49681 | 0.22359 | 5.923 | 19.38% | 1.851% | 0.8328% | 22.06%
G | G North | dundalk | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 16.1 | 50.2987 | 49.3249 | 0 | 0.89601 | 0.077703 | 0.97371 | 0% | 1.781% | 0.1545% | 1.936%
G | G North | dundalk | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 37.9166 | 48.5821 | 37.0077 | 10.6738 | 0.41507 | 0.48551 | 11.5744 | 21.97% | 0.8544% | 0.9994% | 23.82%
G | G North | dundalk | 2035 | 100% ECP | Pro-rata | IE wind priority | 16.1 | 50.2987 | 49.3735 | 0 | 0.50304 | 0.42212 | 0.92515 | 0% | 1% | 0.8392% | 1.839%
G | G North | dundalk | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 54.88 | 70.317 | 53.2242 | 15.4612 | 0.63725 | 0.99441 | 17.0929 | 21.99% | 0.9062% | 1.414% | 24.31%
G | G North | lisdrum | 2035 | 100% ECP | Pro-rata | IE wind not priority | 33.1 | 103.409 | 83.0066 | 19.1783 | 0.35629 | 0.86783 | 20.4024 | 18.55% | 0.3445% | 0.8392% | 19.73%
G | G North | lisdrum | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 33.1 | 103.409 | 71.1648 | 31.4607 | 0.62384 | 0.15975 | 32.2443 | 30.42% | 0.6033% | 0.1545% | 31.18%
G | G North | lisdrum | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 33.1 | 103.409 | 85.4415 | 17.4431 | 0.33303 | 0.19143 | 17.9675 | 16.87% | 0.3221% | 0.1851% | 17.38%
G | G North | lisdrum | 2035 | 66% ECP | Pro-rata | IE wind not priority | 33.1 | 103.409 | 84.8068 | 17.4431 | 0.33303 | 0.82613 | 18.6022 | 16.87% | 0.3221% | 0.7989% | 17.99%
G | G North | lisdrum | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 33.1 | 103.409 | 72.6928 | 28.7427 | 1.7871 | 0.18636 | 30.7162 | 27.8% | 1.728% | 0.1802% | 29.7%
G | G North | dundalk | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 16.1 | 50.2987 | 47.8258 | 0 | 1.9824 | 0.49039 | 2.4728 | 0% | 3.941% | 0.975% | 4.916%
G | G North | lisdrum | 2030 | 100% ECP | Pro-rata | IE wind not priority | 33.1 | 103.409 | 70.381 | 28.7427 | 1.7871 | 2.4982 | 33.028 | 27.8% | 1.728% | 2.416% | 31.94%
G | G North | lisdrum | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 33.1 | 103.409 | 67.1675 | 33.3703 | 1.8055 | 1.0658 | 36.2415 | 32.27% | 1.746% | 1.031% | 35.05%
G | G North | lisdrum | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 33.1 | 103.409 | 69.2945 | 31.3015 | 1.8049 | 1.0082 | 34.1145 | 30.27% | 1.745% | 0.975% | 32.99%
G | G North | lisdrum | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 33.1 | 103.409 | 75.5425 | 24.5736 | 1.8436 | 1.4494 | 27.8665 | 23.76% | 1.783% | 1.402% | 26.95%
G | G North | lisdrum | 2030 | 33% ECP | Pro-rata | IE wind not priority | 33.1 | 103.409 | 81.0126 | 17.9205 | 1.8727 | 2.6033 | 22.3965 | 17.33% | 1.811% | 2.518% | 21.66%
G | G North | lisdrum | 2030 | Initial | Pro-rata | IE wind not priority | 33.1 | 103.409 | 85.5165 | 13.2348 | 1.9126 | 2.7451 | 17.8925 | 12.8% | 1.85% | 2.655% | 17.3%
G | G North | lisdrum | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 33.1 | 103.409 | 83.3958 | 17.9205 | 1.8727 | 0.2201 | 20.0132 | 17.33% | 1.811% | 0.2128% | 19.35%
G | G North | dundalk | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 20.9533 | 26.8472 | 21.7474 | 4.4499 | 0.50093 | 0.14902 | 5.0998 | 16.57% | 1.866% | 0.555% | 19%
G | G North | dundalk | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 16.1 | 50.2987 | 47.7785 | 0 | 1.8152 | 0.70498 | 2.5201 | 0% | 3.609% | 1.402% | 5.01%
G | G North | dundalk | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 20.9533 | 26.8472 | 22.4286 | 3.6482 | 0.49718 | 0.27323 | 4.4186 | 13.59% | 1.852% | 1.018% | 16.46%
G | G North | balruntagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 16.8 | 52.4855 | 42.3277 | 9.0956 | 0.95047 | 0.11171 | 10.1578 | 17.33% | 1.811% | 0.2128% | 19.35%
G | G North | balruntagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 44.6666 | 57.2308 | 42.7087 | 12.901 | 1.1985 | 0.4225 | 14.522 | 22.54% | 2.094% | 0.7382% | 25.37%
G | G North | balruntagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 16.8 | 52.4855 | 34.091 | 16.9372 | 0.91637 | 0.54094 | 18.3945 | 32.27% | 1.746% | 1.031% | 35.05%
G | G North | balruntagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 44.6666 | 57.2308 | 44.6045 | 11.0906 | 1.0591 | 0.47663 | 12.6263 | 19.38% | 1.851% | 0.8328% | 22.06%
G | G North | balruntagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 16.8 | 52.4855 | 35.1706 | 15.8871 | 0.91607 | 0.51171 | 17.3149 | 30.27% | 1.745% | 0.975% | 32.99%
G | G North | balruntagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 44.6666 | 57.2308 | 46.3593 | 9.4859 | 1.0678 | 0.31766 | 10.8714 | 16.57% | 1.866% | 0.555% | 19%
G | G North | balruntagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 16.8 | 52.4855 | 38.3418 | 12.4724 | 0.93571 | 0.73563 | 14.1437 | 23.76% | 1.783% | 1.402% | 26.95%
G | G North | balruntagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 44.6666 | 57.2308 | 48.3797 | 7.7769 | 1.0599 | 0.01429 | 8.851 | 13.59% | 1.852% | 0.02497% | 15.47%
G | G North | balruntagh | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 44.6666 | 57.2308 | 47.8116 | 7.7769 | 1.0599 | 0.58245 | 9.4192 | 13.59% | 1.852% | 1.018% | 16.46%
F | E,F & I | macroom | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 14.1432 | 4.6932 | 0.18809 | 1.816 | 6.6973 | 22.52% | 0.9025% | 8.714% | 32.14%
F | E,F & I | macroom | 2035 | 100% ECP | Pro-rata | IE wind priority | 24 | 77.6717 | 65.5994 | 0 | 0.70994 | 11.3624 | 12.0723 | 0% | 0.914% | 14.63% | 15.54%
F | E,F & I | macroom | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 14.5001 | 4.676 | 0.17937 | 1.485 | 6.3403 | 22.44% | 0.8607% | 7.125% | 30.42%
F | E,F & I | macroom | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 24 | 77.6717 | 71.3289 | 0 | 1.2487 | 5.0941 | 6.3428 | 0% | 1.608% | 6.559% | 8.166%
F | E,F & I | macroom | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 16.3749 | 3.3086 | 0.15296 | 1.004 | 4.4655 | 15.88% | 0.7339% | 4.817% | 21.43%
G | G North | balruntagh | 2030 | 33% ECP | Pro-rata | IE wind not priority | 16.8 | 52.4855 | 41.1181 | 9.0956 | 0.95047 | 1.3213 | 11.3674 | 17.33% | 1.811% | 2.518% | 21.66%
G | G North | lislea | 2030 | Initial | Pro-rata | IE wind not priority | 48.8 | 152.458 | 126.0788 | 19.5124 | 2.8197 | 4.0471 | 26.3793 | 12.8% | 1.85% | 2.655% | 17.3%
G | G North | balruntagh | 2030 | 100% ECP | Pro-rata | IE wind not priority | 50.4 | 157.4567 | 107.1662 | 43.7654 | 2.7211 | 3.8039 | 50.2904 | 27.8% | 1.728% | 2.416% | 31.94%
G | G North | balruntagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 50.4 | 157.4567 | 110.6864 | 43.7654 | 2.7211 | 0.28377 | 46.7703 | 27.8% | 1.728% | 0.1802% | 29.7%
G | G North | dundalk | 2030 | 33% ECP | Pro-rata | IE wind priority | 16.1 | 50.2987 | 47.3928 | 0 | 1.6395 | 1.2663 | 2.9058 | 0% | 3.26% | 2.518% | 5.777%
G | G North | dundalk | 2030 | Initial | Pro-rata | IE Solar not priority | 3.99 | 5.1123 | 4.5757 | 0.40421 | 0.066114 | 0.066354 | 0.53668 | 7.907% | 1.293% | 1.298% | 10.5%
G | G North | dundalk | 2030 | Initial | Pro-rata | IE wind priority | 16.1 | 50.2987 | 47.4936 | 0 | 1.4699 | 1.3352 | 2.8051 | 0% | 2.922% | 2.655% | 5.577%
G | G North | balruntagh | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 134 | 171.6925 | 129.9569 | 37.7515 | 1.556 | 2.428 | 41.7355 | 21.99% | 0.9062% | 1.414% | 24.31%
G | G North | balruntagh | 2035 | 100% ECP | Pro-rata | IE wind not priority | 50.4 | 157.4567 | 126.3908 | 29.202 | 0.54251 | 1.3214 | 31.0659 | 18.55% | 0.3445% | 0.8392% | 19.73%
G | G North | balruntagh | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 134 | 171.6925 | 111.2095 | 54.1817 | 3.7827 | 2.5186 | 60.483 | 31.56% | 2.203% | 1.467% | 35.23%
G | G North | balruntagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 89.3332 | 114.4615 | 87.1918 | 25.1479 | 0.97793 | 1.1439 | 27.2697 | 21.97% | 0.8544% | 0.9994% | 23.82%
G | G North | balruntagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 89.3332 | 114.4615 | 94.59 | 17.5333 | 0.82525 | 1.5129 | 19.8715 | 15.32% | 0.721% | 1.322% | 17.36%
G | G North | balruntagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 33.6 | 104.971 | 86.7321 | 17.7065 | 0.33806 | 0.19432 | 18.2389 | 16.87% | 0.3221% | 0.1851% | 17.38%
G | G North | balruntagh | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 89.3332 | 114.4615 | 94.3838 | 17.5333 | 0.82525 | 1.7192 | 20.0777 | 15.32% | 0.721% | 1.502% | 17.54%
G | G North | balruntagh | 2035 | 66% ECP | Pro-rata | IE wind not priority | 33.6 | 104.971 | 86.0878 | 17.7065 | 0.33806 | 0.8386 | 18.8832 | 16.87% | 0.3221% | 0.7989% | 17.99%
G | G North | balruntagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 134 | 171.6925 | 113.5024 | 54.1817 | 3.7827 | 0.22567 | 58.19 | 31.56% | 2.203% | 0.1314% | 33.89%
G | G North | balruntagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 33.6 | 104.971 | 72.2397 | 31.9359 | 0.63326 | 0.16216 | 32.7313 | 30.42% | 0.6033% | 0.1545% | 31.18%
G | G North | navan | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 81.9656 | 105.0215 | 80.0008 | 23.0739 | 0.89727 | 1.0495 | 25.0207 | 21.97% | 0.8544% | 0.9994% | 23.82%
G | G North | lislea | 2030 | 33% ECP | Pro-rata | IE wind not priority | 48.8 | 152.458 | 119.4385 | 26.4205 | 2.7609 | 3.8381 | 33.0196 | 17.33% | 1.811% | 2.518% | 21.66%
G | G North | lislea | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 48.8 | 152.458 | 102.1623 | 46.1484 | 2.661 | 1.4864 | 50.2958 | 30.27% | 1.745% | 0.975% | 32.99%
G | G North | meath hill | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 16.5 | 51.5483 | 50.9973 | 0 | 0.45563 | 0.095425 | 0.55105 | 0% | 0.8839% | 0.1851% | 1.069%
G | G North | meath hill | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 34.56 | 107.9703 | 89.2102 | 18.2124 | 0.34772 | 0.19987 | 18.76 | 16.87% | 0.3221% | 0.1851% | 17.38%
G | G North | meath hill | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 0.26667 | 0.34168 | 0.28174 | 0.052338 | 0.0024634 | 0.0051319 | 0.059934 | 15.32% | 0.721% | 1.502% | 17.54%
G | G North | meath hill | 2035 | 66% ECP | Pro-rata | IE wind priority | 16.5 | 51.5483 | 50.6809 | 0 | 0.45563 | 0.41181 | 0.86744 | 0% | 0.8839% | 0.7989% | 1.683%
G | G North | meath hill | 2035 | 66% ECP | Pro-rata | IE wind not priority | 34.56 | 107.9703 | 88.5476 | 18.2124 | 0.34772 | 0.86256 | 19.4227 | 16.87% | 0.3221% | 0.7989% | 17.99%
G | G North | meath hill | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 0.4 | 0.51251 | 0.33881 | 0.16174 | 0.011292 | 0.00067365 | 0.1737 | 31.56% | 2.203% | 0.1314% | 33.89%
G | G North | meath hill | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 16.5 | 51.5483 | 49.5172 | 0 | 1.9383 | 0.0929 | 2.0312 | 0% | 3.76% | 0.1802% | 3.94%
G | G North | meath hill | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 34.56 | 107.9703 | 75.8992 | 30.0106 | 1.8659 | 0.19458 | 32.071 | 27.8% | 1.728% | 0.1802% | 29.7%
G | G North | meath hill | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 0.4 | 0.51251 | 0.33197 | 0.16174 | 0.011292 | 0.0075181 | 0.18055 | 31.56% | 2.203% | 1.467% | 35.23%
G | G North | meath hill | 2030 | 100% ECP | Pro-rata | IE wind priority | 16.5 | 51.5483 | 48.3647 | 0 | 1.9383 | 1.2453 | 3.1836 | 0% | 3.76% | 2.416% | 6.176%
G | G North | meath hill | 2030 | 100% ECP | Pro-rata | IE wind not priority | 34.56 | 107.9703 | 73.4854 | 30.0106 | 1.8659 | 2.6084 | 34.4849 | 27.8% | 1.728% | 2.416% | 31.94%
G | G North | meath hill | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 0.13333 | 0.17084 | 0.14442 | 0.023215 | 0.0031638 | 4.2655e-05 | 0.026421 | 13.59% | 1.852% | 0.02497% | 15.47%
G | G North | meath hill | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 0.26667 | 0.34168 | 0.28236 | 0.052338 | 0.0024634 | 0.0045162 | 0.059318 | 15.32% | 0.721% | 1.322% | 17.36%
G | G North | meath hill | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 34.56 | 107.9703 | 74.3038 | 32.8484 | 0.65136 | 0.1668 | 33.6665 | 30.42% | 0.6033% | 0.1545% | 31.18%
G | G North | meath hill | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 16.5 | 51.5483 | 50.5504 | 0 | 0.91827 | 0.079633 | 0.9979 | 0% | 1.781% | 0.1545% | 1.936%
G | G North | meath hill | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 0.26667 | 0.34168 | 0.26027 | 0.075068 | 0.0029192 | 0.0034146 | 0.081402 | 21.97% | 0.8544% | 0.9994% | 23.82%
G | G North | navan | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 81.9656 | 105.0215 | 86.5996 | 16.0873 | 0.75719 | 1.5774 | 18.4219 | 15.32% | 0.721% | 1.502% | 17.54%
G | G North | navan | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 116.449 | 149.2046 | 98.6361 | 47.0851 | 3.2873 | 0.19611 | 50.5685 | 31.56% | 2.203% | 0.1314% | 33.89%
G | G North | navan | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 116.449 | 149.2046 | 96.6436 | 47.0851 | 3.2873 | 2.1887 | 52.561 | 31.56% | 2.203% | 1.467% | 35.23%
G | G North | navan | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 47.4823 | 60.8385 | 51.4295 | 8.2671 | 1.1267 | 0.01519 | 9.409 | 13.59% | 1.852% | 0.02497% | 15.47%
G | G North | navan | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 47.4823 | 60.8385 | 45.401 | 13.7142 | 1.2741 | 0.44913 | 15.4375 | 22.54% | 2.094% | 0.7382% | 25.37%
G | G North | navan | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 47.4823 | 60.8385 | 47.4163 | 11.7897 | 1.1258 | 0.50667 | 13.4222 | 19.38% | 1.851% | 0.8328% | 22.06%
G | G North | meath hill | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 16.5 | 51.5483 | 49.7583 | 0 | 1.6803 | 0.10972 | 1.79 | 0% | 3.26% | 0.2128% | 3.472%
G | G North | navan | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 47.4823 | 60.8385 | 49.2817 | 10.0839 | 1.1352 | 0.33768 | 11.5568 | 16.57% | 1.866% | 0.555% | 19%
G | G North | navan | 2030 | Initial | Pro-rata | IE Solar not priority | 12.999 | 16.6554 | 14.907 | 1.3169 | 0.21539 | 0.21618 | 1.7484 | 7.907% | 1.293% | 1.298% | 10.5%
G | G North | meath hill | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 0.4 | 0.51251 | 0.38793 | 0.11269 | 0.0046446 | 0.0072479 | 0.12458 | 21.99% | 0.9062% | 1.414% | 24.31%
G | G North | meath hill | 2035 | 100% ECP | Pro-rata | IE wind priority | 16.5 | 51.5483 | 50.6002 | 0 | 0.51553 | 0.4326 | 0.94814 | 0% | 1% | 0.8392% | 1.839%
G | G North | meath hill | 2035 | 100% ECP | Pro-rata | IE wind not priority | 34.56 | 107.9703 | 86.668 | 20.0242 | 0.37201 | 0.90611 | 21.3023 | 18.55% | 0.3445% | 0.8392% | 19.73%
G | G North | navan | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 47.4823 | 60.8385 | 50.8255 | 8.2671 | 1.1267 | 0.61916 | 10.013 | 13.59% | 1.852% | 1.018% | 16.46%
G | G North | meath hill | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 34.56 | 107.9703 | 87.0743 | 18.7109 | 1.9553 | 0.22981 | 20.896 | 17.33% | 1.811% | 0.2128% | 19.35%
G | G North | meath hill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 0.13333 | 0.17084 | 0.12749 | 0.03851 | 0.0035777 | 0.0012612 | 0.043349 | 22.54% | 2.094% | 0.7382% | 25.37%
G | G North | meath hill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 16.5 | 51.5483 | 48.9488 | 0 | 2.0682 | 0.53128 | 2.5995 | 0% | 4.012% | 1.031% | 5.043%
G | G North | louth | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 75 | 96.0965 | 81.2347 | 13.0582 | 1.7796 | 0.023994 | 14.8618 | 13.59% | 1.852% | 0.02497% | 15.47%
G | G North | louth | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 75 | 96.0965 | 71.7125 | 21.6621 | 2.0125 | 0.70942 | 24.384 | 22.54% | 2.094% | 0.7382% | 25.37%
G | G North | louth | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 75 | 96.0965 | 74.8957 | 18.6222 | 1.7783 | 0.80031 | 21.2008 | 19.38% | 1.851% | 0.8328% | 22.06%
G | G North | louth | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 75 | 96.0965 | 77.8422 | 15.9279 | 1.793 | 0.53338 | 18.2543 | 16.57% | 1.866% | 0.555% | 19%
G | G North | louth | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 75 | 96.0965 | 80.2807 | 13.0582 | 1.7796 | 0.97799 | 15.8158 | 13.59% | 1.852% | 1.018% | 16.46%
G | G North | louth | 2030 | Initial | Pro-rata | IE Solar not priority | 50 | 64.0644 | 57.339 | 5.0653 | 0.8285 | 0.83151 | 6.7253 | 7.907% | 1.293% | 1.298% | 10.5%
G | G North | louth | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 125 | 160.1609 | 103.7402 | 50.5426 | 3.5286 | 2.3494 | 56.4207 | 31.56% | 2.203% | 1.467% | 35.23%
G | G North | lislea | 2035 | 100% ECP | Pro-rata | IE wind not priority | 48.8 | 152.458 | 122.3784 | 28.2749 | 0.52529 | 1.2795 | 30.0797 | 18.55% | 0.3445% | 0.8392% | 19.73%
G | G North | lislea | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 48.8 | 152.458 | 125.9682 | 25.7166 | 0.49099 | 0.28223 | 26.4899 | 16.87% | 0.3221% | 0.1851% | 17.38%
G | G North | lislea | 2035 | 66% ECP | Pro-rata | IE wind not priority | 48.8 | 152.458 | 125.0324 | 25.7166 | 0.49099 | 1.218 | 27.4256 | 16.87% | 0.3221% | 0.7989% | 17.99%
G | G North | lislea | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 48.8 | 152.458 | 107.1725 | 42.376 | 2.6347 | 0.27476 | 45.2855 | 27.8% | 1.728% | 0.1802% | 29.7%
G | G North | lislea | 2030 | 100% ECP | Pro-rata | IE wind not priority | 48.8 | 152.458 | 103.7641 | 42.376 | 2.6347 | 3.6832 | 48.6939 | 27.8% | 1.728% | 2.416% | 31.94%
G | G North | lislea | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 48.8 | 152.458 | 122.9521 | 26.4205 | 2.7609 | 0.3245 | 29.5059 | 17.33% | 1.811% | 0.2128% | 19.35%
G | G North | lislea | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 48.8 | 152.458 | 99.0264 | 49.1985 | 2.6618 | 1.5713 | 53.4316 | 32.27% | 1.746% | 1.031% | 35.05%
G | G North | lislea | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 48.8 | 152.458 | 104.9197 | 46.3831 | 0.91974 | 0.23552 | 47.5384 | 30.42% | 0.6033% | 0.1545% | 31.18%
G | G North | lislea | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 48.8 | 152.458 | 111.3739 | 36.2293 | 2.718 | 2.1368 | 41.0842 | 23.76% | 1.783% | 1.402% | 26.95%
G | G North | louth | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 125 | 160.1609 | 105.8791 | 50.5426 | 3.5286 | 0.21052 | 54.2818 | 31.56% | 2.203% | 0.1314% | 33.89%
G | G North | louth | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 99.9999 | 128.1286 | 105.6535 | 19.6268 | 0.92379 | 1.9245 | 22.4751 | 15.32% | 0.721% | 1.502% | 17.54%
G | G North | meath hill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 34.56 | 107.9703 | 70.1302 | 34.8422 | 1.8851 | 1.1128 | 37.8401 | 32.27% | 1.746% | 1.031% | 35.05%
G | G North | meath hill | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 0.13333 | 0.17084 | 0.13315 | 0.033106 | 0.0031614 | 0.0014228 | 0.03769 | 19.38% | 1.851% | 0.8328% | 22.06%
G | G North | meath hill | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 16.5 | 51.5483 | 49.0141 | 0 | 2.0317 | 0.50257 | 2.5343 | 0% | 3.941% | 0.975% | 4.916%
G | G North | meath hill | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 34.56 | 107.9703 | 72.351 | 32.6822 | 1.8845 | 1.0527 | 35.6193 | 30.27% | 1.745% | 0.975% | 32.99%
G | G North | meath hill | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 0.13333 | 0.17084 | 0.13839 | 0.028316 | 0.0031876 | 0.00094823 | 0.032452 | 16.57% | 1.866% | 0.555% | 19%
G | G North | meath hill | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 16.5 | 51.5483 | 48.9656 | 0 | 1.8603 | 0.7225 | 2.5828 | 0% | 3.609% | 1.402% | 5.01%
G | G North | meath hill | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 34.56 | 107.9703 | 78.8746 | 25.6575 | 1.9249 | 1.5133 | 29.0957 | 23.76% | 1.783% | 1.402% | 26.95%
G | G North | meath hill | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 0.13333 | 0.17084 | 0.14272 | 0.023215 | 0.0031638 | 0.0017386 | 0.028117 | 13.59% | 1.852% | 1.018% | 16.46%
G | G North | meath hill | 2030 | 33% ECP | Pro-rata | IE wind not priority | 34.56 | 107.9703 | 84.5859 | 18.7109 | 1.9553 | 2.7182 | 23.3844 | 17.33% | 1.811% | 2.518% | 21.66%
G | G North | meath hill | 2030 | Initial | Pro-rata | IE wind priority | 16.5 | 51.5483 | 48.6735 | 0 | 1.5064 | 1.3684 | 2.8748 | 0% | 2.922% | 2.655% | 5.577%
G | G North | meath hill | 2030 | Initial | Pro-rata | IE wind not priority | 34.56 | 107.9703 | 89.2886 | 13.8186 | 1.9969 | 2.8662 | 18.6817 | 12.8% | 1.85% | 2.655% | 17.3%
G | G North | louth | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 125 | 160.1609 | 121.2285 | 35.216 | 1.4515 | 2.265 | 38.9324 | 21.99% | 0.9062% | 1.414% | 24.31%
G | G North | louth | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 99.9999 | 128.1286 | 97.6028 | 28.1507 | 1.0947 | 1.2805 | 30.5258 | 21.97% | 0.8544% | 0.9994% | 23.82%
G | G North | louth | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 99.9999 | 128.1286 | 105.8844 | 19.6268 | 0.92379 | 1.6936 | 22.2442 | 15.32% | 0.721% | 1.322% | 17.36%
G | G North | meath hill | 2030 | 33% ECP | Pro-rata | IE wind priority | 16.5 | 51.5483 | 48.5703 | 0 | 1.6803 | 1.2977 | 2.978 | 0% | 3.26% | 2.518% | 5.777%
F | E,F & I | macroom | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 24 | 77.6717 | 69.4643 | 0 | 0.62619 | 7.5811 | 8.2073 | 0% | 0.8062% | 9.76% | 10.57%
H1 | H1 | ballydine | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 5.9333 | 6.9468 | 5.2012 | 1.1679 | 0.13136 | 0.44636 | 1.7456 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | ballydine | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 5.9333 | 6.9468 | 4.7942 | 1.5812 | 0.14767 | 0.42372 | 2.1526 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | lisheen | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 28.8 | 90.524 | 68.5736 | 16.7056 | 1.69 | 3.5549 | 21.9505 | 18.45% | 1.867% | 3.927% | 24.25%
H1 | H1 | lisheen | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 25.3333 | 29.6605 | 20.4695 | 6.7513 | 0.6305 | 1.8091 | 9.1909 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | lisheen | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 98.6 | 309.9191 | 273.7256 | 0 | 13.2022 | 22.9913 | 36.1935 | 0% | 4.26% | 7.418% | 11.68%
H1 | H1 | lisheen | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 28.8 | 90.524 | 50.7846 | 31.3461 | 1.6779 | 6.7155 | 39.7395 | 34.63% | 1.854% | 7.418% | 43.9%
H1 | H1 | lisheen | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 25.3333 | 29.6605 | 21.5253 | 5.805 | 0.5608 | 1.7694 | 8.1352 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | lisheen | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 98.6 | 309.9191 | 277.9441 | 0 | 13.0973 | 18.8778 | 31.975 | 0% | 4.226% | 6.091% | 10.32%
H1 | H1 | lisheen | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 28.8 | 90.524 | 53.9419 | 29.3808 | 1.6874 | 5.514 | 36.5822 | 32.46% | 1.864% | 6.091% | 40.41%
H1 | H1 | lisheen | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 25.3333 | 29.6605 | 22.2074 | 4.9865 | 0.56085 | 1.9058 | 7.4531 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | lisheen | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 98.6 | 309.9191 | 280.8196 | 0 | 11.8902 | 17.2093 | 29.0995 | 0% | 3.837% | 5.553% | 9.389%
H1 | H1 | lisheen | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 28.8 | 90.524 | 60.918 | 22.8776 | 1.7018 | 5.0266 | 29.606 | 25.27% | 1.88% | 5.553% | 32.71%
H1 | H1 | lisheen | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 25.3333 | 29.6605 | 23.0284 | 4.1098 | 0.55135 | 1.9709 | 6.6321 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | lisheen | 2030 | 33% ECP | Pro-rata | IE wind priority | 98.6 | 309.9191 | 282.0432 | 0 | 10.5892 | 17.2867 | 27.8758 | 0% | 3.417% | 5.578% | 8.995%
H1 | H1 | lisheen | 2030 | 33% ECP | Pro-rata | IE wind not priority | 28.8 | 90.524 | 67.0792 | 16.7056 | 1.69 | 5.0493 | 23.4448 | 18.45% | 1.867% | 5.578% | 25.9%
H1 | H1 | lisheen | 2030 | Initial | Pro-rata | IE wind priority | 98.6 | 309.9191 | 282.2952 | 0 | 9.3893 | 18.2345 | 27.6238 | 0% | 3.03% | 5.884% | 8.913%
H1 | H1 | lisheen | 2030 | Initial | Pro-rata | IE wind not priority | 28.8 | 90.524 | 71.1991 | 12.2798 | 1.719 | 5.3261 | 19.325 | 13.57% | 1.899% | 5.884% | 21.35%
H1 | H1 | lisheen | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 98.6 | 309.9191 | 287.1594 | 0 | 10.5892 | 12.1705 | 22.7596 | 0% | 3.417% | 3.927% | 7.344%
H1 | H1 | lisheen | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 25.3333 | 29.6605 | 23.4086 | 4.1098 | 0.55135 | 1.5907 | 6.2518 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | lisheen | 2030 | 100% ECP | Pro-rata | IE wind not priority | 28.8 | 90.524 | 55.5136 | 26.9829 | 1.6676 | 6.3599 | 35.0105 | 29.81% | 1.842% | 7.026% | 38.68%
H1 | H1 | lisheen | 2030 | 100% ECP | Pro-rata | IE wind priority | 98.6 | 309.9191 | 275.5753 | 0 | 12.5699 | 21.7739 | 34.3438 | 0% | 4.056% | 7.026% | 11.08%
H1 | H1 | lisheen | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 50.6666 | 59.321 | 39.2573 | 13.3099 | 0.51057 | 6.2431 | 20.0636 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | lisheen | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 98.6 | 309.9191 | 281.0277 | 0 | 5.8407 | 23.0506 | 28.8914 | 0% | 1.885% | 7.438% | 9.322%
H1 | H1 | lisheen | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 28.8 | 90.524 | 53.6399 | 29.5694 | 0.58188 | 6.7328 | 36.8841 | 32.66% | 0.6428% | 7.438% | 40.75%
H1 | H1 | lisheen | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 50.6666 | 59.321 | 42.7865 | 9.4178 | 0.43538 | 6.6813 | 16.5345 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | lisheen | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 98.6 | 309.9191 | 275.6734 | 0 | 2.9991 | 31.2466 | 34.2457 | 0% | 0.9677% | 10.08% | 11.05%
H1 | H1 | lisheen | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 28.8 | 90.524 | 64.6479 | 16.4367 | 0.31268 | 9.1268 | 25.8761 | 18.16% | 0.3454% | 10.08% | 28.58%
H1 | H1 | lisheen | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 50.6666 | 59.321 | 40.8132 | 9.4178 | 0.43538 | 8.6546 | 18.5078 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | lisheen | 2035 | 66% ECP | Pro-rata | IE wind priority | 98.6 | 309.9191 | 270.8751 | 0 | 2.9991 | 36.0449 | 39.044 | 0% | 0.9677% | 11.63% | 12.6%
H1 | H1 | lisheen | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 76 | 88.9816 | 51.2658 | 28.2387 | 1.9532 | 7.5239 | 37.7158 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | lisheen | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 98.6 | 309.9191 | 277.6029 | 0 | 12.5699 | 19.7463 | 32.3162 | 0% | 4.056% | 6.371% | 10.43%
H1 | H1 | lisheen | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 28.8 | 90.524 | 56.1058 | 26.9829 | 1.6676 | 5.7677 | 34.4182 | 29.81% | 1.842% | 6.371% | 38.02%
H1 | H1 | lisheen | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 76 | 88.9816 | 50.73 | 28.2387 | 1.9532 | 8.0597 | 38.2516 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | lisheen | 2035 | 66% ECP | Pro-rata | IE wind not priority | 28.8 | 90.524 | 63.2464 | 16.4367 | 0.31268 | 10.5283 | 27.2777 | 18.16% | 0.3454% | 11.63% | 30.13%
H1 | H1 | killonan | 2035 | 100% ECP | Pro-rata | IE wind not priority | 84 | 264.0284 | 175.646 | 52.6336 | 0.97846 | 34.7704 | 88.3825 | 19.93% | 0.3706% | 13.17% | 33.47%
H1 | H1 | killonan | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 84 | 264.0284 | 156.4498 | 86.244 | 1.6972 | 19.6375 | 107.5787 | 32.66% | 0.6428% | 7.438% | 40.75%
H1 | H1 | killonan | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 84 | 264.0284 | 188.5564 | 47.9402 | 0.91198 | 26.6199 | 75.4721 | 18.16% | 0.3454% | 10.08% | 28.58%
H1 | H1 | kill hill | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 80 | 93.6648 | 53.964 | 29.725 | 2.056 | 7.9199 | 39.7008 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | kill hill | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 36 | 113.155 | 101.356 | 0 | 4.5894 | 7.2096 | 11.799 | 0% | 4.056% | 6.371% | 10.43%
H1 | H1 | kill hill | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 80 | 93.6648 | 53.4 | 29.725 | 2.056 | 8.4839 | 40.2648 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | kill hill | 2030 | 100% ECP | Pro-rata | IE wind priority | 36 | 113.155 | 100.6157 | 0 | 4.5894 | 7.9499 | 12.5393 | 0% | 4.056% | 7.026% | 11.08%
H1 | H1 | kill hill | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 26.6666 | 31.2216 | 24.6407 | 4.3261 | 0.58036 | 1.6744 | 6.5809 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | kill hill | 2035 | 66% ECP | Pro-rata | IE wind priority | 36 | 113.155 | 98.8996 | 0 | 1.095 | 13.1604 | 14.2554 | 0% | 0.9677% | 11.63% | 12.6%
H1 | H1 | kill hill | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 36 | 113.155 | 104.8452 | 0 | 3.8662 | 4.4436 | 8.3098 | 0% | 3.417% | 3.927% | 7.344%
H1 | H1 | kill hill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 36 | 113.155 | 99.9404 | 0 | 4.8203 | 8.3944 | 13.2146 | 0% | 4.26% | 7.418% | 11.68%
H1 | H1 | kill hill | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 26.6666 | 31.2216 | 22.6582 | 6.1105 | 0.59031 | 1.8625 | 8.5634 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | kill hill | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 36 | 113.155 | 101.4806 | 0 | 4.782 | 6.8925 | 11.6745 | 0% | 4.226% | 6.091% | 10.32%
H1 | H1 | kill hill | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 26.6666 | 31.2216 | 23.3762 | 5.2489 | 0.59037 | 2.0061 | 7.8454 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | kill hill | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 36 | 113.155 | 102.5305 | 0 | 4.3413 | 6.2833 | 10.6245 | 0% | 3.837% | 5.553% | 9.389%
H1 | H1 | kill hill | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 26.6666 | 31.2216 | 24.2404 | 4.3261 | 0.58036 | 2.0746 | 6.9811 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | kill hill | 2030 | 33% ECP | Pro-rata | IE wind priority | 36 | 113.155 | 102.9772 | 0 | 3.8662 | 6.3116 | 10.1778 | 0% | 3.417% | 5.578% | 8.995%
H1 | H1 | kill hill | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 26.6666 | 31.2216 | 21.5469 | 7.1066 | 0.66368 | 1.9044 | 9.6747 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | lisheen | 2035 | 100% ECP | Pro-rata | IE wind not priority | 28.8 | 90.524 | 60.2215 | 18.0458 | 0.33547 | 11.9213 | 30.3026 | 19.93% | 0.3706% | 13.17% | 33.47%
H1 | H1 | kill hill | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 53.3333 | 62.4431 | 42.9612 | 9.9135 | 0.4583 | 9.1101 | 19.4819 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | kill hill | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 53.3333 | 62.4431 | 45.0384 | 9.9135 | 0.4583 | 7.0329 | 17.4047 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | killonan | 2035 | 66% ECP | Pro-rata | IE wind not priority | 84 | 264.0284 | 184.4686 | 47.9402 | 0.91198 | 30.7077 | 79.5599 | 18.16% | 0.3454% | 11.63% | 30.13%
H1 | H1 | killonan | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 84 | 264.0284 | 163.642 | 78.7002 | 4.8639 | 16.8224 | 100.3865 | 29.81% | 1.842% | 6.371% | 38.02%
H1 | H1 | killonan | 2030 | 100% ECP | Pro-rata | IE wind not priority | 84 | 264.0284 | 161.9146 | 78.7002 | 4.8639 | 18.5498 | 102.1138 | 29.81% | 1.842% | 7.026% | 38.68%
H1 | H1 | killonan | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 84 | 264.0284 | 200.0063 | 48.7245 | 4.9293 | 10.3684 | 64.0222 | 18.45% | 1.867% | 3.927% | 24.25%
H1 | H1 | killonan | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 84 | 264.0284 | 148.1217 | 91.426 | 4.8938 | 19.5869 | 115.9067 | 34.63% | 1.854% | 7.418% | 43.9%
H1 | H1 | killonan | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 84 | 264.0284 | 157.3304 | 85.6939 | 4.9216 | 16.0825 | 106.698 | 32.46% | 1.864% | 6.091% | 40.41%
H1 | H1 | kill hill | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 36 | 113.155 | 100.6515 | 0 | 1.095 | 11.4085 | 12.5035 | 0% | 0.9677% | 10.08% | 11.05%
H1 | H1 | killonan | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 84 | 264.0284 | 177.6774 | 66.7264 | 4.9635 | 14.661 | 86.351 | 25.27% | 1.88% | 5.553% | 32.71%
H1 | H1 | killonan | 2030 | Initial | Pro-rata | IE wind not priority | 84 | 264.0284 | 207.6639 | 35.8162 | 5.0138 | 15.5345 | 56.3645 | 13.57% | 1.899% | 5.884% | 21.35%
H1 | H1 | kill hill | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 80 | 93.6648 | 57.1654 | 21.093 | 0.84533 | 14.5611 | 36.4994 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | kill hill | 2035 | 100% ECP | Pro-rata | IE wind priority | 36 | 113.155 | 97.0296 | 0 | 1.2238 | 14.9016 | 16.1254 | 0% | 1.082% | 13.17% | 14.25%
H1 | H1 | kill hill | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 53.3333 | 62.4431 | 41.3235 | 14.0104 | 0.53745 | 6.5717 | 21.1196 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | kill hill | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 36 | 113.155 | 102.6065 | 0 | 2.1325 | 8.4161 | 10.5486 | 0% | 1.885% | 7.438% | 9.322%
H1 | H1 | killonan | 2030 | 33% ECP | Pro-rata | IE wind not priority | 84 | 264.0284 | 195.6476 | 48.7245 | 4.9293 | 14.727 | 68.3808 | 18.45% | 1.867% | 5.578% | 25.9%
H1 | H1 | kill hill | 2030 | Initial | Pro-rata | IE wind priority | 36 | 113.155 | 103.0693 | 0 | 3.4282 | 6.6576 | 10.0858 | 0% | 3.03% | 5.884% | 8.913%
H1 | H1 | lisheen | 2035 | 100% ECP | Pro-rata | IE wind priority | 98.6 | 309.9191 | 265.7534 | 0 | 3.3518 | 40.8139 | 44.1657 | 0% | 1.082% | 13.17% | 14.25%
H1 | H1 | thurles | 2035 | 66% ECP | Pro-rata | IE wind priority | 34.9 | 109.6975 | 95.8777 | 0 | 1.0615 | 12.7583 | 13.8198 | 0% | 0.9677% | 11.63% | 12.6%
H1 | H1 | thurles | 2035 | 66% ECP | Pro-rata | IE wind not priority | 1.5667 | 4.9243 | 3.4405 | 0.89412 | 0.017009 | 0.57272 | 1.4839 | 18.16% | 0.3454% | 11.63% | 30.13%
H1 | H1 | thurles | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 140 | 163.9134 | 94.437 | 52.0187 | 3.5979 | 13.8597 | 69.4764 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | thurles | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 34.9 | 109.6975 | 98.259 | 0 | 4.4492 | 6.9893 | 11.4385 | 0% | 4.056% | 6.371% | 10.43%
H1 | H1 | thurles | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 2.35 | 7.3865 | 4.5781 | 2.2017 | 0.13607 | 0.47063 | 2.8084 | 29.81% | 1.842% | 6.371% | 38.02%
H1 | H1 | thurles | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 140 | 163.9134 | 93.45 | 52.0187 | 3.5979 | 14.8468 | 70.4634 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | thurles | 2030 | 100% ECP | Pro-rata | IE wind priority | 34.9 | 109.6975 | 97.5413 | 0 | 4.4492 | 7.707 | 12.1562 | 0% | 4.056% | 7.026% | 11.08%
H1 | H1 | thurles | 2030 | 100% ECP | Pro-rata | IE wind not priority | 2.35 | 7.3865 | 4.5298 | 2.2017 | 0.13607 | 0.51895 | 2.8568 | 29.81% | 1.842% | 7.026% | 38.68%
H1 | H1 | thurles | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 46.6666 | 54.6377 | 43.1212 | 7.5707 | 1.0156 | 2.9302 | 11.5166 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | thurles | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 34.9 | 109.6975 | 101.6416 | 0 | 3.7481 | 4.3078 | 8.0559 | 0% | 3.417% | 3.927% | 7.344%
H1 | H1 | thurles | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 0.78333 | 2.4622 | 1.8651 | 0.45438 | 0.045968 | 0.096689 | 0.59703 | 18.45% | 1.867% | 3.927% | 24.25%
H1 | H1 | thurles | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 46.6666 | 54.6377 | 37.7071 | 12.4366 | 1.1614 | 3.3326 | 16.9307 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | thurles | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 93.3332 | 109.2755 | 75.1821 | 17.3486 | 0.80202 | 15.9427 | 34.0934 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | thurles | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 1.5667 | 4.9243 | 3.5167 | 0.89412 | 0.017009 | 0.49648 | 1.4076 | 18.16% | 0.3454% | 10.08% | 28.58%
H1 | H1 | thurles | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 34.9 | 109.6975 | 97.5761 | 0 | 1.0615 | 11.0599 | 12.1214 | 0% | 0.9677% | 10.08% | 11.05%
H1 | H1 | thurles | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 93.3332 | 109.2755 | 78.8173 | 17.3486 | 0.80202 | 12.3076 | 30.4582 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | timoney | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 171.56 | 200.8642 | 114.5163 | 63.7453 | 4.409 | 18.1936 | 86.3479 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | timoney | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 161.56 | 189.1561 | 149.2857 | 26.2098 | 3.5161 | 10.1444 | 39.8704 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | timoney | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 161.56 | 189.1561 | 130.542 | 43.0556 | 4.0209 | 11.5376 | 58.6141 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | timoney | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 161.56 | 189.1561 | 137.2748 | 37.0206 | 3.5764 | 11.2842 | 51.8812 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | timoney | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 161.56 | 189.1561 | 141.6247 | 31.8006 | 3.5768 | 12.154 | 47.5313 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | timoney | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 161.56 | 189.1561 | 146.8609 | 26.2098 | 3.5161 | 12.5692 | 42.2952 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | timoney | 2030 | Initial | Pro-rata | IE Solar not priority | 156.56 | 183.302 | 158.711 | 15.1601 | 2.3619 | 7.0691 | 24.591 | 8.271% | 1.289% | 3.857% | 13.42%
H1 | H1 | thurles | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 34.9 | 109.6975 | 96.8867 | 0 | 4.673 | 8.1379 | 12.8109 | 0% | 4.26% | 7.418% | 11.68%
H1 | H1 | thurles | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 140 | 163.9134 | 100.0395 | 36.9127 | 1.4793 | 25.4819 | 63.8739 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | thurles | 2035 | 100% ECP | Pro-rata | IE wind priority | 34.9 | 109.6975 | 94.0648 | 0 | 1.1864 | 14.4463 | 15.6327 | 0% | 1.082% | 13.17% | 14.25%
H1 | H1 | thurles | 2035 | 100% ECP | Pro-rata | IE wind not priority | 2.35 | 7.3865 | 4.9139 | 1.4725 | 0.027374 | 0.97274 | 2.4726 | 19.93% | 0.3706% | 13.17% | 33.47%
H1 | H1 | thurles | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 93.3332 | 109.2755 | 72.3161 | 24.5183 | 0.94053 | 11.5005 | 36.9593 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | thurles | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 34.9 | 109.6975 | 99.4713 | 0 | 2.0674 | 8.1589 | 10.2263 | 0% | 1.885% | 7.438% | 9.322%
H1 | H1 | thurles | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 1.5667 | 4.9243 | 2.9179 | 1.6085 | 0.031653 | 0.36625 | 2.0064 | 32.66% | 0.6428% | 7.438% | 40.75%
H1 | H1 | thurles | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 0.78333 | 2.4622 | 1.3813 | 0.85258 | 0.045637 | 0.18266 | 1.0809 | 34.63% | 1.854% | 7.418% | 43.9%
H1 | H1 | thurles | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 46.6666 | 54.6377 | 39.6519 | 10.6934 | 1.033 | 3.2594 | 14.9859 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | thurles | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 34.9 | 109.6975 | 98.3798 | 0 | 4.6358 | 6.6819 | 11.3177 | 0% | 4.226% | 6.091% | 10.32%
H1 | H1 | springmount | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 21.6666 | 25.3675 | 19.6954 | 3.515 | 0.47155 | 1.6856 | 5.6722 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | nenagh | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 46 | 53.8573 | 32.8701 | 12.1285 | 0.48606 | 8.3726 | 20.9871 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | nenagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 30.6666 | 35.9048 | 23.761 | 8.056 | 0.30903 | 3.7787 | 12.1438 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | nenagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 30.6666 | 35.9048 | 25.8971 | 5.7003 | 0.26352 | 4.0439 | 10.0077 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | nenagh | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 30.6666 | 35.9048 | 24.7027 | 5.7003 | 0.26352 | 5.2383 | 11.2021 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | springmount | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 21.6666 | 25.3675 | 18.9931 | 4.2647 | 0.47967 | 1.63 | 6.3744 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | nenagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 46 | 53.8573 | 31.0293 | 17.0919 | 1.1822 | 4.5539 | 22.828 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | nenagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 15.3333 | 17.9524 | 14.1684 | 2.4875 | 0.33371 | 0.96279 | 3.784 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | nenagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 15.3333 | 17.9524 | 12.3895 | 4.0863 | 0.38162 | 1.095 | 5.5629 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | nenagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 15.3333 | 17.9524 | 13.0285 | 3.5135 | 0.33943 | 1.071 | 4.9239 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | nenagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 15.3333 | 17.9524 | 13.4413 | 3.0181 | 0.33946 | 1.1535 | 4.5111 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | nenagh | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 15.3333 | 17.9524 | 13.9383 | 2.4875 | 0.33371 | 1.1929 | 4.0141 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | nenagh | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 46 | 53.8573 | 30.705 | 17.0919 | 1.1822 | 4.8782 | 23.1523 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | lisheen | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 76 | 88.9816 | 54.3071 | 20.0383 | 0.80306 | 13.833 | 34.6744 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | springmount | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 21.6666 | 25.3675 | 18.4098 | 4.9648 | 0.47963 | 1.5133 | 6.9577 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | springmount | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 21.6666 | 25.3675 | 20.0205 | 3.515 | 0.47155 | 1.3605 | 5.347 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | thurles | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 0.78333 | 2.4622 | 1.4672 | 0.79913 | 0.045896 | 0.14998 | 0.995 | 32.46% | 1.864% | 6.091% | 40.41%
H1 | H1 | thurles | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 46.6666 | 54.6377 | 40.9083 | 9.1856 | 1.0331 | 3.5107 | 13.7294 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | thurles | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 34.9 | 109.6975 | 99.3976 | 0 | 4.2086 | 6.0913 | 10.2999 | 0% | 3.837% | 5.553% | 9.389%
H1 | H1 | thurles | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 0.78333 | 2.4622 | 1.6569 | 0.62225 | 0.046287 | 0.13672 | 0.80526 | 25.27% | 1.88% | 5.553% | 32.71%
H1 | H1 | thurles | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 46.6666 | 54.6377 | 42.4208 | 7.5707 | 1.0156 | 3.6306 | 12.217 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | thurles | 2030 | 33% ECP | Pro-rata | IE wind priority | 34.9 | 109.6975 | 99.8307 | 0 | 3.7481 | 6.1187 | 9.8668 | 0% | 3.417% | 5.578% | 8.995%
H1 | H1 | thurles | 2030 | 33% ECP | Pro-rata | IE wind not priority | 0.78333 | 2.4622 | 1.8245 | 0.45438 | 0.045968 | 0.13733 | 0.63768 | 18.45% | 1.867% | 5.578% | 25.9%
H1 | H1 | springmount | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 21.6666 | 25.3675 | 17.5069 | 5.7741 | 0.53924 | 1.5473 | 7.8607 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | thurles | 2030 | Initial | Pro-rata | IE wind priority | 34.9 | 109.6975 | 99.9199 | 0 | 3.3234 | 6.4542 | 9.7776 | 0% | 3.03% | 5.884% | 8.913%
H1 | H1 | springmount | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 65 | 76.1026 | 46.4469 | 17.138 | 0.68683 | 11.8309 | 29.6557 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | springmount | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 43.3333 | 50.735 | 33.5754 | 11.3835 | 0.43667 | 5.3395 | 17.1597 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | springmount | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 43.3333 | 50.735 | 36.5937 | 8.0547 | 0.37237 | 5.7142 | 14.1413 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | springmount | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 43.3333 | 50.735 | 34.906 | 8.0547 | 0.37237 | 7.402 | 15.8291 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | springmount | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 65 | 76.1026 | 43.8457 | 24.1516 | 1.6705 | 6.4349 | 32.2569 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | springmount | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 65 | 76.1026 | 43.3875 | 24.1516 | 1.6705 | 6.8931 | 32.7152 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | ballydine | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 5.9333 | 6.9468 | 5.0414 | 1.3596 | 0.13134 | 0.41442 | 1.9053 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | ikerrin | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 35.95 | 112.9979 | 102.464 | 0 | 2.1296 | 8.4044 | 10.5339 | 0% | 1.885% | 7.438% | 9.322%
H1 | H1 | borrisbeg | 2030 | 100% ECP | Pro-rata | IE wind not priority | 54 | 169.7326 | 104.088 | 50.593 | 3.1268 | 11.9249 | 65.6446 | 29.81% | 1.842% | 7.026% | 38.68%
H1 | H1 | borrisbeg | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 18 | 56.5775 | 42.8584 | 10.441 | 1.0563 | 2.2218 | 13.719 | 18.45% | 1.867% | 3.927% | 24.25%
H1 | H1 | borrisbeg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 18 | 56.5775 | 31.7403 | 19.5913 | 1.0487 | 4.1972 | 24.8371 | 34.63% | 1.854% | 7.418% | 43.9%
H1 | H1 | borrisbeg | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 18 | 56.5775 | 33.7136 | 18.363 | 1.0546 | 3.4462 | 22.8638 | 32.46% | 1.864% | 6.091% | 40.41%
H1 | H1 | borrisbeg | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 18 | 56.5775 | 38.0737 | 14.2985 | 1.0636 | 3.1416 | 18.5038 | 25.27% | 1.88% | 5.553% | 32.71%
H1 | H1 | borrisbeg | 2030 | 33% ECP | Pro-rata | IE wind not priority | 18 | 56.5775 | 41.9244 | 10.441 | 1.0563 | 3.1558 | 14.653 | 18.45% | 1.867% | 5.578% | 25.9%
H1 | H1 | barrymore | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 22.45 | 26.2847 | 16.042 | 5.9192 | 0.23722 | 4.0862 | 10.2426 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | barrymore | 2035 | 100% ECP | Pro-rata | IE wind priority | 32.4 | 101.8395 | 87.3267 | 0 | 1.1014 | 13.4115 | 14.5129 | 0% | 1.082% | 13.17% | 14.25%
H1 | H1 | barrymore | 2035 | 100% ECP | Pro-rata | IE wind not priority | 105.6 | 331.9214 | 220.8121 | 66.1679 | 1.2301 | 43.7114 | 111.1094 | 19.93% | 0.3706% | 13.17% | 33.47%
H1 | H1 | barrymore | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 14.9667 | 17.5231 | 11.5964 | 3.9317 | 0.15082 | 1.8442 | 5.9267 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | barrymore | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 32.4 | 101.8395 | 92.3458 | 0 | 1.9193 | 7.5744 | 9.4937 | 0% | 1.885% | 7.438% | 9.322%
H1 | H1 | barrymore | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 70.3999 | 221.2807 | 131.1197 | 72.2807 | 1.4224 | 16.458 | 90.1611 | 32.66% | 0.6428% | 7.438% | 40.75%
H1 | H1 | borrisbeg | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 54 | 169.7326 | 105.1984 | 50.593 | 3.1268 | 10.8144 | 64.5342 | 29.81% | 1.842% | 6.371% | 38.02%
H1 | H1 | borrisbeg | 2035 | 66% ECP | Pro-rata | IE wind not priority | 36 | 113.1549 | 79.0579 | 20.5458 | 0.39085 | 13.1604 | 34.0971 | 18.16% | 0.3454% | 11.63% | 30.13%
H1 | H1 | borrisbeg | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 36 | 113.1549 | 80.8098 | 20.5458 | 0.39085 | 11.4085 | 32.3451 | 18.16% | 0.3454% | 10.08% | 28.58%
H1 | H1 | cahir | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 36.3 | 42.5004 | 25.9388 | 9.5709 | 0.38357 | 6.6071 | 16.5616 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | cahir | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 35.2 | 41.2125 | 27.2735 | 9.2469 | 0.35471 | 4.3373 | 13.939 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | cahir | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 35.2 | 41.2125 | 29.7254 | 6.5429 | 0.30248 | 4.6417 | 11.4871 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | cahir | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 35.2 | 41.2125 | 28.3544 | 6.5429 | 0.30248 | 6.0127 | 12.8581 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | cahir | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 36.3 | 42.5004 | 24.4862 | 13.4877 | 0.93289 | 3.5936 | 18.0142 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | cahir | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 36.3 | 42.5004 | 24.2302 | 13.4877 | 0.93289 | 3.8496 | 18.2702 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | barrymore | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 14.9667 | 17.5231 | 12.6389 | 2.782 | 0.12861 | 1.9736 | 4.8842 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | cahir | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 34.1 | 39.9246 | 31.5093 | 5.532 | 0.74214 | 2.1412 | 8.4153 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | cahir | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 34.1 | 39.9246 | 28.9742 | 7.8138 | 0.75486 | 2.3817 | 10.9504 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | cahir | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 34.1 | 39.9246 | 29.8923 | 6.7121 | 0.75493 | 2.5653 | 10.0323 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | cahir | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 34.1 | 39.9246 | 30.9975 | 5.532 | 0.74214 | 2.653 | 8.9271 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | cahir | 2030 | Initial | Pro-rata | IE Solar not priority | 33 | 38.6367 | 33.4534 | 3.1955 | 0.49784 | 1.49 | 5.1833 | 8.271% | 1.289% | 3.857% | 13.42%
H1 | H1 | borrisbeg | 2035 | 100% ECP | Pro-rata | IE wind not priority | 54 | 169.7326 | 112.9153 | 33.8359 | 0.62901 | 22.3524 | 56.8173 | 19.93% | 0.3706% | 13.17% | 33.47%
H1 | H1 | borrisbeg | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 36 | 113.1549 | 67.0498 | 36.9617 | 0.72735 | 8.416 | 46.1051 | 32.66% | 0.6428% | 7.438% | 40.75%
H1 | H1 | cahir | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 34.1 | 39.9246 | 27.5531 | 9.0876 | 0.84869 | 2.4352 | 12.3715 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | barrymore | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 32.4 | 101.8395 | 90.5864 | 0 | 0.98549 | 10.2677 | 11.2531 | 0% | 0.9677% | 10.08% | 11.05%
H1 | H1 | barrymore | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 70.3999 | 221.2807 | 158.028 | 40.1784 | 0.76432 | 22.31 | 63.2527 | 18.16% | 0.3454% | 10.08% | 28.58%
H1 | H1 | barrymore | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 14.9667 | 17.5231 | 12.056 | 2.782 | 0.12861 | 2.5565 | 5.4671 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | barrymore | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 7.4833 | 8.7616 | 6.5599 | 1.473 | 0.16567 | 0.56296 | 2.2016 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | barrymore | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 32.4 | 101.8395 | 92.2774 | 0 | 3.9071 | 5.655 | 9.5621 | 0% | 3.837% | 5.553% | 9.389%
H1 | H1 | barrymore | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 35.2 | 110.6404 | 74.4552 | 27.9615 | 2.08 | 6.1437 | 36.1851 | 25.27% | 1.88% | 5.553% | 32.71%
H1 | H1 | barrymore | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 7.4833 | 8.7616 | 6.8025 | 1.214 | 0.16286 | 0.5822 | 1.9591 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | barrymore | 2030 | 33% ECP | Pro-rata | IE wind priority | 32.4 | 101.8395 | 92.6795 | 0 | 3.4796 | 5.6804 | 9.16 | 0% | 3.417% | 5.578% | 8.995%
H1 | H1 | barrymore | 2030 | 33% ECP | Pro-rata | IE wind not priority | 35.2 | 110.6404 | 81.9856 | 20.4179 | 2.0656 | 6.1713 | 28.6548 | 18.45% | 1.867% | 5.578% | 25.9%
H1 | H1 | barrymore | 2030 | Initial | Pro-rata | IE wind priority | 32.4 | 101.8395 | 92.7623 | 0 | 3.0853 | 5.9919 | 9.0772 | 0% | 3.03% | 5.884% | 8.913%
H1 | H1 | barrymore | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 35.2 | 110.6404 | 65.9289 | 35.9098 | 2.0624 | 6.7393 | 44.7115 | 32.46% | 1.864% | 6.091% | 40.41%
H1 | H1 | ballydine | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 11.8667 | 13.8936 | 9.1945 | 3.1173 | 0.11958 | 1.4622 | 4.6991 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | ballydine | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 11.8667 | 13.8936 | 10.0211 | 2.2058 | 0.10197 | 1.5648 | 3.8725 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | ballydine | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 11.8667 | 13.8936 | 9.5589 | 2.2058 | 0.10197 | 2.027 | 4.3347 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | ballydine | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 12.007 | 6.6138 | 0.45745 | 1.7622 | 8.8334 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | ballydine | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 11.8815 | 6.6138 | 0.45745 | 1.8877 | 8.9589 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | ballydine | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 5.9333 | 6.9468 | 5.4826 | 0.96256 | 0.12913 | 0.37256 | 1.4642 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | ballydine | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 12.7193 | 4.6932 | 0.18809 | 3.2398 | 8.1211 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | barrymore | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 32.4 | 101.8395 | 91.3325 | 0 | 4.3038 | 6.2032 | 10.507 | 0% | 4.226% | 6.091% | 10.32%
H1 | H1 | barrymore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 35.2 | 110.6404 | 62.07 | 38.3118 | 2.0507 | 8.2078 | 48.5704 | 34.63% | 1.854% | 7.418% | 43.9%
H1 | H1 | barrymore | 2035 | 66% ECP | Pro-rata | IE wind priority | 32.4 | 101.8395 | 89.0097 | 0 | 0.98549 | 11.8444 | 12.8299 | 0% | 0.9677% | 11.63% | 12.6%
H1 | H1 | barrymore | 2035 | 66% ECP | Pro-rata | IE wind not priority | 70.3999 | 221.2807 | 154.6021 | 40.1784 | 0.76432 | 25.7359 | 66.6787 | 18.16% | 0.3454% | 11.63% | 30.13%
H1 | H1 | barrymore | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 22.45 | 26.2847 | 15.1436 | 8.3416 | 0.57695 | 2.2225 | 11.141 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | barrymore | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 32.4 | 101.8395 | 91.2204 | 0 | 4.1305 | 6.4886 | 10.6191 | 0% | 4.056% | 6.371% | 10.43%
H1 | H1 | barrymore | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 7.4833 | 8.7616 | 6.3585 | 1.7148 | 0.16566 | 0.52268 | 2.4031 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | barrymore | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 105.6 | 331.9214 | 205.7213 | 98.9373 | 6.1146 | 21.1482 | 126.2001 | 29.81% | 1.842% | 6.371% | 38.02%
H1 | H1 | barrymore | 2030 | 100% ECP | Pro-rata | IE wind priority | 32.4 | 101.8395 | 90.5541 | 0 | 4.1305 | 7.1549 | 11.2854 | 0% | 4.056% | 7.026% | 11.08%
H1 | H1 | barrymore | 2030 | 100% ECP | Pro-rata | IE wind not priority | 105.6 | 331.9214 | 203.5498 | 98.9373 | 6.1146 | 23.3197 | 128.3717 | 29.81% | 1.842% | 7.026% | 38.68%
H1 | H1 | barrymore | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 7.4833 | 8.7616 | 6.9148 | 1.214 | 0.16286 | 0.46988 | 1.8468 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | barrymore | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 32.4 | 101.8395 | 94.3607 | 0 | 3.4796 | 3.9992 | 7.4788 | 0% | 3.417% | 3.927% | 7.344%
H1 | H1 | barrymore | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 35.2 | 110.6404 | 83.8121 | 20.4179 | 2.0656 | 4.3448 | 26.8283 | 18.45% | 1.867% | 3.927% | 24.25%
H1 | H1 | barrymore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 7.4833 | 8.7616 | 6.0466 | 1.9943 | 0.18625 | 0.53441 | 2.715 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | barrymore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 32.4 | 101.8395 | 89.9463 | 0 | 4.3382 | 7.5549 | 11.8932 | 0% | 4.26% | 7.418% | 11.68%
H1 | H1 | barrymore | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 22.45 | 26.2847 | 14.9854 | 8.3416 | 0.57695 | 2.3808 | 11.2993 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | ikerrin | 2035 | 100% ECP | Pro-rata | IE wind priority | 35.95 | 112.9979 | 96.8949 | 0 | 1.2221 | 14.8809 | 16.103 | 0% | 1.082% | 13.17% | 14.25%
H1 | H1 | cauteen | 2030 | Initial | Pro-rata | IE wind priority | 178.08 | 559.7403 | 509.8492 | 0 | 16.958 | 32.9331 | 49.891 | 0% | 3.03% | 5.884% | 8.913%
H1 | H1 | cauteen | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 83.6666 | 97.9577 | 76.0544 | 13.5732 | 1.8209 | 6.5092 | 21.9033 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | doon | 2035 | 66% ECP | Pro-rata | IE wind not priority | 22.4 | 70.4075 | 49.1916 | 12.784 | 0.24319 | 8.1887 | 21.2159 | 18.16% | 0.3454% | 11.63% | 30.13%
H1 | H1 | doon | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 24.99 | 29.2585 | 16.857 | 9.2853 | 0.64223 | 2.474 | 12.4015 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | doon | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 33.6 | 105.6114 | 65.4568 | 31.4801 | 1.9456 | 6.729 | 40.1546 | 29.81% | 1.842% | 6.371% | 38.02%
H1 | H1 | doon | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 24.99 | 29.2585 | 16.6808 | 9.2853 | 0.64223 | 2.6501 | 12.5777 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | doon | 2030 | 100% ECP | Pro-rata | IE wind not priority | 33.6 | 105.6114 | 64.7658 | 31.4801 | 1.9456 | 7.4199 | 40.8455 | 29.81% | 1.842% | 7.026% | 38.68%
H1 | H1 | doon | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 13.6633 | 15.9972 | 12.6253 | 2.2166 | 0.29736 | 0.85793 | 3.3719 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | doon | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 11.2 | 35.2038 | 26.6675 | 6.4966 | 0.65724 | 1.3824 | 8.5363 | 18.45% | 1.867% | 3.927% | 24.25%
H1 | H1 | doon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 13.6633 | 15.9972 | 11.0401 | 3.6413 | 0.34006 | 0.97575 | 4.9571 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | doon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 11.2 | 35.2038 | 19.7495 | 12.1901 | 0.65251 | 2.6116 | 15.4542 | 34.63% | 1.854% | 7.418% | 43.9%
H1 | H1 | doon | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 13.6633 | 15.9972 | 11.6095 | 3.1309 | 0.30246 | 0.95432 | 4.3877 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | doon | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 11.2 | 35.2038 | 20.9774 | 11.4258 | 0.65621 | 2.1443 | 14.2264 | 32.46% | 1.864% | 6.091% | 40.41%
H1 | H1 | doon | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 13.6633 | 15.9972 | 11.9774 | 2.6894 | 0.30249 | 1.0279 | 4.0198 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | doon | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 11.2 | 35.2038 | 23.6903 | 8.8968 | 0.6618 | 1.9548 | 11.5135 | 25.27% | 1.88% | 5.553% | 32.71%
H1 | H1 | doon | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 19.3267 | 22.6278 | 15.5681 | 3.5924 | 0.16608 | 3.3013 | 7.0598 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | doon | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 22.4 | 70.4075 | 50.2816 | 12.784 | 0.24319 | 7.0986 | 20.1259 | 18.16% | 0.3454% | 10.08% | 28.58%
H1 | H1 | doon | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 19.3267 | 22.6278 | 16.3208 | 3.5924 | 0.16608 | 2.5486 | 6.307 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | doon | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 22.4 | 70.4075 | 41.7199 | 22.9984 | 0.45258 | 5.2367 | 28.6876 | 32.66% | 0.6428% | 7.438% | 40.75%
H1 | H1 | ikerrin | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 35.95 | 112.9979 | 100.5117 | 0 | 1.0935 | 11.3927 | 12.4861 | 0% | 0.9677% | 10.08% | 11.05%
H1 | H1 | ikerrin | 2035 | 66% ECP | Pro-rata | IE wind priority | 35.95 | 112.9979 | 98.7623 | 0 | 1.0935 | 13.1421 | 14.2356 | 0% | 0.9677% | 11.63% | 12.6%
H1 | H1 | ikerrin | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 35.95 | 112.9979 | 101.2152 | 0 | 4.583 | 7.1996 | 11.7826 | 0% | 4.056% | 6.371% | 10.43%
H1 | H1 | ikerrin | 2030 | 100% ECP | Pro-rata | IE wind priority | 35.95 | 112.9979 | 100.476 | 0 | 4.583 | 7.9389 | 12.5219 | 0% | 4.056% | 7.026% | 11.08%
H1 | H1 | ikerrin | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 35.95 | 112.9979 | 104.6996 | 0 | 3.8609 | 4.4374 | 8.2983 | 0% | 3.417% | 3.927% | 7.344%
H1 | H1 | ikerrin | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 35.95 | 112.9979 | 99.8016 | 0 | 4.8136 | 8.3827 | 13.1963 | 0% | 4.26% | 7.418% | 11.68%
H1 | H1 | doon | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 13.6633 | 15.9972 | 12.4202 | 2.2166 | 0.29736 | 1.063 | 3.577 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | ikerrin | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 35.95 | 112.9979 | 101.3396 | 0 | 4.7753 | 6.8829 | 11.6582 | 0% | 4.226% | 6.091% | 10.32%
H1 | H1 | ikerrin | 2030 | 33% ECP | Pro-rata | IE wind priority | 35.95 | 112.9979 | 102.8342 | 0 | 3.8609 | 6.3028 | 10.1637 | 0% | 3.417% | 5.578% | 8.995%
H1 | H1 | ikerrin | 2030 | Initial | Pro-rata | IE wind priority | 35.95 | 112.9979 | 102.9261 | 0 | 3.4234 | 6.6484 | 10.0718 | 0% | 3.03% | 5.884% | 8.913%
H1 | H1 | doon | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 24.99 | 29.2585 | 17.857 | 6.5889 | 0.26406 | 4.5485 | 11.4015 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | doon | 2035 | 100% ECP | Pro-rata | IE wind not priority | 33.6 | 105.6114 | 70.2584 | 21.0534 | 0.39138 | 13.9082 | 35.353 | 19.93% | 0.3706% | 13.17% | 33.47%
H1 | H1 | doon | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 19.3267 | 22.6278 | 14.9746 | 5.077 | 0.19476 | 2.3814 | 7.6532 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | ikerrin | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 35.95 | 112.9979 | 102.3881 | 0 | 4.3352 | 6.2746 | 10.6098 | 0% | 3.837% | 5.553% | 9.389%
H1 | H1 | doon | 2030 | 33% ECP | Pro-rata | IE wind not priority | 11.2 | 35.2038 | 26.0863 | 6.4966 | 0.65724 | 1.9636 | 9.1174 | 18.45% | 1.867% | 5.578% | 25.9%
H1 | H1 | doon | 2030 | Initial | Pro-rata | IE Solar not priority | 8 | 9.3665 | 8.1099 | 0.77466 | 0.12069 | 0.36122 | 1.2566 | 8.271% | 1.289% | 3.857% | 13.42%
H1 | H1 | cauteen | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 167.3332 | 195.9153 | 134.7908 | 31.1036 | 1.4379 | 28.583 | 61.1245 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | cauteen | 2035 | 66% ECP | Pro-rata | IE wind priority | 178.08 | 559.7403 | 489.2235 | 0 | 5.4165 | 65.1002 | 70.5168 | 0% | 0.9677% | 11.63% | 12.6%
H1 | H1 | cauteen | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 251 | 293.8733 | 169.312 | 93.2622 | 6.4505 | 24.8485 | 124.5613 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | cauteen | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 178.08 | 559.7403 | 501.3744 | 0 | 22.7024 | 35.6635 | 58.3658 | 0% | 4.056% | 6.371% | 10.43%
H1 | H1 | cauteen | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 251 | 293.8733 | 167.5424 | 93.2622 | 6.4505 | 26.6181 | 126.3309 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | cauteen | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 178.08 | 559.7403 | 497.8896 | 0 | 5.4165 | 56.4341 | 61.8506 | 0% | 0.9677% | 10.08% | 11.05%
H1 | H1 | cauteen | 2030 | 100% ECP | Pro-rata | IE wind priority | 178.08 | 559.7403 | 497.7124 | 0 | 22.7024 | 39.3255 | 62.0279 | 0% | 4.056% | 7.026% | 11.08%
H1 | H1 | cauteen | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 178.08 | 559.7403 | 518.6344 | 0 | 19.1249 | 21.9809 | 41.1058 | 0% | 3.417% | 3.927% | 7.344%
H1 | H1 | cauteen | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 83.6666 | 97.9577 | 67.6034 | 22.297 | 2.0823 | 5.9749 | 30.3543 | 22.76% | 2.126% | 6.1% | 30.99%
H1 | H1 | cauteen | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 178.08 | 559.7403 | 494.3718 | 0 | 23.8443 | 41.5242 | 65.3685 | 0% | 4.26% | 7.418% | 11.68%
H1 | H1 | cauteen | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 83.6666 | 97.9577 | 71.0901 | 19.1717 | 1.8521 | 5.8437 | 26.8676 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | cauteen | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 178.08 | 559.7403 | 501.9906 | 0 | 23.6548 | 34.0948 | 57.7496 | 0% | 4.226% | 6.091% | 10.32%
H1 | H1 | cauteen | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 83.6666 | 97.9577 | 73.3428 | 16.4685 | 1.8523 | 6.2941 | 24.6149 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | cauteen | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 178.08 | 559.7403 | 507.1842 | 0 | 21.4747 | 31.0814 | 52.5561 | 0% | 3.837% | 5.553% | 9.389%
H1 | H1 | cauteen | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 83.6666 | 97.9577 | 77.3101 | 13.5732 | 1.8209 | 5.2535 | 20.6476 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | cauteen | 2030 | 33% ECP | Pro-rata | IE wind priority | 178.08 | 559.7403 | 509.3941 | 0 | 19.1249 | 31.2212 | 50.3461 | 0% | 3.417% | 5.578% | 8.995%
H1 | H1 | cauteen | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 167.3332 | 195.9153 | 141.3081 | 31.1036 | 1.4379 | 22.0658 | 54.6073 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | cauteen | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 167.3332 | 195.9153 | 129.6525 | 43.9578 | 1.6862 | 20.6188 | 66.2628 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | curraghduff | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 125 | 146.3512 | 89.321 | 32.9578 | 1.3208 | 22.7517 | 57.0303 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | curraghduff | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 83.3333 | 97.5674 | 64.568 | 21.8913 | 0.83976 | 10.2683 | 32.9994 | 22.44% | 0.8607% | 10.52% | 33.82%
H1 | H1 | curraghduff | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 83.3333 | 97.5674 | 70.3726 | 15.4898 | 0.71609 | 10.9889 | 27.1949 | 15.88% | 0.7339% | 11.26% | 27.87%
H1 | H1 | curraghduff | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 83.3333 | 97.5674 | 67.1269 | 15.4898 | 0.71609 | 14.2346 | 30.4405 | 15.88% | 0.7339% | 14.59% | 31.2%
H1 | H1 | curraghduff | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 125 | 146.3512 | 84.3187 | 46.4453 | 3.2124 | 12.3748 | 62.0325 | 31.74% | 2.195% | 8.456% | 42.39%
H1 | H1 | curraghduff | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 125 | 146.3512 | 83.4375 | 46.4453 | 3.2124 | 13.256 | 62.9138 | 31.74% | 2.195% | 9.058% | 42.99%
H1 | H1 | cauteen | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 178.08 | 559.7403 | 507.56 | 0 | 10.5489 | 41.6314 | 52.1803 | 0% | 1.885% | 7.438% | 9.322%
H1 | H1 | curraghduff | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 41.6666 | 48.7837 | 38.5011 | 6.7596 | 0.90682 | 2.6163 | 10.2826 | 13.86% | 1.859% | 5.363% | 21.08%
H1 | H1 | curraghduff | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 41.6666 | 48.7837 | 35.4034 | 9.5477 | 0.92236 | 2.9102 | 13.3803 | 19.57% | 1.891% | 5.966% | 27.43%
H1 | H1 | curraghduff | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 41.6666 | 48.7837 | 36.5253 | 8.2014 | 0.92245 | 3.1345 | 12.2584 | 16.81% | 1.891% | 6.425% | 25.13%
H1 | H1 | curraghduff | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 41.6666 | 48.7837 | 37.8757 | 6.7596 | 0.90682 | 3.2416 | 10.908 | 13.86% | 1.859% | 6.645% | 22.36%
H1 | H1 | cauteen | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 251 | 293.8733 | 179.3565 | 66.1792 | 2.6522 | 45.6854 | 114.5168 | 22.52% | 0.9025% | 15.55% | 38.97%
H1 | H1 | cauteen | 2035 | 100% ECP | Pro-rata | IE wind priority | 178.08 | 559.7403 | 479.9733 | 0 | 6.0537 | 73.7133 | 79.767 | 0% | 1.082% | 13.17% | 14.25%
H1 | H1 | curraghduff | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 41.6666 | 48.7837 | 33.667 | 11.1041 | 1.037 | 2.9756 | 15.1167 | 22.76% | 2.126% | 6.1% | 30.99%
F | E,F & I | macroom | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 15.1939 | 3.3086 | 0.15296 | 2.1849 | 5.6465 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | drombeg | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 94 | 110.0561 | 74.6886 | 24.7842 | 0.99326 | 9.5901 | 35.3676 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | drombeg | 2035 | 100% ECP | Pro-rata | IE wind not priority | 25.2 | 81.59 | 54.9647 | 14.4176 | 0.27211 | 11.9356 | 26.6252 | 17.67% | 0.3335% | 14.63% | 32.63%
E | E,F & I | drombeg | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 79.3333 | 92.8842 | 64.6259 | 20.8406 | 0.79945 | 6.6184 | 28.2584 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | drombeg | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 25.2 | 81.59 | 51.883 | 23.8631 | 0.49284 | 5.3511 | 29.707 | 29.25% | 0.604% | 6.559% | 36.41%
E | E,F & I | drombeg | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 79.3333 | 92.8842 | 72.9816 | 14.7463 | 0.68172 | 4.4746 | 19.9026 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | drombeg | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 25.2 | 81.59 | 60.3496 | 13.0267 | 0.25007 | 7.9636 | 21.2404 | 15.97% | 0.3065% | 9.76% | 26.03%
E | E,F & I | drombeg | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 79.3333 | 92.8842 | 67.7182 | 14.7463 | 0.68172 | 9.738 | 25.1661 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | drombeg | 2035 | 66% ECP | Pro-rata | IE wind not priority | 25.2 | 81.59 | 56.7997 | 13.0267 | 0.25007 | 11.5135 | 24.7903 | 15.97% | 0.3065% | 14.11% | 30.38%
E | E,F & I | drombeg | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 94 | 110.0561 | 71.7866 | 34.9269 | 2.4157 | 0.9269 | 38.2695 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | drombeg | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 25.2 | 81.59 | 55.5992 | 21.767 | 1.3826 | 2.8412 | 25.9908 | 26.68% | 1.695% | 3.482% | 31.86%
E | E,F & I | drombeg | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 94 | 110.0561 | 70.8039 | 34.9269 | 2.4157 | 1.9096 | 39.2522 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | garrow | 2030 | Initial | Pro-rata | IE wind priority | 69.225 | 224.1297 | 197.6183 | 0 | 5.9807 | 20.5306 | 26.5114 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | garrow | 2030 | 33% ECP | Pro-rata | IE wind priority | 69.225 | 224.1297 | 204.5291 | 0 | 6.7134 | 12.8872 | 19.6006 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | garrow | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 69.225 | 224.1297 | 205.8769 | 0 | 7.739 | 10.5137 | 18.2527 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | garrow | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 69.225 | 224.1297 | 207.2382 | 0 | 8.6005 | 8.291 | 16.8915 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | glanlee | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 12 | 38.8523 | 25.4812 | 11.2593 | 0.67462 | 1.4372 | 13.3711 | 28.98% | 1.736% | 3.699% | 34.42%
E | E,F & I | glanlee | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 29.8 | 96.4834 | 88.626 | 0 | 3.3315 | 4.526 | 7.8574 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | glanlee | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 12 | 38.8523 | 27.6768 | 8.6833 | 0.66969 | 1.8225 | 11.1756 | 22.35% | 1.724% | 4.691% | 28.76%
E | E,F & I | glanlee | 2030 | 33% ECP | Pro-rata | IE wind priority | 29.8 | 96.4834 | 88.0457 | 0 | 2.89 | 5.5477 | 8.4377 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | glanlee | 2030 | 33% ECP | Pro-rata | IE wind not priority | 12 | 38.8523 | 29.6771 | 6.3031 | 0.63818 | 2.234 | 9.1753 | 16.22% | 1.643% | 5.75% | 23.62%
E | E,F & I | glanlee | 2030 | Initial | Pro-rata | IE wind priority | 29.8 | 96.4834 | 85.0708 | 0 | 2.5746 | 8.838 | 11.4126 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | drombeg | 2030 | 100% ECP | Pro-rata | IE wind not priority | 25.2 | 81.59 | 54.5074 | 21.767 | 1.3826 | 3.9329 | 27.0825 | 26.68% | 1.695% | 4.82% | 33.19%
E | E,F & I | garrow | 2035 | 100% ECP | Pro-rata | IE wind priority | 69.225 | 224.1297 | 189.152 | 0 | 2.1903 | 32.7873 | 34.9776 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | garrow | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 69.225 | 224.1297 | 200.3408 | 0 | 1.9127 | 21.8762 | 23.7888 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | garrow | 2035 | 66% ECP | Pro-rata | IE wind priority | 69.225 | 224.1297 | 190.5891 | 0 | 1.9127 | 31.6279 | 33.5406 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | garrow | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 69.225 | 224.1297 | 208.1063 | 0 | 8.2184 | 7.8049 | 16.0233 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | garrow | 2030 | 100% ECP | Pro-rata | IE wind priority | 69.225 | 224.1297 | 205.1074 | 0 | 8.2184 | 10.8039 | 19.0223 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | garrow | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 69.225 | 224.1297 | 209.7711 | 0 | 6.7134 | 7.6451 | 14.3585 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | garrow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 69.225 | 224.1297 | 204.4573 | 0 | 8.7064 | 10.9659 | 19.6724 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | garrow | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 69.225 | 224.1297 | 205.5503 | 0 | 3.8798 | 14.6996 | 18.5794 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | drombeg | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 64.6667 | 75.7124 | 61.7027 | 10.4908 | 1.4074 | 2.1114 | 14.0096 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | drombeg | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 25.2 | 81.59 | 64.2302 | 13.2365 | 1.3402 | 2.7831 | 17.3598 | 16.22% | 1.643% | 3.411% | 21.28%
E | E,F & I | drombeg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 64.6667 | 75.7124 | 54.6574 | 17.2336 | 1.6094 | 2.2119 | 21.0549 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | dromada | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 28.5 | 92.2744 | 84.7597 | 0 | 3.1862 | 4.3285 | 7.5147 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | dromada | 2030 | 33% ECP | Pro-rata | IE wind priority | 28.5 | 92.2744 | 84.2048 | 0 | 2.7639 | 5.3057 | 8.0696 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | dromada | 2030 | Initial | Pro-rata | IE wind priority | 28.5 | 92.2744 | 81.3596 | 0 | 2.4623 | 8.4525 | 10.9148 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | cordal | 2035 | 100% ECP | Pro-rata | IE wind priority | 111.75 | 361.8128 | 305.3483 | 0 | 3.5359 | 52.9286 | 56.4644 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | cordal | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 111.75 | 361.8128 | 331.8201 | 0 | 6.2631 | 23.7296 | 29.9927 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | cordal | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 111.75 | 361.8128 | 323.4104 | 0 | 3.0876 | 35.3147 | 38.4023 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | dromada | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 28.5 | 92.2744 | 85.3202 | 0 | 3.5408 | 3.4134 | 6.9542 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | cordal | 2035 | 66% ECP | Pro-rata | IE wind priority | 111.75 | 361.8128 | 307.6681 | 0 | 3.0876 | 51.057 | 54.1446 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | cordal | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 111.75 | 361.8128 | 335.9463 | 0 | 13.267 | 12.5995 | 25.8664 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | cordal | 2030 | 100% ECP | Pro-rata | IE wind priority | 111.75 | 361.8128 | 331.1051 | 0 | 13.267 | 17.4407 | 30.7077 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | cordal | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 111.75 | 361.8128 | 338.6338 | 0 | 10.8374 | 12.3416 | 23.179 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | cordal | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 111.75 | 361.8128 | 330.0556 | 0 | 14.0548 | 17.7023 | 31.7572 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | cordal | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 111.75 | 361.8128 | 334.5448 | 0 | 13.8838 | 13.3841 | 27.2679 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | cordal | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 111.75 | 361.8128 | 332.3473 | 0 | 12.4931 | 16.9723 | 29.4654 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | cordal | 2030 | 33% ECP | Pro-rata | IE wind priority | 111.75 | 361.8128 | 330.1715 | 0 | 10.8374 | 20.8038 | 31.6413 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | glanlee | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 29.8 | 96.4834 | 89.212 | 0 | 3.7024 | 3.5691 | 7.2714 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | dromada | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 28.5 | 92.2744 | 84.1753 | 0 | 3.5845 | 4.5147 | 8.0991 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | dromada | 2030 | 100% ECP | Pro-rata | IE wind priority | 28.5 | 92.2744 | 84.4429 | 0 | 3.3835 | 4.448 | 7.8315 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | drombeg | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 25.2 | 81.59 | 50.8752 | 25.3154 | 1.4075 | 3.9919 | 30.7148 | 31.03% | 1.725% | 4.893% | 37.65%
E | E,F & I | drombeg | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 64.6667 | 75.7124 | 56.4776 | 14.818 | 1.4315 | 2.9852 | 19.2347 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | drombeg | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 25.2 | 81.59 | 53.5106 | 23.6446 | 1.4167 | 3.0182 | 28.0794 | 28.98% | 1.736% | 3.699% | 34.42%
E | E,F & I | drombeg | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 64.6667 | 75.7124 | 57.8511 | 12.7286 | 1.4316 | 3.701 | 17.8613 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | drombeg | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 25.2 | 81.59 | 58.1213 | 18.235 | 1.4064 | 3.8273 | 23.4687 | 22.35% | 1.724% | 4.691% | 28.76%
E | E,F & I | drombeg | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 64.6667 | 75.7124 | 59.6409 | 10.4908 | 1.4074 | 4.1733 | 16.0715 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | drombeg | 2030 | 33% ECP | Pro-rata | IE wind not priority | 25.2 | 81.59 | 62.3219 | 13.2365 | 1.3402 | 4.6913 | 19.2681 | 16.22% | 1.643% | 5.75% | 23.62%
E | E,F & I | dromada | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 28.5 | 92.2744 | 86.363 | 0 | 2.7639 | 3.1475 | 5.9114 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | drombeg | 2030 | Initial | Pro-rata | IE Solar not priority | 50 | 58.5405 | 44.0885 | 4.8416 | 0.7543 | 8.8561 | 14.452 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | dromada | 2035 | 100% ECP | Pro-rata | IE wind priority | 28.5 | 92.2744 | 77.8741 | 0 | 0.90176 | 13.4986 | 14.4003 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | dromada | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 28.5 | 92.2744 | 84.6253 | 0 | 1.5973 | 6.0518 | 7.6491 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | dromada | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 28.5 | 92.2744 | 82.4805 | 0 | 0.78745 | 9.0064 | 9.7939 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | dromada | 2035 | 66% ECP | Pro-rata | IE wind priority | 28.5 | 92.2744 | 78.4657 | 0 | 0.78745 | 13.0213 | 13.8087 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | dromada | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 28.5 | 92.2744 | 85.6776 | 0 | 3.3835 | 3.2133 | 6.5968 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | drombeg | 2030 | Initial | Pro-rata | IE wind not priority | 25.2 | 81.59 | 63.0074 | 9.7392 | 1.3696 | 7.4738 | 18.5826 | 11.94% | 1.679% | 9.16% | 22.78%
E | E,F & I | cordal | 2030 | Initial | Pro-rata | IE wind priority | 111.75 | 361.8128 | 319.0154 | 0 | 9.6547 | 33.1426 | 42.7974 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | glanlee | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 12 | 38.8523 | 24.2263 | 12.0549 | 0.67023 | 1.9009 | 14.6261 | 31.03% | 1.725% | 4.893% | 37.65%
E | E,F & I | glanlee | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 12 | 38.8523 | 30.5858 | 6.3031 | 0.63818 | 1.3253 | 8.2666 | 16.22% | 1.643% | 3.411% | 21.28%
E | E,F & I | glenlara 220kv side | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 53 | 171.598 | 157.3733 | 0 | 2.9704 | 11.2543 | 14.2247 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | glenlara 220kv side | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 13.8 | 44.6802 | 28.4121 | 13.0679 | 0.26989 | 2.9304 | 16.2681 | 29.25% | 0.604% | 6.559% | 36.41%
E | E,F & I | glenlara 220kv side | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 53 | 171.598 | 153.3848 | 0 | 1.4644 | 16.7488 | 18.2132 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | glenlara 220kv side | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 13.8 | 44.6802 | 33.0486 | 7.1337 | 0.13694 | 4.361 | 11.6316 | 15.97% | 0.3065% | 9.76% | 26.03%
E | E,F & I | glenlara 220kv side | 2035 | 66% ECP | Pro-rata | IE wind priority | 53 | 171.598 | 145.9187 | 0 | 1.4644 | 24.215 | 25.6793 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | glenlara 220kv side | 2035 | 66% ECP | Pro-rata | IE wind not priority | 13.8 | 44.6802 | 31.1046 | 7.1337 | 0.13694 | 6.305 | 13.5757 | 15.97% | 0.3065% | 14.11% | 30.38%
E | E,F & I | glenlara 220kv side | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 53 | 171.598 | 159.3302 | 0 | 6.2922 | 5.9756 | 12.2678 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | glenlara 220kv side | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 13.8 | 44.6802 | 30.4472 | 11.92 | 0.75713 | 1.5559 | 14.2331 | 26.68% | 1.695% | 3.482% | 31.86%
E | E,F & I | glenlara 220kv side | 2030 | 100% ECP | Pro-rata | IE wind priority | 53 | 171.598 | 157.0342 | 0 | 6.2922 | 8.2717 | 14.5638 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | glenlara 220kv side | 2030 | 100% ECP | Pro-rata | IE wind not priority | 13.8 | 44.6802 | 29.8493 | 11.92 | 0.75713 | 2.1538 | 14.8309 | 26.68% | 1.695% | 4.82% | 33.19%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 53 | 171.598 | 160.6048 | 0 | 5.1399 | 5.8533 | 10.9932 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 13.8 | 44.6802 | 35.1737 | 7.2486 | 0.73391 | 1.5241 | 9.5066 | 16.22% | 1.643% | 3.411% | 21.28%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 53 | 171.598 | 156.5364 | 0 | 6.6658 | 8.3957 | 15.0616 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | glenlara 220kv side | 2035 | 100% ECP | Pro-rata | IE wind not priority | 13.8 | 44.6802 | 30.0997 | 7.8953 | 0.14901 | 6.5361 | 14.5805 | 17.67% | 0.3335% | 14.63% | 32.63%
E | E,F & I | glenlara 220kv side | 2035 | 100% ECP | Pro-rata | IE wind priority | 53 | 171.598 | 144.8185 | 0 | 1.677 | 25.1026 | 26.7796 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | knockacummer | 2030 | 33% ECP | Pro-rata | IE wind priority | 105 | 339.9583 | 310.2283 | 0 | 10.1828 | 19.5472 | 29.73 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | knockacummer | 2030 | Initial | Pro-rata | IE wind priority | 105 | 339.9583 | 299.746 | 0 | 9.0715 | 31.1407 | 40.2123 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | kilpaddoge | 2035 | 100% ECP | Pro-rata | IE wind priority | 55 | 178.0734 | 150.2833 | 0 | 1.7402 | 26.0499 | 27.7901 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | kilpaddoge | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 55 | 178.0734 | 163.3119 | 0 | 3.0825 | 11.679 | 14.7615 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | kilpaddoge | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 55 | 178.0734 | 159.1729 | 0 | 1.5196 | 17.3808 | 18.9005 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | kilpaddoge | 2035 | 66% ECP | Pro-rata | IE wind priority | 55 | 178.0734 | 151.425 | 0 | 1.5196 | 25.1287 | 26.6484 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 13.8 | 44.6802 | 27.8602 | 13.8632 | 0.77076 | 2.1861 | 16.82 | 31.03% | 1.725% | 4.893% | 37.65%
E | E,F & I | kilpaddoge | 2030 | 100% ECP | Pro-rata | IE wind priority | 55 | 178.0734 | 162.96 | 0 | 6.5296 | 8.5838 | 15.1134 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | kilpaddoge | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 55 | 178.0734 | 166.6654 | 0 | 5.3339 | 6.0742 | 11.408 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | kilpaddoge | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 55 | 178.0734 | 162.4435 | 0 | 6.9174 | 8.7126 | 15.6299 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | kilpaddoge | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 55 | 178.0734 | 164.6529 | 0 | 6.8332 | 6.5873 | 13.4205 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | kilpaddoge | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 55 | 178.0734 | 163.5714 | 0 | 6.1487 | 8.3533 | 14.502 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | kilpaddoge | 2030 | 33% ECP | Pro-rata | IE wind priority | 55 | 178.0734 | 162.5005 | 0 | 5.3339 | 10.239 | 15.5729 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | kilpaddoge | 2030 | Initial | Pro-rata | IE wind priority | 55 | 178.0734 | 157.0098 | 0 | 4.7518 | 16.3118 | 21.0636 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | kilpaddoge | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 55 | 178.0734 | 165.3427 | 0 | 6.5296 | 6.2011 | 12.7307 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 53 | 171.598 | 158.6656 | 0 | 6.5847 | 6.3477 | 12.9324 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 13.8 | 44.6802 | 29.3034 | 12.9482 | 0.77581 | 1.6528 | 15.3768 | 28.98% | 1.736% | 3.699% | 34.42%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 53 | 171.598 | 157.6233 | 0 | 5.9251 | 8.0495 | 13.9747 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | glanlee | 2035 | 100% ECP | Pro-rata | IE wind priority | 29.8 | 96.4834 | 81.4262 | 0 | 0.9429 | 14.1143 | 15.0572 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | glanlee | 2035 | 100% ECP | Pro-rata | IE wind not priority | 36 | 116.5571 | 78.5211 | 20.5965 | 0.38873 | 17.0508 | 38.0361 | 17.67% | 0.3335% | 14.63% | 32.63%
E | E,F & I | glanlee | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 29.8 | 96.4834 | 88.4854 | 0 | 1.6702 | 6.3279 | 7.9981 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | glanlee | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 24 | 77.7047 | 49.4123 | 22.7267 | 0.46937 | 5.0963 | 28.2924 | 29.25% | 0.604% | 6.559% | 36.41%
E | E,F & I | glanlee | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 29.8 | 96.4834 | 86.2428 | 0 | 0.82337 | 9.4173 | 10.2406 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | glanlee | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 24 | 77.7047 | 57.4757 | 12.4064 | 0.23816 | 7.5844 | 20.2289 | 15.97% | 0.3065% | 9.76% | 26.03%
E | E,F & I | glanlee | 2035 | 66% ECP | Pro-rata | IE wind priority | 29.8 | 96.4834 | 82.0448 | 0 | 0.82337 | 13.6152 | 14.4386 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | glanlee | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 29.8 | 96.4834 | 89.5857 | 0 | 3.5379 | 3.3599 | 6.8977 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | glanlee | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 36 | 116.5571 | 79.4274 | 31.0957 | 1.9751 | 4.0589 | 37.1297 | 26.68% | 1.695% | 3.482% | 31.86%
E | E,F & I | glanlee | 2030 | 100% ECP | Pro-rata | IE wind priority | 29.8 | 96.4834 | 88.2947 | 0 | 3.5379 | 4.6509 | 8.1887 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | glanlee | 2030 | 100% ECP | Pro-rata | IE wind not priority | 36 | 116.5571 | 77.8678 | 31.0957 | 1.9751 | 5.6185 | 38.6894 | 26.68% | 1.695% | 4.82% | 33.19%
E | E,F & I | glanlee | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 29.8 | 96.4834 | 90.3023 | 0 | 2.89 | 3.2911 | 6.1811 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | glanlee | 2035 | 66% ECP | Pro-rata | IE wind not priority | 24 | 77.7047 | 54.0949 | 12.4064 | 0.23816 | 10.9653 | 23.6098 | 15.97% | 0.3065% | 14.11% | 30.38%
E | E,F & I | glanlee | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 29.8 | 96.4834 | 88.0148 | 0 | 3.748 | 4.7206 | 8.4686 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | glenlara | 2030 | Initial | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.3648 | 0.47932 | 0.074676 | 0.87675 | 1.4308 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | glenlara | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.4283 | 0.97433 | 0.10959 | 0.2833 | 1.3672 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 13.8 | 44.6802 | 31.8283 | 9.9858 | 0.77015 | 2.0959 | 12.8519 | 22.35% | 1.724% | 4.691% | 28.76%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP | Pro-rata | IE wind priority | 53 | 171.598 | 156.5914 | 0 | 5.1399 | 9.8667 | 15.0066 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | glenlara 220kv side | 2030 | 33% ECP | Pro-rata | IE wind not priority | 13.8 | 44.6802 | 34.1287 | 7.2486 | 0.73391 | 2.5691 | 10.5516 | 16.22% | 1.643% | 5.75% | 23.62%
E | E,F & I | glenlara 220kv side | 2030 | Initial | Pro-rata | IE wind priority | 53 | 171.598 | 151.3004 | 0 | 4.579 | 15.7187 | 20.2976 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | glenlara 220kv side | 2030 | Initial | Pro-rata | IE wind not priority | 13.8 | 44.6802 | 34.504 | 5.3334 | 0.75004 | 4.0928 | 10.1762 | 11.94% | 1.679% | 9.16% | 22.78%
E | E,F & I | glenlara | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 3.9331 | 1.3051 | 0.052305 | 0.50501 | 1.8624 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | glenlara | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.5653 | 0.80304 | 0.10773 | 0.31945 | 1.2302 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | glenlara | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.0323 | 1.3003 | 0.049882 | 0.41295 | 1.7632 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | glenlara | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.2253 | 0.9201 | 0.042536 | 0.6076 | 1.5702 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | glenlara | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 3.7803 | 1.8392 | 0.12721 | 0.04881 | 2.0153 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | glenlara | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 3.7285 | 1.8392 | 0.12721 | 0.10056 | 2.067 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | glenlara | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.7231 | 0.80304 | 0.10773 | 0.16162 | 1.0724 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | glenlara | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.1838 | 1.3192 | 0.1232 | 0.16931 | 1.6117 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | glenlara | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.3232 | 1.1343 | 0.10958 | 0.22851 | 1.4723 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | glenlara | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.5537 | 0.9201 | 0.042536 | 0.27919 | 1.2418 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | knockacummer | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 105 | 339.9583 | 312.2727 | 0 | 11.7385 | 15.9472 | 27.6856 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | coomataggart | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 214.0399 | 692.9967 | 440.6759 | 202.6844 | 4.186 | 45.4504 | 252.3208 | 29.25% | 0.604% | 6.559% | 36.41%
E | E,F & I | charleville | 2035 | 100% ECP | Pro-rata | IE wind not priority | 167.7 | 542.962 | 365.7773 | 95.9455 | 1.8108 | 79.4284 | 177.1847 | 17.67% | 0.3335% | 14.63% | 32.63%
E | E,F & I | charleville | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 114.6666 | 134.2527 | 93.4087 | 30.1225 | 1.1555 | 9.566 | 40.844 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | charleville | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 51.4 | 166.4177 | 152.6224 | 0 | 2.8808 | 10.9146 | 13.7953 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | charleville | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 111.7999 | 361.9743 | 230.1791 | 105.8685 | 2.1865 | 23.7402 | 131.7952 | 29.25% | 0.604% | 6.559% | 36.41%
E | E,F & I | charleville | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 114.6666 | 134.2527 | 105.486 | 21.314 | 0.98534 | 6.4674 | 28.7668 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | charleville | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 51.4 | 166.4177 | 148.7543 | 0 | 1.4202 | 16.2432 | 17.6634 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | charleville | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 111.7999 | 361.9743 | 267.7412 | 57.7932 | 1.1094 | 35.3305 | 94.2331 | 15.97% | 0.3065% | 9.76% | 26.03%
E | E,F & I | charleville | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 114.6666 | 134.2527 | 97.8783 | 21.314 | 0.98534 | 14.0751 | 36.3745 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | charleville | 2035 | 66% ECP | Pro-rata | IE wind priority | 51.4 | 166.4177 | 141.5136 | 0 | 1.4202 | 23.4839 | 24.9041 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | charleville | 2035 | 66% ECP | Pro-rata | IE wind not priority | 111.7999 | 361.9743 | 251.9919 | 57.7932 | 1.1094 | 51.0798 | 109.9824 | 15.97% | 0.3065% | 14.11% | 30.38%
E | E,F & I | charleville | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 172 | 201.3793 | 131.3542 | 63.9087 | 4.4203 | 1.696 | 70.0251 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | charleville | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 51.4 | 166.4177 | 154.5203 | 0 | 6.1022 | 5.7952 | 11.8974 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | charleville | 2035 | 100% ECP | Pro-rata | IE wind priority | 51.4 | 166.4177 | 140.4466 | 0 | 1.6263 | 24.3448 | 25.9711 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | charleville | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 172 | 201.3793 | 136.6642 | 45.3499 | 1.8175 | 17.5478 | 64.7151 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | clahane | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 51.6 | 167.0652 | 155.1215 | 0 | 6.126 | 5.8177 | 11.9437 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | clahane | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 34 | 39.8075 | 25.6099 | 12.6331 | 0.87378 | 0.69071 | 14.1976 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | clahane | 2030 | 100% ECP | Pro-rata | IE wind priority | 51.6 | 167.0652 | 152.8861 | 0 | 6.126 | 8.0532 | 14.1791 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | clahane | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 34 | 39.8075 | 32.4417 | 5.5158 | 0.73997 | 1.1101 | 7.3659 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | clahane | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 51.6 | 167.0652 | 156.3624 | 0 | 5.0041 | 5.6987 | 10.7028 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | clahane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 34 | 39.8075 | 28.7374 | 9.061 | 0.8462 | 1.163 | 11.0701 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | clahane | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 51.6 | 167.0652 | 152.4015 | 0 | 6.4897 | 8.174 | 14.6637 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | charleville | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 167.7 | 542.962 | 369.9992 | 144.8543 | 9.2008 | 18.9076 | 172.9628 | 26.68% | 1.695% | 3.482% | 31.86%
E | E,F & I | clahane | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 34 | 39.8075 | 29.6944 | 7.7909 | 0.75265 | 1.5695 | 10.1131 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | clahane | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 34 | 39.8075 | 30.4166 | 6.6924 | 0.75272 | 1.9459 | 9.391 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | clahane | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 51.6 | 167.0652 | 153.4597 | 0 | 5.7686 | 7.8369 | 13.6055 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | clahane | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 34 | 39.8075 | 31.3576 | 5.5158 | 0.73997 | 2.1942 | 8.45 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | clahane | 2030 | 33% ECP | Pro-rata | IE wind priority | 51.6 | 167.0652 | 152.455 | 0 | 5.0041 | 9.6061 | 14.6102 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | clahane | 2030 | Initial | Pro-rata | IE Solar not priority | 34 | 39.8075 | 29.9802 | 3.2923 | 0.51292 | 6.0222 | 9.8274 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | clahane | 2030 | Initial | Pro-rata | IE wind priority | 51.6 | 167.0652 | 147.3038 | 0 | 4.458 | 15.3035 | 19.7615 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | clahane | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 51.6 | 167.0652 | 154.4744 | 0 | 6.4108 | 6.18 | 12.5908 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | charleville | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 172 | 201.3793 | 129.5561 | 63.9087 | 4.4203 | 3.4942 | 71.8232 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | charleville | 2030 | 100% ECP | Pro-rata | IE wind priority | 51.4 | 166.4177 | 152.2935 | 0 | 6.1022 | 8.022 | 14.1242 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | charleville | 2030 | 100% ECP | Pro-rata | IE wind not priority | 167.7 | 542.962 | 362.7341 | 144.8543 | 9.2008 | 26.1728 | 180.2279 | 26.68% | 1.695% | 4.82% | 33.19%
E | E,F & I | boggeragh | 2035 | 100% ECP | Pro-rata | IE wind priority | 142.7 | 462.0195 | 389.9169 | 0 | 4.5151 | 67.5875 | 72.1027 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | boggeragh | 2035 | 100% ECP | Pro-rata | IE wind not priority | 23.35 | 75.6003 | 50.9296 | 13.3591 | 0.25214 | 11.0593 | 24.6706 | 17.67% | 0.3335% | 14.63% | 32.63%
E | E,F & I | boggeragh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 16.1333 | 18.889 | 13.1424 | 4.2382 | 0.16258 | 1.3459 | 5.7467 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | boggeragh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 142.7 | 462.0195 | 423.7201 | 0 | 7.9977 | 30.3017 | 38.2994 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | boggeragh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 23.35 | 75.6003 | 48.0741 | 22.1112 | 0.45666 | 4.9583 | 27.5261 | 29.25% | 0.604% | 6.559% | 36.41%
E | E,F & I | boggeragh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 16.1333 | 18.889 | 14.8416 | 2.9988 | 0.13864 | 0.90995 | 4.0474 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | boggeragh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 142.7 | 462.0195 | 412.9814 | 0 | 3.9428 | 45.0954 | 49.0382 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | boggeragh | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 24.2 | 28.3336 | 19.2283 | 6.3806 | 0.25571 | 2.4689 | 9.1053 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | boggeragh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 23.35 | 75.6003 | 55.9192 | 12.0704 | 0.23171 | 7.379 | 19.6811 | 15.97% | 0.3065% | 9.76% | 26.03%
E | E,F & I | boggeragh | 2035 | 66% ECP | Pro-rata | IE wind priority | 142.7 | 462.0195 | 392.8791 | 0 | 3.9428 | 65.1976 | 69.1404 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | boggeragh | 2035 | 66% ECP | Pro-rata | IE wind not priority | 23.35 | 75.6003 | 52.6298 | 12.0704 | 0.23171 | 10.6683 | 22.9704 | 15.97% | 0.3065% | 14.11% | 30.38%
E | E,F & I | boggeragh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 24.2 | 28.3336 | 18.4812 | 8.9918 | 0.62193 | 0.23863 | 9.8524 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | boggeragh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 142.7 | 462.0195 | 428.9892 | 0 | 16.9414 | 16.089 | 33.0304 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | boggeragh | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 16.1333 | 18.889 | 13.7712 | 2.9988 | 0.13864 | 1.9803 | 5.1178 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | clahane | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 34 | 39.8075 | 25.9654 | 12.6331 | 0.87378 | 0.33526 | 13.8422 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | charleville | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 57.3333 | 67.1264 | 54.7055 | 9.3011 | 1.2478 | 1.872 | 12.4209 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | charleville | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 51.4 | 166.4177 | 155.7564 | 0 | 4.9847 | 5.6766 | 10.6613 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | charleville | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 55.8999 | 180.9871 | 142.4788 | 29.362 | 2.9729 | 6.1735 | 38.5084 | 16.22% | 1.643% | 3.411% | 21.28%
E | E,F & I | charleville | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 57.3333 | 67.1264 | 48.4591 | 15.2793 | 1.4269 | 1.9611 | 18.6672 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | charleville | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 51.4 | 166.4177 | 151.8108 | 0 | 6.4646 | 8.1423 | 14.6069 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | charleville | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 55.8999 | 180.9871 | 112.854 | 56.1558 | 3.1222 | 8.8551 | 68.1331 | 31.03% | 1.725% | 4.893% | 37.65%
E | E,F & I | charleville | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 57.3333 | 67.1264 | 50.0729 | 13.1376 | 1.2692 | 2.6467 | 17.0535 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | charleville | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 51.4 | 166.4177 | 153.8757 | 0 | 6.3859 | 6.1561 | 12.542 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | charleville | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 57.3333 | 67.1264 | 51.2906 | 11.2852 | 1.2693 | 3.2813 | 15.8358 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | charleville | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 51.4 | 166.4177 | 152.8649 | 0 | 5.7463 | 7.8065 | 13.5528 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | charleville | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 55.8999 | 180.9871 | 128.9277 | 40.4499 | 3.1197 | 8.49 | 52.0595 | 22.35% | 1.724% | 4.691% | 28.76%
E | E,F & I | charleville | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 57.3333 | 67.1264 | 52.8774 | 9.3011 | 1.2478 | 3.7 | 14.249 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | charleville | 2030 | 33% ECP | Pro-rata | IE wind priority | 51.4 | 166.4177 | 151.8641 | 0 | 4.9847 | 9.5688 | 14.5536 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | charleville | 2030 | 33% ECP | Pro-rata | IE wind not priority | 55.8999 | 180.9871 | 138.2457 | 29.362 | 2.9729 | 10.4066 | 42.7414 | 16.22% | 1.643% | 5.75% | 23.62%
E | E,F & I | charleville | 2030 | Initial | Pro-rata | IE wind priority | 51.4 | 166.4177 | 146.7328 | 0 | 4.4407 | 15.2441 | 19.6849 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | charleville | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 55.8999 | 180.9871 | 118.6999 | 52.4496 | 3.1426 | 6.695 | 62.2872 | 28.98% | 1.736% | 3.699% | 34.42%
E | E,F & I | coomataggart | 2035 | 100% ECP | Pro-rata | IE wind not priority | 242.64 | 785.5951 | 529.232 | 138.8206 | 2.62 | 114.9225 | 256.3631 | 17.67% | 0.3335% | 14.63% | 32.63%
E | E,F & I | clahane | 2035 | 66% ECP | Pro-rata | IE wind priority | 51.6 | 167.0652 | 142.0642 | 0 | 1.4257 | 23.5753 | 25.001 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | coomagearlahy | 2035 | 66% ECP | Pro-rata | IE wind priority | 81 | 262.2536 | 223.0078 | 0 | 2.238 | 37.0078 | 39.2458 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | coomagearlahy | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 7 | 8.1957 | 5.3458 | 2.6009 | 0.1799 | 0.069025 | 2.8499 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | coomagearlahy | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 81 | 262.2536 | 243.5047 | 0 | 9.6163 | 9.1325 | 18.7488 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | coomagearlahy | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 7 | 8.1957 | 5.2726 | 2.6009 | 0.1799 | 0.14221 | 2.923 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | coomagearlahy | 2030 | 100% ECP | Pro-rata | IE wind priority | 81 | 262.2536 | 239.9956 | 0 | 9.6163 | 12.6416 | 22.2579 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | coomagearlahy | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 7 | 8.1957 | 6.6792 | 1.1356 | 0.15235 | 0.22855 | 1.5165 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | coomagearlahy | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 81 | 262.2536 | 245.4527 | 0 | 7.8553 | 8.9456 | 16.8009 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | coomagearlahy | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 7 | 8.1957 | 5.9165 | 1.8655 | 0.17422 | 0.23943 | 2.2791 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | coomagearlahy | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 81 | 262.2536 | 239.2349 | 0 | 10.1874 | 12.8312 | 23.0186 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | coomagearlahy | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 7 | 8.1957 | 6.1136 | 1.604 | 0.15496 | 0.32314 | 2.0821 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | coomagearlahy | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 81 | 262.2536 | 242.4889 | 0 | 10.0634 | 9.7012 | 19.7647 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | coomagearlahy | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 7 | 8.1957 | 6.2622 | 1.3778 | 0.15497 | 0.40062 | 1.9334 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | coomagearlahy | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 81 | 262.2536 | 240.8961 | 0 | 9.0554 | 12.3021 | 21.3575 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | coomagearlahy | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 7 | 8.1957 | 5.9751 | 1.3011 | 0.060152 | 0.85924 | 2.2205 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | coomagearlahy | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 81 | 262.2536 | 234.4183 | 0 | 2.238 | 25.5972 | 27.8353 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | coomagearlahy | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 7 | 8.1957 | 6.4396 | 1.3011 | 0.060152 | 0.39481 | 1.7561 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | coomagearlahy | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 81 | 262.2536 | 240.5139 | 0 | 4.5397 | 17.2 | 21.7397 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | coomataggart | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 214.0399 | 692.9967 | 512.5882 | 110.6446 | 2.124 | 67.6399 | 180.4085 | 15.97% | 0.3065% | 9.76% | 26.03%
E | E,F & I | coomataggart | 2035 | 66% ECP | Pro-rata | IE wind not priority | 214.0399 | 692.9967 | 482.4363 | 110.6446 | 2.124 | 97.7918 | 210.5604 | 15.97% | 0.3065% | 14.11% | 30.38%
E | E,F & I | coomataggart | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 242.64 | 785.5951 | 535.3406 | 209.5853 | 13.3123 | 27.3569 | 250.2545 | 26.68% | 1.695% | 3.482% | 31.86%
E | E,F & I | coomataggart | 2030 | 100% ECP | Pro-rata | IE wind not priority | 242.64 | 785.5951 | 524.8288 | 209.5853 | 13.3123 | 37.8686 | 260.7662 | 26.68% | 1.695% | 4.82% | 33.19%
E | E,F & I | coomataggart | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 185.44 | 600.3987 | 472.6526 | 97.4042 | 9.862 | 20.4798 | 127.746 | 16.22% | 1.643% | 3.411% | 21.28%
E | E,F & I | coomataggart | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 185.44 | 600.3987 | 374.3769 | 186.2889 | 10.3573 | 29.3756 | 226.0217 | 31.03% | 1.725% | 4.893% | 37.65%
E | E,F & I | coomagearlahy | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 7 | 8.1957 | 6.456 | 1.1356 | 0.15235 | 0.45175 | 1.7397 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | coomataggart | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 185.44 | 600.3987 | 393.7697 | 173.994 | 10.4251 | 22.2098 | 206.6289 | 28.98% | 1.736% | 3.699% | 34.42%
E | E,F & I | coomataggart | 2030 | 33% ECP | Pro-rata | IE wind not priority | 185.44 | 600.3987 | 458.6102 | 97.4042 | 9.862 | 34.5222 | 141.7884 | 16.22% | 1.643% | 5.75% | 23.62%
E | E,F & I | coomataggart | 2030 | Initial | Pro-rata | IE wind not priority | 156.84 | 507.8006 | 392.1458 | 60.6151 | 8.5243 | 46.5154 | 115.6547 | 11.94% | 1.679% | 9.16% | 22.78%
E | E,F & I | coomagearlahy | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 7 | 8.1957 | 5.5619 | 1.8456 | 0.073966 | 0.71415 | 2.6338 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | coomagearlahy | 2035 | 100% ECP | Pro-rata | IE wind priority | 81 | 262.2536 | 221.3263 | 0 | 2.5629 | 38.3643 | 40.9272 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | coomagearlahy | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 7 | 8.1957 | 5.7023 | 1.8389 | 0.07054 | 0.58397 | 2.4934 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | coomataggart | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 185.44 | 600.3987 | 427.6988 | 134.1866 | 10.349 | 28.1642 | 172.6998 | 22.35% | 1.724% | 4.691% | 28.76%
E | E,F & I | coomagearlahy | 2030 | 33% ECP | Pro-rata | IE wind priority | 81 | 262.2536 | 239.3189 | 0 | 7.8553 | 15.0793 | 22.9346 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | coomagearlahy | 2030 | Initial | Pro-rata | IE Solar not priority | 7 | 8.1957 | 6.1724 | 0.67783 | 0.1056 | 1.2399 | 2.0233 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | coomagearlahy | 2030 | Initial | Pro-rata | IE wind priority | 81 | 262.2536 | 231.2327 | 0 | 6.998 | 24.0229 | 31.0209 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | clashavoon | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 112 | 362.6222 | 247.1074 | 96.7423 | 6.1448 | 12.6276 | 115.5148 | 26.68% | 1.695% | 3.482% | 31.86%
E | E,F & I | clashavoon | 2030 | 100% ECP | Pro-rata | IE wind not priority | 112 | 362.6222 | 242.2553 | 96.7423 | 6.1448 | 17.4797 | 120.3669 | 26.68% | 1.695% | 4.82% | 33.19%
E | E,F & I | clashavoon | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 37.3333 | 120.8739 | 95.1558 | 19.6097 | 1.9854 | 4.1231 | 25.7182 | 16.22% | 1.643% | 3.411% | 21.28%
E | E,F & I | clashavoon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 37.3333 | 120.8739 | 75.3706 | 37.5042 | 2.0852 | 5.914 | 45.5033 | 31.03% | 1.725% | 4.893% | 37.65%
E | E,F & I | clashavoon | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 37.3333 | 120.8739 | 79.2748 | 35.029 | 2.0988 | 4.4713 | 41.5991 | 28.98% | 1.736% | 3.699% | 34.42%
E | E,F & I | clashavoon | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 37.3333 | 120.8739 | 86.1055 | 27.0148 | 2.0835 | 5.6701 | 34.7684 | 22.35% | 1.724% | 4.691% | 28.76%
E | E,F & I | clashavoon | 2030 | 33% ECP | Pro-rata | IE wind not priority | 37.3333 | 120.8739 | 92.3287 | 19.6097 | 1.9854 | 6.9501 | 28.5452 | 16.22% | 1.643% | 5.75% | 23.62%
E | E,F & I | clahane | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 34 | 39.8075 | 27.015 | 8.9645 | 0.35927 | 3.4688 | 12.7925 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | clahane | 2035 | 100% ECP | Pro-rata | IE wind priority | 51.6 | 167.0652 | 140.9931 | 0 | 1.6327 | 24.4395 | 26.0722 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | clahane | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 34 | 39.8075 | 27.6968 | 8.9317 | 0.34262 | 2.8364 | 12.1107 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | clahane | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 51.6 | 167.0652 | 153.2162 | 0 | 2.892 | 10.957 | 13.849 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | clahane | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 34 | 39.8075 | 31.2778 | 6.3199 | 0.29217 | 1.9177 | 8.5297 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | clahane | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 51.6 | 167.0652 | 149.3331 | 0 | 1.4257 | 16.3064 | 17.7321 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | clahane | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 34 | 39.8075 | 29.0221 | 6.3199 | 0.29217 | 4.1734 | 10.7855 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | clashavoon | 2035 | 66% ECP | Pro-rata | IE wind not priority | 74.6666 | 241.7479 | 168.2951 | 38.5977 | 0.74095 | 34.1141 | 73.4528 | 15.97% | 0.3065% | 14.11% | 30.38%
E | E,F & I | clashavoon | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 74.6666 | 241.7479 | 153.7272 | 70.7053 | 1.4603 | 15.8551 | 88.0207 | 29.25% | 0.604% | 6.559% | 36.41%
E | E,F & I | cloghboola | 2035 | 100% ECP | Pro-rata | IE wind priority | 100.549 | 325.5473 | 274.7425 | 0 | 3.1814 | 47.6234 | 50.8049 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | cloghboola | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 100.549 | 325.5473 | 298.5609 | 0 | 5.6353 | 21.3511 | 26.9865 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | cloghboola | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 100.549 | 325.5473 | 290.9941 | 0 | 2.7781 | 31.775 | 34.5532 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | cloghboola | 2035 | 66% ECP | Pro-rata | IE wind priority | 100.549 | 325.5473 | 276.8297 | 0 | 2.7781 | 45.9394 | 48.7176 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | cloghboola | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 100.549 | 325.5473 | 302.2735 | 0 | 11.9372 | 11.3366 | 23.2738 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | clashavoon | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 74.6666 | 241.7479 | 178.8134 | 38.5977 | 0.74095 | 23.5958 | 62.9345 | 15.97% | 0.3065% | 9.76% | 26.03%
E | E,F & I | cloghboola | 2030 | 100% ECP | Pro-rata | IE wind priority | 100.549 | 325.5473 | 297.9175 | 0 | 11.9372 | 15.6926 | 27.6298 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | cloghboola | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 100.549 | 325.5473 | 296.9733 | 0 | 12.6461 | 15.928 | 28.5741 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | cloghboola | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 100.549 | 325.5473 | 301.0125 | 0 | 12.4922 | 12.0426 | 24.5348 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | cloghboola | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 100.549 | 325.5473 | 299.0353 | 0 | 11.2409 | 15.2712 | 26.512 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | cloghboola | 2030 | 33% ECP | Pro-rata | IE wind priority | 100.549 | 325.5473 | 297.0775 | 0 | 9.7512 | 18.7186 | 28.4698 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | cloghboola | 2030 | Initial | Pro-rata | IE wind priority | 100.549 | 325.5473 | 287.0397 | 0 | 8.687 | 29.8207 | 38.5077 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | clashavoon | 2035 | 100% ECP | Pro-rata | IE wind not priority | 112 | 362.6222 | 244.2878 | 64.0781 | 1.2094 | 53.047 | 118.3344 | 17.67% | 0.3335% | 14.63% | 32.63%
E | E,F & I | cloghboola | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 100.549 | 325.5473 | 304.6916 | 0 | 9.7512 | 11.1045 | 20.8557 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | knockacummer | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 105 | 339.9583 | 314.3374 | 0 | 13.0452 | 12.5757 | 25.6209 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | knockacummer | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 105 | 339.9583 | 310.1194 | 0 | 13.2059 | 16.6331 | 29.8389 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | knockacummer | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 105 | 339.9583 | 318.1794 | 0 | 10.1828 | 11.5961 | 21.7789 | 0% | 2.995% | 3.411% | 6.406%
F | E,F & I | ballylickey | 2030 | Initial | Pro-rata | IE wind not priority | 5.82 | 18.8354 | 14.6727 | 2.1289 | 0.3084 | 1.7254 | 4.1626 | 11.3% | 1.637% | 9.16% | 22.1%
E | E,F & I | trien | 2035 | 100% ECP | Pro-rata | IE wind priority | 47.2 | 152.8194 | 128.9704 | 0 | 1.4934 | 22.3555 | 23.849 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | trien | 2035 | 100% ECP | Pro-rata | IE wind not priority | 6.6 | 21.3688 | 14.3955 | 3.776 | 0.071267 | 3.126 | 6.9733 | 17.67% | 0.3335% | 14.63% | 32.63%
E | E,F & I | trien | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 47.2 | 152.8194 | 140.1513 | 0 | 2.6454 | 10.0227 | 12.6681 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | trien | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 6.6 | 21.3688 | 13.5884 | 6.2498 | 0.12908 | 1.4015 | 7.7804 | 29.25% | 0.604% | 6.559% | 36.41%
E | E,F & I | trien | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 47.2 | 152.8194 | 136.5993 | 0 | 1.3041 | 14.9159 | 16.22 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | trien | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 6.6 | 21.3688 | 15.8058 | 3.4118 | 0.065495 | 2.0857 | 5.563 | 15.97% | 0.3065% | 9.76% | 26.03%
E | E,F & I | trien | 2035 | 66% ECP | Pro-rata | IE wind priority | 47.2 | 152.8194 | 129.9502 | 0 | 1.3041 | 21.565 | 22.8691 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | trien | 2035 | 66% ECP | Pro-rata | IE wind not priority | 6.6 | 21.3688 | 14.8761 | 3.4118 | 0.065495 | 3.0154 | 6.4927 | 15.97% | 0.3065% | 14.11% | 30.38%
E | E,F & I | trien | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 47.2 | 152.8194 | 141.8941 | 0 | 5.6036 | 5.3216 | 10.9252 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | trien | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 6.6 | 21.3688 | 14.5617 | 5.7009 | 0.36211 | 0.74413 | 6.8071 | 26.68% | 1.695% | 3.482% | 31.86%
F | E,F & I | ballylickey | 2030 | Initial | Pro-rata | IE wind priority | 51.45 | 166.5087 | 146.9459 | 0 | 4.3103 | 15.2525 | 19.5628 | 0% | 2.589% | 9.16% | 11.75%
F | E,F & I | ballylickey | 2030 | 33% ECP | Pro-rata | IE wind not priority | 5.82 | 18.8354 | 14.5625 | 2.8812 | 0.30872 | 1.083 | 4.2729 | 15.3% | 1.639% | 5.75% | 22.69%
F | E,F & I | ballylickey | 2030 | 33% ECP | Pro-rata | IE wind priority | 51.45 | 166.5087 | 152.0302 | 0 | 4.9044 | 9.5741 | 14.4785 | 0% | 2.945% | 5.75% | 8.695%
F | E,F & I | ballylickey | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 5.82 | 18.8354 | 13.6326 | 4.0002 | 0.31897 | 0.88355 | 5.2028 | 21.24% | 1.693% | 4.691% | 27.62%
F | E,F & I | ballylickey | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 5.82 | 18.8354 | 14.1957 | 2.7434 | 0.057915 | 1.8384 | 4.6397 | 14.56% | 0.3075% | 9.76% | 24.63%
F | E,F & I | ballylickey | 2035 | 66% ECP | Pro-rata | IE wind priority | 51.45 | 166.5087 | 141.6695 | 0 | 1.3424 | 23.4968 | 24.8392 | 0% | 0.8062% | 14.11% | 14.92%
F | E,F & I | ballylickey | 2035 | 66% ECP | Pro-rata | IE wind not priority | 5.82 | 18.8354 | 13.3762 | 2.7434 | 0.057915 | 2.6579 | 5.4592 | 14.56% | 0.3075% | 14.11% | 28.98%
F | E,F & I | ballylickey | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 51.45 | 166.5087 | 154.724 | 0 | 5.9863 | 5.7984 | 11.7847 | 0% | 3.595% | 3.482% | 7.078%
F | E,F & I | ballylickey | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 5.82 | 18.8354 | 13.0402 | 4.8205 | 0.3187 | 0.65591 | 5.7951 | 25.59% | 1.692% | 3.482% | 30.77%
E | E,F & I | trien | 2030 | 100% ECP | Pro-rata | IE wind priority | 47.2 | 152.8194 | 139.8493 | 0 | 5.6036 | 7.3665 | 12.9701 | 0% | 3.667% | 4.82% | 8.487%
F | E,F & I | ballylickey | 2030 | 100% ECP | Pro-rata | IE wind priority | 51.45 | 166.5087 | 152.496 | 0 | 5.9863 | 8.0263 | 14.0127 | 0% | 3.595% | 4.82% | 8.416%
F | E,F & I | ballylickey | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 51.45 | 166.5087 | 155.9245 | 0 | 4.9044 | 5.6797 | 10.5841 | 0% | 2.945% | 3.411% | 6.356%
F | E,F & I | ballylickey | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 5.82 | 18.8354 | 15.003 | 2.8812 | 0.30872 | 0.64248 | 3.8324 | 15.3% | 1.639% | 3.411% | 20.35%
F | E,F & I | ballylickey | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 51.45 | 166.5087 | 152.1644 | 0 | 6.1976 | 8.1467 | 14.3443 | 0% | 3.722% | 4.893% | 8.615%
F | E,F & I | ballylickey | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 5.82 | 18.8354 | 12.017 | 5.5823 | 0.31452 | 0.92155 | 6.8184 | 29.64% | 1.67% | 4.893% | 36.2%
F | E,F & I | ballylickey | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 51.45 | 166.5087 | 154.218 | 0 | 6.1312 | 6.1595 | 12.2906 | 0% | 3.682% | 3.699% | 7.381%
F | E,F & I | ballylickey | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 5.82 | 18.8354 | 12.5988 | 5.2243 | 0.31557 | 0.69675 | 6.2366 | 27.74% | 1.675% | 3.699% | 33.11%
F | E,F & I | ballylickey | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 51.45 | 166.5087 | 153.1152 | 0 | 5.5827 | 7.8108 | 13.3935 | 0% | 3.353% | 4.691% | 8.044%
F | E,F & I | ballylickey | 2030 | 100% ECP | Pro-rata | IE wind not priority | 5.82 | 18.8354 | 12.7882 | 4.8205 | 0.3187 | 0.90794 | 6.0472 | 25.59% | 1.692% | 4.82% | 32.11%
E | E,F & I | trien | 2030 | 100% ECP | Pro-rata | IE wind not priority | 6.6 | 21.3688 | 14.2758 | 5.7009 | 0.36211 | 1.0301 | 7.093 | 26.68% | 1.695% | 4.82% | 33.19%
E | E,F & I | trien | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 47.2 | 152.8194 | 143.0292 | 0 | 4.5774 | 5.2127 | 9.7902 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | trien | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 6.6 | 21.3688 | 16.8222 | 3.4667 | 0.351 | 0.7289 | 4.5466 | 16.22% | 1.643% | 3.411% | 21.28%
E | E,F & I | tralee | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 115.4 | 135.1115 | 88.1295 | 42.8783 | 2.9657 | 1.1379 | 46.9819 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | tralee | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 15 | 48.5655 | 45.0935 | 0 | 1.7808 | 1.6912 | 3.472 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | tralee | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 115.4 | 135.1115 | 86.9231 | 42.8783 | 2.9657 | 2.3444 | 48.1884 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | tralee | 2030 | 100% ECP | Pro-rata | IE wind priority | 15 | 48.5655 | 44.4436 | 0 | 1.7808 | 2.341 | 4.1218 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | tralee | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 45.0666 | 52.7645 | 43.0011 | 7.3111 | 0.98082 | 1.4715 | 9.7634 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | tralee | 2035 | 66% ECP | Pro-rata | IE wind priority | 15 | 48.5655 | 41.2977 | 0 | 0.41445 | 6.8533 | 7.2677 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | tralee | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 15 | 48.5655 | 45.4542 | 0 | 1.4547 | 1.6566 | 3.1113 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | tralee | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 15 | 48.5655 | 44.3028 | 0 | 1.8866 | 2.3762 | 4.2627 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | tralee | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 45.0666 | 52.7645 | 39.3597 | 10.3268 | 0.99763 | 2.0804 | 13.4048 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | tralee | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 15 | 48.5655 | 44.9053 | 0 | 1.8636 | 1.7965 | 3.6601 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | tralee | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 45.0666 | 52.7645 | 40.3168 | 8.8707 | 0.99772 | 2.5793 | 12.4476 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | tralee | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 15 | 48.5655 | 44.6104 | 0 | 1.6769 | 2.2782 | 3.9551 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | tralee | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 45.0666 | 52.7645 | 41.5641 | 7.3111 | 0.98082 | 2.9084 | 11.2003 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | tralee | 2030 | 33% ECP | Pro-rata | IE wind priority | 15 | 48.5655 | 44.3183 | 0 | 1.4547 | 2.7925 | 4.2471 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | tralee | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 45.0666 | 52.7645 | 38.0911 | 12.0102 | 1.1216 | 1.5415 | 14.6733 | 22.76% | 2.126% | 2.921% | 27.81%
F | E,F & I | ballylickey | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 51.45 | 166.5087 | 148.9142 | 0 | 1.3424 | 16.2521 | 17.5945 | 0% | 0.8062% | 9.76% | 10.57%
E | E,F & I | tralee | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 80.2333 | 93.9379 | 68.4863 | 14.9136 | 0.68945 | 9.8485 | 25.4516 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | tralee | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 80.2333 | 93.9379 | 73.8095 | 14.9136 | 0.68945 | 4.5253 | 20.1284 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | trien | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 47.2 | 152.8194 | 139.406 | 0 | 5.9364 | 7.477 | 13.4133 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | trien | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 6.6 | 21.3688 | 13.3245 | 6.6302 | 0.36863 | 1.0455 | 8.0443 | 31.03% | 1.725% | 4.893% | 37.65%
E | E,F & I | trien | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 47.2 | 152.8194 | 141.3022 | 0 | 5.8641 | 5.6531 | 11.5172 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | trien | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 6.6 | 21.3688 | 14.0147 | 6.1926 | 0.37104 | 0.79047 | 7.3541 | 28.98% | 1.736% | 3.699% | 34.42%
E | E,F & I | trien | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 47.2 | 152.8194 | 140.374 | 0 | 5.2767 | 7.1686 | 12.4454 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | trien | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 6.6 | 21.3688 | 15.2222 | 4.7758 | 0.36833 | 1.0024 | 6.1466 | 22.35% | 1.724% | 4.691% | 28.76%
E | E,F & I | trien | 2030 | 33% ECP | Pro-rata | IE wind priority | 47.2 | 152.8194 | 139.455 | 0 | 4.5774 | 8.7869 | 13.3644 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | tralee | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 15 | 48.5655 | 43.4108 | 0 | 0.41445 | 4.7402 | 5.1547 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | trien | 2030 | 33% ECP | Pro-rata | IE wind not priority | 6.6 | 21.3688 | 16.3224 | 3.4667 | 0.351 | 1.2287 | 5.0464 | 16.22% | 1.643% | 5.75% | 23.62%
E | E,F & I | trien | 2030 | Initial | Pro-rata | IE wind not priority | 6.6 | 21.3688 | 16.5019 | 2.5507 | 0.35871 | 1.9574 | 4.8669 | 11.94% | 1.679% | 9.16% | 22.78%
E | E,F & I | tralee | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 115.4 | 135.1115 | 91.6921 | 30.4266 | 1.2194 | 11.7733 | 43.4193 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | tralee | 2035 | 100% ECP | Pro-rata | IE wind priority | 15 | 48.5655 | 40.9864 | 0 | 0.47461 | 7.1045 | 7.5791 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | tralee | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 80.2333 | 93.9379 | 65.359 | 21.077 | 0.80852 | 6.6934 | 28.5789 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | tralee | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 15 | 48.5655 | 44.5396 | 0 | 0.84069 | 3.1852 | 4.0259 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | trien | 2030 | Initial | Pro-rata | IE wind priority | 47.2 | 152.8194 | 134.743 | 0 | 4.0779 | 13.9985 | 18.0764 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | tralee | 2030 | Initial | Pro-rata | IE Solar not priority | 9.9 | 11.591 | 8.7295 | 0.95864 | 0.14935 | 1.7535 | 2.8615 | 8.271% | 1.289% | 15.13% | 24.69%
F | E,F & I | ballylickey | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 5.82 | 18.8354 | 12.2718 | 5.2185 | 0.10975 | 1.2353 | 6.5636 | 27.71% | 0.5827% | 6.559% | 34.85%
F | E,F & I | ballylickey | 2035 | 100% ECP | Pro-rata | IE wind not priority | 5.82 | 18.8354 | 12.9493 | 3.0675 | 0.063241 | 2.7554 | 5.8861 | 16.29% | 0.3358% | 14.63% | 31.25%
F | E,F & I | dunmanway | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 30.75 | 99.5168 | 91.3901 | 0 | 1.5999 | 6.5268 | 8.1267 | 0% | 1.608% | 6.559% | 8.166%
F | E,F & I | dunmanway | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 81.75 | 264.5691 | 172.3742 | 73.3016 | 1.5416 | 17.3518 | 92.195 | 27.71% | 0.5827% | 6.559% | 34.85%
F | E,F & I | dunmanway | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 30.75 | 99.5168 | 89.0012 | 0 | 0.8023 | 9.7133 | 10.5156 | 0% | 0.8062% | 9.76% | 10.57%
F | E,F & I | dunmanway | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 81.75 | 264.5691 | 199.3979 | 38.5344 | 0.8135 | 25.8233 | 65.1712 | 14.56% | 0.3075% | 9.76% | 24.63%
F | E,F & I | dunmanway | 2035 | 66% ECP | Pro-rata | IE wind priority | 30.75 | 99.5168 | 84.6713 | 0 | 0.8023 | 14.0433 | 14.8456 | 0% | 0.8062% | 14.11% | 14.92%
F | E,F & I | dunmanway | 2035 | 66% ECP | Pro-rata | IE wind not priority | 81.75 | 264.5691 | 187.8867 | 38.5344 | 0.8135 | 37.3345 | 76.6825 | 14.56% | 0.3075% | 14.11% | 28.98%
F | E,F & I | dunmanway | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 30.75 | 99.5168 | 92.4735 | 0 | 3.5778 | 3.4655 | 7.0433 | 0% | 3.595% | 3.482% | 7.078%
F | E,F & I | dunmanway | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 81.75 | 264.5691 | 183.1682 | 67.7112 | 4.4766 | 9.2131 | 81.4009 | 25.59% | 1.692% | 3.482% | 30.77%
F | E,F & I | dunmanway | 2030 | 100% ECP | Pro-rata | IE wind priority | 30.75 | 99.5168 | 91.1419 | 0 | 3.5778 | 4.7971 | 8.3749 | 0% | 3.595% | 4.82% | 8.416%
F | E,F & I | dunmanway | 2030 | 100% ECP | Pro-rata | IE wind not priority | 81.75 | 264.5691 | 179.6281 | 67.7112 | 4.4766 | 12.7532 | 84.941 | 25.59% | 1.692% | 4.82% | 32.11%
F | E,F & I | dunmanway | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 30.75 | 99.5168 | 93.191 | 0 | 2.9312 | 3.3946 | 6.3258 | 0% | 2.945% | 3.411% | 6.356%
F | E,F & I | dunmanway | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 81.75 | 264.5691 | 210.7383 | 40.4699 | 4.3364 | 9.0246 | 53.8308 | 15.3% | 1.639% | 3.411% | 20.35%
F | E,F & I | dunmanway | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 30.75 | 99.5168 | 90.9437 | 0 | 3.7041 | 4.869 | 8.5731 | 0% | 3.722% | 4.893% | 8.615%
F | E,F & I | dunmanway | 2035 | 100% ECP | Pro-rata | IE wind not priority | 81.75 | 264.5691 | 181.8903 | 43.0875 | 0.88831 | 38.7031 | 82.6789 | 16.29% | 0.3358% | 14.63% | 31.25%
F | E,F & I | dunmanway | 2035 | 100% ECP | Pro-rata | IE wind priority | 30.75 | 99.5168 | 84.0492 | 0 | 0.90961 | 14.558 | 15.4676 | 0% | 0.914% | 14.63% | 15.54%
F | E,F & I | macroom | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 13.5936 | 6.6138 | 0.45745 | 0.17552 | 7.2468 | 31.74% | 2.195% | 0.8422% | 34.77%
F | E,F & I | macroom | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 24 | 77.6717 | 72.1744 | 0 | 2.7925 | 2.7048 | 5.4972 | 0% | 3.595% | 3.482% | 7.078%
F | E,F & I | macroom | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 13.4075 | 6.6138 | 0.45745 | 0.36161 | 7.4329 | 31.74% | 2.195% | 1.735% | 35.67%
F | E,F & I | macroom | 2030 | 100% ECP | Pro-rata | IE wind priority | 24 | 77.6717 | 71.1351 | 0 | 2.7925 | 3.7441 | 6.5365 | 0% | 3.595% | 4.82% | 8.416%
F | E,F & I | macroom | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 16.9842 | 2.8877 | 0.38739 | 0.58118 | 3.8563 | 13.86% | 1.859% | 2.789% | 18.5%
F | E,F & I | macroom | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 24 | 77.6717 | 72.7345 | 0 | 2.2878 | 2.6494 | 4.9372 | 0% | 2.945% | 3.411% | 6.356%
F | E,F & I | macroom | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 15.0449 | 4.7437 | 0.44301 | 0.60885 | 5.7955 | 22.76% | 2.126% | 2.921% | 27.81%
F | E,F & I | dunmanway | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 81.75 | 264.5691 | 168.7952 | 78.4115 | 4.4179 | 12.9445 | 95.7739 | 29.64% | 1.67% | 4.893% | 36.2%
F | E,F & I | macroom | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 24 | 77.6717 | 70.9805 | 0 | 2.891 | 3.8002 | 6.6912 | 0% | 3.722% | 4.893% | 8.615%
F | E,F & I | macroom | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 24 | 77.6717 | 71.9384 | 0 | 2.86 | 2.8732 | 5.7332 | 0% | 3.682% | 3.699% | 7.381%
F | E,F & I | macroom | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 15.924 | 3.5037 | 0.39407 | 1.0187 | 4.9165 | 16.81% | 1.891% | 4.888% | 23.59%
F | E,F & I | macroom | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 24 | 77.6717 | 71.424 | 0 | 2.6042 | 3.6435 | 6.2477 | 0% | 3.353% | 4.691% | 8.044%
F | E,F & I | macroom | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 16.4166 | 2.8877 | 0.38739 | 1.1487 | 4.4238 | 13.86% | 1.859% | 5.512% | 21.23%
F | E,F & I | macroom | 2030 | 33% ECP | Pro-rata | IE wind priority | 24 | 77.6717 | 70.9179 | 0 | 2.2878 | 4.466 | 6.7538 | 0% | 2.945% | 5.75% | 8.695%
F | E,F & I | macroom | 2030 | Initial | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 15.6955 | 1.7236 | 0.26853 | 3.1528 | 5.1449 | 8.271% | 1.289% | 15.13% | 24.69%
F | E,F & I | macroom | 2030 | Initial | Pro-rata | IE wind priority | 24 | 77.6717 | 68.5462 | 0 | 2.0106 | 7.1149 | 9.1255 | 0% | 2.589% | 9.16% | 11.75%
F | E,F & I | macroom | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 17.8 | 20.8404 | 15.5459 | 4.0788 | 0.39403 | 0.8217 | 5.2945 | 19.57% | 1.891% | 3.943% | 25.4%
F | E,F & I | dunmanway | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 30.75 | 99.5168 | 92.1711 | 0 | 3.6644 | 3.6813 | 7.3457 | 0% | 3.682% | 3.699% | 7.381%
F | E,F & I | dunmanway | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 81.75 | 264.5691 | 176.9677 | 73.3819 | 4.4327 | 9.7869 | 87.6014 | 27.74% | 1.675% | 3.699% | 33.11%
F | E,F & I | dunmanway | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 30.75 | 99.5168 | 91.512 | 0 | 3.3366 | 4.6683 | 8.0048 | 0% | 3.353% | 4.691% | 8.044%
F | E,F & I | bandon | 2030 | 100% ECP | Pro-rata | IE wind priority | 8.75 | 28.3178 | 25.9347 | 0 | 1.0181 | 1.365 | 2.3831 | 0% | 3.595% | 4.82% | 8.416%
F | E,F & I | bandon | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 26.0167 | 30.4606 | 24.8242 | 4.2207 | 0.56622 | 0.84946 | 5.6363 | 13.86% | 1.859% | 2.789% | 18.5%
F | E,F & I | bandon | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 8.75 | 28.3178 | 26.5178 | 0 | 0.83409 | 0.96593 | 1.8 | 0% | 2.945% | 3.411% | 6.356%
F | E,F & I | bandon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 26.0167 | 30.4606 | 21.9898 | 6.9334 | 0.64751 | 0.8899 | 8.4708 | 22.76% | 2.126% | 2.921% | 27.81%
F | E,F & I | bandon | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 8.75 | 28.3178 | 25.8783 | 0 | 1.054 | 1.3855 | 2.4395 | 0% | 3.722% | 4.893% | 8.615%
F | E,F & I | bandon | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 26.0167 | 30.4606 | 22.7221 | 5.9616 | 0.57592 | 1.201 | 7.7385 | 19.57% | 1.891% | 3.943% | 25.4%
F | E,F & I | bandon | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 8.75 | 28.3178 | 26.2276 | 0 | 1.0427 | 1.0475 | 2.0902 | 0% | 3.682% | 3.699% | 7.381%
F | E,F & I | bandon | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 41.25 | 48.2959 | 31.0709 | 15.327 | 1.0601 | 0.838 | 17.2251 | 31.74% | 2.195% | 1.735% | 35.67%
F | E,F & I | bandon | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 26.0167 | 30.4606 | 23.2746 | 5.121 | 0.57598 | 1.489 | 7.1859 | 16.81% | 1.891% | 4.888% | 23.59%
F | E,F & I | bandon | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 26.0167 | 30.4606 | 23.9947 | 4.2207 | 0.56622 | 1.679 | 6.4659 | 13.86% | 1.859% | 5.512% | 21.23%
F | E,F & I | bandon | 2030 | 33% ECP | Pro-rata | IE wind priority | 8.75 | 28.3178 | 25.8555 | 0 | 0.83409 | 1.6282 | 2.4623 | 0% | 2.945% | 5.75% | 8.695%
F | E,F & I | bandon | 2030 | Initial | Pro-rata | IE Solar not priority | 18.4 | 21.5429 | 16.2246 | 1.7817 | 0.27758 | 3.259 | 5.3183 | 8.271% | 1.289% | 15.13% | 24.69%
F | E,F & I | bandon | 2030 | Initial | Pro-rata | IE wind priority | 8.75 | 28.3178 | 24.9908 | 0 | 0.73305 | 2.594 | 3.327 | 0% | 2.589% | 9.16% | 11.75%
F | E,F & I | ballylickey | 2035 | 100% ECP | Pro-rata | IE wind priority | 51.45 | 166.5087 | 140.6286 | 0 | 1.5219 | 24.3581 | 25.88 | 0% | 0.914% | 14.63% | 15.54%
F | E,F & I | bandon | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 8.75 | 28.3178 | 26.04 | 0 | 0.94944 | 1.3284 | 2.2778 | 0% | 3.353% | 4.691% | 8.044%
F | E,F & I | ballylickey | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 51.45 | 166.5087 | 152.9112 | 0 | 2.6769 | 10.9205 | 13.5974 | 0% | 1.608% | 6.559% | 8.166%
F | E,F & I | bandon | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 8.75 | 28.3178 | 26.3136 | 0 | 1.0181 | 0.98611 | 2.0042 | 0% | 3.595% | 3.482% | 7.078%
F | E,F & I | dunmanway | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 81.75 | 264.5691 | 191.4892 | 56.1889 | 4.4803 | 12.4107 | 73.0799 | 21.24% | 1.693% | 4.691% | 27.62%
F | E,F & I | dunmanway | 2030 | 33% ECP | Pro-rata | IE wind priority | 30.75 | 99.5168 | 90.8635 | 0 | 2.9312 | 5.7221 | 8.6533 | 0% | 2.945% | 5.75% | 8.695%
F | E,F & I | dunmanway | 2030 | 33% ECP | Pro-rata | IE wind not priority | 81.75 | 264.5691 | 204.5505 | 40.4699 | 4.3364 | 15.2124 | 60.0187 | 15.3% | 1.639% | 5.75% | 22.69%
F | E,F & I | dunmanway | 2030 | Initial | Pro-rata | IE wind priority | 30.75 | 99.5168 | 87.8248 | 0 | 2.5761 | 9.1159 | 11.692 | 0% | 2.589% | 9.16% | 11.75%
F | E,F & I | dunmanway | 2030 | Initial | Pro-rata | IE wind not priority | 81.75 | 264.5691 | 206.099 | 29.9034 | 4.3319 | 24.235 | 58.4702 | 11.3% | 1.637% | 9.16% | 22.1%
F | E,F & I | bandon | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 41.25 | 48.2959 | 31.5021 | 15.327 | 1.0601 | 0.40675 | 16.7938 | 31.74% | 2.195% | 0.8422% | 34.77%
F | E,F & I | bandon | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 41.25 | 48.2959 | 32.7756 | 10.8761 | 0.43587 | 4.2084 | 15.5203 | 22.52% | 0.9025% | 8.714% | 32.14%
F | E,F & I | bandon | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 33.6333 | 39.3782 | 27.3981 | 8.8353 | 0.33893 | 2.8059 | 11.9801 | 22.44% | 0.8607% | 7.125% | 30.42%
F | E,F & I | bandon | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 8.75 | 28.3178 | 26.0053 | 0 | 0.45525 | 1.8572 | 2.3125 | 0% | 1.608% | 6.559% | 8.166%
F | E,F & I | bandon | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 33.6333 | 39.3782 | 30.9405 | 6.2517 | 0.28902 | 1.897 | 8.4377 | 15.88% | 0.7339% | 4.817% | 21.43%
F | E,F & I | bandon | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 8.75 | 28.3178 | 25.3255 | 0 | 0.2283 | 2.764 | 2.9923 | 0% | 0.8062% | 9.76% | 10.57%
F | E,F & I | bandon | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 33.6333 | 39.3782 | 28.7091 | 6.2517 | 0.28902 | 4.1284 | 10.6691 | 15.88% | 0.7339% | 10.48% | 27.09%
F | E,F & I | bandon | 2035 | 66% ECP | Pro-rata | IE wind priority | 8.75 | 28.3178 | 24.0935 | 0 | 0.2283 | 3.9961 | 4.2243 | 0% | 0.8062% | 14.11% | 14.92%
F | E,F & I | bandon | 2035 | 100% ECP | Pro-rata | IE wind priority | 8.75 | 28.3178 | 23.9164 | 0 | 0.25883 | 4.1425 | 4.4014 | 0% | 0.914% | 14.63% | 15.54%
E | E,F & I | tralee | 2030 | Initial | Pro-rata | IE wind priority | 15 | 48.5655 | 42.8209 | 0 | 1.2959 | 4.4487 | 5.7446 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | mallow | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.3232 | 1.1343 | 0.10958 | 0.22851 | 1.4723 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | mallow | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 13.5 | 43.7089 | 28.6663 | 12.6667 | 0.75895 | 1.6169 | 15.0425 | 28.98% | 1.736% | 3.699% | 34.42%
E | E,F & I | mallow | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.4283 | 0.97433 | 0.10959 | 0.2833 | 1.3672 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | mallow | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 13.5 | 43.7089 | 31.1364 | 9.7688 | 0.75341 | 2.0503 | 12.5725 | 22.35% | 1.724% | 4.691% | 28.76%
E | E,F & I | mallow | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.5653 | 0.80304 | 0.10773 | 0.31945 | 1.2302 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | mallow | 2030 | 33% ECP | Pro-rata | IE wind not priority | 13.5 | 43.7089 | 33.3867 | 7.091 | 0.71795 | 2.5132 | 10.3222 | 16.22% | 1.643% | 5.75% | 23.62%
E | E,F & I | mallow | 2030 | Initial | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.3648 | 0.47932 | 0.074676 | 0.87675 | 1.4308 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | knockearagh | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 4.99 | 5.8423 | 3.9649 | 1.3157 | 0.052727 | 0.50909 | 1.8775 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | knockearagh | 2035 | 100% ECP | Pro-rata | IE wind priority | 9.35 | 30.2725 | 25.5482 | 0 | 0.29584 | 4.4285 | 4.7243 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | knockearagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 3.3267 | 3.8949 | 2.7099 | 0.8739 | 0.033523 | 0.27753 | 1.185 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | knockearagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 9.35 | 30.2725 | 27.763 | 0 | 0.52403 | 1.9854 | 2.5095 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | knockearagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 3.3267 | 3.8949 | 3.0603 | 0.61835 | 0.028586 | 0.18763 | 0.83457 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | knockearagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 9.35 | 30.2725 | 27.0594 | 0 | 0.25834 | 2.9547 | 3.2131 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | mallow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 13.5 | 43.7089 | 27.2546 | 13.5618 | 0.75401 | 2.1385 | 16.4543 | 31.03% | 1.725% | 4.893% | 37.65%
E | E,F & I | mallow | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.1838 | 1.3192 | 0.1232 | 0.16931 | 1.6117 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | mallow | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 13.5 | 43.7089 | 34.409 | 7.091 | 0.71795 | 1.4909 | 9.2999 | 16.22% | 1.643% | 3.411% | 21.28%
E | E,F & I | mallow | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.7231 | 0.80304 | 0.10773 | 0.16162 | 1.0724 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | mallow | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 3.9331 | 1.3051 | 0.052305 | 0.50501 | 1.8624 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | mallow | 2035 | 100% ECP | Pro-rata | IE wind not priority | 40.5 | 131.1268 | 88.3362 | 23.1711 | 0.43732 | 19.1822 | 42.7906 | 17.67% | 0.3335% | 14.63% | 32.63%
E | E,F & I | mallow | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.0323 | 1.3003 | 0.049882 | 0.41295 | 1.7632 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | mallow | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 27 | 87.4178 | 55.5889 | 25.5675 | 0.52805 | 5.7333 | 31.8289 | 29.25% | 0.604% | 6.559% | 36.41%
E | E,F & I | mallow | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.5537 | 0.9201 | 0.042536 | 0.27919 | 1.2418 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | knockearagh | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 3.3267 | 3.8949 | 2.8396 | 0.61835 | 0.028586 | 0.40834 | 1.0553 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | mallow | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 27 | 87.4178 | 64.6602 | 13.9572 | 0.26793 | 8.5324 | 22.7576 | 15.97% | 0.3065% | 9.76% | 26.03%
E | E,F & I | mallow | 2035 | 66% ECP | Pro-rata | IE wind not priority | 27 | 87.4178 | 60.8567 | 13.9572 | 0.26793 | 12.3359 | 26.5611 | 15.97% | 0.3065% | 14.11% | 30.38%
E | E,F & I | mallow | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 3.7803 | 1.8392 | 0.12721 | 0.04881 | 2.0153 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | mallow | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 40.5 | 131.1268 | 89.3558 | 34.9827 | 2.222 | 4.5662 | 41.771 | 26.68% | 1.695% | 3.482% | 31.86%
E | E,F & I | mallow | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 3.7285 | 1.8392 | 0.12721 | 0.10056 | 2.067 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | mallow | 2030 | 100% ECP | Pro-rata | IE wind not priority | 40.5 | 131.1268 | 87.6013 | 34.9827 | 2.222 | 6.3208 | 43.5255 | 26.68% | 1.695% | 4.82% | 33.19%
E | E,F & I | mallow | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 4.95 | 5.7955 | 4.2253 | 0.9201 | 0.042536 | 0.6076 | 1.5702 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | knockearagh | 2035 | 66% ECP | Pro-rata | IE wind priority | 9.35 | 30.2725 | 25.7423 | 0 | 0.25834 | 4.2719 | 4.5302 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | knockanure | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 116 | 135.814 | 88.5877 | 43.1012 | 2.9811 | 1.1438 | 47.2262 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | knockanure | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 116 | 135.814 | 87.375 | 43.1012 | 2.9811 | 2.3566 | 48.4389 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | knockanure | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 38.6666 | 45.2713 | 36.8944 | 6.2729 | 0.84153 | 1.2625 | 8.3769 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | knockanure | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 38.6666 | 45.2713 | 32.6817 | 10.3046 | 0.96234 | 1.3226 | 12.5895 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | knockanure | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 38.6666 | 45.2713 | 33.7701 | 8.8602 | 0.85595 | 1.785 | 11.5012 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | knockanure | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 38.6666 | 45.2713 | 34.5913 | 7.6109 | 0.85603 | 2.213 | 10.6799 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | knockanure | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 77.3333 | 90.5425 | 66.0109 | 14.3746 | 0.66453 | 9.4925 | 24.5316 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | knockanure | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 38.6666 | 45.2713 | 35.6615 | 6.2729 | 0.84153 | 2.4954 | 9.6098 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | knockacummer | 2035 | 100% ECP | Pro-rata | IE wind priority | 105 | 339.9583 | 286.9045 | 0 | 3.3223 | 49.7315 | 53.0538 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | knockacummer | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 105 | 339.9583 | 311.7772 | 0 | 5.8848 | 22.2963 | 28.1811 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | knockacummer | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 105 | 339.9583 | 303.8756 | 0 | 2.9011 | 33.1816 | 36.0827 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | knockacummer | 2035 | 66% ECP | Pro-rata | IE wind priority | 105 | 339.9583 | 289.0842 | 0 | 2.9011 | 47.973 | 50.8741 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | knockacummer | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 105 | 339.9583 | 315.6543 | 0 | 12.4656 | 11.8384 | 24.304 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | knockacummer | 2030 | 100% ECP | Pro-rata | IE wind priority | 105 | 339.9583 | 311.1054 | 0 | 12.4656 | 16.3873 | 28.8529 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | oughtragh | 2030 | Initial | Pro-rata | IE wind priority | 9 | 29.1393 | 25.6925 | 0 | 0.77756 | 2.6692 | 3.4468 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | knockanure | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 77.3333 | 90.5425 | 71.1417 | 14.3746 | 0.66453 | 4.3617 | 19.4008 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | knockanure | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 116 | 135.814 | 92.1689 | 30.5848 | 1.2257 | 11.8346 | 43.6451 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | knockearagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 4.99 | 5.8423 | 3.8108 | 1.8541 | 0.12824 | 0.049205 | 2.0315 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | knockearagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 9.35 | 30.2725 | 28.1083 | 0 | 1.11 | 1.0542 | 2.1642 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | knockearagh | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 4.99 | 5.8423 | 3.7586 | 1.8541 | 0.12824 | 0.10137 | 2.0837 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | knockearagh | 2030 | 100% ECP | Pro-rata | IE wind priority | 9.35 | 30.2725 | 27.7032 | 0 | 1.11 | 1.4592 | 2.5693 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | knockearagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 1.6633 | 1.9474 | 1.5871 | 0.26984 | 0.0362 | 0.054309 | 0.36035 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | knockearagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 9.35 | 30.2725 | 28.3331 | 0 | 0.90676 | 1.0326 | 1.9394 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | knockearagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 1.6633 | 1.9474 | 1.4059 | 0.44328 | 0.041397 | 0.056894 | 0.54157 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | knockanure | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 77.3333 | 90.5425 | 62.9966 | 20.3152 | 0.7793 | 6.4515 | 27.546 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | knockearagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 9.35 | 30.2725 | 27.6154 | 0 | 1.176 | 1.4811 | 2.6571 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | knockearagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 9.35 | 30.2725 | 27.991 | 0 | 1.1616 | 1.1198 | 2.2815 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | knockearagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 1.6633 | 1.9474 | 1.488 | 0.3274 | 0.036824 | 0.095196 | 0.45942 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | knockearagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 9.35 | 30.2725 | 27.8071 | 0 | 1.0453 | 1.4201 | 2.4653 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | knockearagh | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 1.6633 | 1.9474 | 1.5341 | 0.26984 | 0.0362 | 0.10734 | 0.41339 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | knockearagh | 2030 | 33% ECP | Pro-rata | IE wind priority | 9.35 | 30.2725 | 27.6251 | 0 | 0.90676 | 1.7406 | 2.6474 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | knockearagh | 2030 | Initial | Pro-rata | IE wind priority | 9.35 | 30.2725 | 26.6917 | 0 | 0.8078 | 2.773 | 3.5808 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | knockearagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 1.6633 | 1.9474 | 1.4527 | 0.38114 | 0.036821 | 0.076784 | 0.49475 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | oughtragh | 2030 | Initial | Pro-rata | IE Solar not priority | 4 | 4.6832 | 3.5271 | 0.38733 | 0.060344 | 0.70849 | 1.1562 | 8.271% | 1.289% | 15.13% | 24.69%
E | E,F & I | oughtragh | 2030 | 33% ECP | Pro-rata | IE wind priority | 9 | 29.1393 | 26.591 | 0 | 0.87281 | 1.6755 | 2.5483 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | oughtragh | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 5.8 | 6.7907 | 5.3492 | 0.94093 | 0.12623 | 0.3743 | 1.4415 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | reamore | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 57.85 | 187.3008 | 172.0474 | 0 | 6.4673 | 8.7861 | 15.2535 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | reamore | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 26.8 | 86.7703 | 61.8115 | 19.3928 | 1.4957 | 4.0703 | 24.9588 | 22.35% | 1.724% | 4.691% | 28.76%
E | E,F & I | reamore | 2030 | 33% ECP | Pro-rata | IE wind priority | 57.85 | 187.3008 | 170.921 | 0 | 5.6103 | 10.7696 | 16.3798 | 0% | 2.995% | 5.75% | 8.745%
E | E,F & I | reamore | 2030 | 33% ECP | Pro-rata | IE wind not priority | 26.8 | 86.7703 | 66.2789 | 14.077 | 1.4253 | 4.9892 | 20.4914 | 16.22% | 1.643% | 5.75% | 23.62%
E | E,F & I | reamore | 2030 | Initial | Pro-rata | IE wind priority | 57.85 | 187.3008 | 165.1458 | 0 | 4.998 | 17.1571 | 22.155 | 0% | 2.668% | 9.16% | 11.83%
E | E,F & I | reamore | 2030 | Initial | Pro-rata | IE wind not priority | 25.3 | 81.9138 | 63.2574 | 9.7779 | 1.3751 | 7.5034 | 18.6564 | 11.94% | 1.679% | 9.16% | 22.78%
E | E,F & I | reamore | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 26.8 | 86.7703 | 56.9081 | 25.1458 | 1.5066 | 3.2098 | 29.8622 | 28.98% | 1.736% | 3.699% | 34.42%
E | E,F & I | pollagh | 2035 | 100% ECP | Pro-rata | IE wind not priority | 50 | 161.8849 | 109.057 | 28.6063 | 0.5399 | 23.6817 | 52.8279 | 17.67% | 0.3335% | 14.63% | 32.63%
E | E,F & I | pollagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 85.3332 | 99.909 | 69.5135 | 22.4167 | 0.85991 | 7.1189 | 30.3955 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | pollagh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 33.3333 | 107.9232 | 68.6282 | 31.5649 | 0.65191 | 7.0782 | 39.2949 | 29.25% | 0.604% | 6.559% | 36.41%
E | E,F & I | pollagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 85.3332 | 99.909 | 78.5012 | 15.8616 | 0.73328 | 4.813 | 21.4078 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | pollagh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 33.3333 | 107.9232 | 79.8274 | 17.2311 | 0.33078 | 10.5338 | 28.0957 | 15.97% | 0.3065% | 9.76% | 26.03%
E | E,F & I | pollagh | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 85.3332 | 99.909 | 72.8396 | 15.8616 | 0.73328 | 10.4745 | 27.0694 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | pollagh | 2035 | 66% ECP | Pro-rata | IE wind not priority | 33.3333 | 107.9232 | 75.1317 | 17.2311 | 0.33078 | 15.2295 | 32.7914 | 15.97% | 0.3065% | 14.11% | 30.38%
E | E,F & I | pollagh | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 128 | 149.8637 | 101.7036 | 33.7488 | 1.3525 | 13.0588 | 48.1601 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | reamore | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 57.85 | 187.3008 | 173.185 | 0 | 7.1873 | 6.9286 | 14.1159 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | reamore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 57.85 | 187.3008 | 170.861 | 0 | 7.2758 | 9.164 | 16.4398 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | reamore | 2035 | 100% ECP | Pro-rata | IE wind priority | 57.85 | 187.3008 | 158.0707 | 0 | 1.8304 | 27.3997 | 29.2301 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | reamore | 2035 | 100% ECP | Pro-rata | IE wind not priority | 29.8 | 96.4834 | 64.998 | 17.0493 | 0.32178 | 14.1143 | 31.4854 | 17.67% | 0.3335% | 14.63% | 32.63%
E | E,F & I | reamore | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 57.85 | 187.3008 | 171.7744 | 0 | 3.2422 | 12.2842 | 15.5264 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | reamore | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind not priority | 28.3 | 91.6268 | 58.2654 | 26.7986 | 0.55347 | 6.0094 | 33.3614 | 29.25% | 0.604% | 6.559% | 36.41%
E | E,F & I | reamore | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 57.85 | 187.3008 | 167.421 | 0 | 1.5984 | 18.2815 | 19.8799 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | reamore | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 28.3 | 91.6268 | 67.7735 | 14.6292 | 0.28083 | 8.9432 | 23.8533 | 15.97% | 0.3065% | 9.76% | 26.03%
E | E,F & I | reamore | 2035 | 66% ECP | Pro-rata | IE wind priority | 57.85 | 187.3008 | 159.2716 | 0 | 1.5984 | 26.4309 | 28.0292 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | reamore | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 26.8 | 86.7703 | 54.1054 | 26.9227 | 1.4968 | 4.2454 | 32.6649 | 31.03% | 1.725% | 4.893% | 37.65%
E | E,F & I | reamore | 2035 | 66% ECP | Pro-rata | IE wind not priority | 28.3 | 91.6268 | 63.7869 | 14.6292 | 0.28083 | 12.9299 | 27.8399 | 15.97% | 0.3065% | 14.11% | 30.38%
E | E,F & I | reamore | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 57.85 | 187.3008 | 173.9105 | 0 | 6.868 | 6.5224 | 13.3904 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | reamore | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 29.8 | 96.4834 | 65.7482 | 25.7404 | 1.635 | 3.3599 | 30.7352 | 26.68% | 1.695% | 3.482% | 31.86%
E | E,F & I | reamore | 2030 | 100% ECP | Pro-rata | IE wind priority | 57.85 | 187.3008 | 171.4043 | 0 | 6.868 | 9.0286 | 15.8966 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | reamore | 2030 | 100% ECP | Pro-rata | IE wind not priority | 29.8 | 96.4834 | 64.4572 | 25.7404 | 1.635 | 4.6509 | 32.0262 | 26.68% | 1.695% | 4.82% | 33.19%
E | E,F & I | reamore | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 57.85 | 187.3008 | 175.3017 | 0 | 5.6103 | 6.3889 | 11.9992 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | reamore | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 26.8 | 86.7703 | 68.3083 | 14.077 | 1.4253 | 2.9598 | 18.462 | 16.22% | 1.643% | 3.411% | 21.28%
E | E,F & I | pollagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 50 | 161.8849 | 110.3158 | 43.1885 | 2.7432 | 5.6373 | 51.5691 | 26.68% | 1.695% | 3.482% | 31.86%
E | E,F & I | oughtragh | 2035 | 66% ECP | Pro-rata | IE Solar not priority | 7.6 | 8.8982 | 6.4873 | 1.4127 | 0.065308 | 0.93289 | 2.4109 | 15.88% | 0.7339% | 10.48% | 27.09%
E | E,F & I | oughtragh | 2035 | 66% ECP | Pro-rata | IE wind priority | 9 | 29.1393 | 24.7786 | 0 | 0.24867 | 4.112 | 4.3606 | 0% | 0.8534% | 14.11% | 14.96%
E | E,F & I | oughtragh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 9.4 | 11.0056 | 7.1787 | 3.4927 | 0.24157 | 0.09269 | 3.827 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | oughtragh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 9 | 29.1393 | 27.0561 | 0 | 1.0685 | 1.0147 | 2.0832 | 0% | 3.667% | 3.482% | 7.149%
E | E,F & I | oughtragh | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 9.4 | 11.0056 | 7.0804 | 3.4927 | 0.24157 | 0.19096 | 3.9252 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | oughtragh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 9 | 29.1393 | 26.0465 | 0 | 0.24867 | 2.8441 | 3.0928 | 0% | 0.8534% | 9.76% | 10.61%
E | E,F & I | oughtragh | 2030 | 100% ECP | Pro-rata | IE wind priority | 9 | 29.1393 | 26.6662 | 0 | 1.0685 | 1.4046 | 2.4731 | 0% | 3.667% | 4.82% | 8.487%
E | E,F & I | oughtragh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind priority | 9 | 29.1393 | 27.2725 | 0 | 0.87281 | 0.99395 | 1.8668 | 0% | 2.995% | 3.411% | 6.406%
E | E,F & I | oughtragh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 5.8 | 6.7907 | 4.9023 | 1.5457 | 0.14435 | 0.19839 | 1.8884 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | oughtragh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind priority | 9 | 29.1393 | 26.5817 | 0 | 1.1319 | 1.4257 | 2.5576 | 0% | 3.885% | 4.893% | 8.777%
E | E,F & I | oughtragh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 5.8 | 6.7907 | 5.0655 | 1.329 | 0.12839 | 0.26775 | 1.7252 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | oughtragh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind priority | 9 | 29.1393 | 26.9432 | 0 | 1.1182 | 1.0779 | 2.1961 | 0% | 3.837% | 3.699% | 7.536%
E | E,F & I | oughtragh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 5.8 | 6.7907 | 5.1887 | 1.1416 | 0.12841 | 0.33195 | 1.602 | 16.81% | 1.891% | 4.888% | 23.59%
E | E,F & I | oughtragh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind priority | 9 | 29.1393 | 26.7662 | 0 | 1.0062 | 1.3669 | 2.3731 | 0% | 3.453% | 4.691% | 8.144%
E | E,F & I | oughtragh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 5.8 | 6.7907 | 5.5342 | 0.94093 | 0.12623 | 0.18937 | 1.2565 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | pollagh | 2030 | 100% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 128 | 149.8637 | 97.752 | 47.56 | 3.2895 | 1.2622 | 52.1117 | 31.74% | 2.195% | 0.8422% | 34.77%
E | E,F & I | oughtragh | 2035 | 66% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 7.6 | 8.8982 | 6.9915 | 1.4127 | 0.065308 | 0.42865 | 1.9066 | 15.88% | 0.7339% | 4.817% | 21.43%
E | E,F & I | oughtragh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE Solar not priority | 7.6 | 8.8982 | 6.191 | 1.9965 | 0.076586 | 0.63403 | 2.7071 | 22.44% | 0.8607% | 7.125% | 30.42%
E | E,F & I | pollagh | 2030 | 100% ECP | Pro-rata | IE Solar not priority | 128 | 149.8637 | 96.4138 | 47.56 | 3.2895 | 2.6003 | 53.4499 | 31.74% | 2.195% | 1.735% | 35.67%
E | E,F & I | pollagh | 2030 | 100% ECP | Pro-rata | IE wind not priority | 50 | 161.8849 | 108.1497 | 43.1885 | 2.7432 | 7.8035 | 53.7352 | 26.68% | 1.695% | 4.82% | 33.19%
E | E,F & I | pollagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE Solar not priority | 42.6666 | 49.9545 | 40.7111 | 6.9218 | 0.92858 | 1.3931 | 9.2435 | 13.86% | 1.859% | 2.789% | 18.5%
E | E,F & I | pollagh | 2030 | 33% ECP Maintenance Sensitivity | Pro-rata | IE wind not priority | 16.6667 | 53.9616 | 42.4802 | 8.7543 | 0.88636 | 1.8406 | 11.4813 | 16.22% | 1.643% | 3.411% | 21.28%
E | E,F & I | pollagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE Solar not priority | 42.6666 | 49.9545 | 36.0626 | 11.3706 | 1.0619 | 1.4594 | 13.8919 | 22.76% | 2.126% | 2.921% | 27.81%
E | E,F & I | pollagh | 2030 | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | Pro-rata | IE wind not priority | 16.6667 | 53.9616 | 33.6476 | 16.7429 | 0.93087 | 2.6402 | 20.314 | 31.03% | 1.725% | 4.893% | 37.65%
E | E,F & I | pollagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE Solar not priority | 42.6666 | 49.9545 | 37.2636 | 9.7768 | 0.9445 | 1.9696 | 12.6909 | 19.57% | 1.891% | 3.943% | 25.4%
E | E,F & I | oughtragh | 2035 | 66% ECP + 4.7 GW Offshore | Pro-rata | IE wind priority | 9 | 29.1393 | 26.7238 | 0 | 0.50441 | 1.9111 | 2.4155 | 0% | 1.731% | 6.559% | 8.29%
E | E,F & I | pollagh | 2030 | 33% ECP + 2.6 GW Offshore | Pro-rata | IE wind not priority | 16.6667 | 53.9616 | 35.3905 | 15.6379 | 0.93697 | 1.9961 | 18.571 | 28.98% | 1.736% | 3.699% | 34.42%
E | E,F & I | pollagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE wind not priority | 16.6667 | 53.9616 | 38.44 | 12.0602 | 0.93013 | 2.5313 | 15.5216 | 22.35% | 1.724% | 4.691% | 28.76%
E | E,F & I | pollagh | 2030 | 33% ECP | Pro-rata | IE Solar not priority | 42.6666 | 49.9545 | 39.3506 | 6.9218 | 0.92858 | 2.7535 | 10.6039 | 13.86% | 1.859% | 5.512% | 21.23%
E | E,F & I | pollagh | 2030 | 33% ECP | Pro-rata | IE wind not priority | 16.6667 | 53.9616 | 41.2182 | 8.7543 | 0.88636 | 3.1027 | 12.7434 | 16.22% | 1.643% | 5.75% | 23.62%
E | E,F & I | oughtragh | 2035 | 100% ECP | Pro-rata | IE Solar not priority | 9.4 | 11.0056 | 7.4689 | 2.4784 | 0.099326 | 0.95901 | 3.5368 | 22.52% | 0.9025% | 8.714% | 32.14%
E | E,F & I | oughtragh | 2035 | 100% ECP | Pro-rata | IE wind priority | 9 | 29.1393 | 24.5918 | 0 | 0.28477 | 4.2627 | 4.5475 | 0% | 0.9773% | 14.63% | 15.61%
E | E,F & I | pollagh | 2030 | 33% ECP + 1.3 GW Offshore | Pro-rata | IE Solar not priority | 42.6666 | 49.9545 | 38.1698 | 8.3983 | 0.94459 | 2.4419 | 11.7848 | 16.81% | 1.891% | 4.888% | 23.59%

## Helper (hidden)
A | IE wind not priority | 2030 | ardnagappary | pro-rata | Node | Subgroup
I | IE Solar not priority | 2035 | barnahely | grandfathering | Ardnagappary | A, B North | Total Dispatch Down (%) | Column Labels |  |  | Sum of Total Dispatch Down (GWh) | Column Labels
E | IE wind priority |  | kilpaddoge |  | Binbane | A, B North | Row Labels | 2030 | 2035 |  | Row Labels | 2030 | 2035
H2 |  |  | wexford |  | Cathaleen's Fall | A, B North | Initial | 17.64% |  |  | Initial | 6927.2953
F |  |  | knockacummer |  | Corderry | A, B North | 33% ECP | 20.18% |  |  | 33% ECP | 11175.8212
J |  |  | glenlara 220kv side |  | Croaghonagh | A, B North | 66% ECP |  | 23.52% |  | 66% ECP |  | 16817.8156
D |  |  | castleview |  | Garvagh | A, B North | 100% ECP | 33.37% | 28.82% |  | 100% ECP | 29166.608 | 25187.952
H1 |  |  | knockearagh |  | Golagh | A, B North | 33% ECP + 1.3 GW Offshore | 23.36% |  |  | 33% ECP + 1.3 GW Offshore | 14604.5856
G |  |  | knockanure |  | Gortawee | G North | 33% ECP + 2.6 GW Offshore | 26.82% |  |  | 33% ECP + 2.6 GW Offshore | 19033.2819
B |  |  | drombeg |  | Lenalea | A, B North | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | 29.35% |  |  | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | 20827.304
C |  |  | cow cross |  | Lenalea loop-in Letterkenny Tievebrack | A, B North | 33% ECP Maintenance Sensitivity | 18.17% |  |  | 33% ECP Maintenance Sensitivity | 10067.0293
K |  |  | garrow |  | Letterkenny | A, B North | 66% ECP Maintenance Sensitivity |  | 21.1% |  | 66% ECP Maintenance Sensitivity |  | 15086.5729
|  |  | dromada |  | Meentycat | A, B North | 100% ECP Maintenance Sensitivity | 32.2% |  |  | 100% ECP Maintenance Sensitivity | 28142.7813
|  |  | kilbarry |  | Mulreavy | A, B North | 66% ECP + 4.7 GW Offshore |  | 28.49% |  | 66% ECP + 4.7 GW Offshore |  | 27870.4245
|  |  | coolroe |  | Sorne Hill | A, B North
|  |  | glanlee |  | Tievebrack | A, B North
|  |  | glenlara |  | Trillick | A, B North | Row Labels | Surplus (%) | Curtailment (%) | Constrain (%) | Row Labels | Sum of Surplus (GWh) | Sum of Curtailment (GWh) | Sum of Constraint (GWh)
|  |  | lodgewood |  | Arigna | A, B North | 2030 |  |  |  | 2030
|  |  | tralee |  | Bellacorick | A, B North | Initial | 5.417% | 2.199% | 10.02% | Initial | 2127.603 | 863.6622 | 3936.03
|  |  | reamore |  | Castlebar | A, B North | 33% ECP | 9.953% | 2.26% | 7.963% | 33% ECP | 5513.1536 | 1252.0708 | 4410.5969
|  |  | rosspile |  | Cunghill | A, B North | 100% ECP | 22.78% | 2.36% | 8.235% | 100% ECP | 19906.9515 | 2062.8376 | 7196.819
|  |  | trien |  | Dalton | A, B North | 33% ECP + 1.3 GW Offshore | 13.98% | 2.355% | 7.028% | 33% ECP + 1.3 GW Offshore | 8738.9189 | 1472.2492 | 4393.4175
|  |  | kilvinoge |  | Firlough | A, B North | 33% ECP + 2.6 GW Offshore | 18.73% | 2.392% | 5.701% | 33% ECP + 2.6 GW Offshore | 13290 | 1697.5742 | 4045.7077
|  |  | ballylickey |  | Glenree | A, B North | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | 20.44% | 2.464% | 6.443% | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | 14506.7594 | 1748.3752 | 4572.1693
|  |  | kilkenny |  | Moy | A, B North | 33% ECP Maintenance Sensitivity | 9.953% | 2.26% | 5.961% | 33% ECP Maintenance Sensitivity | 5513.1536 | 1252.0708 | 3301.805
|  |  | mallow |  | Sligo | A, B North | 100% ECP Maintenance Sensitivity | 22.78% | 2.36% | 7.063% | 100% ECP Maintenance Sensitivity | 19906.9515 | 2062.8376 | 6172.9922
|  |  | waterford |  | Srahnakilly | A, B North | 2035 |  |  |  | 2035
|  |  | oughtragh |  | Tawnaghmore | A, B North | 66% ECP | 11.64% | 0.6055% | 11.28% | 66% ECP | 8322.732 | 432.9374 | 8062.1462
|  |  | pollagh |  | Tonroe | A, B North | 100% ECP | 15.58% | 0.695% | 12.55% | 100% ECP | 13615.5955 | 607.4284 | 10964.9281
|  |  | tullabeg |  | Knockranny | B South | 66% ECP Maintenance Sensitivity | 11.64% | 0.6055% | 8.854% | 66% ECP Maintenance Sensitivity | 8322.732 | 432.9374 | 6330.9034
|  |  | athea |  | Salthill | B South | 66% ECP + 4.7 GW Offshore | 21.54% | 0.8952% | 6.054% | 66% ECP + 4.7 GW Offshore | 21071.8002 | 875.7946 | 5922.8297
|  |  | crakenstown |  | Screeb | B South
|  |  | ballyvouskil 220 |  | Uggool | B South
|  |  | dunstown |  | Cashla | C
|  |  | rathkeale |  | Cloon | C
|  |  | boggeragh |  | Shantallow | C
|  |  | arodstown |  | Shantallow into Cashla Somerset T | C
|  |  | carrickmines 220kv |  | Belcamp | J City, G South
|  |  | belcamp 220kv |  | Athlone | C
|  |  | glasmore |  | Carrick on Shannon | C
|  |  | ballinknockane |  | Dallow | C
|  |  | gallanstown |  | Derrycarney | C
|  |  | limerick |  | Derrycarney loop into Portlaoise to Dallow T | C
|  |  | tullabrack |  | Belcamp 220 | J City, G South
|  |  | grange |  | Lanesboro | C
|  |  | prospect |  | Lumcloon | C
|  |  | finglas |  | Richmond | C
|  |  | moneypoint |  | Shannonbridge | C
|  |  | timoney |  | Sliabh Bawn | C
|  |  | coomagearlahy |  | Somerset | C
|  |  | lysaghtstown |  | Ardnacrusha | D and E North
|  |  | cloghboola |  | Booltiagh | D and E North
|  |  | clashavoon |  | Derrybrien | D and E North
|  |  | midleton |  | Drumline | D and E North
|  |  | knockraha |  | Ennis | D and E North
|  |  | cordal |  | Slievecallan | D and E North
|  |  | knockraha 220kv |  | Tullabrack | D and E North
|  |  | coomataggart |  | Aghada | E,F & I
|  |  | charleville |  | Ahane | H1
|  |  | trabeg |  | Athea | E,F & I
|  |  | rathcoursey |  | Aughinish | D and E North
|  |  | raffeen |  | Ballinknockane | D and E North
|  |  | clahane |  | Ballinknockane loop into Aughinish Kilpaddoge | D and E North
|  |  | cahir |  | Ballydine | H1
|  |  | ballywater |  | Ballylickey | E,F & I
|  |  | cauteen |  | Ballyvouskil 220 | E,F & I
|  |  | ballyragget |  | Bandon | E,F & I
|  |  | barrymore |  | Barnahely | E,F & I
|  |  | borrisbeg |  | Barrymore | H1
|  |  | curraghduff |  | Boggeragh | E,F & I
|  |  | doon |  | Cahir | H1
|  |  | banoge |  | Carrigdangan tail from Dunmanway | E,F & I
|  |  | carlow |  | Cauteen | H1
|  |  | gorman |  | Charleville | E,F & I
|  |  | ahane |  | Clahane | E,F & I
|  |  | ballydine |  | Cloghboola | E,F & I
|  |  | drybridge |  | Coolroe | E,F & I
|  |  | garballagh |  | Coomagearlahy | E,F & I
|  |  | nenagh |  | Coomataggart | E,F & I
|  |  | arklow |  | Coomnaclohy tail from Ballyvouskil | E,F & I
|  |  | springmount |  | Cordal | E,F & I
|  |  | thurles |  | Cow Cross | E,F & I
|  |  | lisheen |  | Doon | H1
|  |  | tipperary |  | Dromada | E,F & I
|  |  | kill hill |  | Drombeg | E,F & I
|  |  | ballybeg |  | Drombeg loop in Kilpaddoge Tralee 2 | E,F & I
|  |  | ikerrin |  | Dunmanway | E,F & I
|  |  | killonan |  | Garrow | E,F & I
|  |  | arklow 220kv |  | Glanlee | E,F & I
|  |  | great island |  | Glenlara | E,F & I
|  |  | balruntagh |  | Glenlara 220 | E,F & I
|  |  | dundalk |  | Glenlara 220kv side | E,F & I
|  |  | garrintaggart |  | Glenlara_wind | E,F & I
|  |  | macroom |  | Ikerrin | H1
|  |  | great island 220kv |  | Kilbarry | E,F & I
|  |  | effernoge |  | Kill Hill | H1
|  |  | lisdrum |  | Killonan | H1
|  |  | lislea |  | Kilpaddoge | E,F & I
|  |  | kellis |  | Knockacummer | E,F & I
|  |  | bandon |  | Knockearagh | E,F & I
|  |  | kellymount |  | Dundalk | G North
|  |  | dunmanway |  | Lisdrum | G North
|  |  | castledockrell |  | Lislea | G North
|  |  | shankill |  | Louth | G North
|  |  | ratrussan |  | Meath Hill | G North
|  |  | crane |  | Navan | G North
|  |  | ricetown |  | Ratrussan | G North
|  |  | baltrasna |  | Shankill | G North
|  |  | deenes |  | Baltrasna | J City, G South
|  |  | meath hill |  | Drybridge | J City, G South
|  |  | crory |  | Garballagh | J City, G South
|  |  | louth |  | Gaskinstown | J City, G South
|  |  | oriel 220kv |  | Gaskinstown loop-in Drybridge Hawkinstown | J City, G South
|  |  | navan |  | Gillinstown loop-in Gorman Platin | J City, G South
|  |  | kilteel |  | Gillinstown/Garballagh | J City, G South
|  |  | glenree |  | Gorman | J City, G South
|  |  | monread |  | Hawkinstown | J City, G South
|  |  | moy |  | Hawkinstown loop into Baltrasna Drybridge | J City, G South
|  |  | maynooth |  | Oriel 220 | G North
|  |  | firlough |  | Oriel 220kV | G North
|  |  | mount lucas |  | Oriel 220kV | G North
|  |  | kinnegad |  | Knockraha | E,F & I
|  |  | sligo |  | Knockraha 220 | E,F & I
|  |  | mulgeeth |  | Knockraha 220kV | E,F & I
|  |  | castlebar |  | Limerick | D and E North
|  |  | cunghill |  | Lisheen | H1
|  |  | newbridge |  | Lysaghtstown | E,F & I
|  |  | dalton |  | Macroom | E,F & I
|  |  | dunfirth |  | Mallow | E,F & I
|  |  | cashla |  | Midleton | E,F & I
|  |  | cloon |  | Moneypoint | D and E North
|  |  | derryiron |  | Moneypoint 220 | D and E North
|  |  | uggool |  | Moneypoint 220kV | D and E North
|  |  | athlone |  | Mothel | H1
|  |  | cushaling |  | Mothel loop into Ballydine Cullenagh | H1
|  |  | shantallow |  | Nenagh | H1
|  |  | tonroe |  | Oughtragh | E,F & I
|  |  | galway |  | Arklow | H2 & K
|  |  | harristown |  | Arklow 220 | H2 & K
|  |  | tawnaghmore |  | Ballybeg | H2 & K
|  |  | knockranny |  | Ballyragget | H2 & K
|  |  | fosterstown |  | Ballywater | H2 & K
|  |  | salthill |  | Banoge | H2 & K
|  |  | dungarvan |  | Carlow | H2 & K
|  |  | croaghonagh |  | Castledockrell | H2 & K
|  |  | cullenagh |  | Crane | H2 & K
|  |  | garvagh |  | Crory | H2 & K
|  |  | corderry |  | Great Island | H2 & K
|  |  | butlerstown |  | Great Island 220 | H2 & K
|  |  | golagh |  | Kellis | H2 & K
|  |  | timahoe |  | Kilkenny | H2 & K
|  |  | arigna |  | Lodgewood | H2 & K
|  |  | woodhouse |  | Rosspile | H2 & K
|  |  | binbane |  | Rosspile loop in GI Wex | H2 & K
|  |  | cathaleen's fall |  | Tullabeg | H2 & K
|  |  | rathnaskilloge |  | Tullabeg loop into Banoge Crane | H2 & K
|  |  | gortawee |  | Waterford | H2 & K
|  |  | philipstown |  | Wexford | H2 & K
|  |  | tievebrack |  | Arklow 220kV | H2 & K
|  |  | portlaoise |  | Arklow 220kV | H2 & K
|  |  | trillick |  | Great Island 220kV | H2 & K
|  |  | bellacorick |  | Raffeen | E,F & I
|  |  | letterkenny |  | Rathkeale | D and E North
|  |  | thornsberry |  | Reamore | E,F & I
|  |  | meentycat |  | Thurles | H1
|  |  | lenalea |  | Timoney | H1
|  |  | sorne hill |  | Tipperary | H1
|  |  | mulreavy |  | Trabeg | E,F & I
|  |  | stonestown |  | Tralee | E,F & I
|  |  | ardnacrusha |  | Trien | E,F & I
|  |  | somerset |  | Trien 220 | E,F & I
|  |  | poolbeg south 220kv |  | Trien 220kv side | E,F & I
|  |  | coolnabacky |  | Trien_wind | E,F & I
|  |  | coolshamroge |  | Blackrock | J City, G South
|  |  | lanesboro |  | Carrickmines 220 | J City, G South
|  |  | bracklone |  | Finglas | J City, G South
|  |  | derrycarney |  | Griffinrath | J City, G South
|  |  | stephenstown |  | Inchicore | J City, G South
|  |  | clonfad |  | Irishtown | J City, G South
|  |  | booltiagh |  | Poolbeg | J City, G South
|  |  | sliabh bawn |  | Poolbeg 220 north | J City, G South
|  |  | richardstown |  | Poolbeg north 220 | J City, G South
|  |  | athy |  | Poolbeg south 220 | J City, G South
|  |  | derrybrien |  | Belcamp 220kV | J City, G South
|  |  | poolbeg north 220kv |  | Belcamp 220kV | J City, G South
|  |  | dallow |  | Poolbeg north 220kV | J City, G South
|  |  | craddanstown |  | Poolbeg south 220kV | J City, G South
|  |  | griffinrath |  | Gallanstown | J City, G South
|  |  | bracklyn |  | Gallanstown into Corduff Platin | J City, G South
|  |  | shannonbridge |  | Glasmore | J City, G South
|  |  | richmond |  | Poolbeg south 220kV | J City, G South
|  |  | mullingar |  | Carrickmines 220kV | J City, G South
|  |  | carrick on shannon |  | Carrickmines 220kV | J City, G South
|  |  | curraghdoo |  | Maynooth | J Country
|  |  | ennis |  | Mullingar | J Country
|  |  | blundelstown |  | Shanonagh | J Country
|  |  | shanonagh |  | Athy | J Country
|  |  | slievecallan |  | Blake T | J Country
|  |  | cregg |  | Blundelstown | J Country
|  |  | drumline |  | Clonfad | J Country
[5 empty] | Clonfad loop-in Kinnegad - Mullingar | J Country
[5 empty] | Coolnabacky | J Country
[5 empty] | Cushaling | J Country
[5 empty] | Derryiron | J Country
[5 empty] | Dunfirth | J Country
[5 empty] | Harristown | J Country
[5 empty] | Stephenstown | J City, G South
[5 empty] | Harristown loop into Kinnegad Dunfirth T | J Country
[5 empty] | Kilteel | J Country
[5 empty] | Monread | J Country
[5 empty] | Mount Lucas | J Country
[5 empty] | Mulgeeth | J Country
[5 empty] | Newbridge | J Country
[5 empty] | Philipstown | J Country
[5 empty] | Portlaoise | J Country
[5 empty] | Thornsberry | J Country
[5 empty] | Timahoe North | J Country
[5 empty] | Treascon | J Country
[5 empty] | Treascon into Bracklone Portlaoise | J Country
[5 empty] | Butlerstown | H2 & K
[5 empty] | Dungarvan | H2 & K
[5 empty] | Knocknamona tail from Woodhouse | H2 & K
[5 empty] | Rathnaskilloge | H2 & K
[5 empty] | Rathnaskilloge loop-in Cullenagh Dungarvan | H2 & K
[5 empty] | Woodhouse | H2 & K
[5 empty] | Aghyoule | NI group 3
[5 empty] | Agivey | NI group 1
[5 empty] | Antrim | NI group 4
[5 empty] | Ballymena | NI group 4
[5 empty] | Ballynahinch | NI group 4
[5 empty] | Banbridge | NI group 4
[5 empty] | Belfast North | NI group 4
[5 empty] | Brockaghboy | NI group 1
[5 empty] | Cam | NI group 1
[5 empty] | Carnmoney | NI group 4
[5 empty] | Castlereagh | NI group 4
[5 empty] | Coleraine | NI group 1
[5 empty] | Coolkeeragh | NI group 1
[5 empty] | Creagh | NI group 4
[5 empty] | Cregagh | NI group 4
[5 empty] | Curraghamulkin | NI group 2
[5 empty] | Drumnakelly | NI group 4
[5 empty] | Dungannon | NI group 2
[5 empty] | East Antrim | NI group 4
[5 empty] | Eden | NI group 4
[5 empty] | Enniskillen | NI group 3
[5 empty] | Feeney | NI group 1
[5 empty] | Garvagh NI | NI group 1
[5 empty] | Glengormley | NI group 4
[5 empty] | Gort | NI group 2
[5 empty] | Kells | NI group 4
[5 empty] | Kells Cluster | NI group 4
[5 empty] | Killymallaght | NI group 1
[5 empty] | Kilroot | NI group 4
[5 empty] | Larne | NI group 4
[5 empty] | Limavady | NI group 1
[5 empty] | Lisaghmore | NI group 1
[5 empty] | Lisburn | NI group 4
[5 empty] | Loguestown | NI group 1
[5 empty] | Magherafelt | NI group 4
[5 empty] | Magherakeel | NI group 2
[5 empty] | Mid East Antrim | NI group 4
[5 empty] | Newry | NI group 4
[5 empty] | Newtownards | NI group 4
[5 empty] | Omagh | NI group 2
[5 empty] | Rasharkin | NI group 1
[5 empty] | Rathgael | NI group 4
[5 empty] | Rosebank | NI group 4
[5 empty] | Strabane | NI group 1
[5 empty] | Tamnamore | NI group 4
[5 empty] | Tandragee | NI group 4
[5 empty] | Tremoge | NI group 2
[5 empty] | Waringstown | NI group 4
[5 empty] | Drumquin | NI group 2
[5 empty] | Glengormley | NI group 4
[5 empty] | Larne | NI group 4
[5 empty] | Ballylumford | NI group 4
[5 empty] | Kinnegad | J Country
[5 empty] | Fosterstown | J Country
[5 empty] | Blake | J Country
[5 empty] | Bracklone | J Country
[5 empty] | Paddock | J City, G South
[5 empty] | Bracklyn | J Country
[5 empty] | Kilvinoge | H2 & K
[5 empty] | Balruntagh | G North
[5 empty] | Rath | H1
[5 empty] | Arodstown | J City, G South
[5 empty] | Ballyvallagh | NI group 4
[5 empty] | Belfast North Main | NI group 4
[5 empty] | Castleview | E,F & I
[5 empty] | Crakenstown | J City, G South
[5 empty] | Creagh | NI group 4
[5 empty] | Donegall North | NI group 1
[5 empty] | Donegall South | NI group 1
[5 empty] | Feamore | C
[5 empty] | Finaghy | NI group 1
[5 empty] | Flagford | C
[5 empty] | Garrintaggart | H2 & K
[5 empty] | Grange | J City, G South
[5 empty] | Hannahstown | NI group 4
[5 empty] | Knock | NI group 4
[5 empty] | Knockanure | E,F & I
[5 empty] | Pollagh | E,F & I
[5 empty] | Rathgael | NI group 4
[5 empty] | Screebe | B South
[5 empty] | Springtown | NI group 1
[5 empty] | Srananagh | A, B North
[5 empty] | Stonestown | C
[5 empty] | Stratford | H2 & K
[5 empty] | Tarbert | E,F & I
[5 empty] | Timahoe | J Country
[5 empty] | effernoge | H2 & K
[5 empty] | kellymount | H2 & K
[5 empty] | ricetown | G North
[5 empty] | borrisbeg | H1
[5 empty] | clashavoon | E,F & I
[5 empty] | coolshamroge | D and E North
[5 empty] | craddanstown | J Country
[5 empty] | cregg | C
[5 empty] | curraghdoo | J Country
[5 empty] | curraghduff | H1
[5 empty] | deenes | J City, G South
[5 empty] | dunstown | J City, G South
[5 empty] | rathcoursey | E,F & I
[5 empty] | springmount | H1
[5 empty] | galway | B South

## Figures and Tables
The contents of the below tables and figures will automatically update to reflect the filters applied by the slicers at the top of this worksheet. Appropriate filter selection can reproduce every figure and table previously published as part of the Area Reports. Important Note: Grandfathering and Pro-rata should not be selected simultaneously.
| Column Labels | [10 empty] | Nodes
Row Labels | Initial | 33% ECP | 66% ECP | 100% ECP | 33% ECP + 1.3 GW Offshore | 33% ECP + 2.6 GW Offshore | 33% ECP + 2.6 GW Offshore andReduced BESS Sensitivity | 66% ECP + 4.7 GW Offshore | 33% ECP Maintenance Sensitivity | 66% ECP Maintenance Sensitivity | 100% ECP Maintenance Sensitivity | Row Labels
Sum of Installed (MW) | [11 empty] | ahane
2030 | 15431.35 | 24816.2933 |  | 43416.208 | 26516.2933 | 28566.2933 | 28566.2933 |  | 24816.2933 |  | 43416.208 | ardnacrusha
2035 |  |  | 34201.2366 | 43416.208 |  |  |  | 40575.2366 |  | 34201.2366 |  | ardnagappary
Sum of Available Energy (GWh) | [11 empty] | arigna
2030 | 39277.7039 | 55389.4545 |  | 87395.1852 | 62511.6368 | 70965.2715 | 70965.2715 |  | 55389.4545 |  | 87395.1852 | arklow
2035 |  |  | 71501.2051 | 87395.1852 |  |  |  | 97834.4806 |  | 71501.2051 |  | arklow 220kv
Sum of Generation (GWh) | [11 empty] | arodstown
2030 | 32350.4086 | 44213.6333 |  | 58228.5772 | 47907.0512 | 51931.9896 | 50137.9675 |  | 45322.4252 |  | 59252.404 | athea
2035 |  |  | 54683.3895 | 62207.2332 |  |  |  | 69964.0561 |  | 56414.6322 |  | athlone
Sum of Surplus (GWh) | [11 empty] | athy
2030 | 2127.603 | 5513.1536 |  | 19906.9515 | 8738.9189 | 13290 | 14506.7594 |  | 5513.1536 |  | 19906.9515 | ballinknockane
2035 |  |  | 8322.732 | 13615.5955 |  |  |  | 21071.8002 |  | 8322.732 |  | ballybeg
Sum of Curtailment (GWh) | [11 empty] | ballydine
2030 | 863.6622 | 1252.0708 |  | 2062.8376 | 1472.2492 | 1697.5742 | 1748.3752 |  | 1252.0708 |  | 2062.8376 | ballylickey
2035 |  |  | 432.9374 | 607.4284 |  |  |  | 875.7946 |  | 432.9374 |  | ballyragget
Sum of Constraint (GWh) | [11 empty] | ballyvouskil 220
2030 | 3936.03 | 4410.5969 |  | 7196.819 | 4393.4175 | 4045.7077 | 4572.1693 |  | 3301.805 |  | 6172.9922 | ballywater
2035 |  |  | 8062.1462 | 10964.9281 |  |  |  | 5922.8297 |  | 6330.9034 |  | balruntagh
Sum of Total Dispatch Down (GWh) | [11 empty] | baltrasna
2030 | 6927.2953 | 11175.8212 |  | 29166.608 | 14604.5856 | 19033.2819 | 20827.304 |  | 10067.0293 |  | 28142.7813 | bandon
2035 |  |  | 16817.8156 | 25187.952 |  |  |  | 27870.4245 |  | 15086.5729 |  | banoge
Surplus (%) | [11 empty] | barnahely
2030 | 5.417% | 9.953% |  | 22.78% | 13.98% | 18.73% | 20.44% |  | 9.953% |  | 22.78% | barrymore
2035 |  |  | 11.64% | 15.58% |  |  |  | 21.54% |  | 11.64% |  | belcamp 220kv
Curtailment (%) | [11 empty] | bellacorick
2030 | 2.199% | 2.26% |  | 2.36% | 2.355% | 2.392% | 2.464% |  | 2.26% |  | 2.36% | binbane
2035 |  |  | 0.6055% | 0.695% |  |  |  | 0.8952% |  | 0.6055% |  | blundelstown
Constrain (%) | [11 empty] | boggeragh
2030 | 10.02% | 7.963% |  | 8.235% | 7.028% | 5.701% | 6.443% |  | 5.961% |  | 7.063% | booltiagh
2035 |  |  | 11.28% | 12.55% |  |  |  | 6.054% |  | 8.854% |  | borrisbeg
Total Dispatch Down (%) | [11 empty] | bracklone
2030 | 17.64% | 20.18% |  | 33.37% | 23.36% | 26.82% | 29.35% |  | 18.17% |  | 32.2% | bracklyn
2035 |  |  | 23.52% | 28.82% |  |  |  | 28.49% |  | 21.1% |  | butlerstown
cahir
carlow
carrick on shannon
carrickmines 220kv
cashla
castlebar
castledockrell
castleview
cathaleen's fall
cauteen
charleville
clahane
clashavoon
cloghboola
clonfad
cloon
coolnabacky
coolroe
coolshamroge
coomagearlahy
coomataggart
cordal
corderry
cow cross
craddanstown
crakenstown
crane
cregg
croaghonagh
crory
cullenagh
cunghill
curraghdoo
curraghduff
cushaling
dallow
dalton
deenes
derrybrien
derrycarney
derryiron
doon
dromada
drombeg
drumline
drybridge
dundalk
dunfirth
dungarvan
dunmanway
dunstown
effernoge
ennis
finglas
firlough
fosterstown
gallanstown
galway
garballagh
garrintaggart
garrow
garvagh
glanlee
glasmore
glenlara
glenlara 220kv side
glenree
golagh
gorman
gortawee
grange
great island
great island 220kv
griffinrath
harristown
ikerrin
kellis
kellymount
kilbarry
kilkenny
kill hill
killonan
kilpaddoge
kilteel
kilvinoge
kinnegad
knockacummer
knockanure
knockearagh
knockraha
knockraha 220kv
knockranny
lanesboro
lenalea
letterkenny
limerick
lisdrum
lisheen
lislea
lodgewood
louth
lysaghtstown
macroom
mallow
maynooth
meath hill
meentycat
midleton
moneypoint
monread
mount lucas
moy
mulgeeth
mullingar
mulreavy
navan
nenagh
newbridge
oriel 220kv
oughtragh
philipstown
pollagh
poolbeg north 220kv
poolbeg south 220kv
portlaoise
prospect
raffeen
rathcoursey
rathkeale
rathnaskilloge
ratrussan
reamore
ricetown
richardstown
richmond
rosspile
salthill
shankill
shannonbridge
shanonagh
shantallow
sliabh bawn
slievecallan
sligo
somerset
sorne hill
springmount
stephenstown
stonestown
tawnaghmore
thornsberry
thurles
tievebrack
timahoe
timoney
tipperary
tonroe
trabeg
tralee
trien
trillick
tullabeg
tullabrack
uggool
waterford
wexford
woodhouse
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.

## Contingencies and Lines
For different study scenarios, there were several transmission boundaries that limited the power flow. Some of the main overload and contingency pairs binding for more than 200 hours for all the study scenarios can be seen below.
Line | Contingency | Hours Range
|  | 2030 (Initial) | 2030 (33% ECP) | 2030 (33% ECP + 1.3GW Offshore) | 2030 (33% ECP + 2.6GW Offshore) | 2030 (33% ECP + 2.6GW offshore reduced BESS) | 2030 (100% ECP) | 2035 (66% ECP) | 2035 (66% ECP+ 4.7GW Offshore) | 2035 (100% ECP)
Interface (IE to NI NTC ) | Base | 3250-3500 | 3250-3500 | 3500-3750 | 3750-4000 | 3250-3500 | 3750-4000 | 500-750 | 1000-1250 | 750-1000
Line (Arklow - Oaklands_110_1 ) | Loss of Arklow to Lodgewood 220 | 0 | <250 | 0 | 0 | 0 | <250 | <250 | <250 | <250
Line (Arklow T2101 ) | Loss of Arklow 220-110 2 | <250 | <250 | <250 | <250 | <250 | 500-750 | 250-500 | 250-500 | 750-1000
Line (Arklow T2101 ) | Loss of Arklow Banoge 110 1 | <250 | <250 | <250 | <250 | 0 | <250 | 250-500 | 250-500 | 250-500
Line (Arklow T2101 ) | Loss of Arklow to Lodgewood 220 | <250 | <250 | <250 | 250-500 | <250 | <250 | <250 | 250-500 | <250
Line (Arklow T2101 ) | Loss of Banoge to Tullabeg 110 | <250 | <250 | <250 | <250 | <250 | <250 | 500-750 | 250-500 | 750-1000
Line (Arklow T2101 ) | Loss of Crane - Tullabeg_110_1 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 500-750
Line (Arklow T2101 ) | Loss of Glenart Lodgewood 220 | <250 | <250 | <250 | 250-500 | <250 | <250 | <250 | <250 | <250
Line (Arklow T2101 ) | Loss of Lodgewood 220-110 1 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500
Line (Arodstown - Maynooth_220_1 ) | Loss of Crakenstown Woodland 220 1 | <250 | 500-750 | <250 | 500-750 | 250-500 | 1500-1750 | 0 | 0 | 0
Line (Athlone - Lanesboro_110_1 ) | Loss of Derrycarney Portlaoise 110 | <250 | <250 | <250 | <250 | <250 | <250 | 0 | 0 | 0
Line (Athy - Coolnabacky_110_1 ) | Loss of Dunstown-Kellis 220 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 500-750
Line (Athy - Coolnabacky_110_1 ) | Loss of coolnabacky dunstown 400 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250
Line (Ballynahulla - Glenlara_wind_110_1 ) | Loss of Ballynahulla - Ballyvouskil_220_1 | <250 | <250 | <250 | <250 | 0 | <250 | 250-500 | <250 | 250-500
Line (Ballynahulla - Glenlara_wind_110_1 ) | Loss of Charleville - Killonan_110_1 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250
Line (Ballynahulla - Glenlara_wind_110_1 ) | Loss of Charleville - Mallow_110_1 | 0 | <250 | <250 | <250 | <250 | 250-500 | <250 | <250 | 250-500
Line (Ballynahulla - Glenlara_wind_110_1 ) | Loss of Kilbarry - Mallow_110_1 | 0 | <250 | <250 | 0 | 0 | 250-500 | <250 | <250 | 250-500
Line (Ballyragget - Coolnabacky_110_1 ) | Loss of Arklow to Lodgewood 220 | 0 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250
Line (Ballyragget - Coolnabacky_110_1 ) | Loss of Coolnabacky - Garrintaggart_110_1 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250 | <250
Line (Ballyragget - Coolnabacky_110_1 ) | Loss of Dunstown-Kellis 220 | 0 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | <250 | 500-750
Line (Ballyragget - Coolnabacky_110_1 ) | Loss of Kellis - Kellymount_110_1 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250 | 250-500
Line (Ballyvouskil - Coomataggart_110_1 ) | Base | 0 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | <250 | 500-750
Line (Banoge - Tullabeg_110_1 ) | Loss of Arklow to Lodgewood 220 | <250 | <250 | <250 | <250 | 0 | <250 | <250 | 250-500 | <250
Line (Barnahely - Raffeen_110_1 ) | Base | <250 | <250 | <250 | <250 | <250 | <250 | 500-750 | 500-750 | 500-750
Line (Baroda - Monread_110_1 ) | Loss of Coolnabacky Portlaoise 110 | <250 | <250 | <250 | <250 | <250 | 250-500 | 0 | 0 | 0
Line (Baroda - Monread_110_1 ) | Loss of Newbridge - Blake-T_110_1 | <250 | 250-500 | 250-500 | <250 | <250 | 500-750 | 0 | 0 | 0
Line (Baroda - Monread_110_1 ) | Loss of coolnabacky dunstown 400 | <250 | <250 | <250 | <250 | <250 | 250-500 | 0 | 0 | 0
Line (Belcamp - Finglas_220_1 ) | Loss of Belcamp - Eastpoint_220_1 | 0 | 0 | 0 | 0 | 0 | 0 | 250-500 | <250 | 250-500
Line (Belcamp - Finglas_220_1 ) | Loss of Eastpoint Shellybanks 220 | 0 | 0 | 0 | <250 | <250 | 0 | <250 | <250 | <250
Line (Belcamp - Finglas_220_1 ) | Loss of North Wall - Poolbeg 220 | 0 | 0 | 0 | <250 | 0 | 0 | 0 | <250 | 0
Line (Bellacorick - Moy_110_1 ) | Loss of Bellacorick-Castlebar 110 | 250-500 | 750-1000 | 750-1000 | 500-750 | 500-750 | 1500-1750 | 1500-1750 | 1250-1500 | 2000-2250
Line (Blundelstown - Corduff_110_1 ) | Loss of Clonfad to Kinnegad 110 | <250 | 500-750 | 250-500 | 250-500 | <250 | 2000-2250 | 1750-2000 | 1250-1500 | 2500-3000
Line (Blundelstown - Corduff_110_1 ) | Loss of Rinawade Dunfirth T 110 | <250 | 250-500 | <250 | <250 | <250 | 250-500 | 500-750 | 500-750 | 500-750
Line (Blundelstown - Curraghdoo_110_1 ) | Loss of Clonfad to Kinnegad 110 | 0 | <250 | 0 | 0 | 0 | 500-750 | 250-500 | <250 | 750-1000
Line (Booltiagh - Ennis_110_1 ) | Loss of Moneypoint 220-110 1 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | <250 | 500-750
Line (Cahir - Barrymore-T_110_1 ) | Loss of Cahir-Rathkeevin 110 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500
Line (Cahir - Barrymore-T_110_1 ) | Loss of Cahir Doon 110 | <250 | 250-500 | 250-500 | 250-500 | 250-500 | 500-750 | 250-500 | 250-500 | 500-750
Line (Cahir - Barrymore-T_110_1 ) | Loss of Cauteen Killonan 110 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500
Line (Cahir - Barrymore-T_110_1 ) | Loss of Cullenagh to Ballydine 110 | 0 | <250 | <250 | <250 | <250 | 500-750 | <250 | <250 | 500-750
Line (Cahir - Barrymore-T_110_1 ) | Loss of Cullenagh-Knockraha 220 | 250-500 | 500-750 | 500-750 | 750-1000 | 500-750 | 1000-1250 | 500-750 | 750-1000 | 750-1000
Line (Cahir - Barrymore-T_110_1 ) | Loss of Killonan Knockraha 220 | <250 | <250 | <250 | <250 | 250-500 | 500-750 | 250-500 | 250-500 | 250-500
Line (Cahir - Barrymore-T_110_1 ) | Loss of gen Dublin Bay | 0 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | 250-500
Line (Cahir - Barrymore-T_110_1 ) | Loss of gen GI4 | 0 | 0 | 0 | 0 | 0 | 0 | 500-750 | 250-500 | 750-1000
Line (Cahir - Rathkeevin_110_1 ) | Loss of Cullenagh-Knockraha 220 | 250-500 | 250-500 | 250-500 | <250 | <250 | <250 | <250 | <250 | <250
Line (Carlow - Kellis_110_2 ) | Loss of Carlow Kellis 110 1 | 250-500 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 500-750
Line (Carlow - Kellis_110_2 ) | Loss of Dunstown-Kellis 220 | 250-500 | 250-500 | <250 | <250 | <250 | 250-500 | <250 | <250 | <250
Line (Carrick on Shannon - Arigna-T_110_1 ) | Loss of CF-Corraclassy 110 | 500-750 | 750-1000 | 500-750 | 500-750 | 250-500 | 500-750 | 1000-1250 | 750-1000 | 750-1000
Line (Carrick on Shannon - Arigna-T_110_1 ) | Corraclassy - Gortawee_110_1 | 250-500 | 500-750 | 500-750 | 250-500 | 250-500 | 500-750 | 750-1000 | 750-1000 | 1000-1250
Line (Carrick on Shannon - Arigna-T_110_1 ) | Loss of Flagford Louth 220 | 0 | 0 | 0 | 0 | 0 | 0 | 500-750 | 500-750 | 750-1000
Line (Carrick on Shannon - Arigna-T_110_1 ) | Loss of Flagford Tonroe 110 | 0 | 0 | 0 | 0 | 0 | 0 | 250-500 | 250-500 | 500-750
Line (Carrick on Shannon - Arigna-T_110_1 ) | Loss of Flagford-Srananagh 220 circuit 1 | <250 | 1500-1750 | 1500-1750 | 1250-1500 | 750-1000 | 2500-3000 | <250 | <250 | <250
Line (Carrick on Shannon - Arigna-T_110_1 ) | Flagford - Srananagh_220_2 | 0 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250
Line (Carrick on Shannon - Arigna-T_110_1 ) | Loss of Moy - Tonroe_110_1 cable | 0 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250
Line (Carrick on Shannon - Flagford_110_2 ) | Loss of Carrick on Shannon - Flagford_110_1 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500
Line (Carrickmines - Irishtown_220_1 ) | Loss of Dunstown Woodland 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250-500 | 0
Line (Carrickmines - Poolbeg_220_1 ) | Loss of Carrickmines Irishtown 220 | 0 | 0 | <250 | 0 | <250 | 0 | 0 | 0 | 0
Line (Carrickmines - Poolbeg_220_1 ) | Loss of Dunstown Woodland 400 | <250 | 250-500 | <250 | <250 | <250 | 250-500 | 0 | 0 | 0
Line (Carrickmines - Poolbeg_220_1 ) | Loss of gen Dublin Bay | <250 | <250 | <250 | <250 | <250 | <250 | 0 | 0 | 0
Line (Cashla - Shantallow_110_1 ) | Loss of Derrycarney Portlaoise 110 | 0 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250
Line (Cathaleens Fall - Srananagh_110_1 ) | Loss of CF-Srananagh 110 2 | 250-500 | 500-750 | 500-750 | 500-750 | 250-500 | 500-750 | 0 | 0 | 0
Line (Cathaleens Fall - Srananagh_110_1 ) | Loss of Clogher Srananagh 220 | 0 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | 250-500
Line (Cathaleens Fall - Srananagh_110_2 ) | Loss of CF-Corraclassy 110 | <250 | <250 | <250 | <250 | <250 | <250 | 0 | 0 | 0
Line (Cathaleens Fall - Srananagh_110_2 ) | Loss of CF-Srananagh 110 1 | <250 | 250-500 | 250-500 | 250-500 | <250 | 250-500 | 0 | 0 | 0
Line (Cauteen - Killonan_110_1 ) | Loss of Cauteen Tipperary 110 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 250-500 | 500-750
Line (Charleville - Glenlara_110_1 ) | Loss of Ballynahulla Knockanure 220 | 1250-1500 | 750-1000 | 500-750 | 250-500 | 250-500 | 250-500 | 250-500 | 250-500 | 250-500
Line (Charleville - Glenlara_110_1 ) | Loss of Ballynahulla - Ballyvouskil_220_1 | <250 | <250 | <250 | <250 | 0 | <250 | 750-1000 | 250-500 | 1000-1250
Line (Charleville - Killonan_110_1 ) | Loss of Ballynahulla Knockanure 220 | <250 | <250 | <250 | <250 | <250 | 500-750 | 250-500 | 250-500 | 500-750
Line (Clahane - Tralee_110_1 ) | Loss of Ballynahulla Knockanure 220 | <250 | <250 | <250 | 0 | <250 | <250 | 250-500 | <250 | 250-500
Line (Clashavoon - Clonkeen_110_1 ) | Loss of Ballyvouskil Clashavoon 220 | <250 | <250 | 250-500 | 250-500 | 250-500 | 250-500 | 250-500 | <250 | 250-500
Line (Clashavoon - Macroom_110_1 ) | Loss of Clashavoon Knockraha 220 | <250 | 250-500 | 250-500 | 250-500 | 250-500 | 750-1000 | 250-500 | <250 | 500-750
Line (Clashavoon - Macroom_110_2 ) | Loss of Clashavoon - Macroom_110_1 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250
Line (Clogher - Golagh-T_110_1 ) | Loss of Binbane - Cath Fall 110 | 0 | 0 | 0 | 0 | 0 | 0 | 1250-1500 | 1000-1250 | 1750-2000
Line (Clogher - Golagh-T_110_1 ) | Loss of Clogher-Drumkeen 110 | 0 | 0 | 0 | 0 | 0 | 0 | 250-500 | <250 | 250-500
Line (Clonee - Woodland_220_1 ) | Loss of Corduff Woodland 220 1 | <250 | 250-500 | <250 | <250 | <250 | 500-750 | 0 | 0 | 0
Line (Clonkeen - Garrow_110_1 ) | Loss of Ballynahulla Knockanure 220 | <250 | <250 | <250 | <250 | <250 | <250 | 500-750 | 250-500 | 750-1000
Line (Clonkeen - Garrow_110_1 ) | Loss of Ballyvouskil Clashavoon 220 | <250 | <250 | 250-500 | 250-500 | 250-500 | 500-750 | 250-500 | <250 | 250-500
Line (Clonkeen - Knockearagh_110_1 ) | Loss of Ballynahulla Knockanure 220 | 0 | <250 | 0 | <250 | 0 | <250 | 250-500 | <250 | 250-500
Line (Coolnabacky - Dunstown_380_1 ) | Loss of Oldstreet Woodland 400 | 0 | 0 | 0 | 0 | 0 | 0 | 1000-1250 | 250-500 | 1500-1750
Line (Coolnabacky - Portlaoise_110_1 ) | Loss of coolnabacky dunstown 400 | 0 | <250 | <250 | <250 | 0 | <250 | <250 | <250 | <250
Line (Corderry - Srananagh_110_1 ) | Loss of Flagford-Srananagh 220 circuit 1 | <250 | 250-500 | 250-500 | 250-500 | <250 | 500-750 | <250 | <250 | <250
Line (Corduff - Mooretown_220_1 ) | Loss of Finglas Mooretown 220 1 | 500-750 | 500-750 | 250-500 | 250-500 | 250-500 | 250-500 | 500-750 | <250 | 750-1000
Line (Cow Cross - Jamesbrook_110_1 ) | Loss of Knockraha to Midleton 110 | 0 | 0 | <250 | 0 | 0 | <250 | <250 | <250 | 250-500
Line (Craddanstown - Curraghdoo_110_1 ) | Loss of Clonfad to Kinnegad 110 | 0 | <250 | 0 | 0 | 0 | 1500-1750 | 750-1000 | 250-500 | 1500-1750
Line (Crane - Effernoge_110_1 ) | Loss of Arklow to Lodgewood 220 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | 2000-2250 | <250
Line (Crane - Wexford_110_1 ) | Loss of Arklow Carrickmines 220 1 | 0 | <250 | <250 | <250 | <250 | <250 | 0 | 0 | 0
Line (Crane - Wexford_110_1 ) | Loss of Great Island - Lodgewood 220 | 0 | <250 | <250 | 250-500 | <250 | <250 | 0 | 0 | 0
Line (Cullenagh - Waterford_110_1 ) | Loss of Cullenagh-Great Island 220 | <250 | 500-750 | 500-750 | 250-500 | <250 | 750-1000 | 1000-1250 | 250-500 | 1250-1500
Line (Cullenagh - Waterford_110_1 ) | Loss of gen GI4 | 0 | 0 | 0 | 0 | 0 | 0 | 250-500 | 250-500 | 250-500
Line (Cunghill - Glenree_110_1 ) | Loss of Bellacorick-Castlebar 110 | 0 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250
Line (Cunghill - Sligo_110_1 ) | Loss of Bellacorick-Castlebar 110 | <250 | 250-500 | 250-500 | 250-500 | <250 | 1000-1250 | 1250-1500 | 1000-1250 | 1500-1750
Line (Cunghill - Sligo_110_1 ) | Loss of Flagford Tonroe 110 | <250 | <250 | <250 | <250 | <250 | 250-500 | <250 | <250 | 250-500
Line (Cushaling - Newbridge_110_1 ) | Loss of Mount Lucas - Thornsberry 110 | 500-750 | 250-500 | 250-500 | 500-750 | 250-500 | <250 | <250 | <250 | <250
Line (Derrycarney - Portlaoise_110_1 ) | Loss of Coolnabacky Moneypoint 400 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500
Line (Derrycarney - Portlaoise_110_1 ) | Loss of Derrycarney - Dallow-T_110_1 | 0 | 0 | 0 | 0 | 0 | 750-1000 | 250-500 | 250-500 | 500-750
Line (Derrycarney - Portlaoise_110_1 ) | Loss of Oldstreet Woodland 400 | <250 | <250 | <250 | 0 | 0 | <250 | <250 | <250 | 250-500
Line (Derryiron - Timahoe_110_1 ) | Loss of Derryiron Thornsberry 110 | 0 | <250 | <250 | <250 | 0 | <250 | <250 | <250 | 250-500
Line (Derryiron - Timahoe_110_1 ) | Loss of Kinnegad Harristown to Dunfi T 110 | 0 | <250 | <250 | <250 | 0 | <250 | 250-500 | <250 | 500-750
Line (Derryiron - Timahoe_110_1 ) | Loss of Rinawade Dunfirth T 110 | 0 | 250-500 | 250-500 | 250-500 | 0 | <250 | 250-500 | 250-500 | 250-500
Line (Doonacurry - Lanesboro_110_1 ) | Loss of Flagford Louth 220 | 0 | <250 | 0 | 0 | 0 | <250 | <250 | <250 | 250-500
Line (Doonacurry - Shanonagh_110_1 ) | Loss of Flagford Louth 220 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250 | <250
Line (Drybridge - Gorman_110_1 ) | Loss of Gorman T2101 | 0 | 0 | 0 | <250 | 0 | <250 | <250 | <250 | <250
Line (Drybridge - Louth_110_1 ) | Loss of Crakenstown Woodland 220 1 | 250-500 | 500-750 | 250-500 | 750-1000 | 750-1000 | 750-1000 | 0 | 0 | 0
Line (Drybridge - Louth_110_1 ) | Loss of Gorman Louth 220 | 750-1000 | 750-1000 | 250-500 | 250-500 | 250-500 | 500-750 | 0 | 0 | 0
Line (Drybridge - Louth_110_1 ) | Loss of Louth Woodland 220 | <250 | <250 | <250 | 0 | <250 | <250 | 0 | 0 | 0
Line (Drybridge - Louth_110_1 ) | Loss of Richardstown - Crakenstown_220_1 | 250-500 | <250 | <250 | 250-500 | 250-500 | <250 | 0 | 0 | 0
Line (Dungarvan - Woodhouse_110_1 ) | Loss of Cullenagh-Knockraha 220 | 0 | 0 | 0 | 0 | 0 | 250-500 | <250 | <250 | 250-500
Line (Dungarvan - Woodhouse_110_1 ) | Loss of Knockraha - Woodhouse_110_1 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250 | 250-500
Line (Dunstown - Kellis_220_1 ) | Loss of Arklow Carrickmines 220 1 | 250-500 | 250-500 | <250 | <250 | <250 | <250 | 0 | 0 | 0
Line (Effernoge - Lodgewood_110_1 ) | Loss of Arklow to Lodgewood 220 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | 1000-1250 | <250
Line (Effernoge - Lodgewood_110_1 ) | Loss of Banoge - Oaklands_110_1 | 0 | <250 | <250 | <250 | 0 | <250 | <250 | <250 | <250
Line (Finglas - Mooretown_220_1 ) | Loss of Corduff Mooretown 220 1 | 3500-3750 | 2500-3000 | 2500-3000 | 2000-2250 | 2000-2250 | 2250-2500 | 3250-3500 | 2000-2250 | 3250-3500
Line (Finglas - North Wall_220_1 ) | Loss of Belcamp - Eastpoint_220_1 | 0 | 0 | 0 | 0 | 0 | 0 | <250 | 250-500 | <250
Line (Finglas - North Wall_220_1 ) | Loss of Eastpoint Shellybanks 220 | 0 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250
Line (Finglas - North Wall_220_1 ) | Loss of Dunstown Woodland 400 | 0 | 0 | 0 | 0 | 0 | 0 | <250 | 1500-1750 | <250
Line (Galway - Knockranny A1_110_1 ) | Base | 2000-2250 | 2250-2500 | 2000-2250 | 1750-2000 | 1500-1750 | 2500-3000 | 2250-2500 | 2250-2500 | 2500-3000
Line (Galway - Knockranny A1_110_1 ) | Loss of galway salthill 110 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250
Line (Galway - Salthill_110_1 ) | Loss of cashla salthill 110 | 250-500 | 250-500 | 250-500 | 250-500 | 250-500 | 250-500 | 250-500 | 250-500 | 250-500
Line (Gorman - Louth_220_1 ) | Loss of Turleenan Woodland 400 | 0 | 0 | 0 | 0 | 0 | 0 | 250-500 | 250-500 | 250-500
Line (Gorman - Ricetown_110_1 ) | Loss of Louth - Meath Hill 110 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 500-750
Line (Great Island - Lodgewood_220_1 ) | Loss of Arklow Carrickmines 220 1 | 0 | 0 | 0 | <250 | 0 | 0 | 0 | 0 | 0
Line (Great Island - Rosspile_110_1 ) | Loss of Arklow Carrickmines 220 1 | <250 | <250 | <250 | <250 | <250 | <250 | 0 | 0 | 0
Line (Great Island - Rosspile_110_1 ) | Loss of Great Island - Lodgewood 220 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250
Line (Harristown - Mulgeeth_110_1 ) | Loss of Corduff Blundelstown 110 | <250 | 250-500 | <250 | <250 | <250 | 500-750 | 250-500 | 250-500 | 250-500
Line (Inchicore - Irishtown_220_1 ) | Loss of Carrickmines Irishtown 220 | 500-750 | 250-500 | <250 | 250-500 | 250-500 | 250-500 | 1250-1500 | 250-500 | 1000-1250
Line (Inchicore - Irishtown_220_1 ) | Loss of Castlebagot Maynooth 220 1 | 750-1000 | 1000-1250 | 250-500 | 250-500 | 250-500 | 500-750 | 0 | 0 | 0
Line (Inchicore - Irishtown_220_1 ) | Loss of Castlebagot Maynooth 220 2 | <250 | 250-500 | <250 | <250 | <250 | 500-750 | 250-500 | <250 | 250-500
Line (Inchicore - Irishtown_220_1 ) | Loss of Kellystown - Woodland 220 | 500-750 | 250-500 | 250-500 | 250-500 | 250-500 | 250-500 | <250 | <250 | <250
Line (Inchicore - Irishtown_220_1 ) | Loss of Poolbeg Shellybanks 220 1 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 500-750
Line (Inchicore - Irishtown_220_1 ) | Loss of Shellybanks coupler_220_1 | <250 | <250 | <250 | <250 | 0 | 0 | <250 | <250 | <250
Line (Inchicore - Poolbeg_220_1 ) | Loss of Inchicore Poolbeg 220 2 | 0 | 0 | 3000-3250 | 2500-3000 | 2500-3000 | 0 | 0 | 250-500 | 0
Line (Irishtown - Shellybanks_220_1 ) | Loss of Dunstown Woodland 400 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | 1000-1250 | <250
Line (Irishtown - Shellybanks_220_1 ) | Loss of gen Dublin Bay | <250 | <250 | <250 | <250 | <250 | <250 | 250-500 | <250 | <250
Line (Kilbarry - Marina_110_1 ) | Loss of kilbarry marina 110 2 | <250 | 500-750 | 750-1000 | 750-1000 | 500-750 | 2000-2250 | 1250-1500 | 1250-1500 | 2000-2250
Line (Kilkenny - Kilvinoge_110_1 ) | Loss of Arklow Carrickmines 220 1 | <250 | 250-500 | <250 | <250 | <250 | <250 | 0 | 0 | 0
Line (Kilkenny - Kilvinoge_110_1 ) | Loss of Great Island - Kellis 220 | <250 | 250-500 | <250 | <250 | <250 | <250 | <250 | <250 | <250
Line (Killonan - Singland_110_1 ) | Loss of Ardnacrusha - Limerick_110_1 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250 | 250-500
Line (Killoteran - Waterford_110_1 ) | Loss of Cullenagh-Great Island 220 | 250-500 | 500-750 | 500-750 | 750-1000 | 500-750 | 500-750 | 750-1000 | 750-1000 | 750-1000
Line (Killoteran - Waterford_110_1 ) | Loss of Cullenagh-Waterford 110 | 500-750 | 750-1000 | 500-750 | 500-750 | 250-500 | 1250-1500 | 1250-1500 | 750-1000 | 1500-1750
Line (Kilpaddoge - Knockanure_110_1 ) | Loss of Kilpaddoge T2102 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250 | <250
Line (Kilpaddoge - Knockanure_220_2 ) | Loss of Clashavoon Knockraha 220 | <250 | <250 | <250 | <250 | <250 | 500-750 | 250-500 | 250-500 | 250-500
Line (Kilpaddoge - Knockanure_220_2 ) | Loss of gen Dublin Bay | 0 | 0 | 0 | 0 | 0 | 0 | 500-750 | <250 | 500-750
Line (Kilpaddoge T4201 ) | Loss of Moneypoint T4201 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 250-500
Line (Knockanure - Trien_110_2 ) | Loss of Knockanure - Trien - 110_1 | 1500-1750 | 1750-2000 | 1500-1750 | 1250-1500 | 1250-1500 | 1750-2000 | 1500-1750 | 1500-1750 | 1500-1750
Line (Knockraha - Barrymore-T_110_1 ) | Loss of Ballynahulla Knockanure 220 | <250 | 250-500 | <250 | <250 | <250 | <250 | <250 | <250 | <250
Line (Knockraha - Barrymore-T_110_1 ) | Loss of Cahir-Rathkeevin 110 | <250 | 250-500 | 250-500 | 250-500 | 250-500 | 500-750 | 250-500 | 250-500 | 250-500
Line (Knockraha - Barrymore-T_110_1 ) | Loss of Cahir Doon 110 | <250 | 500-750 | 500-750 | 500-750 | 250-500 | 1250-1500 | 750-1000 | 750-1000 | 1000-1250
Line (Knockraha - Barrymore-T_110_1 ) | Loss of Cauteen Killonan 110 | 250-500 | 250-500 | <250 | 250-500 | 250-500 | 250-500 | 250-500 | 500-750 | 250-500
Line (Knockraha - Barrymore-T_110_1 ) | Loss of Clashavoon Knockraha 220 | 250-500 | 250-500 | 250-500 | 250-500 | <250 | <250 | <250 | <250 | <250
Line (Knockraha - Barrymore-T_110_1 ) | Loss of Cullenagh to Ballydine 110 | <250 | <250 | <250 | <250 | <250 | 500-750 | 250-500 | 250-500 | 500-750
Line (Knockraha - Barrymore-T_110_1 ) | Loss of Cullenagh-Knockraha 220 | 1750-2000 | 1750-2000 | 2000-2250 | 2000-2250 | 1500-1750 | 1750-2000 | 1000-1250 | 1250-1500 | 750-1000
Line (Knockraha - Barrymore-T_110_1 ) | Loss of Killonan Knockraha 220 | 2000-2250 | 1500-1750 | 1250-1500 | 1250-1500 | 1250-1500 | 1000-1250 | 500-750 | 500-750 | 500-750
Line (Knockraha - Barrymore-T_110_1 ) | Loss of gen AD2 | <250 | <250 | <250 | <250 | <250 | 250-500 | 0 | 0 | 0
Line (Knockraha - Barrymore-T_110_1 ) | Loss of gen Dublin Bay | 0 | 0 | 0 | 0 | 0 | 0 | 1250-1500 | 1250-1500 | 1000-1250
Line (Knockraha - Barrymore-T_110_1 ) | Loss of gen GI4 | 0 | 0 | 0 | <250 | 0 | <250 | 2250-2500 | 2000-2250 | 2000-2250
Line (Knockraha - Barrymore-T_110_1 ) | Loss of gen HN2 | 0 | 0 | 0 | 0 | 0 | 0 | 250-500 | 250-500 | <250
Line (Knockraha - Barrymore-T_110_1 ) | Loss of gen HNC | 0 | 0 | 0 | 0 | 0 | 0 | 250-500 | 250-500 | 250-500
Line (Knockraha - Barrymore-T_110_1 ) | Loss of loss of Knockraha Offshore | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Line (Knockraha - Lysaghtstown_110_1 ) | Loss of Lysaghtstown- Midleton_110_1 | 0 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 250-500 | 250-500
Line (Knockraha - Lysaghtstown_110_1 ) | Loss of Midleton - Whitegate_110_1 | 0 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 250-500 | 500-750
Line (Knockraha - Woodhouse_110_1 ) | Loss of Dungarvan - Woodhouse_110_1 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250 | 250-500
Line (Lanesboro - Sliabh Bawn_110_1 ) | Loss of Athlone Shannonbridge 110 | 750-1000 | <250 | <250 | 250-500 | <250 | <250 | 0 | 0 | <250
Line (Lanesboro - Sliabh Bawn_110_1 ) | Loss of Bellacorick-Castlebar 110 | 500-750 | 750-1000 | 1000-1250 | 1250-1500 | 1000-1250 | 500-750 | 0 | <250 | 0
Line (Lanesboro - Sliabh Bawn_110_1 ) | Loss of Cashla-Flagford 220 | <250 | 250-500 | 250-500 | 500-750 | 250-500 | 500-750 | <250 | <250 | <250
Line (Lanesboro - Sliabh Bawn_110_1 ) | Loss of Corduff Blundelstown 110 | <250 | 250-500 | 250-500 | 250-500 | 250-500 | 500-750 | <250 | 0 | <250
Line (Lanesboro - Sliabh Bawn_110_1 ) | Loss of Flagford Louth 220 | 2250-2500 | 2500-3000 | 2250-2500 | 1750-2000 | 1500-1750 | 2250-2500 | <250 | <250 | <250
Line (Lenalea - Letterkenny 110 ) | Loss of Binbane - Cath Fall 110 | 0 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | 250-500
Line (Letterkenny - Golagh-T_110_1 ) | Loss of Binbane - Cath Fall 110 | <250 | 500-750 | 500-750 | 750-1000 | 500-750 | 1250-1500 | 500-750 | 250-500 | 750-1000
Line (Letterkenny - Golagh-T_110_1 ) | Binbane - Tievebrack_110_1 | 0 | <250 | <250 | <250 | <250 | 250-500 | 0 | 0 | 0
Line (Letterkenny - Golagh-T_110_1 ) | Loss of Clogher-Drumkeen 110 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250
Line (Letterkenny - Golagh-T_110_1 ) | Loss of Leanalea Tievebrack 110 | <250 | <250 | <250 | <250 | <250 | 250-500 | 0 | 0 | 0
Line (Lisdrum - Lislea 110 1 ) | Loss of Louth - Ratrussan 110 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500 | <250 | 500-750
Line (Lisdrum - Louth_110_1 ) | Loss of Louth - Ratrussan 110 | <250 | 250-500 | <250 | <250 | <250 | 250-500 | <250 | <250 | <250
Line (Louth - Meath Hill_110_1 ) | Loss of Gorman T2101 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500
Line (Louth - Meath Hill_110_1 ) | Loss of Gorman Louth 220 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250
Line (Louth AT1 300 MVA ) | Loss of Louth AT2 | 0 | 0 | 0 | 0 | 0 | 0 | <250 | 250-500 | <250
Line (Maynooth - Timahoe_110_1 ) | Loss of Blundlestown Curraghdoo 110 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250 | 250-500
Line (Maynooth - Timahoe_110_1 ) | Loss of Corduff Blundelstown 110 | 0 | 0 | 0 | 0 | 0 | <250 | 250-500 | 250-500 | 500-750
Line (Maynooth - Timahoe_110_1 ) | Loss of Craddanstown Curraghdoo 110 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250 | 250-500
Line (Maynooth - Timahoe_110_1 ) | Loss of Cushaling Newbridge 110 | 1500-1750 | 3250-3500 | 3250-3500 | 3000-3250 | 2000-2250 | 4250-4500 | 3000-3250 | 3250-3500 | 2500-3000
Line (Maynooth - Timahoe_110_1 ) | Loss of Derryiron Kinnegad 110 | <250 | 500-750 | 750-1000 | 750-1000 | <250 | 750-1000 | 1250-1500 | 1500-1750 | 1250-1500
Line (Maynooth - Timahoe_110_1 ) | Loss of Kinnegad Harristown to Dunfi T 110 | <250 | 500-750 | <250 | <250 | <250 | 1750-2000 | 1500-1750 | 750-1000 | 1750-2000
Line (Maynooth - Timahoe_110_1 ) | Loss of Newbridge - Blake-T_110_1 | 0 | 0 | 0 | 0 | 0 | <250 | 1250-1500 | 750-1000 | 1750-2000
Line (Maynooth - Timahoe_110_1 ) | Loss of Rinawade Dunfirth T 110 | 500-750 | 750-1000 | 750-1000 | 750-1000 | 750-1000 | 1000-1250 | 750-1000 | 750-1000 | 750-1000
Line (Maynooth - Timahoe_110_1 ) | Loss of coolnabacky dunstown 400 | 0 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 500-750
Line (Meath Hill - Ricetown_110_1 ) | Loss of Drybridge - Louth_110_1 | 0 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 250-500
Line (Meath Hill - Ricetown_110_1 ) | Loss of Gorman T2101 | 0 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 500-750
Line (Meath Hill - Ricetown_110_1 ) | Loss of Louth - Meath Hill 110 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 250-500 | 500-750
Line (Moneypoint - Tullabrack-T_110_1 ) | Loss of Ballynahulla Knockanure 220 | 0 | <250 | 0 | 0 | 0 | <250 | 250-500 | <250 | 250-500
Line (Mount Lucas - Thornsberry_110_1 ) | Loss of Coolnabacky Portlaoise 110 | 0 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250
Line (Mount Lucas - Thornsberry_110_1 ) | Loss of Cushaling Newbridge 110 | 1500-1750 | 1000-1250 | 1250-1500 | 1000-1250 | 750-1000 | 500-750 | 250-500 | 500-750 | 250-500
Line (Mullingar - Shanonagh_110_1 ) | Loss of Coolnabacky Moneypoint 400 | 0 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500
Line (Mullingar - Shanonagh_110_1 ) | Loss of Flagford Louth 220 | 0 | <250 | <250 | <250 | 0 | 250-500 | 500-750 | 250-500 | 750-1000
Line (Mullingar - Shanonagh_110_1 ) | Loss of Flagford-Sliabh Bawn 110 | 0 | 0 | 0 | 0 | 0 | <250 | 250-500 | 250-500 | 500-750
Line (Mullingar - Shanonagh_110_1 ) | Loss of Oldstreet Woodland 400 | 0 | <250 | <250 | <250 | <250 | 250-500 | <250 | <250 | <250
Line (Newbridge - Blake-T_110_1 ) | Loss of Castlebagot Maynooth 220 1 | <250 | 250-500 | <250 | <250 | <250 | 750-1000 | 0 | 0 | 0
Line (Newbridge - Blake-T_110_1 ) | Loss of Coolnabacky Portlaoise 110 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500 | 500-750 | 250-500
Line (Newbridge - Blake-T_110_1 ) | Loss of Kinnegad Harristown to Dunfi T 110 | <250 | 250-500 | 250-500 | <250 | <250 | 500-750 | <250 | <250 | <250
Line (Newbridge - Blake-T_110_1 ) | Loss of Mount Lucas - Thornsberry 110 | 250-500 | 250-500 | 250-500 | 250-500 | <250 | <250 | 750-1000 | 750-1000 | 750-1000
Line (Newbridge - Blake-T_110_1 ) | Loss of Rinawade Dunfirth T 110 | <250 | 250-500 | 250-500 | 250-500 | 250-500 | 250-500 | <250 | <250 | 0
Line (Newbridge - Blake-T_110_1 ) | Loss of coolnabacky dunstown 400 | 1000-1250 | 2000-2250 | 1000-1250 | 500-750 | 500-750 | 3000-3250 | 3750-4000 | 3000-3250 | 4750-5000
Line (Newbridge - Blake-T_110_1 ) | Loss of Dunstown Woodland 400 | <250 | 250-500 | <250 | <250 | <250 | 250-500 | 0 | <250 | 0
Line (North Wall - Poolbeg_220_1 ) | Loss of Belcamp - Finglas_220_1 | 0 | 0 | <250 | 1250-1500 | 1250-1500 | 0 | 0 | 0 | 0
Line (North Wall - Poolbeg_220_1 ) | Loss of Inchicore - Irishtown 220_1 | <250 | <250 | 250-500 | <250 | <250 | <250 | <250 | <250 | <250
Line (North Wall - Poolbeg_220_1 ) | Loss of Poolbeg Shellybanks 220 1 | 0 | 0 | 250-500 | <250 | <250 | 0 | 0 | 0 | 0
Line (North Wall - Poolbeg_220_1 ) | Loss of Dunstown Woodland 400 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500 | <250
Line (North Wall - Poolbeg_220_1 ) | Loss of gen HN2 | <250 | <250 | 500-750 | 250-500 | 250-500 | <250 | <250 | <250 | <250
Line (North Wall - Poolbeg_220_1 ) | Loss of gen HNC | <250 | <250 | 500-750 | 250-500 | 250-500 | <250 | 0 | <250 | 0
Line (Oldstreet - Tynagh_220_1 ) | Loss of Flagford Louth 220 | <250 | <250 | <250 | <250 | 0 | <250 | 750-1000 | 250-500 | 750-1000
Line (Oldstreet - Tynagh_220_1 ) | Loss of Moneypoint Oldstreet 400 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500
Line (Rabbitpark - Lanesboro_110_1 ) | Loss of Cashla - Cloon_110_1 | 0 | 0 | 0 | 0 | 0 | <250 | <250 | <250 | 250-500
Line (Rath - Shannonbridge_110_1 ) | Loss of Cahir - Kill Hill 110 | <250 | <250 | <250 | <250 | <250 | 250-500 | 250-500 | 250-500 | 250-500
Line (Rath - Timoney_110_1 ) | Loss of Cahir - Kill Hill 110 | <250 | <250 | <250 | <250 | <250 | <250 | 250-500 | <250 | 250-500
Line (Rathkeevin - Doon_110_1 ) | Loss of Cullenagh-Knockraha 220 | <250 | 250-500 | 250-500 | 250-500 | <250 | 250-500 | 750-1000 | <250 | 500-750
Line (Ratrussan - Shankill_110_1 ) | Loss of Balruntagh Navan 110 | 0 | <250 | <250 | <250 | <250 | <250 | <250 | <250 | <250
Line (Thornsberry - Timahoe_110_1 ) | Loss of Derryiron Thornsberry 110 | 0 | 0 | <250 | 0 | 0 | <250 | <250 | <250 | 250-500
Line (Thornsberry - Timahoe_110_1 ) | Loss of Derryiron Maynooth 110 | 0 | <250 | <250 | <250 | 0 | 500-750 | 1250-1500 | 1000-1250 | 1750-2000

## Interconnector Flows
The table below details the flows of the interconnectors that are included in the model run for that forecast scenario. *Please note positive figures are importing in all flows, while negative figures are exporting. **The interconnector flows are the same for all 3 core runs (Surplus, Curtailment, and Constraint)
Interconnector Flows
| Scenario | Celtic Flow (MW) | EWIC Flow (MW) | Greenlink Flow (MW) | Moyle Flow (MW) | LirIC (MW) | Mares (MW) | Surplus DD Occurring?
2030-01-01 | 2030 Initial | -174.41 | 300 | 210 | 188.4 | 0 | 0 | No
2030-01-01 01:00 | 2030 Initial | 245.59 | 228.98 | 510 | 439.01 | 0 | 0 | No
2030-01-01 02:00 | 2030 Initial | 665.59 | 0 | 210 | 139.01 | 0 | 0 | No
2030-01-01 03:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-01 04:00 | 2030 Initial | 700 | 0 | -300 | 0 | 0 | 0 | No
2030-01-01 05:00 | 2030 Initial | 700 | 0 | -331.05 | 0 | 0 | 0 | No
2030-01-01 06:00 | 2030 Initial | 280 | 0 | -163.52 | 0 | 0 | 0 | No
2030-01-01 07:00 | 2030 Initial | 0 | 0 | 0 | 0 | 0 | 0 | No
2030-01-01 08:00 | 2030 Initial | 231.56 | 0 | 0 | 0 | 0 | 0 | No
2030-01-01 09:00 | 2030 Initial | 140 | 0 | 96.83 | 0 | 0 | 0 | No
2030-01-01 10:00 | 2030 Initial | -280 | 241.89 | 0 | 82.97 | 0 | 0 | No
2030-01-01 11:00 | 2030 Initial | -700 | 0 | -300 | -217.03 | 0 | 0 | No
2030-01-01 12:00 | 2030 Initial | -700 | -60.19 | 0 | -150.64 | 0 | 0 | No
2030-01-01 13:00 | 2030 Initial | -700 | 0 | 300 | 149.36 | 0 | 0 | No
2030-01-01 14:00 | 2030 Initial | -700 | 0 | 510 | 402.71 | 0 | 0 | No
2030-01-01 15:00 | 2030 Initial | -700 | 0 | 300 | 124.99 | 0 | 0 | No
2030-01-01 16:00 | 2030 Initial | -700 | -66.11 | 0 | -175.01 | 0 | 0 | No
2030-01-01 17:00 | 2030 Initial | -700 | 0 | -152.77 | 0 | 0 | 0 | No
2030-01-01 18:00 | 2030 Initial | -700 | 0 | -356.07 | 0 | 0 | 0 | No
2030-01-01 19:00 | 2030 Initial | -700 | 0 | -348.15 | 0 | 0 | 0 | No
2030-01-01 20:00 | 2030 Initial | -280 | -191.92 | -510 | 57.2 | 0 | 0 | No
2030-01-01 21:00 | 2030 Initial | -700 | -31.21 | -510 | -172.84 | 0 | 0 | No
2030-01-01 22:00 | 2030 Initial | -700 | 0 | -287.56 | -8.97 | 0 | 0 | No
2030-01-01 23:00 | 2030 Initial | -700 | 300 | 12.44 | 291.03 | 0 | 0 | Yes
2030-01-02 | 2030 Initial | -700 | 505 | 312.44 | 510 | 0 | 0 | Yes
2030-01-02 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 15:00 | 2030 Initial | -700 | 300 | 463.98 | 350.56 | 0 | 0 | Yes
2030-01-02 16:00 | 2030 Initial | -700 | 0 | 163.98 | 50.56 | 0 | 0 | No
2030-01-02 17:00 | 2030 Initial | -700 | 0 | 463.98 | 85.77 | 0 | 0 | No
2030-01-02 18:00 | 2030 Initial | -420 | 0 | 510 | 385.77 | 0 | 0 | No
2030-01-02 19:00 | 2030 Initial | 0 | 0 | 510 | 510 | 0 | 0 | No
2030-01-02 20:00 | 2030 Initial | 345.58 | 205 | 510 | 283.93 | 0 | 0 | No
2030-01-02 21:00 | 2030 Initial | -74.42 | 505 | 510 | 510 | 0 | 0 | No
2030-01-02 22:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-01-02 23:00 | 2030 Initial | -341.7 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-03 | 2030 Initial | 78.3 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 01:00 | 2030 Initial | 393.73 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 02:00 | 2030 Initial | 461.04 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 03:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 04:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 07:00 | 2030 Initial | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-03 08:00 | 2030 Initial | -700 | 0 | 412.08 | 210 | 0 | 0 | No
2030-01-03 09:00 | 2030 Initial | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-03 10:00 | 2030 Initial | -700 | 94.12 | 510 | 510 | 0 | 0 | No
2030-01-03 11:00 | 2030 Initial | -700 | 300 | 510 | 510 | 0 | 0 | No
2030-01-03 12:00 | 2030 Initial | -280 | 0 | 225.68 | 301.37 | 0 | 0 | No
2030-01-03 13:00 | 2030 Initial | -700 | 0 | 510 | 326.86 | 0 | 0 | No
2030-01-03 14:00 | 2030 Initial | -700 | 0 | 510 | 372.45 | 0 | 0 | No
2030-01-03 15:00 | 2030 Initial | -700 | 158.11 | 510 | 510 | 0 | 0 | No
2030-01-03 16:00 | 2030 Initial | -700 | 249.44 | 510 | 510 | 0 | 0 | No
2030-01-03 17:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 18:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 19:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 20:00 | 2030 Initial | -700 | 357.2 | 510 | 510 | 0 | 0 | No
2030-01-03 21:00 | 2030 Initial | -700 | 115.58 | 510 | 475.72 | 0 | 0 | No
2030-01-03 22:00 | 2030 Initial | -700 | 205 | 510 | 496.95 | 0 | 0 | No
2030-01-03 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-04 | 2030 Initial | -458.79 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-04 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 07:00 | 2030 Initial | -700 | 205 | 390.65 | 210 | 0 | 0 | No
2030-01-04 08:00 | 2030 Initial | -700 | 0 | 352.45 | 144.54 | 0 | 0 | No
2030-01-04 09:00 | 2030 Initial | -700 | 205 | 510 | 444.54 | 0 | 0 | No
2030-01-04 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 12:00 | 2030 Initial | -700 | 358.84 | 510 | 510 | 0 | 0 | No
2030-01-04 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 14:00 | 2030 Initial | -700 | 465.82 | 510 | 510 | 0 | 0 | No
2030-01-04 15:00 | 2030 Initial | -700 | 171.52 | 510 | 510 | 0 | 0 | No
2030-01-04 16:00 | 2030 Initial | -700 | 0 | 300 | 292.69 | 0 | 0 | No
2030-01-04 17:00 | 2030 Initial | -465.57 | 0 | 0 | 0 | 0 | 0 | No
2030-01-04 18:00 | 2030 Initial | -700 | 0 | 122.64 | 0 | 0 | 0 | No
2030-01-04 19:00 | 2030 Initial | -700 | 107.4 | 422.64 | 300 | 0 | 0 | No
2030-01-04 20:00 | 2030 Initial | -280 | 0 | 122.64 | 0 | 0 | 0 | No
2030-01-04 21:00 | 2030 Initial | -700 | 280.53 | 422.64 | 300 | 0 | 0 | No
2030-01-04 22:00 | 2030 Initial | -700 | 0 | 422.22 | 0 | 0 | 0 | No
2030-01-04 23:00 | 2030 Initial | -700 | 0 | 338.39 | 0 | 0 | 0 | No
2030-01-05 | 2030 Initial | -700 | 0 | 265.89 | 0 | 0 | 0 | No
2030-01-05 01:00 | 2030 Initial | -700 | 0 | 226.72 | 0 | 0 | 0 | No
2030-01-05 02:00 | 2030 Initial | -700 | 205 | 354.3 | 214.67 | 0 | 0 | No
2030-01-05 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-05 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-05 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-05 06:00 | 2030 Initial | -700 | 300 | 428.43 | 300 | 0 | 0 | No
2030-01-05 07:00 | 2030 Initial | -700 | 0 | 128.43 | 0 | 0 | 0 | No
2030-01-05 08:00 | 2030 Initial | -700 | 0 | 44.16 | 300 | 0 | 0 | No
2030-01-05 09:00 | 2030 Initial | -700 | 0 | -72.97 | 0 | 0 | 0 | No
2030-01-05 10:00 | 2030 Initial | -700 | 0 | 94.13 | 300 | 0 | 0 | No
2030-01-05 11:00 | 2030 Initial | -700 | 0 | 164.42 | 216.35 | 0 | 0 | No
2030-01-05 12:00 | 2030 Initial | -700 | 0 | -135.58 | 345.47 | 0 | 0 | No
2030-01-05 13:00 | 2030 Initial | -700 | 0 | 164.42 | 339.36 | 0 | 0 | No
2030-01-05 14:00 | 2030 Initial | -700 | 0 | 147.44 | 365.87 | 0 | 0 | No
2030-01-05 15:00 | 2030 Initial | -700 | 0 | 365.68 | 65.87 | 0 | 0 | No
2030-01-05 16:00 | 2030 Initial | -700 | 0 | 65.68 | 276.71 | 0 | 0 | No
2030-01-05 17:00 | 2030 Initial | -700 | 0 | 234.31 | 510 | 0 | 0 | No
2030-01-05 18:00 | 2030 Initial | -700 | 0 | 75.4 | 510 | 0 | 0 | No
2030-01-05 19:00 | 2030 Initial | -700 | 0 | 97.95 | 464.75 | 0 | 0 | No
2030-01-05 20:00 | 2030 Initial | -700 | 0 | 0.97 | 386.32 | 0 | 0 | No
2030-01-05 21:00 | 2030 Initial | -700 | 0 | -72.06 | 300 | 0 | 0 | No
2030-01-05 22:00 | 2030 Initial | -700 | 0 | -87.48 | 0 | 0 | 0 | No
2030-01-05 23:00 | 2030 Initial | -700 | 300 | 212.52 | 300 | 0 | 0 | No
2030-01-06 | 2030 Initial | -700 | 505 | 510 | 396.82 | 0 | 0 | Yes
2030-01-06 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 02:00 | 2030 Initial | -700 | 505 | 510 | 301.37 | 0 | 0 | Yes
2030-01-06 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 04:00 | 2030 Initial | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-01-06 05:00 | 2030 Initial | -700 | 505 | 510 | 90.78 | 0 | 0 | Yes
2030-01-06 06:00 | 2030 Initial | -700 | 505 | 510 | 122.95 | 0 | 0 | Yes
2030-01-06 07:00 | 2030 Initial | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-01-06 08:00 | 2030 Initial | -700 | 505 | 510 | 47.6 | 0 | 0 | Yes
2030-01-06 09:00 | 2030 Initial | -700 | 505 | 510 | 219.91 | 0 | 0 | Yes
2030-01-06 10:00 | 2030 Initial | -700 | 505 | 510 | 446.15 | 0 | 0 | Yes
2030-01-06 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-06 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 15:00 | 2030 Initial | -616.63 | 505 | 510 | 510 | 0 | 0 | No
2030-01-06 16:00 | 2030 Initial | -700 | 205 | 462.05 | 210 | 0 | 0 | No
2030-01-06 17:00 | 2030 Initial | -700 | 215.93 | 510 | 510 | 0 | 0 | No
2030-01-06 18:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-06 19:00 | 2030 Initial | -383.53 | 505 | 510 | 510 | 0 | 0 | No
2030-01-06 20:00 | 2030 Initial | 36.47 | 505 | 510 | 510 | 0 | 0 | No
2030-01-06 21:00 | 2030 Initial | 178.77 | 505 | 510 | 510 | 0 | 0 | No
2030-01-06 22:00 | 2030 Initial | -155.84 | 205 | 510 | 430.31 | 0 | 0 | No
2030-01-06 23:00 | 2030 Initial | -575.84 | 505 | 510 | 510 | 0 | 0 | No
2030-01-07 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-07 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-07 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 16:00 | 2030 Initial | -700 | 505 | 510 | 354.81 | 0 | 0 | Yes
2030-01-07 17:00 | 2030 Initial | -700 | 248.53 | 510 | 54.81 | 0 | 0 | No
2030-01-07 18:00 | 2030 Initial | -700 | 505 | 510 | 354.81 | 0 | 0 | No
2030-01-07 19:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 20:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 23:00 | 2030 Initial | -643.88 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-08 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-08 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-08 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-08 03:00 | 2030 Initial | -361.09 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 04:00 | 2030 Initial | -453.87 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 07:00 | 2030 Initial | -700 | 205 | 480.84 | 210 | 0 | 0 | No
2030-01-08 08:00 | 2030 Initial | -700 | 475.55 | 510 | 376.08 | 0 | 0 | No
2030-01-08 09:00 | 2030 Initial | -700 | 298.81 | 510 | 510 | 0 | 0 | No
2030-01-08 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 11:00 | 2030 Initial | -700 | 431.96 | 510 | 510 | 0 | 0 | No
2030-01-08 12:00 | 2030 Initial | -700 | 338.16 | 510 | 510 | 0 | 0 | No
2030-01-08 13:00 | 2030 Initial | -700 | 316.29 | 510 | 510 | 0 | 0 | No
2030-01-08 14:00 | 2030 Initial | -700 | 443.63 | 510 | 482.39 | 0 | 0 | No
2030-01-08 15:00 | 2030 Initial | -700 | 505 | 510 | 449.22 | 0 | 0 | No
2030-01-08 16:00 | 2030 Initial | -453.93 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 17:00 | 2030 Initial | -33.93 | 300 | 510 | 487.96 | 0 | 0 | No
2030-01-08 18:00 | 2030 Initial | 35.25 | 0 | 210 | 187.96 | 0 | 0 | No
2030-01-08 19:00 | 2030 Initial | 280 | -300 | -90 | -112.04 | 0 | 0 | No
2030-01-08 20:00 | 2030 Initial | 700 | 0 | 0 | 176.03 | 0 | 0 | No
2030-01-08 21:00 | 2030 Initial | 280 | -77.28 | -300 | 69.3 | 0 | 0 | No
2030-01-08 22:00 | 2030 Initial | 700 | 0 | -291.13 | 173.23 | 0 | 0 | No
2030-01-08 23:00 | 2030 Initial | 700 | 0 | 8.87 | 276.55 | 0 | 0 | No
2030-01-09 | 2030 Initial | 700 | 0 | 260.06 | 180.8 | 0 | 0 | No
2030-01-09 01:00 | 2030 Initial | 456.33 | -300 | -39.94 | -119.2 | 0 | 0 | No
2030-01-09 02:00 | 2030 Initial | 516.03 | 0 | 210 | 180.8 | 0 | 0 | No
2030-01-09 03:00 | 2030 Initial | 700 | 300 | 510 | 480.8 | 0 | 0 | No
2030-01-09 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 05:00 | 2030 Initial | 311.94 | 505 | 510 | 486.85 | 0 | 0 | No
2030-01-09 06:00 | 2030 Initial | 700 | 205 | 210 | 186.85 | 0 | 0 | No
2030-01-09 07:00 | 2030 Initial | 280 | 312.04 | 510 | 472.88 | 0 | 0 | No
2030-01-09 08:00 | 2030 Initial | 361.38 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 09:00 | 2030 Initial | 700 | 355.73 | 510 | 510 | 0 | 0 | No
2030-01-09 10:00 | 2030 Initial | 700 | 424.21 | 510 | 510 | 0 | 0 | No
2030-01-09 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 12:00 | 2030 Initial | 700 | 318.23 | 510 | 510 | 0 | 0 | No
2030-01-09 13:00 | 2030 Initial | 462.08 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 14:00 | 2030 Initial | 280 | 489.41 | 510 | 510 | 0 | 0 | No
2030-01-09 15:00 | 2030 Initial | 700 | 189.41 | 459.96 | 210 | 0 | 0 | No
2030-01-09 16:00 | 2030 Initial | 700 | 0 | 300 | 343.25 | 0 | 0 | No
2030-01-09 17:00 | 2030 Initial | 700 | 0 | 0 | 406.95 | 0 | 0 | No
2030-01-09 18:00 | 2030 Initial | 700 | -300 | -300 | 106.95 | 0 | 0 | No
2030-01-09 19:00 | 2030 Initial | 700 | -486.5 | -510 | 16.42 | 0 | 0 | No
2030-01-09 20:00 | 2030 Initial | 700 | -306.71 | -510 | 292.4 | 0 | 0 | No
2030-01-09 21:00 | 2030 Initial | 554.4 | -375.34 | -510 | 296.54 | 0 | 0 | No
2030-01-09 22:00 | 2030 Initial | 700 | -75.34 | -210 | 48.73 | 0 | 0 | No
2030-01-09 23:00 | 2030 Initial | 700 | 0 | 24.51 | 0 | 0 | 0 | No
2030-01-10 | 2030 Initial | 700 | 0 | 324.51 | 294.71 | 0 | 0 | No
2030-01-10 01:00 | 2030 Initial | 700 | 0 | 510 | 294.71 | 0 | 0 | No
2030-01-10 02:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-10 03:00 | 2030 Initial | 700 | 0 | 510 | 278.67 | 0 | 0 | No
2030-01-10 04:00 | 2030 Initial | 420 | 0 | 510 | 510 | 0 | 0 | No
2030-01-10 05:00 | 2030 Initial | 0 | 0 | 510 | 386.61 | 0 | 0 | No
2030-01-10 06:00 | 2030 Initial | -420 | 0 | 390 | 510 | 0 | 0 | No
2030-01-10 07:00 | 2030 Initial | -700 | 300 | 90 | 247.02 | 0 | 0 | No
2030-01-10 08:00 | 2030 Initial | -415.44 | 0 | -210 | -52.98 | 0 | 0 | No
2030-01-10 09:00 | 2030 Initial | -565.33 | -300 | -510 | -352.98 | 0 | 0 | No
2030-01-10 10:00 | 2030 Initial | -700 | -226 | -309.83 | -52.98 | 0 | 0 | No
2030-01-10 11:00 | 2030 Initial | -700 | -526 | -510 | -189.09 | 0 | 0 | No
2030-01-10 12:00 | 2030 Initial | -700 | -526 | -510 | -79.39 | 0 | 0 | No
2030-01-10 13:00 | 2030 Initial | -700 | -526 | -510 | -306.07 | 0 | 0 | No
2030-01-10 14:00 | 2030 Initial | -700 | -226 | -510 | -215.82 | 0 | 0 | No
2030-01-10 15:00 | 2030 Initial | -700 | -526 | -510 | -263 | 0 | 0 | No
2030-01-10 16:00 | 2030 Initial | -700 | -519.14 | -510 | -421.56 | 0 | 0 | No
2030-01-10 17:00 | 2030 Initial | -700 | -298.6 | -510 | -185.74 | 0 | 0 | No
2030-01-10 18:00 | 2030 Initial | -700 | 0 | -510 | -8.68 | 0 | 0 | No
2030-01-10 19:00 | 2030 Initial | -700 | -66.54 | -253.43 | -274.38 | 0 | 0 | No
2030-01-10 20:00 | 2030 Initial | -700 | 0 | 46.57 | -71.39 | 0 | 0 | No
2030-01-10 21:00 | 2030 Initial | -700 | 300 | 346.57 | 228.61 | 0 | 0 | Yes
2030-01-10 22:00 | 2030 Initial | -700 | 505 | 510 | 464.63 | 0 | 0 | Yes
2030-01-10 23:00 | 2030 Initial | -700 | 505 | 510 | 369.02 | 0 | 0 | Yes
2030-01-11 | 2030 Initial | -700 | 505 | 510 | 453.8 | 0 | 0 | Yes
2030-01-11 01:00 | 2030 Initial | -700 | 505 | 510 | 265.33 | 0 | 0 | Yes
2030-01-11 02:00 | 2030 Initial | -700 | 505 | 510 | 323.98 | 0 | 0 | Yes
2030-01-11 03:00 | 2030 Initial | -700 | 505 | 510 | 207.5 | 0 | 0 | Yes
2030-01-11 04:00 | 2030 Initial | -700 | 505 | 510 | 118.77 | 0 | 0 | Yes
2030-01-11 05:00 | 2030 Initial | -700 | 505 | 510 | 334.78 | 0 | 0 | Yes
2030-01-11 06:00 | 2030 Initial | -700 | 505 | 510 | 318.22 | 0 | 0 | Yes
2030-01-11 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 12:00 | 2030 Initial | -470.11 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 14:00 | 2030 Initial | -424.6 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 15:00 | 2030 Initial | -280.91 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 16:00 | 2030 Initial | -700 | 462.55 | 510 | 314.91 | 0 | 0 | No
2030-01-11 17:00 | 2030 Initial | -628.26 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 18:00 | 2030 Initial | -208.26 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 19:00 | 2030 Initial | 211.74 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 20:00 | 2030 Initial | 631.74 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 22:00 | 2030 Initial | 605.97 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 05:00 | 2030 Initial | 280 | 205 | 210 | 348.12 | 0 | 0 | No
2030-01-12 06:00 | 2030 Initial | -140 | -95 | -90 | 48.12 | 0 | 0 | No
2030-01-12 07:00 | 2030 Initial | -438.37 | 0 | 210 | 53.55 | 0 | 0 | No
2030-01-12 08:00 | 2030 Initial | -420 | 0 | 510 | 353.55 | 0 | 0 | No
2030-01-12 09:00 | 2030 Initial | 0 | 0 | 510 | 407.96 | 0 | 0 | No
2030-01-12 10:00 | 2030 Initial | 0 | 0 | 510 | 304.37 | 0 | 0 | No
2030-01-12 11:00 | 2030 Initial | 0 | 300 | 510 | 510 | 0 | 0 | No
2030-01-12 12:00 | 2030 Initial | 0 | 33.19 | 510 | 510 | 0 | 0 | No
2030-01-12 13:00 | 2030 Initial | 0 | 0 | 510 | 481.82 | 0 | 0 | No
2030-01-12 14:00 | 2030 Initial | -280 | 119.76 | 510 | 510 | 0 | 0 | No
2030-01-12 15:00 | 2030 Initial | -700 | 419.76 | 510 | 510 | 0 | 0 | No
2030-01-12 16:00 | 2030 Initial | -700 | 152.49 | 510 | 510 | 0 | 0 | No
2030-01-12 17:00 | 2030 Initial | -700 | 152.49 | 510 | 510 | 0 | 0 | No
2030-01-12 18:00 | 2030 Initial | -700 | 450.35 | 510 | 510 | 0 | 0 | No
2030-01-12 19:00 | 2030 Initial | -700 | 412.01 | 510 | 510 | 0 | 0 | No
2030-01-12 20:00 | 2030 Initial | -700 | 112.01 | 510 | 510 | 0 | 0 | No
2030-01-12 21:00 | 2030 Initial | -700 | 0 | 510 | 396.17 | 0 | 0 | No
2030-01-12 22:00 | 2030 Initial | -511.84 | 0 | 210 | 96.17 | 0 | 0 | No
2030-01-12 23:00 | 2030 Initial | -618.42 | 135.85 | 210 | 210 | 0 | 0 | No
2030-01-13 | 2030 Initial | -687.92 | 435.85 | 510 | 510 | 0 | 0 | No
2030-01-13 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-13 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 06:00 | 2030 Initial | -700 | 505 | 510 | 256.36 | 0 | 0 | Yes
2030-01-13 07:00 | 2030 Initial | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-01-13 08:00 | 2030 Initial | -700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-01-13 09:00 | 2030 Initial | -700 | 505 | 510 | 464.21 | 0 | 0 | Yes
2030-01-13 10:00 | 2030 Initial | -700 | 505 | 510 | 383.98 | 0 | 0 | Yes
2030-01-13 11:00 | 2030 Initial | -700 | 505 | 510 | 422.98 | 0 | 0 | Yes
2030-01-13 12:00 | 2030 Initial | -700 | 505 | 510 | 422.51 | 0 | 0 | Yes
2030-01-13 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 14:00 | 2030 Initial | -700 | 505 | 427.17 | 418.58 | 0 | 0 | Yes
2030-01-13 15:00 | 2030 Initial | -700 | 505 | 127.17 | 118.58 | 0 | 0 | Yes
2030-01-13 16:00 | 2030 Initial | -700 | 300 | -172.83 | -181.42 | 0 | 0 | No
2030-01-13 17:00 | 2030 Initial | -700 | 0 | -472.83 | -481.42 | 0 | 0 | No
2030-01-13 18:00 | 2030 Initial | -700 | 0 | -192.87 | -181.42 | 0 | 0 | No
2030-01-13 19:00 | 2030 Initial | -602.3 | 300 | 107.13 | 118.58 | 0 | 0 | No
2030-01-13 20:00 | 2030 Initial | -700 | 505 | 407.13 | 418.58 | 0 | 0 | Yes
2030-01-13 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 23:00 | 2030 Initial | -700 | 505 | 510 | 328.26 | 0 | 0 | Yes
2030-01-14 | 2030 Initial | -578.29 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 01:00 | 2030 Initial | -700 | 505 | 510 | 467.89 | 0 | 0 | Yes
2030-01-14 02:00 | 2030 Initial | -700 | 505 | 510 | 467.89 | 0 | 0 | Yes
2030-01-14 03:00 | 2030 Initial | -700 | 505 | 510 | 297.73 | 0 | 0 | Yes
2030-01-14 04:00 | 2030 Initial | -700 | 505 | 510 | 403.3 | 0 | 0 | Yes
2030-01-14 05:00 | 2030 Initial | -621.13 | 505 | 510 | 277.44 | 0 | 0 | Yes
2030-01-14 06:00 | 2030 Initial | -201.13 | 505 | 510 | 277.44 | 0 | 0 | Yes
2030-01-14 07:00 | 2030 Initial | 218.87 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 08:00 | 2030 Initial | 638.87 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 16:00 | 2030 Initial | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-01-14 17:00 | 2030 Initial | 461.9 | -95 | -90 | 510 | 0 | 0 | No
2030-01-14 18:00 | 2030 Initial | 414.49 | 205 | 210 | 510 | 0 | 0 | No
2030-01-14 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 20:00 | 2030 Initial | 487.34 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 21:00 | 2030 Initial | 67.34 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 22:00 | 2030 Initial | -352.66 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 04:00 | 2030 Initial | -700 | 505 | 510 | 495.56 | 0 | 0 | Yes
2030-01-15 05:00 | 2030 Initial | -700 | 505 | 510 | 353.52 | 0 | 0 | Yes
2030-01-15 06:00 | 2030 Initial | -700 | 505 | 510 | 459.61 | 0 | 0 | Yes
2030-01-15 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-15 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-15 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-15 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 16:00 | 2030 Initial | -700 | 205 | 510 | 279.63 | 0 | 0 | No
2030-01-15 17:00 | 2030 Initial | -700 | 176.38 | 510 | 510 | 0 | 0 | No
2030-01-15 18:00 | 2030 Initial | -700 | 345.01 | 510 | 510 | 0 | 0 | No
2030-01-15 19:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-15 20:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-15 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-15 22:00 | 2030 Initial | -637.04 | 505 | 510 | 510 | 0 | 0 | No
2030-01-15 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-16 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-16 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-16 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 07:00 | 2030 Initial | -700 | 300 | 510 | 463.19 | 0 | 0 | Yes
2030-01-16 08:00 | 2030 Initial | -700 | 0 | 210 | 163.19 | 0 | 0 | Yes
2030-01-16 09:00 | 2030 Initial | -700 | 205 | 221.96 | 210 | 0 | 0 | Yes
2030-01-16 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-16 16:00 | 2030 Initial | -280 | 205 | 346.15 | 210 | 0 | 0 | No
2030-01-16 17:00 | 2030 Initial | 140 | 0 | 99.44 | 510 | 0 | 0 | No
2030-01-16 18:00 | 2030 Initial | 560 | 0 | 258.09 | 510 | 0 | 0 | No
2030-01-16 19:00 | 2030 Initial | 700 | 0 | 448.55 | 435.94 | 0 | 0 | No
2030-01-16 20:00 | 2030 Initial | 700 | 205 | 510 | 210 | 0 | 0 | No
2030-01-16 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-16 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-16 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 04:00 | 2030 Initial | 539.61 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 05:00 | 2030 Initial | 119.61 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 06:00 | 2030 Initial | -300.39 | 205 | 210 | 210 | 0 | 0 | No
2030-01-17 07:00 | 2030 Initial | -300.84 | 0 | 47.22 | 0 | 0 | 0 | No
2030-01-17 08:00 | 2030 Initial | -68.65 | 0 | 347.22 | 300 | 0 | 0 | No
2030-01-17 09:00 | 2030 Initial | 105.41 | 300 | 510 | 510 | 0 | 0 | No
2030-01-17 10:00 | 2030 Initial | 325.76 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 11:00 | 2030 Initial | -94.24 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 12:00 | 2030 Initial | 325.76 | 205 | 510 | 217.96 | 0 | 0 | No
2030-01-17 13:00 | 2030 Initial | 280 | 0 | 389.1 | 17.22 | 0 | 0 | No
2030-01-17 14:00 | 2030 Initial | 700 | 0 | 510 | 317.22 | 0 | 0 | No
2030-01-17 15:00 | 2030 Initial | 700 | 228.09 | 510 | 510 | 0 | 0 | No
2030-01-17 16:00 | 2030 Initial | 564.93 | 320.36 | 510 | 495 | 0 | 0 | No
2030-01-17 17:00 | 2030 Initial | 144.93 | 505 | 510 | 195 | 0 | 0 | No
2030-01-17 18:00 | 2030 Initial | 564.93 | 505 | 510 | 305.71 | 0 | 0 | No
2030-01-17 19:00 | 2030 Initial | 700 | 505 | 510 | 393.86 | 0 | 0 | No
2030-01-17 20:00 | 2030 Initial | 700 | 505 | 510 | 93.86 | 0 | 0 | No
2030-01-17 21:00 | 2030 Initial | 700 | 505 | 510 | 393.86 | 0 | 0 | No
2030-01-17 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 04:00 | 2030 Initial | 677.14 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 05:00 | 2030 Initial | 257.14 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 06:00 | 2030 Initial | -162.86 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 07:00 | 2030 Initial | -582.86 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 08:00 | 2030 Initial | -250.56 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 09:00 | 2030 Initial | 19.67 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 10:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 11:00 | 2030 Initial | -92.66 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 12:00 | 2030 Initial | -288.51 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 13:00 | 2030 Initial | -178.15 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 14:00 | 2030 Initial | -171.92 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 15:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 16:00 | 2030 Initial | 324.58 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 17:00 | 2030 Initial | 391.31 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 18:00 | 2030 Initial | 612.32 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 22:00 | 2030 Initial | 700 | 361.63 | 510 | 510 | 0 | 0 | No
2030-01-18 23:00 | 2030 Initial | 700 | 242.38 | 510 | 510 | 0 | 0 | No
2030-01-19 | 2030 Initial | 700 | 134.08 | 510 | 510 | 0 | 0 | No
2030-01-19 01:00 | 2030 Initial | 700 | 0 | 510 | 437.06 | 0 | 0 | No
2030-01-19 02:00 | 2030 Initial | 700 | 0 | 510 | 391.19 | 0 | 0 | No
2030-01-19 03:00 | 2030 Initial | 700 | 0 | 510 | 91.19 | 0 | 0 | No
2030-01-19 04:00 | 2030 Initial | 700 | 0 | 510 | 43.44 | 0 | 0 | No
2030-01-19 05:00 | 2030 Initial | 420 | 0 | 510 | 43.44 | 0 | 0 | No
2030-01-19 06:00 | 2030 Initial | 0 | 0 | 364.35 | 300 | 0 | 0 | No
2030-01-19 07:00 | 2030 Initial | -217.95 | 267.13 | 64.35 | 0 | 0 | 0 | No
2030-01-19 08:00 | 2030 Initial | -637.95 | 0 | -235.65 | -300 | 0 | 0 | No
2030-01-19 09:00 | 2030 Initial | -217.95 | -300 | -510 | -460.31 | 0 | 0 | No
2030-01-19 10:00 | 2030 Initial | 202.05 | 0 | -210 | -160.31 | 0 | 0 | No
2030-01-19 11:00 | 2030 Initial | 0 | -101.19 | -510 | 0 | 0 | 0 | No
2030-01-19 12:00 | 2030 Initial | 420 | -401.19 | -510 | 0 | 0 | 0 | No
2030-01-19 13:00 | 2030 Initial | 700 | -526 | -510 | -177.83 | 0 | 0 | No
2030-01-19 14:00 | 2030 Initial | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 15:00 | 2030 Initial | 420 | -526 | -510 | -61.19 | 0 | 0 | No
2030-01-19 16:00 | 2030 Initial | 0 | -226 | -510 | -61.19 | 0 | 0 | No
2030-01-19 17:00 | 2030 Initial | -140 | -526 | -510 | -352.39 | 0 | 0 | No
2030-01-19 18:00 | 2030 Initial | 280 | -526 | -510 | -352.39 | 0 | 0 | No
2030-01-19 19:00 | 2030 Initial | 700 | -301.76 | -510 | -69.55 | 0 | 0 | No
2030-01-19 20:00 | 2030 Initial | 700 | -1.76 | -210 | 230.45 | 0 | 0 | No
2030-01-19 21:00 | 2030 Initial | 700 | 0 | 90 | 223.44 | 0 | 0 | No
2030-01-19 22:00 | 2030 Initial | 700 | -83.55 | -210 | -76.56 | 0 | 0 | No
2030-01-19 23:00 | 2030 Initial | 670.88 | -383.55 | -510 | -364.44 | 0 | 0 | No
2030-01-20 | 2030 Initial | 277.63 | -395 | -479.67 | -238.93 | 0 | 0 | No
2030-01-20 01:00 | 2030 Initial | 372.44 | -95 | -179.67 | 61.07 | 0 | 0 | No
2030-01-20 02:00 | 2030 Initial | 280 | 205 | 120.33 | 210 | 0 | 0 | No
2030-01-20 03:00 | 2030 Initial | 700 | 505 | 420.33 | 510 | 0 | 0 | No
2030-01-20 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-20 05:00 | 2030 Initial | 328.87 | 300 | 223.13 | 398.55 | 0 | 0 | No
2030-01-20 06:00 | 2030 Initial | -91.13 | 0 | -76.87 | 98.55 | 0 | 0 | No
2030-01-20 07:00 | 2030 Initial | -31.97 | -300 | -376.87 | -201.45 | 0 | 0 | No
2030-01-20 08:00 | 2030 Initial | 388.03 | -14.66 | -510 | -304.57 | 0 | 0 | No
2030-01-20 09:00 | 2030 Initial | 700 | -241.3 | -510 | -263.76 | 0 | 0 | No
2030-01-20 10:00 | 2030 Initial | 700 | 0 | -473.22 | 0 | 0 | 0 | No
2030-01-20 11:00 | 2030 Initial | 290.14 | -300 | -510 | -5.19 | 0 | 0 | No
2030-01-20 12:00 | 2030 Initial | 274.73 | -526 | -510 | 50.19 | 0 | 0 | No
2030-01-20 13:00 | 2030 Initial | 694.73 | -226 | -478.49 | 36.24 | 0 | 0 | No
2030-01-20 14:00 | 2030 Initial | 700 | -100.46 | -300 | 35.81 | 0 | 0 | No
2030-01-20 15:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-20 16:00 | 2030 Initial | 700 | 0 | 269.01 | 0 | 0 | 0 | No
2030-01-20 17:00 | 2030 Initial | 700 | 0 | 510 | 167.42 | 0 | 0 | No
2030-01-20 18:00 | 2030 Initial | 700 | 12.33 | 510 | 467.42 | 0 | 0 | No
2030-01-20 19:00 | 2030 Initial | 700 | 291.04 | 510 | 483.79 | 0 | 0 | No
2030-01-20 20:00 | 2030 Initial | 700 | 505 | 510 | 483.79 | 0 | 0 | No
2030-01-20 21:00 | 2030 Initial | 700 | 319.88 | 510 | 393.07 | 0 | 0 | No
2030-01-20 22:00 | 2030 Initial | 700 | 476.46 | 510 | 306.12 | 0 | 0 | No
2030-01-20 23:00 | 2030 Initial | 700 | 222.41 | 510 | 419.18 | 0 | 0 | No
2030-01-21 | 2030 Initial | 700 | 241.43 | 510 | 510 | 0 | 0 | No
2030-01-21 01:00 | 2030 Initial | 700 | 0 | 510 | 420.01 | 0 | 0 | No
2030-01-21 02:00 | 2030 Initial | 700 | 0 | 510 | 420.01 | 0 | 0 | No
2030-01-21 03:00 | 2030 Initial | 700 | 0 | 510 | 368.57 | 0 | 0 | No
2030-01-21 04:00 | 2030 Initial | 700 | 0 | 510 | 368.57 | 0 | 0 | No
2030-01-21 05:00 | 2030 Initial | 700 | 0 | 510 | 140.18 | 0 | 0 | No
2030-01-21 06:00 | 2030 Initial | 700 | 0 | 510 | 240.55 | 0 | 0 | No
2030-01-21 07:00 | 2030 Initial | 700 | 0 | 510 | 240.55 | 0 | 0 | No
2030-01-21 08:00 | 2030 Initial | 700 | 239.24 | 510 | 510 | 0 | 0 | No
2030-01-21 09:00 | 2030 Initial | 700 | 426.96 | 510 | 510 | 0 | 0 | No
2030-01-21 10:00 | 2030 Initial | 700 | 126.96 | 510 | 393.51 | 0 | 0 | No
2030-01-21 11:00 | 2030 Initial | 700 | 0 | 510 | 93.51 | 0 | 0 | No
2030-01-21 12:00 | 2030 Initial | 700 | 147.63 | 295.06 | 210 | 0 | 0 | No
2030-01-21 13:00 | 2030 Initial | 700 | 447.63 | 510 | 510 | 0 | 0 | No
2030-01-21 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 15:00 | 2030 Initial | 700 | 205 | 411.49 | 210 | 0 | 0 | No
2030-01-21 16:00 | 2030 Initial | 700 | 0 | 510 | 401.16 | 0 | 0 | No
2030-01-21 17:00 | 2030 Initial | 700 | 31.9 | 510 | 510 | 0 | 0 | No
2030-01-21 18:00 | 2030 Initial | 700 | 331.9 | 510 | 510 | 0 | 0 | No
2030-01-21 19:00 | 2030 Initial | 700 | 327.57 | 510 | 510 | 0 | 0 | No
2030-01-21 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 21:00 | 2030 Initial | 700 | 226.94 | 510 | 510 | 0 | 0 | No
2030-01-21 22:00 | 2030 Initial | 700 | 492.39 | 510 | 510 | 0 | 0 | No
2030-01-21 23:00 | 2030 Initial | 700 | 257.11 | 510 | 510 | 0 | 0 | No
2030-01-22 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 05:00 | 2030 Initial | 589.94 | 300 | 510 | 510 | 0 | 0 | No
2030-01-22 06:00 | 2030 Initial | 169.94 | 0 | 210 | 210 | 0 | 0 | No
2030-01-22 07:00 | 2030 Initial | 547.73 | 0 | 0 | -90 | 0 | 0 | No
2030-01-22 08:00 | 2030 Initial | 700 | 93.68 | 300 | 0 | 0 | 0 | No
2030-01-22 09:00 | 2030 Initial | 700 | 315.38 | 510 | 66.12 | 0 | 0 | No
2030-01-22 10:00 | 2030 Initial | 700 | 355.09 | 510 | 136.65 | 0 | 0 | No
2030-01-22 11:00 | 2030 Initial | 700 | 276.68 | 510 | 128.47 | 0 | 0 | No
2030-01-22 12:00 | 2030 Initial | 700 | 228.63 | 510 | 103.72 | 0 | 0 | No
2030-01-22 13:00 | 2030 Initial | 700 | 299.35 | 510 | 107.92 | 0 | 0 | No
2030-01-22 14:00 | 2030 Initial | 700 | 421.12 | 510 | 89.78 | 0 | 0 | No
2030-01-22 15:00 | 2030 Initial | 700 | 144.97 | 248.92 | 89.53 | 0 | 0 | No
2030-01-22 16:00 | 2030 Initial | 700 | 0 | -51.08 | -210 | 0 | 0 | No
2030-01-22 17:00 | 2030 Initial | 700 | -189.21 | -351.08 | -510 | 0 | 0 | No
2030-01-22 18:00 | 2030 Initial | 700 | 0 | -510 | -510 | 0 | 0 | No
2030-01-22 19:00 | 2030 Initial | 700 | 0 | -217.44 | -300 | 0 | 0 | No
2030-01-22 20:00 | 2030 Initial | 700 | 255.4 | 82.56 | 0 | 0 | 0 | No
2030-01-22 21:00 | 2030 Initial | 700 | 505 | 382.56 | 170.97 | 0 | 0 | No
2030-01-22 22:00 | 2030 Initial | 700 | 347.55 | 510 | 210 | 0 | 0 | No
2030-01-22 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 05:00 | 2030 Initial | 494.8 | 505 | 510 | 499.85 | 0 | 0 | No
2030-01-23 06:00 | 2030 Initial | 74.8 | 249.36 | 246.18 | 199.85 | 0 | 0 | No
2030-01-23 07:00 | 2030 Initial | 280 | -50.64 | -53.82 | -100.15 | 0 | 0 | No
2030-01-23 08:00 | 2030 Initial | 700 | 0 | 246.18 | 0 | 0 | 0 | No
2030-01-23 09:00 | 2030 Initial | 700 | 141.56 | 510 | 0 | 0 | 0 | No
2030-01-23 10:00 | 2030 Initial | 700 | 264.74 | 510 | 0 | 0 | 0 | No
2030-01-23 11:00 | 2030 Initial | 700 | 50.35 | 510 | 0 | 0 | 0 | No
2030-01-23 12:00 | 2030 Initial | 700 | 0 | 399.22 | 0 | 0 | 0 | No
2030-01-23 13:00 | 2030 Initial | 700 | 0 | 453.09 | 0 | 0 | 0 | No
2030-01-23 14:00 | 2030 Initial | 700 | 0 | 412.52 | 0 | 0 | 0 | No
2030-01-23 15:00 | 2030 Initial | 700 | 58.19 | 510 | 0 | 0 | 0 | No
2030-01-23 16:00 | 2030 Initial | 700 | 300 | 263.12 | -49.54 | 0 | 0 | No
2030-01-23 17:00 | 2030 Initial | 700 | 0 | -36.88 | -349.54 | 0 | 0 | No
2030-01-23 18:00 | 2030 Initial | 700 | -178.62 | -311.85 | -510 | 0 | 0 | No
2030-01-23 19:00 | 2030 Initial | 700 | 0 | -11.85 | -390.37 | 0 | 0 | No
2030-01-23 20:00 | 2030 Initial | 700 | 300 | 288.15 | -90.37 | 0 | 0 | No
2030-01-23 21:00 | 2030 Initial | 700 | 418.89 | 510 | 0 | 0 | 0 | No
2030-01-23 22:00 | 2030 Initial | 700 | 345.24 | 510 | 8.38 | 0 | 0 | No
2030-01-23 23:00 | 2030 Initial | 700 | 483.7 | 510 | 308.38 | 0 | 0 | No
2030-01-24 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 04:00 | 2030 Initial | 311.34 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 05:00 | 2030 Initial | -108.66 | 505 | 510 | 312.01 | 0 | 0 | No
2030-01-24 06:00 | 2030 Initial | -116.77 | 205 | 210 | 12.01 | 0 | 0 | No
2030-01-24 07:00 | 2030 Initial | 0 | 44.49 | 510 | -100.42 | 0 | 0 | No
2030-01-24 08:00 | 2030 Initial | 0 | 0 | 284.01 | -153.34 | 0 | 0 | No
2030-01-24 09:00 | 2030 Initial | 0 | 3.7 | 510 | 0 | 0 | 0 | No
2030-01-24 10:00 | 2030 Initial | -150.86 | 0 | 210 | -1.11 | 0 | 0 | No
2030-01-24 11:00 | 2030 Initial | 1.1 | 0 | 0 | -226.93 | 0 | 0 | No
2030-01-24 12:00 | 2030 Initial | 421.1 | 236.1 | 300 | 0 | 0 | 0 | No
2030-01-24 13:00 | 2030 Initial | 1.1 | 0 | 0 | -253.71 | 0 | 0 | No
2030-01-24 14:00 | 2030 Initial | 42.75 | 0 | -17.67 | -138.83 | 0 | 0 | No
2030-01-24 15:00 | 2030 Initial | 462.75 | 0 | -210 | -201.1 | 0 | 0 | No
2030-01-24 16:00 | 2030 Initial | 700 | -226 | -510 | -501.1 | 0 | 0 | No
2030-01-24 17:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 18:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 19:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 20:00 | 2030 Initial | 700 | -226 | -244.72 | -300 | 0 | 0 | No
2030-01-24 21:00 | 2030 Initial | 700 | 3.56 | 55.28 | 0 | 0 | 0 | No
2030-01-24 22:00 | 2030 Initial | 646.33 | 0 | -92.9 | 0 | 0 | 0 | No
2030-01-24 23:00 | 2030 Initial | 226.33 | 0 | 0 | 0 | 0 | 0 | No
2030-01-25 | 2030 Initial | 101.46 | 0 | 0 | 0 | 0 | 0 | No
2030-01-25 01:00 | 2030 Initial | 521.46 | 0 | 0 | 0 | 0 | 0 | No
2030-01-25 02:00 | 2030 Initial | 329.97 | 0 | 0 | 0 | 0 | 0 | No
2030-01-25 03:00 | 2030 Initial | -90.03 | 0 | 0 | -150.96 | 0 | 0 | No
2030-01-25 04:00 | 2030 Initial | -510.03 | 0 | 0 | -113.13 | 0 | 0 | No
2030-01-25 05:00 | 2030 Initial | -700 | 0 | 0 | -413.13 | 0 | 0 | No
2030-01-25 06:00 | 2030 Initial | -700 | 0 | 0 | -376.61 | 0 | 0 | No
2030-01-25 07:00 | 2030 Initial | -700 | 0 | 117.68 | -114.96 | 0 | 0 | No
2030-01-25 08:00 | 2030 Initial | -700 | 0 | 204.46 | 0 | 0 | 0 | No
2030-01-25 09:00 | 2030 Initial | -700 | 300 | 504.46 | 215.64 | 0 | 0 | No
2030-01-25 10:00 | 2030 Initial | -700 | 505 | 510 | 428.25 | 0 | 0 | No
2030-01-25 11:00 | 2030 Initial | -700 | 337.94 | 510 | 387.69 | 0 | 0 | No
2030-01-25 12:00 | 2030 Initial | -700 | 244.11 | 510 | 170.24 | 0 | 0 | No
2030-01-25 13:00 | 2030 Initial | -700 | 3.18 | 510 | 65.44 | 0 | 0 | No
2030-01-25 14:00 | 2030 Initial | -700 | 40.14 | 510 | 0 | 0 | 0 | No
2030-01-25 15:00 | 2030 Initial | -700 | 0 | 493.69 | 27.38 | 0 | 0 | No
2030-01-25 16:00 | 2030 Initial | -700 | 0 | 193.69 | -134.24 | 0 | 0 | No
2030-01-25 17:00 | 2030 Initial | -700 | 0 | -106.31 | -318.04 | 0 | 0 | No
2030-01-25 18:00 | 2030 Initial | -700 | 0 | -369.95 | -163.67 | 0 | 0 | No
2030-01-25 19:00 | 2030 Initial | -280 | 0 | -69.95 | -3.85 | 0 | 0 | No
2030-01-25 20:00 | 2030 Initial | -700 | 68.66 | 230.05 | 296.15 | 0 | 0 | No
2030-01-25 21:00 | 2030 Initial | -700 | 0 | -37.23 | 0 | 0 | 0 | No
2030-01-25 22:00 | 2030 Initial | -700 | 0 | -201.6 | -181.07 | 0 | 0 | No
2030-01-25 23:00 | 2030 Initial | -700 | -95 | -118.01 | -60.74 | 0 | 0 | No
2030-01-26 | 2030 Initial | -700 | 205 | 181.99 | 239.26 | 0 | 0 | No
2030-01-26 01:00 | 2030 Initial | -700 | 505 | 481.99 | 510 | 0 | 0 | Yes
2030-01-26 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-26 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-26 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-26 05:00 | 2030 Initial | -700 | 505 | 510 | 472.5 | 0 | 0 | Yes
2030-01-26 06:00 | 2030 Initial | -700 | 505 | 510 | 172.5 | 0 | 0 | Yes
2030-01-26 07:00 | 2030 Initial | -700 | 205 | 210 | -127.5 | 0 | 0 | No
2030-01-26 08:00 | 2030 Initial | -700 | 0 | 388.99 | 172.5 | 0 | 0 | No
2030-01-26 09:00 | 2030 Initial | -700 | 41.64 | 510 | 472.5 | 0 | 0 | No
2030-01-26 10:00 | 2030 Initial | -700 | 181.83 | 510 | 387.13 | 0 | 0 | No
2030-01-26 11:00 | 2030 Initial | -700 | 381.72 | 510 | 176.11 | 0 | 0 | No
2030-01-26 12:00 | 2030 Initial | -700 | 505 | 510 | 82.95 | 0 | 0 | No
2030-01-26 13:00 | 2030 Initial | -700 | 505 | 510 | 382.95 | 0 | 0 | No
2030-01-26 14:00 | 2030 Initial | -700 | 478.28 | 510 | 347.6 | 0 | 0 | No
2030-01-26 15:00 | 2030 Initial | -700 | 451.9 | 412.81 | 510 | 0 | 0 | No
2030-01-26 16:00 | 2030 Initial | -700 | 300 | 112.81 | 265.29 | 0 | 0 | No
2030-01-26 17:00 | 2030 Initial | -700 | 0 | -187.19 | -34.71 | 0 | 0 | No
2030-01-26 18:00 | 2030 Initial | -700 | -233.21 | -487.19 | -334.71 | 0 | 0 | No
2030-01-26 19:00 | 2030 Initial | -280 | -300 | -510 | -338.65 | 0 | 0 | No
2030-01-26 20:00 | 2030 Initial | -700 | 0 | -210 | -38.65 | 0 | 0 | No
2030-01-26 21:00 | 2030 Initial | -672.91 | 276.81 | 90 | 261.35 | 0 | 0 | No
2030-01-26 22:00 | 2030 Initial | -252.91 | 0 | -90 | 22.27 | 0 | 0 | No
2030-01-26 23:00 | 2030 Initial | -494 | -300 | -390 | -250.71 | 0 | 0 | No
2030-01-27 | 2030 Initial | -700 | -95 | -90 | 49.29 | 0 | 0 | No
2030-01-27 01:00 | 2030 Initial | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-27 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 08:00 | 2030 Initial | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-27 09:00 | 2030 Initial | -700 | 0 | 228.94 | 0 | 0 | 0 | No
2030-01-27 10:00 | 2030 Initial | -700 | 0 | 510 | 148.55 | 0 | 0 | No
2030-01-27 11:00 | 2030 Initial | -700 | 0 | 215.91 | 56.4 | 0 | 0 | No
2030-01-27 12:00 | 2030 Initial | -700 | 0 | 510 | 356.4 | 0 | 0 | No
2030-01-27 13:00 | 2030 Initial | -417.76 | 0 | 210 | 86.66 | 0 | 0 | No
2030-01-27 14:00 | 2030 Initial | 0 | 64.69 | 510 | 386.66 | 0 | 0 | No
2030-01-27 15:00 | 2030 Initial | 93.72 | 0 | 510 | 385.25 | 0 | 0 | No
2030-01-27 16:00 | 2030 Initial | 166.5 | 300 | 510 | 510 | 0 | 0 | No
2030-01-27 17:00 | 2030 Initial | 0 | 0 | 210 | 210 | 0 | 0 | No
2030-01-27 18:00 | 2030 Initial | 0 | 0 | 305.62 | 210 | 0 | 0 | No
2030-01-27 19:00 | 2030 Initial | 280 | 22.26 | 510 | 510 | 0 | 0 | No
2030-01-27 20:00 | 2030 Initial | 700 | 305.37 | 510 | 510 | 0 | 0 | No
2030-01-27 21:00 | 2030 Initial | 700 | 379.66 | 510 | 510 | 0 | 0 | No
2030-01-27 22:00 | 2030 Initial | 700 | 103.23 | 510 | 510 | 0 | 0 | No
2030-01-27 23:00 | 2030 Initial | 700 | 0 | 510 | 276.65 | 0 | 0 | No
2030-01-28 | 2030 Initial | 700 | 5.96 | 300 | 300 | 0 | 0 | No
2030-01-28 01:00 | 2030 Initial | 671.22 | -50.51 | 0 | 0 | 0 | 0 | No
2030-01-28 02:00 | 2030 Initial | 353.01 | 0 | 0 | 250.4 | 0 | 0 | No
2030-01-28 03:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-28 04:00 | 2030 Initial | 630.14 | 505 | 510 | 510 | 0 | 0 | No
2030-01-28 05:00 | 2030 Initial | 210.14 | 505 | 510 | 510 | 0 | 0 | No
2030-01-28 06:00 | 2030 Initial | -209.86 | 505 | 510 | 510 | 0 | 0 | No
2030-01-28 07:00 | 2030 Initial | -629.86 | 205 | 210 | 210 | 0 | 0 | No
2030-01-28 08:00 | 2030 Initial | -479.25 | 0 | -28.59 | 476.23 | 0 | 0 | No
2030-01-28 09:00 | 2030 Initial | -59.25 | 0 | -127.89 | 176.23 | 0 | 0 | No
2030-01-28 10:00 | 2030 Initial | 0 | 0 | -171.92 | 418.03 | 0 | 0 | No
2030-01-28 11:00 | 2030 Initial | -280 | 0 | 49.29 | 281.58 | 0 | 0 | No
2030-01-28 12:00 | 2030 Initial | -700 | 0 | -250.71 | 123.45 | 0 | 0 | No
2030-01-28 13:00 | 2030 Initial | -700 | 0 | -238.63 | 423.45 | 0 | 0 | No
2030-01-28 14:00 | 2030 Initial | -700 | 0 | -305.16 | 459.61 | 0 | 0 | No
2030-01-28 15:00 | 2030 Initial | -280 | -201.26 | -196.6 | 348.37 | 0 | 0 | No
2030-01-28 16:00 | 2030 Initial | -280 | 0 | 103.4 | 385.31 | 0 | 0 | No
2030-01-28 17:00 | 2030 Initial | -700 | 0 | 403.4 | 510 | 0 | 0 | No
2030-01-28 18:00 | 2030 Initial | -700 | 300 | 510 | 510 | 0 | 0 | No
2030-01-28 19:00 | 2030 Initial | -700 | 89.07 | 510 | 510 | 0 | 0 | No
2030-01-28 20:00 | 2030 Initial | -280 | 0 | 510 | 510 | 0 | 0 | No
2030-01-28 21:00 | 2030 Initial | -226.15 | 248.64 | 510 | 510 | 0 | 0 | No
2030-01-28 22:00 | 2030 Initial | -646.15 | 505 | 510 | 510 | 0 | 0 | No
2030-01-28 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 | 2030 Initial | -637.8 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 01:00 | 2030 Initial | -634.13 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 07:00 | 2030 Initial | -700 | 205 | 210 | 274 | 0 | 0 | No
2030-01-29 08:00 | 2030 Initial | -700 | 0 | 510 | 386.57 | 0 | 0 | No
2030-01-29 09:00 | 2030 Initial | -700 | 300 | 510 | 510 | 0 | 0 | No
2030-01-29 10:00 | 2030 Initial | -700 | 130.12 | 510 | 510 | 0 | 0 | No
2030-01-29 11:00 | 2030 Initial | -700 | 0 | 232.93 | 377.89 | 0 | 0 | No
2030-01-29 12:00 | 2030 Initial | -700 | 0 | 61.13 | 182.92 | 0 | 0 | No
2030-01-29 13:00 | 2030 Initial | -700 | 0 | -238.87 | -70.97 | 0 | 0 | No
2030-01-29 14:00 | 2030 Initial | -700 | 0 | -212.73 | -143.87 | 0 | 0 | No
2030-01-29 15:00 | 2030 Initial | -700 | 0 | 87.27 | -59.52 | 0 | 0 | No
2030-01-29 16:00 | 2030 Initial | -700 | 0 | 387.27 | -202.12 | 0 | 0 | No
2030-01-29 17:00 | 2030 Initial | -700 | 152.29 | 510 | -149.85 | 0 | 0 | No
2030-01-29 18:00 | 2030 Initial | -700 | 126.06 | 510 | 150.15 | 0 | 0 | No
2030-01-29 19:00 | 2030 Initial | -700 | 426.06 | 510 | 450.15 | 0 | 0 | No
2030-01-29 20:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 | 2030 Initial | -690.13 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 01:00 | 2030 Initial | -695.56 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 06:00 | 2030 Initial | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-30 07:00 | 2030 Initial | -700 | 0 | 143.56 | 0 | 0 | 0 | No
2030-01-30 08:00 | 2030 Initial | -700 | 205 | 443.56 | 300 | 0 | 0 | No
2030-01-30 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 10:00 | 2030 Initial | -700 | 248.71 | 510 | 510 | 0 | 0 | No
2030-01-30 11:00 | 2030 Initial | -700 | 0 | 510 | 349.15 | 0 | 0 | No
2030-01-30 12:00 | 2030 Initial | -700 | 205 | 210 | 340.38 | 0 | 0 | No
2030-01-30 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 16:00 | 2030 Initial | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-30 17:00 | 2030 Initial | -700 | 324.96 | 510 | 64.62 | 0 | 0 | No
2030-01-30 18:00 | 2030 Initial | -700 | 505 | 510 | 161.02 | 0 | 0 | No
2030-01-30 19:00 | 2030 Initial | -700 | 505 | 510 | 461.02 | 0 | 0 | No
2030-01-30 20:00 | 2030 Initial | -504.35 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 21:00 | 2030 Initial | -217.1 | 400.99 | 510 | 510 | 0 | 0 | No
2030-01-30 22:00 | 2030 Initial | -637.1 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 07:00 | 2030 Initial | -700 | 436.49 | 510 | 510 | 0 | 0 | No
2030-01-31 08:00 | 2030 Initial | -700 | 136.49 | 210 | 210 | 0 | 0 | No
2030-01-31 09:00 | 2030 Initial | -700 | 0 | -32.06 | 264.39 | 0 | 0 | No
2030-01-31 10:00 | 2030 Initial | -700 | 0 | 0 | 398.11 | 0 | 0 | No
2030-01-31 11:00 | 2030 Initial | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-01-31 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 15:00 | 2030 Initial | -700 | 410.58 | 438.09 | 510 | 0 | 0 | No
2030-01-31 16:00 | 2030 Initial | -700 | 110.58 | 138.09 | 210 | 0 | 0 | No
2030-01-31 17:00 | 2030 Initial | -700 | -189.42 | -161.91 | 93.95 | 0 | 0 | No
2030-01-31 18:00 | 2030 Initial | -700 | -125.09 | -461.91 | 194.54 | 0 | 0 | No
2030-01-31 19:00 | 2030 Initial | -690.66 | -95 | -161.91 | 193.97 | 0 | 0 | No
2030-01-31 20:00 | 2030 Initial | -700 | 205 | 138.09 | 192.46 | 0 | 0 | No
2030-01-31 21:00 | 2030 Initial | -700 | 505 | 438.09 | 492.46 | 0 | 0 | No
2030-01-31 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 15:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 16:00 | 2030 Initial | 0 | 239.43 | 510 | 510 | 0 | 0 | No
2030-02-01 17:00 | 2030 Initial | 379.27 | 505 | 510 | 510 | 0 | 0 | No
2030-02-01 18:00 | 2030 Initial | 367.31 | 505 | 510 | 510 | 0 | 0 | No
2030-02-01 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-01 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-01 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-01 22:00 | 2030 Initial | 700 | 300 | 300 | 510 | 0 | 0 | No
2030-02-01 23:00 | 2030 Initial | 617.91 | 0 | 0 | 277.3 | 0 | 0 | No
2030-02-02 | 2030 Initial | 700 | 0 | -300 | 112.86 | 0 | 0 | No
2030-02-02 01:00 | 2030 Initial | 700 | -106.96 | -300 | 124.5 | 0 | 0 | No
2030-02-02 02:00 | 2030 Initial | 700 | 0 | 0 | 275.62 | 0 | 0 | No
2030-02-02 03:00 | 2030 Initial | 700 | -181.84 | -300 | -24.38 | 0 | 0 | No
2030-02-02 04:00 | 2030 Initial | 700 | -296.04 | -510 | -40.22 | 0 | 0 | No
2030-02-02 05:00 | 2030 Initial | 682.58 | -526 | -510 | -38.53 | 0 | 0 | No
2030-02-02 06:00 | 2030 Initial | 366.31 | -488.59 | -510 | -160.17 | 0 | 0 | No
2030-02-02 07:00 | 2030 Initial | 0 | -188.59 | -510 | 9.93 | 0 | 0 | No
2030-02-02 08:00 | 2030 Initial | 0 | 0 | -287.43 | 41.27 | 0 | 0 | No
2030-02-02 09:00 | 2030 Initial | 160.57 | -300 | -510 | -25.11 | 0 | 0 | No
2030-02-02 10:00 | 2030 Initial | 140 | -526 | -510 | 41.55 | 0 | 0 | No
2030-02-02 11:00 | 2030 Initial | -280 | -526 | -510 | 94.55 | 0 | 0 | No
2030-02-02 12:00 | 2030 Initial | -700 | -526 | -510 | 125.69 | 0 | 0 | No
2030-02-02 13:00 | 2030 Initial | -700 | -526 | -510 | 79.97 | 0 | 0 | No
2030-02-02 14:00 | 2030 Initial | -700 | -526 | -510 | -53.22 | 0 | 0 | No
2030-02-02 15:00 | 2030 Initial | -700 | -526 | -510 | -105.81 | 0 | 0 | No
2030-02-02 16:00 | 2030 Initial | -471.02 | -526 | -510 | -121.17 | 0 | 0 | No
2030-02-02 17:00 | 2030 Initial | -700 | -526 | -510 | 178.83 | 0 | 0 | No
2030-02-02 18:00 | 2030 Initial | -700 | -319.22 | -510 | 267.48 | 0 | 0 | No
2030-02-02 19:00 | 2030 Initial | -299.49 | -395 | -390 | -32.52 | 0 | 0 | No
2030-02-02 20:00 | 2030 Initial | -289.5 | -95 | -90 | -60.11 | 0 | 0 | No
2030-02-02 21:00 | 2030 Initial | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-02-02 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-02 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-03 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 01:00 | 2030 Initial | -700 | 505 | 510 | 325.25 | 0 | 0 | Yes
2030-02-03 02:00 | 2030 Initial | -700 | 505 | 510 | 172.26 | 0 | 0 | Yes
2030-02-03 03:00 | 2030 Initial | -700 | 505 | 510 | 273.5 | 0 | 0 | Yes
2030-02-03 04:00 | 2030 Initial | -700 | 505 | 510 | 161.69 | 0 | 0 | Yes
2030-02-03 05:00 | 2030 Initial | -700 | 505 | 510 | 396.56 | 0 | 0 | Yes
2030-02-03 06:00 | 2030 Initial | -700 | 505 | 510 | 443.17 | 0 | 0 | Yes
2030-02-03 07:00 | 2030 Initial | -700 | 505 | 510 | 266.45 | 0 | 0 | Yes
2030-02-03 08:00 | 2030 Initial | -700 | 505 | 510 | 243.3 | 0 | 0 | Yes
2030-02-03 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-03 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 16:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-03 17:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-03 18:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-03 19:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-03 20:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-03 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 01:00 | 2030 Initial | -700 | 505 | 510 | 378.37 | 0 | 0 | Yes
2030-02-04 02:00 | 2030 Initial | -700 | 505 | 510 | 109.96 | 0 | 0 | Yes
2030-02-04 03:00 | 2030 Initial | -700 | 505 | 510 | 241.19 | 0 | 0 | Yes
2030-02-04 04:00 | 2030 Initial | -700 | 505 | 510 | 36.06 | 0 | 0 | Yes
2030-02-04 05:00 | 2030 Initial | -700 | 505 | 510 | -17.13 | 0 | 0 | Yes
2030-02-04 06:00 | 2030 Initial | -700 | 505 | 510 | -15.05 | 0 | 0 | Yes
2030-02-04 07:00 | 2030 Initial | -700 | 505 | 510 | 284.95 | 0 | 0 | Yes
2030-02-04 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 09:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 10:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 11:00 | 2030 Initial | 383.79 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 12:00 | 2030 Initial | 373.71 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 13:00 | 2030 Initial | 419.7 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 16:00 | 2030 Initial | 700 | 343.52 | 510 | 510 | 0 | 0 | No
2030-02-04 17:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 18:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 23:00 | 2030 Initial | 700 | 439.9 | 510 | 510 | 0 | 0 | No
2030-02-05 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 04:00 | 2030 Initial | 444.22 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 05:00 | 2030 Initial | 24.22 | 300 | 466.89 | 300 | 0 | 0 | No
2030-02-05 06:00 | 2030 Initial | -395.78 | 0 | 166.89 | 0 | 0 | 0 | No
2030-02-05 07:00 | 2030 Initial | -280 | 0 | 230.33 | 0 | 0 | 0 | No
2030-02-05 08:00 | 2030 Initial | -700 | 0 | -69.67 | -78.31 | 0 | 0 | No
2030-02-05 09:00 | 2030 Initial | -280 | 300 | 230.33 | 221.69 | 0 | 0 | No
2030-02-05 10:00 | 2030 Initial | 140 | 0 | 176.44 | 0 | 0 | 0 | No
2030-02-05 11:00 | 2030 Initial | 0 | 0 | -53.41 | 0 | 0 | 0 | No
2030-02-05 12:00 | 2030 Initial | 0 | 0 | 0 | 35.67 | 0 | 0 | No
2030-02-05 13:00 | 2030 Initial | 0 | 0 | 101.75 | 59.64 | 0 | 0 | No
2030-02-05 14:00 | 2030 Initial | 0 | 0 | 236.36 | 36.95 | 0 | 0 | No
2030-02-05 15:00 | 2030 Initial | 0 | 0 | 43.38 | 65.01 | 0 | 0 | No
2030-02-05 16:00 | 2030 Initial | 139.4 | 0 | 161.96 | 0 | 0 | 0 | No
2030-02-05 17:00 | 2030 Initial | 0 | 300 | 210 | 286.95 | 0 | 0 | No
2030-02-05 18:00 | 2030 Initial | 0 | 0 | -90 | -13.05 | 0 | 0 | No
2030-02-05 19:00 | 2030 Initial | 379.12 | 0 | 210 | 71.08 | 0 | 0 | No
2030-02-05 20:00 | 2030 Initial | 700 | 300 | 510 | 371.08 | 0 | 0 | No
2030-02-05 21:00 | 2030 Initial | 700 | 0 | 510 | 244.66 | 0 | 0 | No
2030-02-05 22:00 | 2030 Initial | 280 | 0 | 323.28 | 210 | 0 | 0 | No
2030-02-05 23:00 | 2030 Initial | 190.83 | 40.62 | 510 | 510 | 0 | 0 | No
2030-02-06 | 2030 Initial | 140 | 0 | 510 | 510 | 0 | 0 | No
2030-02-06 01:00 | 2030 Initial | 560 | 0 | 510 | 419.05 | 0 | 0 | No
2030-02-06 02:00 | 2030 Initial | 140 | 0 | 510 | 421.19 | 0 | 0 | No
2030-02-06 03:00 | 2030 Initial | -280 | 0 | 510 | 498.33 | 0 | 0 | No
2030-02-06 04:00 | 2030 Initial | -700 | 0 | 510 | 385.86 | 0 | 0 | No
2030-02-06 05:00 | 2030 Initial | -700 | 106.09 | 210 | 85.86 | 0 | 0 | No
2030-02-06 06:00 | 2030 Initial | -700 | 0 | -90 | -214.14 | 0 | 0 | No
2030-02-06 07:00 | 2030 Initial | -700 | 4.19 | 0 | 0 | 0 | 0 | No
2030-02-06 08:00 | 2030 Initial | -280 | -295.81 | -300 | -300 | 0 | 0 | No
2030-02-06 09:00 | 2030 Initial | 140 | 0 | 0 | 0 | 0 | 0 | No
2030-02-06 10:00 | 2030 Initial | 560 | 0 | 0 | 0 | 0 | 0 | No
2030-02-06 11:00 | 2030 Initial | 700 | 0 | -238.27 | 0 | 0 | 0 | No
2030-02-06 12:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-02-06 13:00 | 2030 Initial | 700 | 0 | -501.54 | 0 | 0 | 0 | No
2030-02-06 14:00 | 2030 Initial | 700 | 0 | -501.54 | 0 | 0 | 0 | No
2030-02-06 15:00 | 2030 Initial | 700 | -226 | -510 | -210 | 0 | 0 | No
2030-02-06 16:00 | 2030 Initial | 513.21 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 17:00 | 2030 Initial | 93.21 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 18:00 | 2030 Initial | 280 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 19:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 20:00 | 2030 Initial | 398.54 | -226 | -510 | -302.67 | 0 | 0 | No
2030-02-06 21:00 | 2030 Initial | -21.46 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 22:00 | 2030 Initial | -265.59 | -226 | -510 | -373.42 | 0 | 0 | No
2030-02-06 23:00 | 2030 Initial | 0 | -169.17 | -510 | -387.04 | 0 | 0 | No
2030-02-07 | 2030 Initial | 0 | -198.99 | -510 | -103.13 | 0 | 0 | No
2030-02-07 01:00 | 2030 Initial | 0 | -295.3 | -510 | -53.55 | 0 | 0 | No
2030-02-07 02:00 | 2030 Initial | -141.64 | -526 | -510 | -11.29 | 0 | 0 | No
2030-02-07 03:00 | 2030 Initial | -561.64 | -526 | -510 | -311.29 | 0 | 0 | No
2030-02-07 04:00 | 2030 Initial | -303 | -526 | -510 | -215.88 | 0 | 0 | No
2030-02-07 05:00 | 2030 Initial | -700 | -526 | -510 | -88.21 | 0 | 0 | No
2030-02-07 06:00 | 2030 Initial | -700 | -526 | -510 | 211.79 | 0 | 0 | No
2030-02-07 07:00 | 2030 Initial | -700 | -526 | -510 | -88.21 | 0 | 0 | No
2030-02-07 08:00 | 2030 Initial | -700 | -226 | -510 | -213.15 | 0 | 0 | No
2030-02-07 09:00 | 2030 Initial | -700 | -63.68 | -510 | -286.62 | 0 | 0 | No
2030-02-07 10:00 | 2030 Initial | -700 | 0 | -510 | 0 | 0 | 0 | No
2030-02-07 11:00 | 2030 Initial | -700 | -130.8 | -510 | -87.99 | 0 | 0 | No
2030-02-07 12:00 | 2030 Initial | -700 | 0 | -508.77 | 0 | 0 | 0 | No
2030-02-07 13:00 | 2030 Initial | -700 | 0 | -295.44 | 217.55 | 0 | 0 | No
2030-02-07 14:00 | 2030 Initial | -700 | 0 | -70.59 | 78.31 | 0 | 0 | No
2030-02-07 15:00 | 2030 Initial | -700 | 300 | 229.41 | 378.31 | 0 | 0 | No
2030-02-07 16:00 | 2030 Initial | -700 | 0 | -70.59 | 78.31 | 0 | 0 | No
2030-02-07 17:00 | 2030 Initial | -700 | 0 | -370.59 | -214.72 | 0 | 0 | No
2030-02-07 18:00 | 2030 Initial | -700 | 0 | -390 | 0 | 0 | 0 | No
2030-02-07 19:00 | 2030 Initial | -280 | 0 | -90 | 0 | 0 | 0 | No
2030-02-07 20:00 | 2030 Initial | -506.76 | 205 | 210 | 210 | 0 | 0 | No
2030-02-07 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-07 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-07 23:00 | 2030 Initial | -627.86 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 | 2030 Initial | -682.7 | 505 | 510 | 510 | 0 | 0 | No
2030-02-08 01:00 | 2030 Initial | -640.99 | 505 | 510 | 510 | 0 | 0 | No
2030-02-08 02:00 | 2030 Initial | -591.32 | 505 | 510 | 510 | 0 | 0 | No
2030-02-08 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-08 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-08 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-08 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-08 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-08 08:00 | 2030 Initial | -700 | 505 | 510 | 478.93 | 0 | 0 | No
2030-02-08 09:00 | 2030 Initial | -700 | 205 | 412.97 | 178.93 | 0 | 0 | No
2030-02-08 10:00 | 2030 Initial | -700 | 505 | 510 | 478.93 | 0 | 0 | Yes
2030-02-08 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 16:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 17:00 | 2030 Initial | -700 | 372.34 | 510 | 419.62 | 0 | 0 | Yes
2030-02-08 18:00 | 2030 Initial | -700 | 72.34 | 210 | 119.62 | 0 | 0 | No
2030-02-08 19:00 | 2030 Initial | -280 | 372.34 | 510 | 419.62 | 0 | 0 | No
2030-02-08 20:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-02-08 21:00 | 2030 Initial | 211.41 | 505 | 510 | 510 | 0 | 0 | No
2030-02-08 22:00 | 2030 Initial | 267.2 | 505 | 510 | 510 | 0 | 0 | No
2030-02-08 23:00 | 2030 Initial | -152.8 | 505 | 510 | 510 | 0 | 0 | No
2030-02-09 | 2030 Initial | -572.8 | 505 | 510 | 510 | 0 | 0 | No
2030-02-09 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 06:00 | 2030 Initial | -700 | 505 | 510 | 507.52 | 0 | 0 | Yes
2030-02-09 07:00 | 2030 Initial | -700 | 505 | 510 | 207.52 | 0 | 0 | Yes
2030-02-09 08:00 | 2030 Initial | -700 | 300 | 300 | -92.48 | 0 | 0 | No
2030-02-09 09:00 | 2030 Initial | -652.7 | 0 | 0 | -392.48 | 0 | 0 | No
2030-02-09 10:00 | 2030 Initial | -700 | 0 | 0 | -114.8 | 0 | 0 | No
2030-02-09 11:00 | 2030 Initial | -700 | 0 | -210 | -115.41 | 0 | 0 | No
2030-02-09 12:00 | 2030 Initial | -512.26 | -300 | -510 | -415.41 | 0 | 0 | No
2030-02-09 13:00 | 2030 Initial | -700 | 0 | -510 | -351.69 | 0 | 0 | No
2030-02-09 14:00 | 2030 Initial | -700 | 0 | -285.43 | -51.69 | 0 | 0 | No
2030-02-09 15:00 | 2030 Initial | -700 | 0 | 14.57 | 85.28 | 0 | 0 | No
2030-02-09 16:00 | 2030 Initial | -700 | 0 | -168.1 | 0 | 0 | 0 | No
2030-02-09 17:00 | 2030 Initial | -700 | 0 | 0 | 0 | 0 | 0 | No
2030-02-09 18:00 | 2030 Initial | -700 | 0 | 0 | 0 | 0 | 0 | No
2030-02-09 19:00 | 2030 Initial | -700 | 300 | 300 | 300 | 0 | 0 | No
2030-02-09 20:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-09 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 | 2030 Initial | -700 | 505 | 510 | 446.61 | 0 | 0 | Yes
2030-02-10 01:00 | 2030 Initial | -700 | 505 | 510 | 225.43 | 0 | 0 | Yes
2030-02-10 02:00 | 2030 Initial | -700 | 505 | 510 | 232.68 | 0 | 0 | Yes
2030-02-10 03:00 | 2030 Initial | -700 | 505 | 510 | 388.87 | 0 | 0 | Yes
2030-02-10 04:00 | 2030 Initial | -700 | 505 | 510 | 372.57 | 0 | 0 | Yes
2030-02-10 05:00 | 2030 Initial | -700 | 505 | 510 | 108.74 | 0 | 0 | Yes
2030-02-10 06:00 | 2030 Initial | -700 | 505 | 510 | 76.22 | 0 | 0 | Yes
2030-02-10 07:00 | 2030 Initial | -700 | 505 | 510 | 253.37 | 0 | 0 | Yes
2030-02-10 08:00 | 2030 Initial | -700 | 505 | 510 | 396.91 | 0 | 0 | Yes
2030-02-10 09:00 | 2030 Initial | -700 | 505 | 510 | 208.71 | 0 | 0 | Yes
2030-02-10 10:00 | 2030 Initial | -700 | 505 | 510 | 366.42 | 0 | 0 | Yes
2030-02-10 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 12:00 | 2030 Initial | -700 | 505 | 510 | 304.69 | 0 | 0 | Yes
2030-02-10 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 15:00 | 2030 Initial | -700 | 505 | 510 | 271.29 | 0 | 0 | Yes
2030-02-10 16:00 | 2030 Initial | -700 | 505 | 510 | 460.24 | 0 | 0 | Yes
2030-02-10 17:00 | 2030 Initial | -700 | 505 | 510 | 350.86 | 0 | 0 | Yes
2030-02-10 18:00 | 2030 Initial | -700 | 505 | 510 | 468.33 | 0 | 0 | Yes
2030-02-10 19:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 20:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 22:00 | 2030 Initial | -700 | 505 | 510 | 461.88 | 0 | 0 | Yes
2030-02-10 23:00 | 2030 Initial | -700 | 505 | 510 | 319.32 | 0 | 0 | Yes
2030-02-11 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 01:00 | 2030 Initial | -700 | 505 | 510 | 400.7 | 0 | 0 | Yes
2030-02-11 02:00 | 2030 Initial | -700 | 505 | 510 | 265.58 | 0 | 0 | Yes
2030-02-11 03:00 | 2030 Initial | -700 | 505 | 510 | 224.46 | 0 | 0 | Yes
2030-02-11 04:00 | 2030 Initial | -700 | 505 | 510 | 261.17 | 0 | 0 | Yes
2030-02-11 05:00 | 2030 Initial | -700 | 505 | 510 | 359.23 | 0 | 0 | Yes
2030-02-11 06:00 | 2030 Initial | -700 | 505 | 510 | 320.67 | 0 | 0 | Yes
2030-02-11 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-11 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-11 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 16:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 17:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 18:00 | 2030 Initial | 132.7 | 505 | 510 | 510 | 0 | 0 | No
2030-02-11 19:00 | 2030 Initial | 552.7 | 505 | 510 | 510 | 0 | 0 | No
2030-02-11 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-11 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-11 22:00 | 2030 Initial | 631.09 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 23:00 | 2030 Initial | 211.09 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 | 2030 Initial | 631.09 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 03:00 | 2030 Initial | 657.69 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 04:00 | 2030 Initial | 237.69 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 05:00 | 2030 Initial | -182.31 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 06:00 | 2030 Initial | -602.31 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 07:00 | 2030 Initial | -246.41 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 08:00 | 2030 Initial | 173.59 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 09:00 | 2030 Initial | 593.59 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 10:00 | 2030 Initial | 237.83 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 11:00 | 2030 Initial | -138.74 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 12:00 | 2030 Initial | -164.12 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 13:00 | 2030 Initial | 255.88 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 14:00 | 2030 Initial | 675.88 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 15:00 | 2030 Initial | 255.88 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 16:00 | 2030 Initial | -164.12 | 428.58 | 510 | 510 | 0 | 0 | No
2030-02-12 17:00 | 2030 Initial | -584.12 | 428.58 | 510 | 510 | 0 | 0 | No
2030-02-12 18:00 | 2030 Initial | -700 | 300 | 510 | 510 | 0 | 0 | No
2030-02-12 19:00 | 2030 Initial | -280 | 0 | 210 | 510 | 0 | 0 | No
2030-02-12 20:00 | 2030 Initial | 5.13 | -300 | -90 | 230.6 | 0 | 0 | No
2030-02-12 21:00 | 2030 Initial | -353.42 | -300 | -90 | 303.19 | 0 | 0 | No
2030-02-12 22:00 | 2030 Initial | 66.58 | 0 | 210 | 3.19 | 0 | 0 | No
2030-02-12 23:00 | 2030 Initial | 0.77 | 300 | 510 | 303.19 | 0 | 0 | Yes
2030-02-13 | 2030 Initial | 420.77 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 01:00 | 2030 Initial | 700 | 505 | 510 | 433.32 | 0 | 0 | Yes
2030-02-13 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 03:00 | 2030 Initial | 700 | 505 | 510 | 263.89 | 0 | 0 | Yes
2030-02-13 04:00 | 2030 Initial | 700 | 505 | 510 | 250.95 | 0 | 0 | Yes
2030-02-13 05:00 | 2030 Initial | 700 | 505 | 510 | 330.14 | 0 | 0 | Yes
2030-02-13 06:00 | 2030 Initial | 700 | 505 | 510 | 417.5 | 0 | 0 | Yes
2030-02-13 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 08:00 | 2030 Initial | 700 | 300 | 341.88 | 301.85 | 0 | 0 | No
2030-02-13 09:00 | 2030 Initial | 700 | 0 | 41.88 | 1.85 | 0 | 0 | No
2030-02-13 10:00 | 2030 Initial | 698.94 | -300 | -258.12 | 301.85 | 0 | 0 | No
2030-02-13 11:00 | 2030 Initial | 461.3 | -526 | -510 | 332.85 | 0 | 0 | No
2030-02-13 12:00 | 2030 Initial | 700 | -526 | -510 | 32.85 | 0 | 0 | No
2030-02-13 13:00 | 2030 Initial | 280 | -526 | -510 | -267.15 | 0 | 0 | No
2030-02-13 14:00 | 2030 Initial | 628.62 | -385.62 | -390.27 | 30.44 | 0 | 0 | No
2030-02-13 15:00 | 2030 Initial | 700 | -85.62 | -90.27 | 330.44 | 0 | 0 | No
2030-02-13 16:00 | 2030 Initial | 700 | 99.55 | 209.73 | 510 | 0 | 0 | No
2030-02-13 17:00 | 2030 Initial | 700 | 205 | 509.73 | 510 | 0 | 0 | No
2030-02-13 18:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-13 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-13 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-13 21:00 | 2030 Initial | 700 | 501 | 510 | 510 | 0 | 0 | No
2030-02-13 22:00 | 2030 Initial | 668.15 | 201 | 210 | 402.13 | 0 | 0 | No
2030-02-13 23:00 | 2030 Initial | 248.15 | -99 | -90 | 102.13 | 0 | 0 | No
2030-02-14 | 2030 Initial | 140 | -279.89 | -390 | -185.21 | 0 | 0 | No
2030-02-14 01:00 | 2030 Initial | -280 | -298.8 | -510 | -0.3 | 0 | 0 | No
2030-02-14 02:00 | 2030 Initial | -700 | -526 | -510 | -106.26 | 0 | 0 | No
2030-02-14 03:00 | 2030 Initial | -700 | -526 | -510 | -146.97 | 0 | 0 | No
2030-02-14 04:00 | 2030 Initial | -700 | -526 | -510 | -107.87 | 0 | 0 | No
2030-02-14 05:00 | 2030 Initial | -700 | -526 | -510 | -344.16 | 0 | 0 | No
2030-02-14 06:00 | 2030 Initial | -700 | -526 | -510 | -500.98 | 0 | 0 | No
2030-02-14 07:00 | 2030 Initial | -700 | -306.98 | -510 | -483.23 | 0 | 0 | No
2030-02-14 08:00 | 2030 Initial | -700 | -6.98 | -210 | -183.23 | 0 | 0 | No
2030-02-14 09:00 | 2030 Initial | -700 | 293.02 | 90 | 116.77 | 0 | 0 | No
2030-02-14 10:00 | 2030 Initial | -700 | 505 | 390 | 416.77 | 0 | 0 | Yes
2030-02-14 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-14 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 16:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-14 17:00 | 2030 Initial | -700 | 205 | 411.5 | 210 | 0 | 0 | No
2030-02-14 18:00 | 2030 Initial | -515.07 | 505 | 510 | 510 | 0 | 0 | No
2030-02-14 19:00 | 2030 Initial | -95.07 | 505 | 510 | 510 | 0 | 0 | No
2030-02-14 20:00 | 2030 Initial | 324.93 | 505 | 510 | 510 | 0 | 0 | No
2030-02-14 21:00 | 2030 Initial | 352.65 | 346.53 | 510 | 510 | 0 | 0 | No
2030-02-14 22:00 | 2030 Initial | -67.35 | 205 | 466.33 | 329.24 | 0 | 0 | No
2030-02-14 23:00 | 2030 Initial | -276.91 | 505 | 510 | 510 | 0 | 0 | No
2030-02-15 | 2030 Initial | -669.58 | 505 | 510 | 510 | 0 | 0 | No
2030-02-15 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 13:00 | 2030 Initial | -700 | 300 | 510 | 510 | 0 | 0 | Yes
2030-02-15 14:00 | 2030 Initial | -280 | 0 | 263.92 | 210 | 0 | 0 | No
2030-02-15 15:00 | 2030 Initial | -336.67 | 300 | 300 | 300 | 0 | 0 | No
2030-02-15 16:00 | 2030 Initial | 83.33 | 0 | 0 | 0 | 0 | 0 | No
2030-02-15 17:00 | 2030 Initial | 503.33 | -300 | -300 | 256.72 | 0 | 0 | No
2030-02-15 18:00 | 2030 Initial | 700 | -344.52 | -510 | 150.28 | 0 | 0 | No
2030-02-15 19:00 | 2030 Initial | 700 | -88.5 | -210 | 450.28 | 0 | 0 | No
2030-02-15 20:00 | 2030 Initial | 280 | 181.28 | 90 | 420.52 | 0 | 0 | No
2030-02-15 21:00 | 2030 Initial | -140 | 481.28 | 390 | 510 | 0 | 0 | No
2030-02-15 22:00 | 2030 Initial | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-02-15 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 01:00 | 2030 Initial | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-02-16 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 03:00 | 2030 Initial | -700 | 505 | 510 | 346.77 | 0 | 0 | Yes
2030-02-16 04:00 | 2030 Initial | -700 | 505 | 510 | 108.26 | 0 | 0 | Yes
2030-02-16 05:00 | 2030 Initial | -700 | 505 | 510 | 297.84 | 0 | 0 | Yes
2030-02-16 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 15:00 | 2030 Initial | -700 | 505 | 510 | 393.07 | 0 | 0 | Yes
2030-02-16 16:00 | 2030 Initial | -700 | 505 | 303 | 157.98 | 0 | 0 | Yes
2030-02-16 17:00 | 2030 Initial | -700 | 205 | 3 | -142.02 | 0 | 0 | No
2030-02-16 18:00 | 2030 Initial | -700 | -95 | -297 | -442.02 | 0 | 0 | No
2030-02-16 19:00 | 2030 Initial | -700 | 205 | 3 | -142.02 | 0 | 0 | No
2030-02-16 20:00 | 2030 Initial | -700 | 505 | 303 | 157.98 | 0 | 0 | No
2030-02-16 21:00 | 2030 Initial | -700 | 505 | 510 | 457.98 | 0 | 0 | Yes
2030-02-16 22:00 | 2030 Initial | -700 | 505 | 510 | 328.18 | 0 | 0 | Yes
2030-02-16 23:00 | 2030 Initial | -700 | 505 | 510 | 237.37 | 0 | 0 | Yes
2030-02-17 | 2030 Initial | -700 | 505 | 510 | 345.14 | 0 | 0 | Yes
2030-02-17 01:00 | 2030 Initial | -700 | 505 | 510 | 148.5 | 0 | 0 | Yes
2030-02-17 02:00 | 2030 Initial | -700 | 505 | 510 | 237.64 | 0 | 0 | Yes
2030-02-17 03:00 | 2030 Initial | -700 | 505 | 510 | 166.65 | 0 | 0 | Yes
2030-02-17 04:00 | 2030 Initial | -700 | 505 | 510 | 350.92 | 0 | 0 | Yes
2030-02-17 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 16:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 17:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 18:00 | 2030 Initial | -420 | 505 | 510 | 510 | 0 | 0 | No
2030-02-17 19:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-02-17 20:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-02-17 21:00 | 2030 Initial | -226.12 | 505 | 510 | 510 | 0 | 0 | No
2030-02-17 22:00 | 2030 Initial | -646.12 | 505 | 510 | 510 | 0 | 0 | No
2030-02-17 23:00 | 2030 Initial | -700 | 505 | 510 | 393.01 | 0 | 0 | Yes
2030-02-18 | 2030 Initial | -511.11 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 07:00 | 2030 Initial | -666.44 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 10:00 | 2030 Initial | -559.63 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 16:00 | 2030 Initial | -374.77 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 17:00 | 2030 Initial | 45.23 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 18:00 | 2030 Initial | 465.23 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 05:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 06:00 | 2030 Initial | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 07:00 | 2030 Initial | -560 | 205 | 210 | 510 | 0 | 0 | No
2030-02-19 08:00 | 2030 Initial | -160.4 | -95 | -90 | 474.63 | 0 | 0 | No
2030-02-19 09:00 | 2030 Initial | -194.73 | -95 | -90 | 412.2 | 0 | 0 | No
2030-02-19 10:00 | 2030 Initial | -451.04 | 205 | 210 | 457.14 | 0 | 0 | No
2030-02-19 11:00 | 2030 Initial | -31.04 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 12:00 | 2030 Initial | -225.22 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 13:00 | 2030 Initial | -645.22 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 15:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 16:00 | 2030 Initial | -233.98 | 303.15 | 510 | 510 | 0 | 0 | No
2030-02-19 17:00 | 2030 Initial | 0 | 3.15 | 210 | 326.03 | 0 | 0 | No
2030-02-19 18:00 | 2030 Initial | 154.35 | -95 | -90 | 193.23 | 0 | 0 | No
2030-02-19 19:00 | 2030 Initial | 299.82 | 205 | 210 | 493.23 | 0 | 0 | No
2030-02-19 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 23:00 | 2030 Initial | 604.77 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 04:00 | 2030 Initial | 661.72 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 05:00 | 2030 Initial | 241.72 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 06:00 | 2030 Initial | -178.28 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 07:00 | 2030 Initial | -598.28 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 08:00 | 2030 Initial | -240.72 | 205 | 510 | 298.04 | 0 | 0 | No
2030-02-20 09:00 | 2030 Initial | 179.28 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 10:00 | 2030 Initial | -240.72 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 11:00 | 2030 Initial | -660.72 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 16:00 | 2030 Initial | -700 | 300 | 510 | 510 | 0 | 0 | Yes
2030-02-20 17:00 | 2030 Initial | -280 | 0 | 510 | 355.57 | 0 | 0 | No
2030-02-20 18:00 | 2030 Initial | 140 | 0 | 510 | 55.57 | 0 | 0 | No
2030-02-20 19:00 | 2030 Initial | 560 | 205 | 483.62 | 210 | 0 | 0 | No
2030-02-20 20:00 | 2030 Initial | 423.81 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 21:00 | 2030 Initial | 3.81 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 22:00 | 2030 Initial | -365.54 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-21 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 16:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 17:00 | 2030 Initial | -700 | 300 | 341.21 | 300 | 0 | 0 | No
2030-02-21 18:00 | 2030 Initial | -700 | 0 | 41.21 | 0 | 0 | 0 | No
2030-02-21 19:00 | 2030 Initial | -602.89 | 135.08 | 210 | 126.86 | 0 | 0 | No
2030-02-21 20:00 | 2030 Initial | -700 | 435.08 | 510 | 426.86 | 0 | 0 | No
2030-02-21 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 23:00 | 2030 Initial | -700 | 505 | 510 | 374.47 | 0 | 0 | Yes
2030-02-22 | 2030 Initial | -700 | 505 | 510 | 426.61 | 0 | 0 | Yes
2030-02-22 01:00 | 2030 Initial | -700 | 505 | 510 | 437.03 | 0 | 0 | Yes
2030-02-22 02:00 | 2030 Initial | -700 | 505 | 510 | 392.51 | 0 | 0 | Yes
2030-02-22 03:00 | 2030 Initial | -700 | 505 | 510 | 309.51 | 0 | 0 | Yes
2030-02-22 04:00 | 2030 Initial | -700 | 505 | 510 | 180.16 | 0 | 0 | Yes
2030-02-22 05:00 | 2030 Initial | -700 | 505 | 510 | 145.17 | 0 | 0 | Yes
2030-02-22 06:00 | 2030 Initial | -700 | 505 | 510 | 312.48 | 0 | 0 | Yes
2030-02-22 07:00 | 2030 Initial | -700 | 505 | 510 | 337.88 | 0 | 0 | Yes
2030-02-22 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 15:00 | 2030 Initial | -695.57 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 16:00 | 2030 Initial | -439.81 | 505 | 510 | 281.71 | 0 | 0 | Yes
2030-02-22 17:00 | 2030 Initial | -580.35 | 205 | 210 | -18.29 | 0 | 0 | No
2030-02-22 18:00 | 2030 Initial | -160.35 | 0 | 0 | 0 | 0 | 0 | No
2030-02-22 19:00 | 2030 Initial | 259.65 | 0 | 0 | 251.63 | 0 | 0 | No
2030-02-22 20:00 | 2030 Initial | 679.65 | 205 | 243.25 | 510 | 0 | 0 | No
2030-02-22 21:00 | 2030 Initial | 443.03 | 505 | 510 | 510 | 0 | 0 | No
2030-02-22 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-22 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 05:00 | 2030 Initial | 632.22 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 06:00 | 2030 Initial | 212.22 | 205 | 210 | 416.04 | 0 | 0 | No
2030-02-23 07:00 | 2030 Initial | -207.78 | -95 | -90 | 408.62 | 0 | 0 | No
2030-02-23 08:00 | 2030 Initial | -75.09 | -395 | -390 | 108.62 | 0 | 0 | No
2030-02-23 09:00 | 2030 Initial | 280 | -95 | -90 | 0 | 0 | 0 | No
2030-02-23 10:00 | 2030 Initial | 700 | 205 | 210 | 300 | 0 | 0 | No
2030-02-23 11:00 | 2030 Initial | 533.88 | 505 | 510 | 225.69 | 0 | 0 | No
2030-02-23 12:00 | 2030 Initial | 113.88 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-23 13:00 | 2030 Initial | 404.62 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-23 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-23 15:00 | 2030 Initial | 700 | 505 | 510 | 383.64 | 0 | 0 | No
2030-02-23 16:00 | 2030 Initial | 700 | 205 | 210 | 83.64 | 0 | 0 | No
2030-02-23 17:00 | 2030 Initial | 700 | 237.33 | 510 | 184.45 | 0 | 0 | No
2030-02-23 18:00 | 2030 Initial | 700 | 505 | 510 | 484.45 | 0 | 0 | No
2030-02-23 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 20:00 | 2030 Initial | 700 | 435.69 | 510 | 510 | 0 | 0 | No
2030-02-23 21:00 | 2030 Initial | 280 | 135.69 | 210 | 457.06 | 0 | 0 | No
2030-02-23 22:00 | 2030 Initial | -140 | 0 | -5.29 | 449.71 | 0 | 0 | No
2030-02-23 23:00 | 2030 Initial | 229.87 | -300 | -305.29 | 383.82 | 0 | 0 | No
2030-02-24 | 2030 Initial | -9.42 | -272.75 | -510 | 115.81 | 0 | 0 | No
2030-02-24 01:00 | 2030 Initial | -429.42 | -526 | -510 | -184.19 | 0 | 0 | No
2030-02-24 02:00 | 2030 Initial | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-02-24 03:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-24 04:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-24 05:00 | 2030 Initial | -700 | -226 | -254.83 | -510 | 0 | 0 | No
2030-02-24 06:00 | 2030 Initial | -700 | 74 | 45.17 | -210 | 0 | 0 | Yes
2030-02-24 07:00 | 2030 Initial | -700 | 374 | 345.17 | 90 | 0 | 0 | Yes
2030-02-24 08:00 | 2030 Initial | -700 | 409.07 | 510 | 390 | 0 | 0 | Yes
2030-02-24 09:00 | 2030 Initial | -700 | 109.07 | 210 | 210 | 0 | 0 | No
2030-02-24 10:00 | 2030 Initial | -413.46 | 0 | 0 | 510 | 0 | 0 | No
2030-02-24 11:00 | 2030 Initial | -541.18 | 0 | 0 | 510 | 0 | 0 | No
2030-02-24 12:00 | 2030 Initial | -653.7 | 0 | 0 | 473.25 | 0 | 0 | No
2030-02-24 13:00 | 2030 Initial | -370.81 | -300 | -300 | 510 | 0 | 0 | No
2030-02-24 14:00 | 2030 Initial | -700 | 0 | -42.85 | 210 | 0 | 0 | No
2030-02-24 15:00 | 2030 Initial | -700 | 0 | -193.06 | 0 | 0 | 0 | No
2030-02-24 16:00 | 2030 Initial | -590.96 | 0 | 0 | -13.95 | 0 | 0 | No
2030-02-24 17:00 | 2030 Initial | -420 | -227.23 | -300 | -313.95 | 0 | 0 | No
2030-02-24 18:00 | 2030 Initial | 0 | 0 | 0 | -13.95 | 0 | 0 | No
2030-02-24 19:00 | 2030 Initial | 420 | 0 | 114.85 | 244.56 | 0 | 0 | No
2030-02-24 20:00 | 2030 Initial | 700 | 0 | 181.82 | 66.7 | 0 | 0 | No
2030-02-24 21:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-02-24 22:00 | 2030 Initial | 323.46 | 505 | 510 | 510 | 0 | 0 | No
2030-02-24 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 04:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 05:00 | 2030 Initial | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 06:00 | 2030 Initial | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 07:00 | 2030 Initial | -440.86 | 205 | 210 | 232.12 | 0 | 0 | No
2030-02-25 08:00 | 2030 Initial | -20.86 | 0 | -68.31 | 336.17 | 0 | 0 | No
2030-02-25 09:00 | 2030 Initial | 399.14 | 0 | -368.31 | 510 | 0 | 0 | No
2030-02-25 10:00 | 2030 Initial | 188.49 | -226 | -510 | 340.39 | 0 | 0 | No
2030-02-25 11:00 | 2030 Initial | -231.51 | -526 | -510 | 462.35 | 0 | 0 | No
2030-02-25 12:00 | 2030 Initial | -120.46 | -526 | -510 | 450.76 | 0 | 0 | No
2030-02-25 13:00 | 2030 Initial | 47.16 | -526 | -510 | 302.27 | 0 | 0 | No
2030-02-25 14:00 | 2030 Initial | 171.06 | -526 | -510 | 124.72 | 0 | 0 | No
2030-02-25 15:00 | 2030 Initial | 591.06 | -526 | -510 | 424.72 | 0 | 0 | No
2030-02-25 16:00 | 2030 Initial | 171.06 | -526 | -510 | 510 | 0 | 0 | No
2030-02-25 17:00 | 2030 Initial | 416.57 | -349.15 | -510 | 210 | 0 | 0 | No
2030-02-25 18:00 | 2030 Initial | 700 | -49.15 | -510 | 417.88 | 0 | 0 | No
2030-02-25 19:00 | 2030 Initial | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-02-25 20:00 | 2030 Initial | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-02-25 21:00 | 2030 Initial | 496.9 | -300 | -510 | 510 | 0 | 0 | No
2030-02-25 22:00 | 2030 Initial | 280 | -300 | -391.11 | 510 | 0 | 0 | No
2030-02-25 23:00 | 2030 Initial | 700 | 0 | -91.11 | 510 | 0 | 0 | No
2030-02-26 | 2030 Initial | 700 | 0 | 208.89 | 436.44 | 0 | 0 | No
2030-02-26 01:00 | 2030 Initial | 700 | 205 | 508.89 | 510 | 0 | 0 | No
2030-02-26 02:00 | 2030 Initial | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-02-26 03:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-02-26 04:00 | 2030 Initial | -280 | 222.11 | 210 | 210 | 0 | 0 | No
2030-02-26 05:00 | 2030 Initial | -700 | -77.89 | -90 | -90 | 0 | 0 | No
2030-02-26 06:00 | 2030 Initial | -700 | -264.65 | -390 | -300 | 0 | 0 | No
2030-02-26 07:00 | 2030 Initial | -700 | -176.06 | -90 | 0 | 0 | 0 | No
2030-02-26 08:00 | 2030 Initial | -280 | 123.94 | 210 | 300 | 0 | 0 | No
2030-02-26 09:00 | 2030 Initial | 140 | 0 | 43.55 | 379.9 | 0 | 0 | No
2030-02-26 10:00 | 2030 Initial | 310.19 | -300 | -256.45 | 79.9 | 0 | 0 | No
2030-02-26 11:00 | 2030 Initial | 0 | -64.48 | -510 | 32.46 | 0 | 0 | No
2030-02-26 12:00 | 2030 Initial | 0 | -10.29 | -510 | -151.55 | 0 | 0 | No
2030-02-26 13:00 | 2030 Initial | 0 | -118.84 | -510 | -223.3 | 0 | 0 | No
2030-02-26 14:00 | 2030 Initial | 10.98 | 0 | -390 | -200 | 0 | 0 | No
2030-02-26 15:00 | 2030 Initial | 430.98 | 0 | -90 | -49.81 | 0 | 0 | No
2030-02-26 16:00 | 2030 Initial | 424.56 | 205 | 210 | 210 | 0 | 0 | No
2030-02-26 17:00 | 2030 Initial | 47.06 | 505 | 510 | 510 | 0 | 0 | No
2030-02-26 18:00 | 2030 Initial | 467.06 | 301.8 | 510 | 510 | 0 | 0 | No
2030-02-26 19:00 | 2030 Initial | 700 | 1.8 | 510 | 510 | 0 | 0 | No
2030-02-26 20:00 | 2030 Initial | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-02-26 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-26 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-26 23:00 | 2030 Initial | 700 | 205 | 510 | 453.35 | 0 | 0 | No
2030-02-27 | 2030 Initial | 700 | 138.51 | 510 | 498.02 | 0 | 0 | No
2030-02-27 01:00 | 2030 Initial | 700 | 182.29 | 510 | 467.53 | 0 | 0 | No
2030-02-27 02:00 | 2030 Initial | 700 | 0 | 430.89 | 167.53 | 0 | 0 | No
2030-02-27 03:00 | 2030 Initial | 700 | 0 | 300 | 107.67 | 0 | 0 | No
2030-02-27 04:00 | 2030 Initial | 700 | 0 | 0 | -59.14 | 0 | 0 | No
2030-02-27 05:00 | 2030 Initial | 696.25 | 0 | -300 | -116.83 | 0 | 0 | No
2030-02-27 06:00 | 2030 Initial | 276.25 | 0 | 0 | 0 | 0 | 0 | No
2030-02-27 07:00 | 2030 Initial | 579.35 | 0 | 141.64 | 0 | 0 | 0 | No
2030-02-27 08:00 | 2030 Initial | 700 | 144.59 | 441.64 | 300 | 0 | 0 | No
2030-02-27 09:00 | 2030 Initial | 700 | 0 | 229.14 | 116.26 | 0 | 0 | No
2030-02-27 10:00 | 2030 Initial | 280 | 0 | -33.86 | 0 | 0 | 0 | No
2030-02-27 11:00 | 2030 Initial | -140 | -17.47 | -333.86 | -25.67 | 0 | 0 | No
2030-02-27 12:00 | 2030 Initial | -560 | -95 | -90 | -90 | 0 | 0 | No
2030-02-27 13:00 | 2030 Initial | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-02-27 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-27 15:00 | 2030 Initial | -280 | 205 | 405.7 | 210 | 0 | 0 | No
2030-02-27 16:00 | 2030 Initial | 140 | 205 | 468.63 | 184.24 | 0 | 0 | No
2030-02-27 17:00 | 2030 Initial | 560 | 505 | 510 | 484.24 | 0 | 0 | No
2030-02-27 18:00 | 2030 Initial | 140 | 205 | 510 | 188.39 | 0 | 0 | No
2030-02-27 19:00 | 2030 Initial | -254.87 | 205 | 210 | 210 | 0 | 0 | No
2030-02-27 20:00 | 2030 Initial | 103.59 | 505 | 510 | 510 | 0 | 0 | No
2030-02-27 21:00 | 2030 Initial | -316.41 | 505 | 510 | 510 | 0 | 0 | No
2030-02-27 22:00 | 2030 Initial | 0 | 300 | 456.07 | 510 | 0 | 0 | No
2030-02-27 23:00 | 2030 Initial | -9.29 | 0 | 156.07 | 210 | 0 | 0 | No
2030-02-28 | 2030 Initial | 0 | -162.04 | -143.93 | -70.42 | 0 | 0 | No
2030-02-28 01:00 | 2030 Initial | 251.13 | 0 | -102.02 | 229.58 | 0 | 0 | No
2030-02-28 02:00 | 2030 Initial | 0 | 0 | -402.02 | 183.83 | 0 | 0 | No
2030-02-28 03:00 | 2030 Initial | 0 | 0 | -232.23 | 115.46 | 0 | 0 | No
2030-02-28 04:00 | 2030 Initial | -290.13 | 0 | -415.46 | 158.2 | 0 | 0 | No
2030-02-28 05:00 | 2030 Initial | -700 | 0 | -281.32 | 75 | 0 | 0 | No
2030-02-28 06:00 | 2030 Initial | -700 | -32.15 | -510 | -225 | 0 | 0 | No
2030-02-28 07:00 | 2030 Initial | -700 | -332.15 | -510 | -107.14 | 0 | 0 | No
2030-02-28 08:00 | 2030 Initial | -333.67 | -526 | -510 | -407.14 | 0 | 0 | No
2030-02-28 09:00 | 2030 Initial | -35.7 | -526 | -510 | -510 | 0 | 0 | No
2030-02-28 10:00 | 2030 Initial | 0 | -226 | -510 | -294.93 | 0 | 0 | No
2030-02-28 11:00 | 2030 Initial | -160.68 | -300 | -390 | -85.91 | 0 | 0 | No
2030-02-28 12:00 | 2030 Initial | -140 | 0 | -90 | 214.09 | 0 | 0 | No
2030-02-28 13:00 | 2030 Initial | 280 | 221.05 | 210 | 510 | 0 | 0 | No
2030-02-28 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-28 15:00 | 2030 Initial | 700 | 505 | 390 | 510 | 0 | 0 | No
2030-02-28 16:00 | 2030 Initial | 280 | 205 | 90 | 210 | 0 | 0 | No
2030-02-28 17:00 | 2030 Initial | 700 | 0 | -210 | 183.66 | 0 | 0 | No
2030-02-28 18:00 | 2030 Initial | 700 | 0 | -510 | 483.66 | 0 | 0 | No
2030-02-28 19:00 | 2030 Initial | 700 | -126.34 | -510 | 356.63 | 0 | 0 | No
2030-02-28 20:00 | 2030 Initial | 700 | -235.98 | -510 | 166.52 | 0 | 0 | No
2030-02-28 21:00 | 2030 Initial | 700 | -149.35 | -210 | 390.39 | 0 | 0 | No
2030-02-28 22:00 | 2030 Initial | 526.75 | 150.65 | 90 | 210 | 0 | 0 | No
2030-02-28 23:00 | 2030 Initial | 106.75 | 450.65 | 390 | 510 | 0 | 0 | No
2030-03-01 | 2030 Initial | -313.25 | 505 | 510 | 399.51 | 0 | 0 | Yes
2030-03-01 01:00 | 2030 Initial | -700 | 505 | 510 | 162.02 | 0 | 0 | Yes
2030-03-01 02:00 | 2030 Initial | -700 | 505 | 510 | 347.93 | 0 | 0 | Yes
2030-03-01 03:00 | 2030 Initial | -700 | 505 | 510 | 244.13 | 0 | 0 | Yes
2030-03-01 04:00 | 2030 Initial | -700 | 505 | 510 | 31.02 | 0 | 0 | Yes
2030-03-01 05:00 | 2030 Initial | -700 | 505 | 510 | 75.68 | 0 | 0 | Yes
2030-03-01 06:00 | 2030 Initial | -700 | 505 | 510 | 91.67 | 0 | 0 | Yes
2030-03-01 07:00 | 2030 Initial | -700 | 505 | 510 | 316.88 | 0 | 0 | Yes
2030-03-01 08:00 | 2030 Initial | -700 | 505 | 510 | 342.31 | 0 | 0 | Yes
2030-03-01 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-01 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-01 16:00 | 2030 Initial | -529.37 | 505 | 510 | 510 | 0 | 0 | No
2030-03-01 17:00 | 2030 Initial | -109.37 | 379.53 | 510 | 510 | 0 | 0 | No
2030-03-01 18:00 | 2030 Initial | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-03-01 19:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-01 20:00 | 2030 Initial | 700 | 320.89 | 510 | 510 | 0 | 0 | No
2030-03-01 21:00 | 2030 Initial | 700 | 20.89 | 510 | 510 | 0 | 0 | No
2030-03-01 22:00 | 2030 Initial | 700 | 4 | 510 | 390.17 | 0 | 0 | No
2030-03-01 23:00 | 2030 Initial | 700 | 205 | 419.05 | 509.13 | 0 | 0 | No
2030-03-02 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-02 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-02 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-02 03:00 | 2030 Initial | 700 | 300 | 300 | 510 | 0 | 0 | No
2030-03-02 04:00 | 2030 Initial | 280 | 0 | 0 | 235.85 | 0 | 0 | No
2030-03-02 05:00 | 2030 Initial | 140 | 0 | -244.01 | 48.51 | 0 | 0 | No
2030-03-02 06:00 | 2030 Initial | -280 | 0 | -488.36 | 0 | 0 | 0 | No
2030-03-02 07:00 | 2030 Initial | -700 | -92.96 | -311.63 | 0 | 0 | 0 | No
2030-03-02 08:00 | 2030 Initial | -700 | -392.96 | -510 | -171.19 | 0 | 0 | No
2030-03-02 09:00 | 2030 Initial | -586.59 | -92.96 | -212.37 | 128.81 | 0 | 0 | No
2030-03-02 10:00 | 2030 Initial | -700 | -226 | -210 | 27.9 | 0 | 0 | No
2030-03-02 11:00 | 2030 Initial | -700 | -526 | -510 | -272.1 | 0 | 0 | No
2030-03-02 12:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-02 13:00 | 2030 Initial | -700 | -526 | -510 | -384.6 | 0 | 0 | No
2030-03-02 14:00 | 2030 Initial | -700 | -526 | -510 | -202.45 | 0 | 0 | No
2030-03-02 15:00 | 2030 Initial | -700 | -526 | -510 | -376.36 | 0 | 0 | No
2030-03-02 16:00 | 2030 Initial | -314.1 | -526 | -510 | -205.99 | 0 | 0 | No
2030-03-02 17:00 | 2030 Initial | -106.17 | -226 | -210 | 19.92 | 0 | 0 | No
2030-03-02 18:00 | 2030 Initial | -526.17 | -526 | -510 | -219.26 | 0 | 0 | No
2030-03-02 19:00 | 2030 Initial | -106.17 | -226 | -210 | 80.74 | 0 | 0 | No
2030-03-02 20:00 | 2030 Initial | 313.83 | 0 | 0 | 170.25 | 0 | 0 | No
2030-03-02 21:00 | 2030 Initial | 700 | 0 | -243.64 | 262.39 | 0 | 0 | No
2030-03-02 22:00 | 2030 Initial | 395.65 | -300 | -510 | 227.81 | 0 | 0 | No
2030-03-02 23:00 | 2030 Initial | 392.11 | -471.85 | -510 | 41.3 | 0 | 0 | No
2030-03-03 | 2030 Initial | 116.11 | -171.85 | -300 | -28.21 | 0 | 0 | No
2030-03-03 01:00 | 2030 Initial | 536.11 | 0 | 0 | 0 | 0 | 0 | No
2030-03-03 02:00 | 2030 Initial | 318.29 | 0 | 300 | 186.74 | 0 | 0 | No
2030-03-03 03:00 | 2030 Initial | 0 | 0 | 90 | 9.34 | 0 | 0 | No
2030-03-03 04:00 | 2030 Initial | 346.09 | 0 | -210 | -189.2 | 0 | 0 | No
2030-03-03 05:00 | 2030 Initial | 0 | -76.64 | -510 | -489.2 | 0 | 0 | No
2030-03-03 06:00 | 2030 Initial | 20.37 | -300 | -510 | -466.15 | 0 | 0 | No
2030-03-03 07:00 | 2030 Initial | -265.43 | 0 | -362.62 | -166.15 | 0 | 0 | No
2030-03-03 08:00 | 2030 Initial | -90 | 0 | -192.14 | -355.99 | 0 | 0 | No
2030-03-03 09:00 | 2030 Initial | 318.13 | 0 | -492.14 | -55.99 | 0 | 0 | No
2030-03-03 10:00 | 2030 Initial | -101.87 | -300 | -510 | -355.99 | 0 | 0 | No
2030-03-03 11:00 | 2030 Initial | -521.87 | -526 | -510 | -510 | 0 | 0 | No
2030-03-03 12:00 | 2030 Initial | -431.67 | -526 | -510 | -510 | 0 | 0 | No
2030-03-03 13:00 | 2030 Initial | -11.67 | -226 | -510 | -510 | 0 | 0 | No
2030-03-03 14:00 | 2030 Initial | 64.35 | -526 | -510 | -510 | 0 | 0 | No
2030-03-03 15:00 | 2030 Initial | 484.35 | -226 | -401.84 | -210 | 0 | 0 | No
2030-03-03 16:00 | 2030 Initial | 700 | -82.74 | -101.84 | -51.13 | 0 | 0 | No
2030-03-03 17:00 | 2030 Initial | 700 | 0 | 198.16 | 248.87 | 0 | 0 | No
2030-03-03 18:00 | 2030 Initial | 700 | 0 | 251.67 | 0 | 0 | 0 | No
2030-03-03 19:00 | 2030 Initial | 700 | 205 | 346.37 | 210 | 0 | 0 | No
2030-03-03 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-03 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-03 22:00 | 2030 Initial | 700 | 495.54 | 510 | 510 | 0 | 0 | No
2030-03-03 23:00 | 2030 Initial | 700 | 195.54 | 510 | 270.68 | 0 | 0 | No
2030-03-04 | 2030 Initial | 700 | 313.05 | 510 | 510 | 0 | 0 | No
2030-03-04 01:00 | 2030 Initial | 700 | 13.05 | 510 | 510 | 0 | 0 | No
2030-03-04 02:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-04 03:00 | 2030 Initial | 700 | 0 | 510 | 403.66 | 0 | 0 | No
2030-03-04 04:00 | 2030 Initial | 700 | 0 | 510 | 274.71 | 0 | 0 | No
2030-03-04 05:00 | 2030 Initial | 700 | 0 | 510 | 299.58 | 0 | 0 | No
2030-03-04 06:00 | 2030 Initial | 700 | 0 | 510 | 127.3 | 0 | 0 | No
2030-03-04 07:00 | 2030 Initial | 700 | 64.24 | 510 | 427.3 | 0 | 0 | No
2030-03-04 08:00 | 2030 Initial | 700 | 364.24 | 510 | 510 | 0 | 0 | No
2030-03-04 09:00 | 2030 Initial | 700 | 354.15 | 510 | 210 | 0 | 0 | No
2030-03-04 10:00 | 2030 Initial | 700 | 54.15 | 361.68 | 5.36 | 0 | 0 | No
2030-03-04 11:00 | 2030 Initial | 700 | 0 | 61.68 | 0 | 0 | 0 | No
2030-03-04 12:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-03-04 13:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-03-04 14:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-03-04 15:00 | 2030 Initial | 700 | 0 | 227.88 | 0 | 0 | 0 | No
2030-03-04 16:00 | 2030 Initial | 700 | 54.97 | 209.78 | 19.32 | 0 | 0 | No
2030-03-04 17:00 | 2030 Initial | 700 | 0 | -90.22 | -280.68 | 0 | 0 | No
2030-03-04 18:00 | 2030 Initial | 700 | -300 | -390.22 | -510 | 0 | 0 | No
2030-03-04 19:00 | 2030 Initial | 700 | 0 | -90.22 | -235.45 | 0 | 0 | No
2030-03-04 20:00 | 2030 Initial | 700 | 171.19 | 209.78 | -60.19 | 0 | 0 | No
2030-03-04 21:00 | 2030 Initial | 700 | 471.19 | 509.78 | 149.24 | 0 | 0 | No
2030-03-04 22:00 | 2030 Initial | 700 | 505 | 510 | 0 | 0 | 0 | No
2030-03-04 23:00 | 2030 Initial | 700 | 339.02 | 510 | 0 | 0 | 0 | No
2030-03-05 | 2030 Initial | 700 | 505 | 510 | 0 | 0 | 0 | No
2030-03-05 01:00 | 2030 Initial | 700 | 205 | 429.15 | 37.65 | 0 | 0 | No
2030-03-05 02:00 | 2030 Initial | 700 | 505 | 510 | 337.65 | 0 | 0 | No
2030-03-05 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-05 04:00 | 2030 Initial | 700 | 505 | 510 | 348.93 | 0 | 0 | No
2030-03-05 05:00 | 2030 Initial | 280 | 247.34 | 510 | 48.93 | 0 | 0 | No
2030-03-05 06:00 | 2030 Initial | 700 | 0 | 210 | -49.61 | 0 | 0 | No
2030-03-05 07:00 | 2030 Initial | 700 | 0 | 317.52 | 0 | 0 | 0 | No
2030-03-05 08:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-03-05 09:00 | 2030 Initial | 700 | 0 | 444.75 | 0 | 0 | 0 | No
2030-03-05 10:00 | 2030 Initial | 700 | 0 | 340.66 | 210 | 0 | 0 | No
2030-03-05 11:00 | 2030 Initial | 700 | 190.57 | 510 | 510 | 0 | 0 | No
2030-03-05 12:00 | 2030 Initial | 700 | 373.55 | 510 | 510 | 0 | 0 | No
2030-03-05 13:00 | 2030 Initial | 700 | 489.83 | 510 | 510 | 0 | 0 | No
2030-03-05 14:00 | 2030 Initial | 700 | 260.55 | 510 | 510 | 0 | 0 | No
2030-03-05 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-05 16:00 | 2030 Initial | 700 | 263.99 | 396.64 | 310.59 | 0 | 0 | No
2030-03-05 17:00 | 2030 Initial | 700 | 242.74 | 96.64 | 50.92 | 0 | 0 | No
2030-03-05 18:00 | 2030 Initial | 700 | 0 | -203.36 | -249.08 | 0 | 0 | No
2030-03-05 19:00 | 2030 Initial | 700 | 0 | -503.36 | -510 | 0 | 0 | No
2030-03-05 20:00 | 2030 Initial | 700 | 0 | -203.36 | -227.38 | 0 | 0 | No
2030-03-05 21:00 | 2030 Initial | 700 | 241.21 | 96.64 | 72.62 | 0 | 0 | No
2030-03-05 22:00 | 2030 Initial | 700 | 0 | 86.29 | 0 | 0 | 0 | No
2030-03-05 23:00 | 2030 Initial | 700 | 0 | 386.29 | 300 | 0 | 0 | No
2030-03-06 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-03-06 01:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-03-06 02:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-03-06 03:00 | 2030 Initial | 450.02 | 0 | 390 | 0 | 0 | 0 | No
2030-03-06 04:00 | 2030 Initial | 30.02 | 0 | 90 | 0 | 0 | 0 | No
2030-03-06 05:00 | 2030 Initial | -389.98 | -58.01 | -210 | -242.29 | 0 | 0 | No
2030-03-06 06:00 | 2030 Initial | -700 | -358.01 | -510 | -510 | 0 | 0 | No
2030-03-06 07:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 08:00 | 2030 Initial | -661.72 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 09:00 | 2030 Initial | -533.39 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 10:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 11:00 | 2030 Initial | -700 | -526 | -510 | -392.05 | 0 | 0 | No
2030-03-06 12:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 13:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 14:00 | 2030 Initial | -492.4 | -526 | -510 | -245.79 | 0 | 0 | No
2030-03-06 15:00 | 2030 Initial | -72.4 | -526 | -510 | -216.92 | 0 | 0 | No
2030-03-06 16:00 | 2030 Initial | 340.15 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 17:00 | 2030 Initial | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-03-06 18:00 | 2030 Initial | 700 | -416.01 | -510 | -510 | 0 | 0 | No
2030-03-06 19:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 20:00 | 2030 Initial | 700 | -226 | -263.53 | -210 | 0 | 0 | No
2030-03-06 21:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-03-06 22:00 | 2030 Initial | 700 | 0 | -300 | -102.48 | 0 | 0 | No
2030-03-06 23:00 | 2030 Initial | 700 | 134.54 | 0 | 197.52 | 0 | 0 | No
2030-03-07 | 2030 Initial | 563.58 | -165.46 | -300 | -102.48 | 0 | 0 | No
2030-03-07 01:00 | 2030 Initial | 700 | -153.23 | -510 | -256.1 | 0 | 0 | No
2030-03-07 02:00 | 2030 Initial | 560 | -424.04 | -510 | -158.52 | 0 | 0 | No
2030-03-07 03:00 | 2030 Initial | 140 | -394.24 | -510 | -17.91 | 0 | 0 | No
2030-03-07 04:00 | 2030 Initial | -280 | -113.72 | -510 | -270.69 | 0 | 0 | No
2030-03-07 05:00 | 2030 Initial | -700 | -77.88 | -510 | -1.14 | 0 | 0 | No
2030-03-07 06:00 | 2030 Initial | -700 | -216.28 | -510 | -151.85 | 0 | 0 | No
2030-03-07 07:00 | 2030 Initial | -700 | -197.56 | -510 | -178.22 | 0 | 0 | No
2030-03-07 08:00 | 2030 Initial | -700 | -211.07 | -510 | -156.12 | 0 | 0 | No
2030-03-07 09:00 | 2030 Initial | -700 | -511.07 | -510 | -112.54 | 0 | 0 | No
2030-03-07 10:00 | 2030 Initial | -700 | -211.07 | -390 | -119.04 | 0 | 0 | No
2030-03-07 11:00 | 2030 Initial | -700 | 88.93 | -90 | 180.96 | 0 | 0 | No
2030-03-07 12:00 | 2030 Initial | -700 | 388.93 | 210 | 480.96 | 0 | 0 | Yes
2030-03-07 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-07 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-07 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-07 16:00 | 2030 Initial | -700 | 407.17 | 300 | 300 | 0 | 0 | Yes
2030-03-07 17:00 | 2030 Initial | -700 | 107.17 | 0 | 0 | 0 | 0 | No
2030-03-07 18:00 | 2030 Initial | -700 | -192.83 | -300 | -300 | 0 | 0 | No
2030-03-07 19:00 | 2030 Initial | -541.3 | -95 | -90 | -288.52 | 0 | 0 | No
2030-03-07 20:00 | 2030 Initial | -541.3 | 205 | 210 | 11.48 | 0 | 0 | No
2030-03-07 21:00 | 2030 Initial | -700 | 505 | 510 | 311.48 | 0 | 0 | No
2030-03-07 22:00 | 2030 Initial | -689.7 | 505 | 510 | 510 | 0 | 0 | No
2030-03-07 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 01:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 02:00 | 2030 Initial | -296.87 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 03:00 | 2030 Initial | -296.87 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 04:00 | 2030 Initial | -42.24 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 05:00 | 2030 Initial | -105.88 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 06:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 07:00 | 2030 Initial | 0 | 205 | 510 | 284.26 | 0 | 0 | No
2030-03-08 08:00 | 2030 Initial | 0 | 0 | 510 | 428.6 | 0 | 0 | No
2030-03-08 09:00 | 2030 Initial | 140 | 99.27 | 510 | 510 | 0 | 0 | No
2030-03-08 10:00 | 2030 Initial | -280 | 208.51 | 510 | 510 | 0 | 0 | No
2030-03-08 11:00 | 2030 Initial | -700 | 221.81 | 510 | 510 | 0 | 0 | Yes
2030-03-08 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-08 13:00 | 2030 Initial | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-03-08 14:00 | 2030 Initial | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-08 15:00 | 2030 Initial | -515.76 | -226 | -210 | 510 | 0 | 0 | No
2030-03-08 16:00 | 2030 Initial | -95.76 | -526 | -510 | 235.22 | 0 | 0 | No
2030-03-08 17:00 | 2030 Initial | 324.24 | -526 | -510 | 510 | 0 | 0 | No
2030-03-08 18:00 | 2030 Initial | 0 | -456.06 | -510 | 510 | 0 | 0 | No
2030-03-08 19:00 | 2030 Initial | 420 | -526 | -510 | 510 | 0 | 0 | No
2030-03-08 20:00 | 2030 Initial | 700 | -349.8 | -510 | 510 | 0 | 0 | No
2030-03-08 21:00 | 2030 Initial | 411.69 | -455.6 | -510 | 510 | 0 | 0 | No
2030-03-08 22:00 | 2030 Initial | -8.31 | -155.6 | -300 | 387.66 | 0 | 0 | No
2030-03-08 23:00 | 2030 Initial | 0 | 144.4 | 0 | 510 | 0 | 0 | No
2030-03-09 | 2030 Initial | 7.07 | 444.4 | 300 | 510 | 0 | 0 | No
2030-03-09 01:00 | 2030 Initial | 328.43 | 505 | 510 | 510 | 0 | 0 | No
2030-03-09 02:00 | 2030 Initial | 485.43 | 505 | 510 | 510 | 0 | 0 | No
2030-03-09 03:00 | 2030 Initial | 65.43 | 505 | 510 | 510 | 0 | 0 | No
2030-03-09 04:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-09 05:00 | 2030 Initial | -410.51 | 205 | 510 | 375.53 | 0 | 0 | No
2030-03-09 06:00 | 2030 Initial | 9.49 | 0 | 210 | 75.53 | 0 | 0 | No
2030-03-09 07:00 | 2030 Initial | 429.49 | 0 | 0 | 182.33 | 0 | 0 | No
2030-03-09 08:00 | 2030 Initial | 700 | 0 | 0 | 304 | 0 | 0 | No
2030-03-09 09:00 | 2030 Initial | 700 | -161.65 | -300 | 401.99 | 0 | 0 | No
2030-03-09 10:00 | 2030 Initial | 357.56 | -417.28 | -510 | 101.99 | 0 | 0 | No
2030-03-09 11:00 | 2030 Initial | -62.44 | -526 | -510 | -198.01 | 0 | 0 | No
2030-03-09 12:00 | 2030 Initial | -77.95 | -526 | -510 | -498.01 | 0 | 0 | No
2030-03-09 13:00 | 2030 Initial | -296.5 | -320.1 | -510 | -272.6 | 0 | 0 | No
2030-03-09 14:00 | 2030 Initial | 123.5 | -20.1 | -210 | 27.4 | 0 | 0 | No
2030-03-09 15:00 | 2030 Initial | 543.5 | 279.9 | 90 | 327.4 | 0 | 0 | No
2030-03-09 16:00 | 2030 Initial | 420 | 0 | -14.29 | 510 | 0 | 0 | No
2030-03-09 17:00 | 2030 Initial | 0 | -271.95 | -314.29 | 449.42 | 0 | 0 | No
2030-03-09 18:00 | 2030 Initial | -345.31 | -300 | -375.36 | 180.74 | 0 | 0 | No
2030-03-09 19:00 | 2030 Initial | 0 | 0 | -75.36 | 74.97 | 0 | 0 | No
2030-03-09 20:00 | 2030 Initial | -280 | 300 | 224.64 | 304.91 | 0 | 0 | No
2030-03-09 21:00 | 2030 Initial | -700 | 505 | 510 | 497.37 | 0 | 0 | Yes
2030-03-09 22:00 | 2030 Initial | -700 | 505 | 510 | 306.35 | 0 | 0 | Yes
2030-03-09 23:00 | 2030 Initial | -700 | 505 | 510 | 396.28 | 0 | 0 | Yes
2030-03-10 | 2030 Initial | -700 | 505 | 510 | 491.88 | 0 | 0 | Yes
2030-03-10 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 02:00 | 2030 Initial | -700 | 505 | 510 | 357.33 | 0 | 0 | Yes
2030-03-10 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 05:00 | 2030 Initial | -700 | 505 | 510 | 311.17 | 0 | 0 | Yes
2030-03-10 06:00 | 2030 Initial | -700 | 505 | 510 | 489.54 | 0 | 0 | Yes
2030-03-10 07:00 | 2030 Initial | -700 | 505 | 510 | 189.54 | 0 | 0 | Yes
2030-03-10 08:00 | 2030 Initial | -700 | 505 | 510 | 366.07 | 0 | 0 | Yes
2030-03-10 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 10:00 | 2030 Initial | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-03-10 11:00 | 2030 Initial | -700 | 505 | 510 | 182.68 | 0 | 0 | Yes
2030-03-10 12:00 | 2030 Initial | -700 | 505 | 510 | 127.02 | 0 | 0 | Yes
2030-03-10 13:00 | 2030 Initial | -700 | 505 | 510 | 158.3 | 0 | 0 | Yes
2030-03-10 14:00 | 2030 Initial | -700 | 505 | 510 | 162.01 | 0 | 0 | Yes
2030-03-10 15:00 | 2030 Initial | -640.61 | 505 | 510 | 459.39 | 0 | 0 | Yes
2030-03-10 16:00 | 2030 Initial | -220.61 | 505 | 510 | 497.12 | 0 | 0 | Yes
2030-03-10 17:00 | 2030 Initial | 199.39 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 18:00 | 2030 Initial | 619.39 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 23:00 | 2030 Initial | 534.52 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 | 2030 Initial | 114.52 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 01:00 | 2030 Initial | -305.48 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 16:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 17:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 18:00 | 2030 Initial | 560 | 205 | 210 | 306.53 | 0 | 0 | No
2030-03-11 19:00 | 2030 Initial | 700 | 205 | 210 | 498.1 | 0 | 0 | No
2030-03-11 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 21:00 | 2030 Initial | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 22:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 23:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-12 | 2030 Initial | -674.5 | 505 | 510 | 510 | 0 | 0 | No
2030-03-12 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-12 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-12 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-12 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 16:00 | 2030 Initial | -700 | 505 | 510 | 342.32 | 0 | 0 | Yes
2030-03-12 17:00 | 2030 Initial | -700 | 300 | 216.97 | 42.32 | 0 | 0 | No
2030-03-12 18:00 | 2030 Initial | -280 | 0 | -83.03 | -257.68 | 0 | 0 | No
2030-03-12 19:00 | 2030 Initial | 22.4 | -95 | -90 | -90 | 0 | 0 | No
2030-03-12 20:00 | 2030 Initial | 97.45 | 205 | 210 | 210 | 0 | 0 | No
2030-03-12 21:00 | 2030 Initial | 517.45 | 505 | 510 | 510 | 0 | 0 | No
2030-03-12 22:00 | 2030 Initial | 548.97 | 505 | 510 | 510 | 0 | 0 | No
2030-03-12 23:00 | 2030 Initial | 128.97 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 | 2030 Initial | 548.97 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 04:00 | 2030 Initial | 420 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 05:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 06:00 | 2030 Initial | 96.95 | 205 | 210 | 210 | 0 | 0 | No
2030-03-13 07:00 | 2030 Initial | 0 | 178.85 | 510 | 510 | 0 | 0 | No
2030-03-13 08:00 | 2030 Initial | 255.64 | 300 | 510 | 510 | 0 | 0 | No
2030-03-13 09:00 | 2030 Initial | 675.64 | 0 | 269.16 | 404.22 | 0 | 0 | No
2030-03-13 10:00 | 2030 Initial | 700 | 0 | -30.84 | 134.89 | 0 | 0 | No
2030-03-13 11:00 | 2030 Initial | 292.85 | -300 | -330.84 | -165.11 | 0 | 0 | No
2030-03-13 12:00 | 2030 Initial | 363.29 | -526 | -510 | -465.11 | 0 | 0 | No
2030-03-13 13:00 | 2030 Initial | -24.75 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 14:00 | 2030 Initial | 161.08 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 15:00 | 2030 Initial | 581.08 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 16:00 | 2030 Initial | 684.58 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 17:00 | 2030 Initial | 659.17 | -226 | -510 | -510 | 0 | 0 | No
2030-03-13 18:00 | 2030 Initial | 659.17 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 19:00 | 2030 Initial | 700 | -226 | -300 | -408.79 | 0 | 0 | No
2030-03-13 20:00 | 2030 Initial | 700 | 0 | 0 | -108.79 | 0 | 0 | No
2030-03-13 21:00 | 2030 Initial | 700 | 207.99 | 300 | 191.21 | 0 | 0 | No
2030-03-13 22:00 | 2030 Initial | 700 | 186.73 | 510 | -58.13 | 0 | 0 | No
2030-03-13 23:00 | 2030 Initial | 700 | 0 | 459.49 | -358.13 | 0 | 0 | No
2030-03-14 | 2030 Initial | 700 | 0 | 213.81 | -119.53 | 0 | 0 | No
2030-03-14 01:00 | 2030 Initial | 535.93 | 205 | 210 | 180.47 | 0 | 0 | No
2030-03-14 02:00 | 2030 Initial | 700 | 505 | 510 | 480.47 | 0 | 0 | No
2030-03-14 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-14 04:00 | 2030 Initial | 687.73 | 505 | 510 | 510 | 0 | 0 | No
2030-03-14 05:00 | 2030 Initial | 267.73 | 300.24 | 510 | 510 | 0 | 0 | No
2030-03-14 06:00 | 2030 Initial | 310.64 | 0.24 | 210 | 215.47 | 0 | 0 | No
2030-03-14 07:00 | 2030 Initial | -90.56 | 0 | 18.65 | 232.02 | 0 | 0 | No
2030-03-14 08:00 | 2030 Initial | 189.35 | 0 | -46.78 | 193.29 | 0 | 0 | No
2030-03-14 09:00 | 2030 Initial | -230.65 | -195.02 | -346.78 | 414.06 | 0 | 0 | No
2030-03-14 10:00 | 2030 Initial | -650.65 | -53.07 | -300 | 414.06 | 0 | 0 | No
2030-03-14 11:00 | 2030 Initial | -280 | 246.93 | 0 | 510 | 0 | 0 | No
2030-03-14 12:00 | 2030 Initial | -700 | 505 | 300 | 510 | 0 | 0 | No
2030-03-14 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-14 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-14 15:00 | 2030 Initial | -700 | 505 | 378.96 | 510 | 0 | 0 | Yes
2030-03-14 16:00 | 2030 Initial | -700 | 300 | 78.96 | 210 | 0 | 0 | No
2030-03-14 17:00 | 2030 Initial | -700 | 0 | -221.04 | -90 | 0 | 0 | No
2030-03-14 18:00 | 2030 Initial | -678.46 | 0 | 34.16 | 0 | 0 | 0 | No
2030-03-14 19:00 | 2030 Initial | -258.46 | 0 | 301.88 | 221.72 | 0 | 0 | No
2030-03-14 20:00 | 2030 Initial | 50.9 | 205 | 417.9 | 408.87 | 0 | 0 | No
2030-03-14 21:00 | 2030 Initial | -369.1 | 505 | 510 | 510 | 0 | 0 | No
2030-03-14 22:00 | 2030 Initial | -27.78 | 505 | 510 | 510 | 0 | 0 | No
2030-03-14 23:00 | 2030 Initial | -447.78 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 | 2030 Initial | -125.15 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 01:00 | 2030 Initial | -125.15 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 02:00 | 2030 Initial | -29.69 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 03:00 | 2030 Initial | 91.98 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 04:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 07:00 | 2030 Initial | -700 | 505 | 510 | 417.5 | 0 | 0 | Yes
2030-03-15 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 09:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 10:00 | 2030 Initial | -299.02 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 11:00 | 2030 Initial | -700 | 505 | 510 | 417.25 | 0 | 0 | Yes
2030-03-15 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 13:00 | 2030 Initial | -700 | 505 | 510 | 493.01 | 0 | 0 | Yes
2030-03-15 14:00 | 2030 Initial | -700 | 505 | 510 | 197.28 | 0 | 0 | Yes
2030-03-15 15:00 | 2030 Initial | -591.76 | 248.95 | 210 | -102.72 | 0 | 0 | No
2030-03-15 16:00 | 2030 Initial | -700 | -51.05 | -90 | -252.13 | 0 | 0 | No
2030-03-15 17:00 | 2030 Initial | -700 | 205 | 210 | 47.87 | 0 | 0 | No
2030-03-15 18:00 | 2030 Initial | -647.18 | 505 | 510 | 347.87 | 0 | 0 | No
2030-03-15 19:00 | 2030 Initial | -227.18 | 205 | 210 | 210 | 0 | 0 | No
2030-03-15 20:00 | 2030 Initial | 192.82 | 505 | 510 | 510 | 0 | 0 | No
2030-03-15 21:00 | 2030 Initial | 612.82 | 505 | 510 | 510 | 0 | 0 | No
2030-03-15 22:00 | 2030 Initial | 700 | 356.17 | 510 | 510 | 0 | 0 | No
2030-03-15 23:00 | 2030 Initial | 700 | 230.2 | 510 | 510 | 0 | 0 | No
2030-03-16 | 2030 Initial | 700 | 0 | 510 | 210 | 0 | 0 | No
2030-03-16 01:00 | 2030 Initial | 700 | 0 | 510 | 6.72 | 0 | 0 | No
2030-03-16 02:00 | 2030 Initial | 700 | 0 | 510 | 186.27 | 0 | 0 | No
2030-03-16 03:00 | 2030 Initial | 582.32 | 0 | 390 | 0 | 0 | 0 | No
2030-03-16 04:00 | 2030 Initial | 162.32 | 0 | 90 | 40.04 | 0 | 0 | No
2030-03-16 05:00 | 2030 Initial | -257.68 | -226 | -210 | -210 | 0 | 0 | No
2030-03-16 06:00 | 2030 Initial | -677.68 | -526 | -510 | -510 | 0 | 0 | No
2030-03-16 07:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-16 08:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-16 09:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-16 10:00 | 2030 Initial | -700 | -526 | -510 | -488.45 | 0 | 0 | No
2030-03-16 11:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-16 12:00 | 2030 Initial | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-03-16 13:00 | 2030 Initial | -700 | -526 | -510 | -490.67 | 0 | 0 | No
2030-03-16 14:00 | 2030 Initial | -700 | -526 | -510 | -368.56 | 0 | 0 | No
2030-03-16 15:00 | 2030 Initial | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-03-16 16:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-16 17:00 | 2030 Initial | -700 | -526 | -510 | -386.67 | 0 | 0 | No
2030-03-16 18:00 | 2030 Initial | -700 | -395 | -395.59 | -175.39 | 0 | 0 | No
2030-03-16 19:00 | 2030 Initial | -700 | -95 | -95.59 | -19.46 | 0 | 0 | No
2030-03-16 20:00 | 2030 Initial | -700 | 205 | 204.41 | 267.91 | 0 | 0 | No
2030-03-16 21:00 | 2030 Initial | -700 | 505 | 504.41 | 510 | 0 | 0 | No
2030-03-16 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-16 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 01:00 | 2030 Initial | -684.77 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 02:00 | 2030 Initial | -695.62 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 09:00 | 2030 Initial | -511.14 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 10:00 | 2030 Initial | -426.13 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 11:00 | 2030 Initial | -370.35 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 12:00 | 2030 Initial | -426.12 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 13:00 | 2030 Initial | -215.07 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 14:00 | 2030 Initial | -632.35 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 15:00 | 2030 Initial | -684.54 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 16:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 17:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 18:00 | 2030 Initial | -700 | 205 | 210 | 463.15 | 0 | 0 | No
2030-03-17 19:00 | 2030 Initial | -540.71 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 20:00 | 2030 Initial | -163.02 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 21:00 | 2030 Initial | 155.16 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 22:00 | 2030 Initial | 413.67 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 06:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 07:00 | 2030 Initial | 677.01 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 08:00 | 2030 Initial | 421.08 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 10:00 | 2030 Initial | 700 | 205 | 449.31 | 300 | 0 | 0 | No
2030-03-18 11:00 | 2030 Initial | 700 | 0 | 149.31 | 0 | 0 | 0 | No
2030-03-18 12:00 | 2030 Initial | 700 | 0 | -150.69 | -228.23 | 0 | 0 | No
2030-03-18 13:00 | 2030 Initial | 700 | 0 | -274.94 | 0 | 0 | 0 | No
2030-03-18 14:00 | 2030 Initial | 700 | 0 | -88.72 | 0 | 0 | 0 | No
2030-03-18 15:00 | 2030 Initial | 700 | -73.91 | -90 | -127.85 | 0 | 0 | No
2030-03-18 16:00 | 2030 Initial | 700 | 0 | 210 | 172.15 | 0 | 0 | No
2030-03-18 17:00 | 2030 Initial | 700 | 0 | 510 | 472.15 | 0 | 0 | No
2030-03-18 18:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-18 19:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-18 20:00 | 2030 Initial | 700 | 287.96 | 510 | 510 | 0 | 0 | No
2030-03-18 21:00 | 2030 Initial | 700 | 405.34 | 510 | 504.45 | 0 | 0 | No
2030-03-18 22:00 | 2030 Initial | 700 | 240.23 | 510 | 510 | 0 | 0 | No
2030-03-18 23:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-19 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-19 01:00 | 2030 Initial | 700 | 0 | 510 | 469.94 | 0 | 0 | No
2030-03-19 02:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-19 03:00 | 2030 Initial | 700 | 0 | 510 | 307.78 | 0 | 0 | No
2030-03-19 04:00 | 2030 Initial | 700 | 0 | 510 | 406.99 | 0 | 0 | No
2030-03-19 05:00 | 2030 Initial | 420 | 0 | 468.84 | 510 | 0 | 0 | No
2030-03-19 06:00 | 2030 Initial | 0 | 200.19 | 168.84 | 300 | 0 | 0 | No
2030-03-19 07:00 | 2030 Initial | 0 | 0 | -131.16 | 0 | 0 | 0 | No
2030-03-19 08:00 | 2030 Initial | 280 | -94.42 | -431.16 | -144.62 | 0 | 0 | No
2030-03-19 09:00 | 2030 Initial | 700 | -394.42 | -510 | -118.7 | 0 | 0 | No
2030-03-19 10:00 | 2030 Initial | 700 | -526 | -510 | -118.7 | 0 | 0 | No
2030-03-19 11:00 | 2030 Initial | 528.39 | -526 | -510 | -201.22 | 0 | 0 | No
2030-03-19 12:00 | 2030 Initial | 659.76 | -526 | -510 | -192.18 | 0 | 0 | No
2030-03-19 13:00 | 2030 Initial | 629.52 | -526 | -510 | -419 | 0 | 0 | No
2030-03-19 14:00 | 2030 Initial | 620.04 | -526 | -510 | -437.44 | 0 | 0 | No
2030-03-19 15:00 | 2030 Initial | 485.05 | -526 | -510 | -510 | 0 | 0 | No
2030-03-19 16:00 | 2030 Initial | 670.37 | -526 | -510 | -421.47 | 0 | 0 | No
2030-03-19 17:00 | 2030 Initial | 700 | -226 | -510 | -309.89 | 0 | 0 | No
2030-03-19 18:00 | 2030 Initial | 700 | 0 | -510 | -9.89 | 0 | 0 | No
2030-03-19 19:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-03-19 20:00 | 2030 Initial | 700 | 0 | -335.3 | 0 | 0 | 0 | No
2030-03-19 21:00 | 2030 Initial | 700 | 0 | -35.3 | 0 | 0 | 0 | No
2030-03-19 22:00 | 2030 Initial | 700 | 0 | 264.7 | 239.04 | 0 | 0 | No
2030-03-19 23:00 | 2030 Initial | 700 | 0 | 50.95 | 0 | 0 | 0 | No
2030-03-20 | 2030 Initial | 700 | 0 | -249.05 | -82.13 | 0 | 0 | No
2030-03-20 01:00 | 2030 Initial | 700 | 0 | -510 | -147.55 | 0 | 0 | No
2030-03-20 02:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-03-20 03:00 | 2030 Initial | 700 | 0 | -510 | -44.02 | 0 | 0 | No
2030-03-20 04:00 | 2030 Initial | 700 | 0 | -510 | -190.79 | 0 | 0 | No
2030-03-20 05:00 | 2030 Initial | 700 | 0 | -510 | -306.51 | 0 | 0 | No
2030-03-20 06:00 | 2030 Initial | 280 | 0 | -510 | -6.51 | 0 | 0 | No
2030-03-20 07:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-03-20 08:00 | 2030 Initial | 700 | 0 | -448.34 | 0 | 0 | 0 | No
2030-03-20 09:00 | 2030 Initial | 342.35 | -293.25 | -510 | -101.8 | 0 | 0 | No
2030-03-20 10:00 | 2030 Initial | -77.65 | -526 | -510 | -117.73 | 0 | 0 | No
2030-03-20 11:00 | 2030 Initial | 153.93 | -526 | -510 | -230.93 | 0 | 0 | No
2030-03-20 12:00 | 2030 Initial | -266.07 | -526 | -510 | -187.28 | 0 | 0 | No
2030-03-20 13:00 | 2030 Initial | -534.84 | -526 | -510 | -261.32 | 0 | 0 | No
2030-03-20 14:00 | 2030 Initial | -114.84 | -526 | -510 | -257.14 | 0 | 0 | No
2030-03-20 15:00 | 2030 Initial | 305.16 | -526 | -510 | -199.05 | 0 | 0 | No
2030-03-20 16:00 | 2030 Initial | 700 | -526 | -510 | 24.17 | 0 | 0 | No
2030-03-20 17:00 | 2030 Initial | 700 | -226 | -249.53 | 78.73 | 0 | 0 | No
2030-03-20 18:00 | 2030 Initial | 700 | 0 | 5.92 | 226.97 | 0 | 0 | No
2030-03-20 19:00 | 2030 Initial | 700 | 0 | 305.92 | 91.67 | 0 | 0 | No
2030-03-20 20:00 | 2030 Initial | 700 | 0 | 116.64 | 0 | 0 | 0 | No
2030-03-20 21:00 | 2030 Initial | 700 | 0 | -90 | -103.96 | 0 | 0 | No
2030-03-20 22:00 | 2030 Initial | 700 | 0 | 210 | 142.37 | 0 | 0 | No
2030-03-20 23:00 | 2030 Initial | 280 | 300 | 510 | 442.37 | 0 | 0 | No
2030-03-21 | 2030 Initial | 0 | 462.93 | 510 | 496.08 | 0 | 0 | No
2030-03-21 01:00 | 2030 Initial | 0 | 362.68 | 510 | 201.68 | 0 | 0 | No
2030-03-21 02:00 | 2030 Initial | 0 | 234.8 | 510 | 253.32 | 0 | 0 | No
2030-03-21 03:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 04:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 05:00 | 2030 Initial | -280 | 505 | 510 | 292.54 | 0 | 0 | Yes
2030-03-21 06:00 | 2030 Initial | -700 | 205 | 210 | -7.46 | 0 | 0 | No
2030-03-21 07:00 | 2030 Initial | -280 | -95 | -90 | -307.46 | 0 | 0 | No
2030-03-21 08:00 | 2030 Initial | 0 | -95 | -210.25 | -339.57 | 0 | 0 | No
2030-03-21 09:00 | 2030 Initial | 420 | 205 | 89.75 | -39.57 | 0 | 0 | No
2030-03-21 10:00 | 2030 Initial | 194.91 | 505 | 389.75 | -8.24 | 0 | 0 | No
2030-03-21 11:00 | 2030 Initial | 194.91 | 505 | 510 | 291.76 | 0 | 0 | Yes
2030-03-21 12:00 | 2030 Initial | 413.29 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 15:00 | 2030 Initial | 700 | 505 | 510 | 405.12 | 0 | 0 | Yes
2030-03-21 16:00 | 2030 Initial | 700 | 205 | 210 | 105.12 | 0 | 0 | No
2030-03-21 17:00 | 2030 Initial | 700 | 0 | 510 | 212.86 | 0 | 0 | No
2030-03-21 18:00 | 2030 Initial | 700 | 160.27 | 510 | 510 | 0 | 0 | No
2030-03-21 19:00 | 2030 Initial | 700 | 160.27 | 510 | 510 | 0 | 0 | No
2030-03-21 20:00 | 2030 Initial | 700 | 460.27 | 510 | 510 | 0 | 0 | No
2030-03-21 21:00 | 2030 Initial | 700 | 249.43 | 510 | 510 | 0 | 0 | No
2030-03-21 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-21 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 04:00 | 2030 Initial | 700 | 505 | 464.23 | 510 | 0 | 0 | No
2030-03-22 05:00 | 2030 Initial | 280 | 205 | 164.23 | 269.2 | 0 | 0 | No
2030-03-22 06:00 | 2030 Initial | 97.3 | -95 | -135.77 | 426.01 | 0 | 0 | No
2030-03-22 07:00 | 2030 Initial | 517.3 | -395 | -435.77 | 462.99 | 0 | 0 | No
2030-03-22 08:00 | 2030 Initial | 700 | -290.22 | -510 | 470.54 | 0 | 0 | No
2030-03-22 09:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-22 10:00 | 2030 Initial | 700 | -526 | -510 | 379.75 | 0 | 0 | No
2030-03-22 11:00 | 2030 Initial | 700 | -526 | -510 | 271.34 | 0 | 0 | No
2030-03-22 12:00 | 2030 Initial | 700 | -526 | -510 | 105.03 | 0 | 0 | No
2030-03-22 13:00 | 2030 Initial | 700 | -526 | -510 | 46.11 | 0 | 0 | No
2030-03-22 14:00 | 2030 Initial | 700 | -526 | -510 | -48.48 | 0 | 0 | No
2030-03-22 15:00 | 2030 Initial | 700 | -526 | -510 | -194.55 | 0 | 0 | No
2030-03-22 16:00 | 2030 Initial | 700 | -526 | -510 | -32.41 | 0 | 0 | No
2030-03-22 17:00 | 2030 Initial | 700 | -226 | -210 | 267.59 | 0 | 0 | No
2030-03-22 18:00 | 2030 Initial | 700 | 74 | 90 | 510 | 0 | 0 | No
2030-03-22 19:00 | 2030 Initial | 700 | 234.83 | 390 | 510 | 0 | 0 | No
2030-03-22 20:00 | 2030 Initial | 700 | 234.83 | 510 | 510 | 0 | 0 | No
2030-03-22 21:00 | 2030 Initial | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-03-22 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 05:00 | 2030 Initial | 420 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 06:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 07:00 | 2030 Initial | -140 | 205 | 210 | 210 | 0 | 0 | No
2030-03-23 08:00 | 2030 Initial | 280 | 0 | -90 | -90 | 0 | 0 | No
2030-03-23 09:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-03-23 10:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 11:00 | 2030 Initial | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 12:00 | 2030 Initial | -262.14 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 13:00 | 2030 Initial | -104.53 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 14:00 | 2030 Initial | -467.78 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 15:00 | 2030 Initial | -580.44 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 16:00 | 2030 Initial | -160.44 | 205 | 300 | 416.85 | 0 | 0 | No
2030-03-23 17:00 | 2030 Initial | 259.56 | 0 | 0 | 242.37 | 0 | 0 | No
2030-03-23 18:00 | 2030 Initial | 679.56 | 0 | 0 | 13.98 | 0 | 0 | No
2030-03-23 19:00 | 2030 Initial | 700 | 0 | 180.84 | 0 | 0 | 0 | No
2030-03-23 20:00 | 2030 Initial | 561.44 | 0 | 480.84 | 210 | 0 | 0 | No
2030-03-23 21:00 | 2030 Initial | 141.44 | 276.8 | 510 | 510 | 0 | 0 | No
2030-03-23 22:00 | 2030 Initial | -278.56 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 23:00 | 2030 Initial | -698.56 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 05:00 | 2030 Initial | -700 | 505 | 510 | 483.87 | 0 | 0 | Yes
2030-03-24 06:00 | 2030 Initial | -700 | 505 | 510 | 500.31 | 0 | 0 | Yes
2030-03-24 07:00 | 2030 Initial | -700 | 505 | 510 | 382.79 | 0 | 0 | Yes
2030-03-24 08:00 | 2030 Initial | -700 | 505 | 510 | 476.18 | 0 | 0 | Yes
2030-03-24 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 16:00 | 2030 Initial | -700 | 505 | 510 | 359.3 | 0 | 0 | Yes
2030-03-24 17:00 | 2030 Initial | -700 | 300 | 510 | 59.3 | 0 | 0 | Yes
2030-03-24 18:00 | 2030 Initial | -700 | 0 | 232.86 | -240.7 | 0 | 0 | No
2030-03-24 19:00 | 2030 Initial | -700 | 205 | 210 | 46.65 | 0 | 0 | No
2030-03-24 20:00 | 2030 Initial | -280 | 505 | 510 | 346.65 | 0 | 0 | No
2030-03-24 21:00 | 2030 Initial | 2.66 | 505 | 510 | 510 | 0 | 0 | No
2030-03-24 22:00 | 2030 Initial | 46.03 | 505 | 510 | 510 | 0 | 0 | No
2030-03-24 23:00 | 2030 Initial | -373.97 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 | 2030 Initial | 46.03 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 01:00 | 2030 Initial | 466.03 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 05:00 | 2030 Initial | 673.14 | 300 | 411.82 | 510 | 0 | 0 | No
2030-03-25 06:00 | 2030 Initial | 253.14 | 0 | 111.82 | 210 | 0 | 0 | No
2030-03-25 07:00 | 2030 Initial | 633.26 | -244.02 | -188.18 | -52.75 | 0 | 0 | No
2030-03-25 08:00 | 2030 Initial | 700 | -226 | -441.23 | 0 | 0 | 0 | No
2030-03-25 09:00 | 2030 Initial | 700 | -526 | -510 | -170.93 | 0 | 0 | No
2030-03-25 10:00 | 2030 Initial | 700 | -526 | -510 | -257.12 | 0 | 0 | No
2030-03-25 11:00 | 2030 Initial | 700 | -526 | -510 | -139.43 | 0 | 0 | No
2030-03-25 12:00 | 2030 Initial | 700 | -526 | -510 | -182.37 | 0 | 0 | No
2030-03-25 13:00 | 2030 Initial | 700 | -280.83 | -510 | -93.26 | 0 | 0 | No
2030-03-25 14:00 | 2030 Initial | 700 | -61.47 | -510 | 12.29 | 0 | 0 | No
2030-03-25 15:00 | 2030 Initial | 700 | 0 | -433.16 | 68.66 | 0 | 0 | No
2030-03-25 16:00 | 2030 Initial | 700 | 0 | -173.65 | 151.82 | 0 | 0 | No
2030-03-25 17:00 | 2030 Initial | 700 | 0 | 126.35 | 41.93 | 0 | 0 | No
2030-03-25 18:00 | 2030 Initial | 700 | 0 | 426.35 | 341.93 | 0 | 0 | No
2030-03-25 19:00 | 2030 Initial | 700 | 0 | 510 | 448.3 | 0 | 0 | No
2030-03-25 20:00 | 2030 Initial | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-03-25 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 22:00 | 2030 Initial | 700 | 399.89 | 510 | 510 | 0 | 0 | No
2030-03-25 23:00 | 2030 Initial | 700 | 103.72 | 510 | 439.7 | 0 | 0 | No
2030-03-26 | 2030 Initial | 700 | 0 | 510 | 439.7 | 0 | 0 | No
2030-03-26 01:00 | 2030 Initial | 700 | 0 | 510 | 245.9 | 0 | 0 | No
2030-03-26 02:00 | 2030 Initial | 700 | 0 | 510 | 61.94 | 0 | 0 | No
2030-03-26 03:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-03-26 04:00 | 2030 Initial | 700 | 0 | 510 | 40.73 | 0 | 0 | No
2030-03-26 05:00 | 2030 Initial | 700 | 0 | 266.92 | 19.51 | 0 | 0 | No
2030-03-26 06:00 | 2030 Initial | 700 | 0 | -33.08 | 0 | 0 | 0 | No
2030-03-26 07:00 | 2030 Initial | 700 | -300 | -333.08 | -300 | 0 | 0 | No
2030-03-26 08:00 | 2030 Initial | 700 | -312.38 | -510 | -308.57 | 0 | 0 | No
2030-03-26 09:00 | 2030 Initial | 700 | -12.38 | -210 | -8.57 | 0 | 0 | No
2030-03-26 10:00 | 2030 Initial | 587.02 | -312.38 | -510 | 33.28 | 0 | 0 | No
2030-03-26 11:00 | 2030 Initial | 700 | -526 | -510 | 1.14 | 0 | 0 | No
2030-03-26 12:00 | 2030 Initial | 617.2 | -526 | -510 | 56.59 | 0 | 0 | No
2030-03-26 13:00 | 2030 Initial | 273.66 | -526 | -510 | 10.46 | 0 | 0 | No
2030-03-26 14:00 | 2030 Initial | 377.46 | -526 | -510 | 46.97 | 0 | 0 | No
2030-03-26 15:00 | 2030 Initial | 700 | -526 | -510 | 166.89 | 0 | 0 | No
2030-03-26 16:00 | 2030 Initial | 700 | -300 | -481.31 | 91.57 | 0 | 0 | No
2030-03-26 17:00 | 2030 Initial | 700 | 0 | -181.31 | 0 | 0 | 0 | No
2030-03-26 18:00 | 2030 Initial | 700 | 0 | 20.78 | 0 | 0 | 0 | No
2030-03-26 19:00 | 2030 Initial | 700 | 0 | 196.29 | 0 | 0 | 0 | No
2030-03-26 20:00 | 2030 Initial | 700 | 0 | 496.29 | 0 | 0 | 0 | No
2030-03-26 21:00 | 2030 Initial | 700 | 0 | 300.14 | 210 | 0 | 0 | No
2030-03-26 22:00 | 2030 Initial | 700 | 53.38 | 510 | 510 | 0 | 0 | No
2030-03-26 23:00 | 2030 Initial | 700 | 0 | 264.32 | 210 | 0 | 0 | No
2030-03-27 | 2030 Initial | 700 | 0 | 174.07 | 0 | 0 | 0 | No
2030-03-27 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-03-27 02:00 | 2030 Initial | 700 | 0 | -58.68 | 0 | 0 | 0 | No
2030-03-27 03:00 | 2030 Initial | 700 | 0 | -20.9 | 0 | 0 | 0 | No
2030-03-27 04:00 | 2030 Initial | 700 | 0 | -320.9 | 0 | 0 | 0 | No
2030-03-27 05:00 | 2030 Initial | 420 | 0 | -454.07 | 0 | 0 | 0 | No
2030-03-27 06:00 | 2030 Initial | 0 | 0 | -154.07 | 0 | 0 | 0 | No
2030-03-27 07:00 | 2030 Initial | 30.65 | 0 | -300 | -292.09 | 0 | 0 | No
2030-03-27 08:00 | 2030 Initial | 450.65 | 0 | 0 | 0 | 0 | 0 | No
2030-03-27 09:00 | 2030 Initial | 140 | -131.18 | -300 | 2.64 | 0 | 0 | No
2030-03-27 10:00 | 2030 Initial | -280 | -431.18 | -510 | -35.8 | 0 | 0 | No
2030-03-27 11:00 | 2030 Initial | -700 | -526 | -510 | -61.41 | 0 | 0 | No
2030-03-27 12:00 | 2030 Initial | -700 | -526 | -510 | -193.51 | 0 | 0 | No
2030-03-27 13:00 | 2030 Initial | -700 | -526 | -510 | -174.56 | 0 | 0 | No
2030-03-27 14:00 | 2030 Initial | -700 | -526 | -510 | -209.63 | 0 | 0 | No
2030-03-27 15:00 | 2030 Initial | -504.3 | -526 | -510 | -136.27 | 0 | 0 | No
2030-03-27 16:00 | 2030 Initial | -84.3 | -406.84 | -510 | -28.24 | 0 | 0 | No
2030-03-27 17:00 | 2030 Initial | 335.7 | -106.84 | -435.89 | 67.46 | 0 | 0 | No
2030-03-27 18:00 | 2030 Initial | 254.71 | 0 | -135.89 | 0 | 0 | 0 | No
2030-03-27 19:00 | 2030 Initial | 404.8 | 0 | 0 | 0 | 0 | 0 | No
2030-03-27 20:00 | 2030 Initial | 700 | 0 | -300 | 0 | 0 | 0 | No
2030-03-27 21:00 | 2030 Initial | 700 | 0 | -355 | -210 | 0 | 0 | No
2030-03-27 22:00 | 2030 Initial | 423.85 | -95 | -90 | -510 | 0 | 0 | No
2030-03-27 23:00 | 2030 Initial | 448.83 | 205 | 210 | -301.54 | 0 | 0 | No
2030-03-28 | 2030 Initial | 700 | 505 | 510 | -66.78 | 0 | 0 | No
2030-03-28 01:00 | 2030 Initial | 700 | 505 | 510 | 210 | 0 | 0 | No
2030-03-28 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 03:00 | 2030 Initial | 517.8 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 04:00 | 2030 Initial | 97.8 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 05:00 | 2030 Initial | -322.2 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 07:00 | 2030 Initial | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-03-28 08:00 | 2030 Initial | -700 | 0 | 172.9 | 230.32 | 0 | 0 | No
2030-03-28 09:00 | 2030 Initial | -700 | 300 | 472.9 | 510 | 0 | 0 | No
2030-03-28 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 16:00 | 2030 Initial | -567.48 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 17:00 | 2030 Initial | -147.48 | 300 | 300 | 510 | 0 | 0 | Yes
2030-03-28 18:00 | 2030 Initial | 272.52 | 0 | 0 | 210 | 0 | 0 | No
2030-03-28 19:00 | 2030 Initial | 692.52 | 0 | -90 | -52.89 | 0 | 0 | No
2030-03-28 20:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-03-28 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 23:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 07:00 | 2030 Initial | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 08:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 09:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 15:00 | 2030 Initial | -560 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 16:00 | 2030 Initial | -140 | 255.72 | 300 | 510 | 0 | 0 | No
2030-03-29 17:00 | 2030 Initial | 280 | -44.28 | 0 | 436.53 | 0 | 0 | No
2030-03-29 18:00 | 2030 Initial | 700 | 79.82 | 300 | 510 | 0 | 0 | No
2030-03-29 19:00 | 2030 Initial | 700 | 379.82 | 510 | 510 | 0 | 0 | No
2030-03-29 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 21:00 | 2030 Initial | 700 | 408.13 | 510 | 510 | 0 | 0 | No
2030-03-29 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-30 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-30 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-30 06:00 | 2030 Initial | 700 | 505 | 510 | 311.36 | 0 | 0 | Yes
2030-03-30 07:00 | 2030 Initial | 700 | 505 | 510 | 11.36 | 0 | 0 | No
2030-03-30 08:00 | 2030 Initial | 420 | 452.34 | 510 | 168.25 | 0 | 0 | No
2030-03-30 09:00 | 2030 Initial | 0 | 152.34 | 292.44 | -64.21 | 0 | 0 | No
2030-03-30 10:00 | 2030 Initial | -420 | 0 | 0 | 0 | 0 | 0 | No
2030-03-30 11:00 | 2030 Initial | -563.47 | 0 | 0 | 0 | 0 | 0 | No
2030-03-30 12:00 | 2030 Initial | -443.4 | 0 | 0 | 0 | 0 | 0 | No
2030-03-30 13:00 | 2030 Initial | -599.97 | 0 | 0 | 0 | 0 | 0 | No
2030-03-30 14:00 | 2030 Initial | -179.97 | 0 | 0 | 0 | 0 | 0 | No
2030-03-30 15:00 | 2030 Initial | 223.48 | 0 | 0 | 0 | 0 | 0 | No
2030-03-30 16:00 | 2030 Initial | 643.48 | -226 | -210 | 81.23 | 0 | 0 | No
2030-03-30 17:00 | 2030 Initial | 700 | -526 | -510 | 178.73 | 0 | 0 | No
2030-03-30 18:00 | 2030 Initial | 700 | -226 | -341.81 | 431.03 | 0 | 0 | No
2030-03-30 19:00 | 2030 Initial | 700 | 0 | -188.98 | 341.56 | 0 | 0 | No
2030-03-30 20:00 | 2030 Initial | 700 | 0 | -65.75 | 300.39 | 0 | 0 | No
2030-03-30 21:00 | 2030 Initial | 700 | 205 | 210 | 337.07 | 0 | 0 | No
2030-03-30 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-31 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-03-31 01:00 | 2030 Initial | 700 | 0 | -90 | -1.2 | 0 | 0 | No
2030-03-31 02:00 | 2030 Initial | 700 | 0 | -390 | 0 | 0 | 0 | No
2030-03-31 03:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-03-31 04:00 | 2030 Initial | 700 | 0 | -510 | 50.12 | 0 | 0 | No
2030-03-31 05:00 | 2030 Initial | 700 | 0 | -510 | 52.67 | 0 | 0 | No
2030-03-31 06:00 | 2030 Initial | 700 | 0 | -510 | -63.78 | 0 | 0 | No
2030-03-31 07:00 | 2030 Initial | 700 | 0 | -510 | -1.6 | 0 | 0 | No
2030-03-31 08:00 | 2030 Initial | 700 | -226 | -510 | 70.65 | 0 | 0 | No
2030-03-31 09:00 | 2030 Initial | 700 | -526 | -510 | 112 | 0 | 0 | No
2030-03-31 10:00 | 2030 Initial | 700 | -526 | -510 | 245.92 | 0 | 0 | No
2030-03-31 11:00 | 2030 Initial | 700 | -526 | -510 | 351.17 | 0 | 0 | No
2030-03-31 12:00 | 2030 Initial | 700 | -526 | -510 | 303.31 | 0 | 0 | No
2030-03-31 13:00 | 2030 Initial | 700 | -526 | -510 | 282.31 | 0 | 0 | No
2030-03-31 14:00 | 2030 Initial | 700 | -526 | -510 | 232.98 | 0 | 0 | No
2030-03-31 15:00 | 2030 Initial | 700 | -526 | -510 | 35.06 | 0 | 0 | No
2030-03-31 16:00 | 2030 Initial | 700 | -526 | -510 | -6.04 | 0 | 0 | No
2030-03-31 17:00 | 2030 Initial | 700 | -226 | -246.61 | -71.67 | 0 | 0 | No
2030-03-31 18:00 | 2030 Initial | 700 | 0 | 53.39 | 228.33 | 0 | 0 | No
2030-03-31 19:00 | 2030 Initial | 700 | 0 | 353.39 | 463.38 | 0 | 0 | No
2030-03-31 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-31 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-31 22:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-31 23:00 | 2030 Initial | 700 | 0 | 510 | 449.09 | 0 | 0 | No
2030-04-01 | 2030 Initial | 700 | 0 | 510 | 361.98 | 0 | 0 | No
2030-04-01 01:00 | 2030 Initial | 700 | 0 | 510 | 218.36 | 0 | 0 | No
2030-04-01 02:00 | 2030 Initial | 700 | 0 | 510 | 257.82 | 0 | 0 | No
2030-04-01 03:00 | 2030 Initial | 700 | 0 | 510 | 286.09 | 0 | 0 | No
2030-04-01 04:00 | 2030 Initial | 700 | 0 | 505.31 | 207.68 | 0 | 0 | No
2030-04-01 05:00 | 2030 Initial | 700 | 0 | 394.13 | 172.87 | 0 | 0 | No
2030-04-01 06:00 | 2030 Initial | 700 | 0 | 510 | 229.44 | 0 | 0 | No
2030-04-01 07:00 | 2030 Initial | 700 | 3.34 | 510 | 427.26 | 0 | 0 | No
2030-04-01 08:00 | 2030 Initial | 700 | 303.34 | 510 | 510 | 0 | 0 | No
2030-04-01 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-01 10:00 | 2030 Initial | 700 | 205 | 510 | 500.78 | 0 | 0 | No
2030-04-01 11:00 | 2030 Initial | 647 | 505 | 510 | 510 | 0 | 0 | No
2030-04-01 12:00 | 2030 Initial | 297.45 | 505 | 510 | 510 | 0 | 0 | No
2030-04-01 13:00 | 2030 Initial | 348.16 | 505 | 510 | 510 | 0 | 0 | No
2030-04-01 14:00 | 2030 Initial | 348.16 | 457.1 | 300 | 510 | 0 | 0 | No
2030-04-01 15:00 | 2030 Initial | 699.19 | 157.1 | 0 | 510 | 0 | 0 | No
2030-04-01 16:00 | 2030 Initial | 700 | -142.9 | -300 | 259.56 | 0 | 0 | No
2030-04-01 17:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-04-01 18:00 | 2030 Initial | 700 | 0 | 300 | 210 | 0 | 0 | No
2030-04-01 19:00 | 2030 Initial | 700 | 0 | 510 | 358.85 | 0 | 0 | No
2030-04-01 20:00 | 2030 Initial | 700 | 0 | 510 | 79.04 | 0 | 0 | No
2030-04-01 21:00 | 2030 Initial | 700 | 0 | 510 | 173.29 | 0 | 0 | No
2030-04-01 22:00 | 2030 Initial | 700 | 205 | 442.36 | 465.38 | 0 | 0 | No
2030-04-01 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 04:00 | 2030 Initial | 429.67 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 05:00 | 2030 Initial | 172.22 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 06:00 | 2030 Initial | 10.1 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 07:00 | 2030 Initial | 329.67 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 08:00 | 2030 Initial | 23.17 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 09:00 | 2030 Initial | -396.83 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 11:00 | 2030 Initial | -700 | 505 | 510 | 467.91 | 0 | 0 | Yes
2030-04-02 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 16:00 | 2030 Initial | -387.33 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 17:00 | 2030 Initial | 32.67 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 18:00 | 2030 Initial | 45.83 | 205 | 210 | 227.9 | 0 | 0 | No
2030-04-02 19:00 | 2030 Initial | 465.83 | 0 | 118.33 | 510 | 0 | 0 | No
2030-04-02 20:00 | 2030 Initial | 700 | 0 | 118.33 | 510 | 0 | 0 | No
2030-04-02 21:00 | 2030 Initial | 700 | 0 | 418.33 | 454.74 | 0 | 0 | No
2030-04-02 22:00 | 2030 Initial | 700 | 0 | 118.33 | 437.88 | 0 | 0 | No
2030-04-02 23:00 | 2030 Initial | 700 | 0 | 353.75 | 510 | 0 | 0 | No
2030-04-03 | 2030 Initial | 700 | 0 | 53.75 | 210 | 0 | 0 | No
2030-04-03 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-03 02:00 | 2030 Initial | 700 | 0 | 0 | 23.73 | 0 | 0 | No
2030-04-03 03:00 | 2030 Initial | 700 | 0 | 0 | 0.23 | 0 | 0 | No
2030-04-03 04:00 | 2030 Initial | 420 | 0 | -300 | -32.04 | 0 | 0 | No
2030-04-03 05:00 | 2030 Initial | 0 | 0 | -8.06 | -149.94 | 0 | 0 | No
2030-04-03 06:00 | 2030 Initial | -420 | 0 | 291.94 | 0 | 0 | 0 | No
2030-04-03 07:00 | 2030 Initial | -184.76 | 0 | 349.08 | 0 | 0 | 0 | No
2030-04-03 08:00 | 2030 Initial | 235.24 | 58.96 | 90 | 300 | 0 | 0 | No
2030-04-03 09:00 | 2030 Initial | 655.24 | -174.9 | -210 | 0 | 0 | 0 | No
2030-04-03 10:00 | 2030 Initial | 700 | -474.9 | -510 | -94.76 | 0 | 0 | No
2030-04-03 11:00 | 2030 Initial | 692.93 | -526 | -510 | -114.78 | 0 | 0 | No
2030-04-03 12:00 | 2030 Initial | 407.15 | -526 | -510 | -284.66 | 0 | 0 | No
2030-04-03 13:00 | 2030 Initial | 593.69 | -526 | -510 | -222.96 | 0 | 0 | No
2030-04-03 14:00 | 2030 Initial | 326.92 | -526 | -510 | -510 | 0 | 0 | No
2030-04-03 15:00 | 2030 Initial | 700 | -526 | -510 | -410.93 | 0 | 0 | No
2030-04-03 16:00 | 2030 Initial | 700 | -274.56 | -510 | -110.93 | 0 | 0 | No
2030-04-03 17:00 | 2030 Initial | 700 | 0 | -327.67 | 0 | 0 | 0 | No
2030-04-03 18:00 | 2030 Initial | 700 | 0 | -493.59 | 0 | 0 | 0 | No
2030-04-03 19:00 | 2030 Initial | 700 | 0 | -193.59 | 0 | 0 | 0 | No
2030-04-03 20:00 | 2030 Initial | 700 | 0 | 106.41 | 2.06 | 0 | 0 | No
2030-04-03 21:00 | 2030 Initial | 700 | 300 | 406.41 | 302.06 | 0 | 0 | No
2030-04-03 22:00 | 2030 Initial | 700 | 45.63 | 295.29 | 300 | 0 | 0 | No
2030-04-03 23:00 | 2030 Initial | 700 | 0 | -4.71 | 0 | 0 | 0 | No
2030-04-04 | 2030 Initial | 700 | 0 | -304.71 | -27.78 | 0 | 0 | No
2030-04-04 01:00 | 2030 Initial | 700 | 0 | -510 | -89.87 | 0 | 0 | No
2030-04-04 02:00 | 2030 Initial | 700 | 0 | -510 | -89.87 | 0 | 0 | No
2030-04-04 03:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-04 04:00 | 2030 Initial | 404.86 | 0 | -510 | -58.74 | 0 | 0 | No
2030-04-04 05:00 | 2030 Initial | -15.14 | 0 | -510 | -128.47 | 0 | 0 | No
2030-04-04 06:00 | 2030 Initial | -435.14 | 0 | -442.29 | 0 | 0 | 0 | No
2030-04-04 07:00 | 2030 Initial | -15.14 | 0 | -376.67 | 0 | 0 | 0 | No
2030-04-04 08:00 | 2030 Initial | 204.88 | -300 | -510 | 60.91 | 0 | 0 | No
2030-04-04 09:00 | 2030 Initial | 68.46 | -526 | -510 | 243.3 | 0 | 0 | No
2030-04-04 10:00 | 2030 Initial | 488.46 | -526 | -510 | -56.7 | 0 | 0 | No
2030-04-04 11:00 | 2030 Initial | 68.46 | -526 | -510 | 210 | 0 | 0 | No
2030-04-04 12:00 | 2030 Initial | -87.6 | -226 | -210 | 510 | 0 | 0 | No
2030-04-04 13:00 | 2030 Initial | -367.36 | 0 | -474.03 | 510 | 0 | 0 | No
2030-04-04 14:00 | 2030 Initial | -447.41 | -90.92 | -210 | 510 | 0 | 0 | No
2030-04-04 15:00 | 2030 Initial | -27.41 | -390.92 | -510 | 376.3 | 0 | 0 | No
2030-04-04 16:00 | 2030 Initial | -11.16 | -526 | -510 | 222.66 | 0 | 0 | No
2030-04-04 17:00 | 2030 Initial | -210.39 | -526 | -510 | 327.36 | 0 | 0 | No
2030-04-04 18:00 | 2030 Initial | 140.87 | -526 | -510 | 310.69 | 0 | 0 | No
2030-04-04 19:00 | 2030 Initial | 406.63 | -300 | -314.25 | 248.69 | 0 | 0 | No
2030-04-04 20:00 | 2030 Initial | 560 | 0 | -14.25 | 248.69 | 0 | 0 | No
2030-04-04 21:00 | 2030 Initial | 140 | 300 | 285.75 | 510 | 0 | 0 | No
2030-04-04 22:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-04-04 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-05 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-05 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 03:00 | 2030 Initial | -700 | 505 | 510 | 486.03 | 0 | 0 | Yes
2030-04-05 04:00 | 2030 Initial | -700 | 505 | 510 | 186.03 | 0 | 0 | Yes
2030-04-05 05:00 | 2030 Initial | -700 | 505 | 510 | 162.31 | 0 | 0 | Yes
2030-04-05 06:00 | 2030 Initial | -700 | 505 | 510 | 243.87 | 0 | 0 | Yes
2030-04-05 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 12:00 | 2030 Initial | -700 | 505 | 510 | 489.25 | 0 | 0 | Yes
2030-04-05 13:00 | 2030 Initial | -700 | 505 | 510 | 275.32 | 0 | 0 | Yes
2030-04-05 14:00 | 2030 Initial | -700 | 505 | 510 | 221.03 | 0 | 0 | Yes
2030-04-05 15:00 | 2030 Initial | -700 | 505 | 510 | 223.62 | 0 | 0 | Yes
2030-04-05 16:00 | 2030 Initial | -700 | 505 | 510 | 319.73 | 0 | 0 | Yes
2030-04-05 17:00 | 2030 Initial | -700 | 505 | 510 | 362.49 | 0 | 0 | Yes
2030-04-05 18:00 | 2030 Initial | -700 | 505 | 510 | 336.65 | 0 | 0 | Yes
2030-04-05 19:00 | 2030 Initial | -700 | 505 | 510 | 299.66 | 0 | 0 | Yes
2030-04-05 20:00 | 2030 Initial | -700 | 505 | 510 | 311.33 | 0 | 0 | Yes
2030-04-05 21:00 | 2030 Initial | -700 | 505 | 510 | 304.78 | 0 | 0 | Yes
2030-04-05 22:00 | 2030 Initial | -700 | 505 | 510 | 229.19 | 0 | 0 | Yes
2030-04-05 23:00 | 2030 Initial | -700 | 505 | 510 | 158.3 | 0 | 0 | Yes
2030-04-06 | 2030 Initial | -454.29 | 505 | 510 | 458.3 | 0 | 0 | Yes
2030-04-06 01:00 | 2030 Initial | -618.85 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 02:00 | 2030 Initial | -618.85 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 03:00 | 2030 Initial | -550.17 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 04:00 | 2030 Initial | -202.81 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 05:00 | 2030 Initial | -480.98 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-06 08:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 13:00 | 2030 Initial | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-04-06 14:00 | 2030 Initial | -700 | 470.88 | 90 | 510 | 0 | 0 | Yes
2030-04-06 15:00 | 2030 Initial | -280 | 170.88 | -210 | 510 | 0 | 0 | No
2030-04-06 16:00 | 2030 Initial | 140 | -129.12 | -510 | 240.01 | 0 | 0 | No
2030-04-06 17:00 | 2030 Initial | 280 | -300 | -328.03 | 180.05 | 0 | 0 | No
2030-04-06 18:00 | 2030 Initial | 700 | 0 | -28.03 | 459.44 | 0 | 0 | No
2030-04-06 19:00 | 2030 Initial | 700 | 0 | 271.97 | 459.44 | 0 | 0 | No
2030-04-06 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-04-06 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-04-06 22:00 | 2030 Initial | 700 | 0 | 510 | 485 | 0 | 0 | No
2030-04-06 23:00 | 2030 Initial | 700 | 0 | 510 | 458.91 | 0 | 0 | No
2030-04-07 | 2030 Initial | 700 | 0 | 437.01 | 329.67 | 0 | 0 | No
2030-04-07 01:00 | 2030 Initial | 700 | 0 | 437.32 | 374.93 | 0 | 0 | No
2030-04-07 02:00 | 2030 Initial | 700 | 0 | 364.14 | 349.74 | 0 | 0 | No
2030-04-07 03:00 | 2030 Initial | 700 | 0 | 163.91 | 265.83 | 0 | 0 | No
2030-04-07 04:00 | 2030 Initial | 700 | 0 | -59.58 | 214.46 | 0 | 0 | No
2030-04-07 05:00 | 2030 Initial | 700 | 0 | 0 | 223.88 | 0 | 0 | No
2030-04-07 06:00 | 2030 Initial | 700 | 0 | -148.76 | 214.83 | 0 | 0 | No
2030-04-07 07:00 | 2030 Initial | 371.2 | -226 | -439.05 | 296.91 | 0 | 0 | No
2030-04-07 08:00 | 2030 Initial | -48.8 | -526 | -510 | 252.13 | 0 | 0 | No
2030-04-07 09:00 | 2030 Initial | -3.43 | -526 | -510 | 125.8 | 0 | 0 | No
2030-04-07 10:00 | 2030 Initial | -423.43 | -526 | -510 | -58.02 | 0 | 0 | No
2030-04-07 11:00 | 2030 Initial | -700 | -526 | -510 | -193.53 | 0 | 0 | No
2030-04-07 12:00 | 2030 Initial | -700 | -226 | -210 | 106.47 | 0 | 0 | No
2030-04-07 13:00 | 2030 Initial | -700 | -526 | -510 | 43.18 | 0 | 0 | No
2030-04-07 14:00 | 2030 Initial | -557.76 | -517.12 | -510 | 0 | 0 | 0 | No
2030-04-07 15:00 | 2030 Initial | -137.76 | -226 | -497.66 | 155.29 | 0 | 0 | No
2030-04-07 16:00 | 2030 Initial | 282.24 | -526 | -510 | -51.82 | 0 | 0 | No
2030-04-07 17:00 | 2030 Initial | 257.86 | -526 | -510 | 182.47 | 0 | 0 | No
2030-04-07 18:00 | 2030 Initial | 677.86 | -226 | -210 | 482.47 | 0 | 0 | No
2030-04-07 19:00 | 2030 Initial | 700 | 0 | -115.87 | 469.25 | 0 | 0 | No
2030-04-07 20:00 | 2030 Initial | 700 | 0 | 0 | 479.3 | 0 | 0 | No
2030-04-07 21:00 | 2030 Initial | 700 | 0 | 0 | 491.04 | 0 | 0 | No
2030-04-07 22:00 | 2030 Initial | 700 | 0 | -65.68 | 376.03 | 0 | 0 | No
2030-04-07 23:00 | 2030 Initial | 700 | 0 | -365.68 | 301.79 | 0 | 0 | No
2030-04-08 | 2030 Initial | 700 | 0 | -119.59 | 1.79 | 0 | 0 | No
2030-04-08 01:00 | 2030 Initial | 700 | 0 | -211.9 | 0 | 0 | 0 | No
2030-04-08 02:00 | 2030 Initial | 700 | 0 | -51.74 | 0 | 0 | 0 | No
2030-04-08 03:00 | 2030 Initial | 700 | 0 | -63.6 | 0 | 0 | 0 | No
2030-04-08 04:00 | 2030 Initial | 700 | 0 | -358.07 | 0 | 0 | 0 | No
2030-04-08 05:00 | 2030 Initial | 700 | 0 | -216.61 | 0 | 0 | 0 | No
2030-04-08 06:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-08 07:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-08 08:00 | 2030 Initial | 700 | -14.48 | -210 | 73.21 | 0 | 0 | No
2030-04-08 09:00 | 2030 Initial | 700 | -314.48 | -510 | 115.5 | 0 | 0 | No
2030-04-08 10:00 | 2030 Initial | 700 | -526 | -510 | 91.62 | 0 | 0 | No
2030-04-08 11:00 | 2030 Initial | 700 | -526 | -510 | 70.04 | 0 | 0 | No
2030-04-08 12:00 | 2030 Initial | 700 | -526 | -510 | 51.01 | 0 | 0 | No
2030-04-08 13:00 | 2030 Initial | 700 | -526 | -510 | 40.59 | 0 | 0 | No
2030-04-08 14:00 | 2030 Initial | 700 | -526 | -510 | 26.94 | 0 | 0 | No
2030-04-08 15:00 | 2030 Initial | 700 | -526 | -510 | 13.27 | 0 | 0 | No
2030-04-08 16:00 | 2030 Initial | 700 | -300 | -412.49 | 210 | 0 | 0 | No
2030-04-08 17:00 | 2030 Initial | 700 | 0 | -112.49 | 510 | 0 | 0 | No
2030-04-08 18:00 | 2030 Initial | 700 | 0 | 187.51 | 210 | 0 | 0 | No
2030-04-08 19:00 | 2030 Initial | 700 | 0 | 487.51 | 0 | 0 | 0 | No
2030-04-08 20:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-04-08 21:00 | 2030 Initial | 700 | 0 | 510 | 140.88 | 0 | 0 | No
2030-04-08 22:00 | 2030 Initial | 700 | 0 | 510 | 439.68 | 0 | 0 | No
2030-04-08 23:00 | 2030 Initial | 700 | 0 | 279.78 | 139.68 | 0 | 0 | No
2030-04-09 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-04-09 01:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-04-09 02:00 | 2030 Initial | 700 | 0 | 510 | 50.83 | 0 | 0 | No
2030-04-09 03:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-04-09 04:00 | 2030 Initial | 700 | 0 | 300 | 0 | 0 | 0 | No
2030-04-09 05:00 | 2030 Initial | 280 | 0 | 0 | 0 | 0 | 0 | No
2030-04-09 06:00 | 2030 Initial | 0 | -66.87 | -300 | -300 | 0 | 0 | No
2030-04-09 07:00 | 2030 Initial | 0 | -121.83 | -510 | -510 | 0 | 0 | No
2030-04-09 08:00 | 2030 Initial | 173.27 | -421.83 | -510 | -510 | 0 | 0 | No
2030-04-09 09:00 | 2030 Initial | -37.16 | -526 | -510 | -210 | 0 | 0 | No
2030-04-09 10:00 | 2030 Initial | -457.16 | -526 | -510 | -87.17 | 0 | 0 | No
2030-04-09 11:00 | 2030 Initial | -671.93 | -526 | -510 | -385.27 | 0 | 0 | No
2030-04-09 12:00 | 2030 Initial | -251.93 | -526 | -510 | -408.53 | 0 | 0 | No
2030-04-09 13:00 | 2030 Initial | -531.54 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 14:00 | 2030 Initial | -300.47 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 15:00 | 2030 Initial | 119.53 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 16:00 | 2030 Initial | 539.53 | -226 | -506.52 | -403.31 | 0 | 0 | No
2030-04-09 17:00 | 2030 Initial | 700 | 0 | -206.52 | -159.4 | 0 | 0 | No
2030-04-09 18:00 | 2030 Initial | 280 | -179.19 | -506.52 | -459.4 | 0 | 0 | No
2030-04-09 19:00 | 2030 Initial | 280 | 0 | -206.52 | -231.66 | 0 | 0 | No
2030-04-09 20:00 | 2030 Initial | 700 | 300 | 93.48 | 68.34 | 0 | 0 | No
2030-04-09 21:00 | 2030 Initial | 700 | 113.29 | 300 | 233.7 | 0 | 0 | No
2030-04-09 22:00 | 2030 Initial | 700 | -55.19 | 0 | -66.3 | 0 | 0 | No
2030-04-09 23:00 | 2030 Initial | 700 | 0 | -234.42 | -133.81 | 0 | 0 | No
2030-04-10 | 2030 Initial | 700 | 0 | 52.13 | 0 | 0 | 0 | No
2030-04-10 01:00 | 2030 Initial | 700 | 0 | 352.13 | 0 | 0 | 0 | No
2030-04-10 02:00 | 2030 Initial | 700 | 0 | 340.84 | 0 | 0 | 0 | No
2030-04-10 03:00 | 2030 Initial | 700 | 0 | 40.84 | 0 | 0 | 0 | No
2030-04-10 04:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-10 05:00 | 2030 Initial | 420 | 0 | 224.56 | 0 | 0 | 0 | No
2030-04-10 06:00 | 2030 Initial | 0 | 0 | 0 | 0 | 0 | 0 | No
2030-04-10 07:00 | 2030 Initial | 280 | -99.57 | -300 | -222.19 | 0 | 0 | No
2030-04-10 08:00 | 2030 Initial | 700 | 200.43 | 0 | 77.81 | 0 | 0 | No
2030-04-10 09:00 | 2030 Initial | 700 | 0 | 0 | 85.26 | 0 | 0 | No
2030-04-10 10:00 | 2030 Initial | 700 | 0 | -120.67 | 0 | 0 | 0 | No
2030-04-10 11:00 | 2030 Initial | 700 | 0 | -393.81 | 0 | 0 | 0 | No
2030-04-10 12:00 | 2030 Initial | 700 | 0 | -418.91 | 0 | 0 | 0 | No
2030-04-10 13:00 | 2030 Initial | 700 | 0 | -338.01 | 0 | 0 | 0 | No
2030-04-10 14:00 | 2030 Initial | 700 | 0 | -131.61 | 0 | 0 | 0 | No
2030-04-10 15:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-10 16:00 | 2030 Initial | 700 | 0 | 291.87 | 41.05 | 0 | 0 | No
2030-04-10 17:00 | 2030 Initial | 700 | 0 | 376.35 | 0 | 0 | 0 | No
2030-04-10 18:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-04-10 19:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-04-10 20:00 | 2030 Initial | 700 | 205 | 367.9 | 210 | 0 | 0 | No
2030-04-10 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-10 22:00 | 2030 Initial | 700 | 205 | 510 | 456.11 | 0 | 0 | No
2030-04-10 23:00 | 2030 Initial | 700 | 0 | 300 | 156.11 | 0 | 0 | No
2030-04-11 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-04-11 01:00 | 2030 Initial | 700 | 0 | 210 | 0 | 0 | 0 | No
2030-04-11 02:00 | 2030 Initial | 700 | 0 | 26.55 | 0 | 0 | 0 | No
2030-04-11 03:00 | 2030 Initial | 700 | 0 | 245.03 | 0 | 0 | 0 | No
2030-04-11 04:00 | 2030 Initial | 280 | 0 | 300 | 0 | 0 | 0 | No
2030-04-11 05:00 | 2030 Initial | -140 | 0 | 300 | 0 | 0 | 0 | No
2030-04-11 06:00 | 2030 Initial | -560 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 07:00 | 2030 Initial | -199.66 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 08:00 | 2030 Initial | 220.34 | 0 | 0 | 97.56 | 0 | 0 | No
2030-04-11 09:00 | 2030 Initial | 325.27 | -300 | -300 | 0 | 0 | 0 | No
2030-04-11 10:00 | 2030 Initial | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-04-11 11:00 | 2030 Initial | -320.46 | -526 | -510 | -49.95 | 0 | 0 | No
2030-04-11 12:00 | 2030 Initial | -618.56 | -526 | -510 | -57.94 | 0 | 0 | No
2030-04-11 13:00 | 2030 Initial | -700 | -526 | -510 | -76.67 | 0 | 0 | No
2030-04-11 14:00 | 2030 Initial | -690.23 | -526 | -510 | -95.93 | 0 | 0 | No
2030-04-11 15:00 | 2030 Initial | -270.23 | -526 | -510 | -326.97 | 0 | 0 | No
2030-04-11 16:00 | 2030 Initial | 149.77 | -526 | -510 | -224.14 | 0 | 0 | No
2030-04-11 17:00 | 2030 Initial | 569.77 | -226 | -409.96 | 0 | 0 | 0 | No
2030-04-11 18:00 | 2030 Initial | 316.98 | 0 | -109.96 | 0 | 0 | 0 | No
2030-04-11 19:00 | 2030 Initial | 700 | 0 | -300 | -300 | 0 | 0 | No
2030-04-11 20:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 21:00 | 2030 Initial | 700 | 270.66 | 300 | 300 | 0 | 0 | No
2030-04-11 22:00 | 2030 Initial | 700 | 0 | 510 | 437.03 | 0 | 0 | No
2030-04-11 23:00 | 2030 Initial | 700 | 0 | 510 | 137.03 | 0 | 0 | No
2030-04-12 | 2030 Initial | 700 | 0 | 510 | 437.03 | 0 | 0 | No
2030-04-12 01:00 | 2030 Initial | 700 | 0 | 510 | 185.45 | 0 | 0 | No
2030-04-12 02:00 | 2030 Initial | 700 | 0 | 510 | 70.7 | 0 | 0 | No
2030-04-12 03:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-04-12 04:00 | 2030 Initial | 700 | 0 | 300 | 182.93 | 0 | 0 | No
2030-04-12 05:00 | 2030 Initial | 318.41 | 0 | 0 | 0 | 0 | 0 | No
2030-04-12 06:00 | 2030 Initial | 700 | 0 | -300 | -221.83 | 0 | 0 | No
2030-04-12 07:00 | 2030 Initial | 700 | 0 | -510 | -263 | 0 | 0 | No
2030-04-12 08:00 | 2030 Initial | 700 | 0 | -510 | -185.09 | 0 | 0 | No
2030-04-12 09:00 | 2030 Initial | 700 | 0 | -510 | -300 | 0 | 0 | No
2030-04-12 10:00 | 2030 Initial | 700 | 0 | -480.48 | 0 | 0 | 0 | No
2030-04-12 11:00 | 2030 Initial | 700 | -28.42 | -510 | -227.55 | 0 | 0 | No
2030-04-12 12:00 | 2030 Initial | 280 | -328.42 | -510 | -226.31 | 0 | 0 | No
2030-04-12 13:00 | 2030 Initial | -10.34 | -526 | -510 | -140.78 | 0 | 0 | No
2030-04-12 14:00 | 2030 Initial | -30.57 | -526 | -510 | -320.71 | 0 | 0 | No
2030-04-12 15:00 | 2030 Initial | -336.04 | -526 | -510 | -185.34 | 0 | 0 | No
2030-04-12 16:00 | 2030 Initial | -634.52 | -526 | -510 | -47.72 | 0 | 0 | No
2030-04-12 17:00 | 2030 Initial | -465.31 | -526 | -510 | 93.46 | 0 | 0 | No
2030-04-12 18:00 | 2030 Initial | -386.9 | -526 | -510 | -6.77 | 0 | 0 | No
2030-04-12 19:00 | 2030 Initial | -319.02 | -395 | -390 | 83.1 | 0 | 0 | No
2030-04-12 20:00 | 2030 Initial | -341.39 | -95 | -90 | 78.75 | 0 | 0 | No
2030-04-12 21:00 | 2030 Initial | -655.24 | 205 | 210 | -188.94 | 0 | 0 | No
2030-04-12 22:00 | 2030 Initial | -235.24 | 505 | 510 | 73.93 | 0 | 0 | Yes
2030-04-12 23:00 | 2030 Initial | -151.5 | 505 | 510 | 0 | 0 | 0 | Yes
2030-04-13 | 2030 Initial | 0 | 505 | 510 | 300 | 0 | 0 | Yes
2030-04-13 01:00 | 2030 Initial | -49.33 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-13 02:00 | 2030 Initial | 0 | 505 | 510 | 501.25 | 0 | 0 | Yes
2030-04-13 03:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-13 04:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-13 05:00 | 2030 Initial | -200.5 | 505 | 510 | 423.45 | 0 | 0 | No
2030-04-13 06:00 | 2030 Initial | -88.27 | 205 | 210 | 123.45 | 0 | 0 | No
2030-04-13 07:00 | 2030 Initial | 52.58 | -95 | -90 | 1.66 | 0 | 0 | No
2030-04-13 08:00 | 2030 Initial | 472.58 | 0 | 79.83 | 301.66 | 0 | 0 | No
2030-04-13 09:00 | 2030 Initial | 52.58 | -133 | -220.17 | 510 | 0 | 0 | No
2030-04-13 10:00 | 2030 Initial | 0 | -133 | -510 | 510 | 0 | 0 | No
2030-04-13 11:00 | 2030 Initial | 0 | -415.17 | -510 | 510 | 0 | 0 | No
2030-04-13 12:00 | 2030 Initial | 0 | -115.17 | -510 | 510 | 0 | 0 | No
2030-04-13 13:00 | 2030 Initial | 0 | 0 | -510 | 510 | 0 | 0 | No
2030-04-13 14:00 | 2030 Initial | 280 | -226 | -239.03 | 510 | 0 | 0 | No
2030-04-13 15:00 | 2030 Initial | 700 | -526 | -510 | 492.34 | 0 | 0 | No
2030-04-13 16:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-13 17:00 | 2030 Initial | 700 | -513.06 | -510 | 510 | 0 | 0 | No
2030-04-13 18:00 | 2030 Initial | 700 | -213.06 | -210 | 510 | 0 | 0 | No
2030-04-13 19:00 | 2030 Initial | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-04-13 20:00 | 2030 Initial | 700 | 0 | 390 | 510 | 0 | 0 | No
2030-04-13 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-04-13 22:00 | 2030 Initial | 700 | 0 | 414.44 | 463.56 | 0 | 0 | No
2030-04-13 23:00 | 2030 Initial | 700 | 0 | 305.14 | 451.08 | 0 | 0 | No
2030-04-14 | 2030 Initial | 700 | 0 | 463.67 | 151.08 | 0 | 0 | No
2030-04-14 01:00 | 2030 Initial | 700 | 0 | 375.09 | 170.65 | 0 | 0 | No
2030-04-14 02:00 | 2030 Initial | 700 | 0 | 75.09 | 182.19 | 0 | 0 | No
2030-04-14 03:00 | 2030 Initial | 700 | 0 | 263.06 | 93.46 | 0 | 0 | No
2030-04-14 04:00 | 2030 Initial | 700 | 0 | 362.23 | 88.48 | 0 | 0 | No
2030-04-14 05:00 | 2030 Initial | 700 | 0 | 197.86 | 92.78 | 0 | 0 | No
2030-04-14 06:00 | 2030 Initial | 700 | 0 | 90 | 166.98 | 0 | 0 | No
2030-04-14 07:00 | 2030 Initial | 700 | -226 | -210 | 199.35 | 0 | 0 | No
2030-04-14 08:00 | 2030 Initial | 700 | -526 | -510 | 148.23 | 0 | 0 | No
2030-04-14 09:00 | 2030 Initial | 700 | -526 | -510 | 95.46 | 0 | 0 | No
2030-04-14 10:00 | 2030 Initial | 700 | -526 | -510 | 114.07 | 0 | 0 | No
2030-04-14 11:00 | 2030 Initial | 700 | -526 | -510 | 77.94 | 0 | 0 | No
2030-04-14 12:00 | 2030 Initial | 700 | -526 | -510 | 130.37 | 0 | 0 | No
2030-04-14 13:00 | 2030 Initial | 700 | -526 | -510 | 72.98 | 0 | 0 | No
2030-04-14 14:00 | 2030 Initial | 700 | -526 | -510 | 104.48 | 0 | 0 | No
2030-04-14 15:00 | 2030 Initial | 700 | -526 | -510 | 106.98 | 0 | 0 | No
2030-04-14 16:00 | 2030 Initial | 700 | -526 | -510 | 183.91 | 0 | 0 | No
2030-04-14 17:00 | 2030 Initial | 700 | -280.59 | -300 | 275.81 | 0 | 0 | No
2030-04-14 18:00 | 2030 Initial | 700 | 0 | 0 | 334.5 | 0 | 0 | No
2030-04-14 19:00 | 2030 Initial | 700 | 0 | 300 | 510 | 0 | 0 | No
2030-04-14 20:00 | 2030 Initial | 700 | 0 | 510 | 382.37 | 0 | 0 | No
2030-04-14 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-04-14 22:00 | 2030 Initial | 700 | 0 | 510 | 447.65 | 0 | 0 | No
2030-04-14 23:00 | 2030 Initial | 700 | 0 | 510 | 147.65 | 0 | 0 | No
2030-04-15 | 2030 Initial | 700 | 0 | 510 | 447.65 | 0 | 0 | No
2030-04-15 01:00 | 2030 Initial | 700 | 0 | 510 | 424.79 | 0 | 0 | No
2030-04-15 02:00 | 2030 Initial | 700 | 0 | 510 | 258.77 | 0 | 0 | No
2030-04-15 03:00 | 2030 Initial | 700 | 0 | 510 | 389.04 | 0 | 0 | No
2030-04-15 04:00 | 2030 Initial | 700 | 0 | 510 | 263.04 | 0 | 0 | No
2030-04-15 05:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-04-15 06:00 | 2030 Initial | 700 | 21.34 | 390 | 510 | 0 | 0 | No
2030-04-15 07:00 | 2030 Initial | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-04-15 08:00 | 2030 Initial | 700 | -226 | -210 | 510 | 0 | 0 | No
2030-04-15 09:00 | 2030 Initial | 700 | -526 | -510 | 255.79 | 0 | 0 | No
2030-04-15 10:00 | 2030 Initial | 700 | -526 | -510 | 222.86 | 0 | 0 | No
2030-04-15 11:00 | 2030 Initial | 700 | -526 | -510 | 218.12 | 0 | 0 | No
2030-04-15 12:00 | 2030 Initial | 700 | -526 | -510 | 222.36 | 0 | 0 | No
2030-04-15 13:00 | 2030 Initial | 700 | -526 | -510 | 189 | 0 | 0 | No
2030-04-15 14:00 | 2030 Initial | 700 | -526 | -510 | 164.55 | 0 | 0 | No
2030-04-15 15:00 | 2030 Initial | 700 | -526 | -510 | 188.89 | 0 | 0 | No
2030-04-15 16:00 | 2030 Initial | 700 | -526 | -510 | 287.11 | 0 | 0 | No
2030-04-15 17:00 | 2030 Initial | 700 | -226 | -210 | 510 | 0 | 0 | No
2030-04-15 18:00 | 2030 Initial | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-04-15 19:00 | 2030 Initial | 700 | 277.63 | 390 | 510 | 0 | 0 | No
2030-04-15 20:00 | 2030 Initial | 700 | 256.22 | 510 | 510 | 0 | 0 | No
2030-04-15 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-04-15 22:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-04-15 23:00 | 2030 Initial | 700 | 0 | 510 | 304.72 | 0 | 0 | No
2030-04-16 | 2030 Initial | 700 | -3.21 | 210 | 4.72 | 0 | 0 | No
2030-04-16 01:00 | 2030 Initial | 700 | 0 | -90 | 0 | 0 | 0 | No
2030-04-16 02:00 | 2030 Initial | 700 | 0 | -203.03 | 0 | 0 | 0 | No
2030-04-16 03:00 | 2030 Initial | 700 | 0 | -234.72 | 0 | 0 | 0 | No
2030-04-16 04:00 | 2030 Initial | 700 | 0 | -492.17 | 0 | 0 | 0 | No
2030-04-16 05:00 | 2030 Initial | 700 | 0 | -510 | -32.1 | 0 | 0 | No
2030-04-16 06:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-16 07:00 | 2030 Initial | 700 | 0 | -510 | 145.49 | 0 | 0 | No
2030-04-16 08:00 | 2030 Initial | 416.29 | -241.15 | -510 | 232.84 | 0 | 0 | No
2030-04-16 09:00 | 2030 Initial | -3.71 | -526 | -510 | 198.73 | 0 | 0 | No
2030-04-16 10:00 | 2030 Initial | -423.71 | -526 | -510 | 112.75 | 0 | 0 | No
2030-04-16 11:00 | 2030 Initial | -700 | -526 | -510 | -23.37 | 0 | 0 | No
2030-04-16 12:00 | 2030 Initial | -700 | -526 | -510 | -232.49 | 0 | 0 | No
2030-04-16 13:00 | 2030 Initial | -700 | -526 | -510 | -329.69 | 0 | 0 | No
2030-04-16 14:00 | 2030 Initial | -450.99 | -526 | -510 | -281.67 | 0 | 0 | No
2030-04-16 15:00 | 2030 Initial | -30.99 | -526 | -510 | -193 | 0 | 0 | No
2030-04-16 16:00 | 2030 Initial | 389.01 | -253.01 | -510 | -44.41 | 0 | 0 | No
2030-04-16 17:00 | 2030 Initial | 700 | 0 | -224.37 | 248.74 | 0 | 0 | No
2030-04-16 18:00 | 2030 Initial | 700 | 0 | 0 | 300 | 0 | 0 | No
2030-04-16 19:00 | 2030 Initial | 280 | -300 | -300 | 0 | 0 | 0 | No
2030-04-16 20:00 | 2030 Initial | 610.4 | 0 | 0 | -30.41 | 0 | 0 | No
2030-04-16 21:00 | 2030 Initial | 700 | 0 | -23.6 | -136.3 | 0 | 0 | No
2030-04-16 22:00 | 2030 Initial | 700 | 0 | 275.16 | -215.3 | 0 | 0 | No
2030-04-16 23:00 | 2030 Initial | 700 | 0 | 4.93 | -462.49 | 0 | 0 | No
2030-04-17 | 2030 Initial | 700 | 12.99 | 300 | -162.49 | 0 | 0 | No
2030-04-17 01:00 | 2030 Initial | 700 | 0 | 0 | -224.46 | 0 | 0 | No
2030-04-17 02:00 | 2030 Initial | 700 | 0 | -74.38 | 0 | 0 | 0 | No
2030-04-17 03:00 | 2030 Initial | 700 | 0 | -95 | 0 | 0 | 0 | No
2030-04-17 04:00 | 2030 Initial | 700 | 0 | -56.68 | -256.91 | 0 | 0 | No
2030-04-17 05:00 | 2030 Initial | 700 | 0 | -305.94 | -313.07 | 0 | 0 | No
2030-04-17 06:00 | 2030 Initial | 280 | 0 | -5.94 | -13.07 | 0 | 0 | No
2030-04-17 07:00 | 2030 Initial | 317.17 | 0 | -184.98 | 0 | 0 | 0 | No
2030-04-17 08:00 | 2030 Initial | 700 | 0 | -484.98 | -300 | 0 | 0 | No
2030-04-17 09:00 | 2030 Initial | 395.34 | -268.45 | -510 | -322.6 | 0 | 0 | No
2030-04-17 10:00 | 2030 Initial | -24.66 | -526 | -510 | -72.63 | 0 | 0 | No
2030-04-17 11:00 | 2030 Initial | 395.34 | -526 | -510 | -372.63 | 0 | 0 | No
2030-04-17 12:00 | 2030 Initial | -24.66 | -526 | -510 | -409.32 | 0 | 0 | No
2030-04-17 13:00 | 2030 Initial | -444.66 | -526 | -510 | -510 | 0 | 0 | No
2030-04-17 14:00 | 2030 Initial | -700 | -526 | -510 | -381.44 | 0 | 0 | No
2030-04-17 15:00 | 2030 Initial | -414.39 | -526 | -510 | -128.65 | 0 | 0 | No
2030-04-17 16:00 | 2030 Initial | 5.61 | -386.87 | -510 | -77.51 | 0 | 0 | No
2030-04-17 17:00 | 2030 Initial | 425.61 | -194.18 | -510 | 140.58 | 0 | 0 | No
2030-04-17 18:00 | 2030 Initial | 631.03 | 0 | -510 | -23.78 | 0 | 0 | No
2030-04-17 19:00 | 2030 Initial | 211.03 | 0 | -281.33 | 217.8 | 0 | 0 | No
2030-04-17 20:00 | 2030 Initial | 280 | 0 | 0 | 291.33 | 0 | 0 | No
2030-04-17 21:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-17 22:00 | 2030 Initial | 700 | 0 | -242.92 | 0 | 0 | 0 | No
2030-04-17 23:00 | 2030 Initial | 700 | 0 | -210 | -62.22 | 0 | 0 | No
2030-04-18 | 2030 Initial | 700 | 0 | -510 | -362.22 | 0 | 0 | No
2030-04-18 01:00 | 2030 Initial | 700 | 0 | -510 | -259.16 | 0 | 0 | No
2030-04-18 02:00 | 2030 Initial | 700 | -52.73 | -510 | -259.16 | 0 | 0 | No
2030-04-18 03:00 | 2030 Initial | 700 | -202.94 | -510 | -110.35 | 0 | 0 | No
2030-04-18 04:00 | 2030 Initial | 420 | -188.51 | -510 | -112.29 | 0 | 0 | No
2030-04-18 05:00 | 2030 Initial | 0 | 0 | -510 | -135.28 | 0 | 0 | No
2030-04-18 06:00 | 2030 Initial | 0 | 0 | -510 | -21.41 | 0 | 0 | No
2030-04-18 07:00 | 2030 Initial | 58.56 | 0 | -510 | -51.35 | 0 | 0 | No
2030-04-18 08:00 | 2030 Initial | 478.56 | -226 | -510 | -38.49 | 0 | 0 | No
2030-04-18 09:00 | 2030 Initial | 656.07 | -526 | -510 | -111.45 | 0 | 0 | No
2030-04-18 10:00 | 2030 Initial | 236.07 | -526 | -510 | -95.17 | 0 | 0 | No
2030-04-18 11:00 | 2030 Initial | 129.5 | -526 | -510 | 0 | 0 | 0 | No
2030-04-18 12:00 | 2030 Initial | 0 | -526 | -510 | -148.18 | 0 | 0 | No
2030-04-18 13:00 | 2030 Initial | 62.32 | -526 | -510 | -353.97 | 0 | 0 | No
2030-04-18 14:00 | 2030 Initial | 140.92 | -526 | -510 | -53.97 | 0 | 0 | No
2030-04-18 15:00 | 2030 Initial | 427.34 | -526 | -510 | -353.97 | 0 | 0 | No
2030-04-18 16:00 | 2030 Initial | 613.2 | -340.94 | -510 | -214.8 | 0 | 0 | No
2030-04-18 17:00 | 2030 Initial | 700 | -40.94 | -510 | -242.71 | 0 | 0 | No
2030-04-18 18:00 | 2030 Initial | 700 | 0 | -510 | -371.85 | 0 | 0 | No
2030-04-18 19:00 | 2030 Initial | 700 | 0 | -510 | -71.85 | 0 | 0 | No
2030-04-18 20:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-18 21:00 | 2030 Initial | 700 | 0 | -388.42 | 0 | 0 | 0 | No
2030-04-18 22:00 | 2030 Initial | 700 | 0 | -88.42 | 0 | 0 | 0 | No
2030-04-18 23:00 | 2030 Initial | 700 | 0 | -388.42 | -25.6 | 0 | 0 | No
2030-04-19 | 2030 Initial | 700 | -178.49 | -510 | -246.65 | 0 | 0 | No
2030-04-19 01:00 | 2030 Initial | 700 | -303.72 | -510 | -316.33 | 0 | 0 | No
2030-04-19 02:00 | 2030 Initial | 700 | -227.12 | -510 | -322.15 | 0 | 0 | No
2030-04-19 03:00 | 2030 Initial | 700 | -29.12 | -510 | -121.51 | 0 | 0 | No
2030-04-19 04:00 | 2030 Initial | 700 | -290.24 | -510 | -389.64 | 0 | 0 | No
2030-04-19 05:00 | 2030 Initial | 643.42 | -500.74 | -510 | -89.64 | 0 | 0 | No
2030-04-19 06:00 | 2030 Initial | 223.42 | -200.74 | -510 | 22.69 | 0 | 0 | No
2030-04-19 07:00 | 2030 Initial | 0 | -92.42 | -510 | -266.55 | 0 | 0 | No
2030-04-19 08:00 | 2030 Initial | 0 | -278.43 | -510 | 33.45 | 0 | 0 | No
2030-04-19 09:00 | 2030 Initial | -420 | -526 | -510 | -266.55 | 0 | 0 | No
2030-04-19 10:00 | 2030 Initial | -700 | -526 | -510 | -460.19 | 0 | 0 | No
2030-04-19 11:00 | 2030 Initial | -700 | -526 | -510 | -391.35 | 0 | 0 | No
2030-04-19 12:00 | 2030 Initial | -700 | -526 | -510 | -167.81 | 0 | 0 | No
2030-04-19 13:00 | 2030 Initial | -700 | -526 | -510 | -467.81 | 0 | 0 | No
2030-04-19 14:00 | 2030 Initial | -700 | -526 | -510 | -330.3 | 0 | 0 | No
2030-04-19 15:00 | 2030 Initial | -700 | -526 | -510 | -88.07 | 0 | 0 | No
2030-04-19 16:00 | 2030 Initial | -700 | -526 | -510 | -38.41 | 0 | 0 | No
2030-04-19 17:00 | 2030 Initial | -280 | -526 | -510 | 94.15 | 0 | 0 | No
2030-04-19 18:00 | 2030 Initial | 140 | -526 | -510 | 240.91 | 0 | 0 | No
2030-04-19 19:00 | 2030 Initial | 560 | -277.46 | -510 | 187.49 | 0 | 0 | No
2030-04-19 20:00 | 2030 Initial | 700 | -81.29 | -510 | -102.47 | 0 | 0 | No
2030-04-19 21:00 | 2030 Initial | 700 | 0 | -258.58 | 9.88 | 0 | 0 | No
2030-04-19 22:00 | 2030 Initial | 280 | 0 | 41.42 | 157.94 | 0 | 0 | No
2030-04-19 23:00 | 2030 Initial | 700 | 300 | 341.42 | 457.94 | 0 | 0 | No
2030-04-20 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-20 05:00 | 2030 Initial | 293.57 | 205 | 210 | 259.87 | 0 | 0 | No
2030-04-20 06:00 | 2030 Initial | 0 | -95 | -90 | -40.13 | 0 | 0 | No
2030-04-20 07:00 | 2030 Initial | -40.26 | -395 | -390 | -340.13 | 0 | 0 | No
2030-04-20 08:00 | 2030 Initial | -78.92 | -396.85 | -510 | -510 | 0 | 0 | No
2030-04-20 09:00 | 2030 Initial | -280 | -96.85 | -210 | -210 | 0 | 0 | No
2030-04-20 10:00 | 2030 Initial | -700 | 203.15 | 90 | 90 | 0 | 0 | No
2030-04-20 11:00 | 2030 Initial | -700 | 503.15 | 390 | 390 | 0 | 0 | Yes
2030-04-20 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-20 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-20 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-20 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-20 16:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-20 17:00 | 2030 Initial | -280 | 492.58 | 510 | 510 | 0 | 0 | No
2030-04-20 18:00 | 2030 Initial | 131.72 | 192.58 | 210 | 322.75 | 0 | 0 | No
2030-04-20 19:00 | 2030 Initial | 551.72 | 0 | 30.1 | 249.89 | 0 | 0 | No
2030-04-20 20:00 | 2030 Initial | 636.3 | 205 | 210 | 235.73 | 0 | 0 | No
2030-04-20 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-21 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 02:00 | 2030 Initial | 700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-04-21 03:00 | 2030 Initial | 700 | 505 | 510 | 171.15 | 0 | 0 | Yes
2030-04-21 04:00 | 2030 Initial | 700 | 505 | 510 | 373.98 | 0 | 0 | Yes
2030-04-21 05:00 | 2030 Initial | 700 | 505 | 510 | 361.88 | 0 | 0 | Yes
2030-04-21 06:00 | 2030 Initial | 280 | 505 | 510 | 105.28 | 0 | 0 | Yes
2030-04-21 07:00 | 2030 Initial | -140 | 505 | 510 | 75.09 | 0 | 0 | Yes
2030-04-21 08:00 | 2030 Initial | -560 | 505 | 510 | 58.4 | 0 | 0 | Yes
2030-04-21 09:00 | 2030 Initial | -700 | 505 | 510 | 358.4 | 0 | 0 | Yes
2030-04-21 10:00 | 2030 Initial | -700 | 505 | 510 | 425.47 | 0 | 0 | Yes
2030-04-21 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-21 16:00 | 2030 Initial | -328.93 | 505 | 510 | 510 | 0 | 0 | No
2030-04-21 17:00 | 2030 Initial | 91.07 | 505 | 510 | 510 | 0 | 0 | No
2030-04-21 18:00 | 2030 Initial | 420 | 380.07 | 510 | 510 | 0 | 0 | No
2030-04-21 19:00 | 2030 Initial | 0 | 80.07 | 210 | 210 | 0 | 0 | No
2030-04-21 20:00 | 2030 Initial | 364.87 | 205 | 510 | 456.96 | 0 | 0 | No
2030-04-21 21:00 | 2030 Initial | 700 | 505 | 510 | 372.29 | 0 | 0 | Yes
2030-04-21 22:00 | 2030 Initial | 700 | 505 | 510 | 187.43 | 0 | 0 | Yes
2030-04-21 23:00 | 2030 Initial | 700 | 505 | 510 | 245.72 | 0 | 0 | Yes
2030-04-22 | 2030 Initial | 700 | 505 | 510 | 303.51 | 0 | 0 | Yes
2030-04-22 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-22 02:00 | 2030 Initial | 700 | 505 | 510 | 300.8 | 0 | 0 | Yes
2030-04-22 03:00 | 2030 Initial | 700 | 505 | 510 | 0.8 | 0 | 0 | Yes
2030-04-22 04:00 | 2030 Initial | 700 | 505 | 510 | 300.8 | 0 | 0 | Yes
2030-04-22 05:00 | 2030 Initial | 700 | 505 | 510 | 102 | 0 | 0 | No
2030-04-22 06:00 | 2030 Initial | 700 | 505 | 510 | 402 | 0 | 0 | No
2030-04-22 07:00 | 2030 Initial | 700 | 505 | 510 | 341.61 | 0 | 0 | No
2030-04-22 08:00 | 2030 Initial | 280 | 205 | 510 | 336.48 | 0 | 0 | No
2030-04-22 09:00 | 2030 Initial | 0 | 0 | 406.07 | 36.48 | 0 | 0 | No
2030-04-22 10:00 | 2030 Initial | 0 | 0 | 431.47 | 0 | 0 | 0 | No
2030-04-22 11:00 | 2030 Initial | 0 | 0 | 431.47 | 172.99 | 0 | 0 | No
2030-04-22 12:00 | 2030 Initial | 0 | 0 | 510 | 472.99 | 0 | 0 | No
2030-04-22 13:00 | 2030 Initial | 0 | 205 | 455.27 | 210 | 0 | 0 | No
2030-04-22 14:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-04-22 15:00 | 2030 Initial | 700 | 269 | 210 | 510 | 0 | 0 | No
2030-04-22 16:00 | 2030 Initial | 700 | -31 | -90 | 325.31 | 0 | 0 | No
2030-04-22 17:00 | 2030 Initial | 690.06 | -300 | -390 | 196.24 | 0 | 0 | No
2030-04-22 18:00 | 2030 Initial | 700 | 0 | -93.17 | 69.42 | 0 | 0 | No
2030-04-22 19:00 | 2030 Initial | 700 | 0 | -136.52 | 0 | 0 | 0 | No
2030-04-22 20:00 | 2030 Initial | 700 | 0 | 3.69 | 0 | 0 | 0 | No
2030-04-22 21:00 | 2030 Initial | 700 | 0 | 103.96 | 293.45 | 0 | 0 | No
2030-04-22 22:00 | 2030 Initial | 700 | 0 | 55.26 | 140.69 | 0 | 0 | No
2030-04-22 23:00 | 2030 Initial | 700 | 0 | 0 | 22.34 | 0 | 0 | No
2030-04-23 | 2030 Initial | 700 | 0 | -98.73 | 0 | 0 | 0 | No
2030-04-23 01:00 | 2030 Initial | 700 | 0 | -312.65 | 0 | 0 | 0 | No
2030-04-23 02:00 | 2030 Initial | 700 | 0 | -436.05 | 0 | 0 | 0 | No
2030-04-23 03:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-23 04:00 | 2030 Initial | 700 | 0 | -440.24 | 0 | 0 | 0 | No
2030-04-23 05:00 | 2030 Initial | 700 | 0 | -510 | -48.93 | 0 | 0 | No
2030-04-23 06:00 | 2030 Initial | 280 | 0 | -342.73 | 0 | 0 | 0 | No
2030-04-23 07:00 | 2030 Initial | 280 | 0 | -427.7 | 0 | 0 | 0 | No
2030-04-23 08:00 | 2030 Initial | 700 | -181.68 | -510 | 0 | 0 | 0 | No
2030-04-23 09:00 | 2030 Initial | 280 | -481.68 | -510 | -266.4 | 0 | 0 | No
2030-04-23 10:00 | 2030 Initial | -107.12 | -526 | -510 | -309.51 | 0 | 0 | No
2030-04-23 11:00 | 2030 Initial | -527.12 | -526 | -510 | -179.12 | 0 | 0 | No
2030-04-23 12:00 | 2030 Initial | -610.11 | -526 | -510 | -212.24 | 0 | 0 | No
2030-04-23 13:00 | 2030 Initial | -525.27 | -526 | -510 | -22.51 | 0 | 0 | No
2030-04-23 14:00 | 2030 Initial | -105.27 | -526 | -510 | -175.93 | 0 | 0 | No
2030-04-23 15:00 | 2030 Initial | 28.66 | -526 | -510 | -147.5 | 0 | 0 | No
2030-04-23 16:00 | 2030 Initial | 448.66 | -282.66 | -510 | -54.56 | 0 | 0 | No
2030-04-23 17:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-23 18:00 | 2030 Initial | 700 | 0 | -310.11 | 0 | 0 | 0 | No
2030-04-23 19:00 | 2030 Initial | 700 | 0 | -10.11 | 0 | 0 | 0 | No
2030-04-23 20:00 | 2030 Initial | 700 | 0 | -10.11 | 0 | 0 | 0 | No
2030-04-23 21:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-23 22:00 | 2030 Initial | 700 | 0 | 1.54 | 0 | 0 | 0 | No
2030-04-23 23:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-24 | 2030 Initial | 700 | 0 | 300 | 51.88 | 0 | 0 | No
2030-04-24 01:00 | 2030 Initial | 700 | 0 | 510 | 51.88 | 0 | 0 | No
2030-04-24 02:00 | 2030 Initial | 700 | 0 | 510 | 93.39 | 0 | 0 | No
2030-04-24 03:00 | 2030 Initial | 700 | 0 | 390 | 1.94 | 0 | 0 | No
2030-04-24 04:00 | 2030 Initial | 700 | 0 | 90 | 0 | 0 | 0 | No
2030-04-24 05:00 | 2030 Initial | 280 | 0 | -210 | -129.25 | 0 | 0 | No
2030-04-24 06:00 | 2030 Initial | 212.65 | 0 | -510 | -222.18 | 0 | 0 | No
2030-04-24 07:00 | 2030 Initial | 212.65 | 0 | -510 | 0 | 0 | 0 | No
2030-04-24 08:00 | 2030 Initial | 191.17 | -226 | -510 | 0 | 0 | 0 | No
2030-04-24 09:00 | 2030 Initial | 471.5 | -526 | -510 | 0 | 0 | 0 | No
2030-04-24 10:00 | 2030 Initial | 136.53 | -526 | -510 | 0 | 0 | 0 | No
2030-04-24 11:00 | 2030 Initial | 0 | -526 | -510 | 241.74 | 0 | 0 | No
2030-04-24 12:00 | 2030 Initial | 0 | -526 | -510 | 510 | 0 | 0 | No
2030-04-24 13:00 | 2030 Initial | 0 | -526 | -510 | 510 | 0 | 0 | No
2030-04-24 14:00 | 2030 Initial | 135.69 | -526 | -510 | 269.72 | 0 | 0 | No
2030-04-24 15:00 | 2030 Initial | 555.69 | -526 | -510 | 6.96 | 0 | 0 | No
2030-04-24 16:00 | 2030 Initial | 700 | -279.15 | -498.99 | -77.78 | 0 | 0 | No
2030-04-24 17:00 | 2030 Initial | 700 | 0 | -198.99 | 0 | 0 | 0 | No
2030-04-24 18:00 | 2030 Initial | 700 | 0 | -408.62 | -187.34 | 0 | 0 | No
2030-04-24 19:00 | 2030 Initial | 700 | -300 | -446.13 | -487.34 | 0 | 0 | No
2030-04-24 20:00 | 2030 Initial | 700 | 0 | -146.13 | -187.34 | 0 | 0 | No
2030-04-24 21:00 | 2030 Initial | 700 | 300 | 153.87 | 112.66 | 0 | 0 | No
2030-04-24 22:00 | 2030 Initial | 700 | 0 | 453.87 | 395.68 | 0 | 0 | No
2030-04-24 23:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-04-25 | 2030 Initial | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-04-25 01:00 | 2030 Initial | 700 | 120.21 | 510 | 510 | 0 | 0 | No
2030-04-25 02:00 | 2030 Initial | 700 | 420.21 | 510 | 510 | 0 | 0 | No
2030-04-25 03:00 | 2030 Initial | 700 | 374.67 | 510 | 510 | 0 | 0 | No
2030-04-25 04:00 | 2030 Initial | 700 | 300 | 300 | 300 | 0 | 0 | No
2030-04-25 05:00 | 2030 Initial | 280 | 0 | 0 | 0 | 0 | 0 | No
2030-04-25 06:00 | 2030 Initial | 412.55 | 0 | -300 | -224.27 | 0 | 0 | No
2030-04-25 07:00 | 2030 Initial | 307.8 | 0 | -510 | -76.4 | 0 | 0 | No
2030-04-25 08:00 | 2030 Initial | 268.06 | -226 | -510 | 0 | 0 | 0 | No
2030-04-25 09:00 | 2030 Initial | 212.31 | -526 | -510 | -103.6 | 0 | 0 | No
2030-04-25 10:00 | 2030 Initial | -207.69 | -526 | -510 | 123.99 | 0 | 0 | No
2030-04-25 11:00 | 2030 Initial | -458.8 | -526 | -510 | 409.22 | 0 | 0 | No
2030-04-25 12:00 | 2030 Initial | -458.8 | -526 | -510 | 510 | 0 | 0 | No
2030-04-25 13:00 | 2030 Initial | -140.2 | -526 | -510 | 510 | 0 | 0 | No
2030-04-25 14:00 | 2030 Initial | 0 | -526 | -510 | 212.72 | 0 | 0 | No
2030-04-25 15:00 | 2030 Initial | 280 | -526 | -510 | 212.72 | 0 | 0 | No
2030-04-25 16:00 | 2030 Initial | 700 | -526 | -510 | -86.67 | 0 | 0 | No
2030-04-25 17:00 | 2030 Initial | 700 | -226 | -210 | 17.07 | 0 | 0 | No
2030-04-25 18:00 | 2030 Initial | 700 | 43.73 | 0 | 0 | 0 | 0 | No
2030-04-25 19:00 | 2030 Initial | 700 | -250.28 | -300 | -300 | 0 | 0 | No
2030-04-25 20:00 | 2030 Initial | 700 | 0 | -149.99 | 0 | 0 | 0 | No
2030-04-25 21:00 | 2030 Initial | 700 | 300 | 150.01 | 300 | 0 | 0 | No
2030-04-25 22:00 | 2030 Initial | 700 | 0 | 410.41 | 0 | 0 | 0 | No
2030-04-25 23:00 | 2030 Initial | 700 | 0 | 234.64 | 0 | 0 | 0 | No
2030-04-26 | 2030 Initial | 700 | 0 | 510 | 300 | 0 | 0 | No
2030-04-26 01:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-04-26 02:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-04-26 03:00 | 2030 Initial | 700 | 0 | 390 | 390 | 0 | 0 | No
2030-04-26 04:00 | 2030 Initial | 700 | 0 | 90 | 90 | 0 | 0 | No
2030-04-26 05:00 | 2030 Initial | 361.05 | 0 | -210 | -210 | 0 | 0 | No
2030-04-26 06:00 | 2030 Initial | 635 | 0 | -510 | -510 | 0 | 0 | No
2030-04-26 07:00 | 2030 Initial | 635 | 0 | -510 | -510 | 0 | 0 | No
2030-04-26 08:00 | 2030 Initial | 635 | 0 | -510 | -510 | 0 | 0 | No
2030-04-26 09:00 | 2030 Initial | 700 | 0 | -455.29 | -210 | 0 | 0 | No
2030-04-26 10:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-26 11:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-26 12:00 | 2030 Initial | 700 | 0 | -454.43 | 0 | 0 | 0 | No
2030-04-26 13:00 | 2030 Initial | 700 | 0 | -378.4 | 0 | 0 | 0 | No
2030-04-26 14:00 | 2030 Initial | 700 | 0 | -458.4 | 0 | 0 | 0 | No
2030-04-26 15:00 | 2030 Initial | 700 | 0 | -358.55 | 0 | 0 | 0 | No
2030-04-26 16:00 | 2030 Initial | 700 | 0 | -58.55 | 0 | 0 | 0 | No
2030-04-26 17:00 | 2030 Initial | 700 | 0 | -277.7 | 0 | 0 | 0 | No
2030-04-26 18:00 | 2030 Initial | 700 | 0 | -510 | -63.06 | 0 | 0 | No
2030-04-26 19:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-26 20:00 | 2030 Initial | 700 | 0 | -396.69 | 0 | 0 | 0 | No
2030-04-26 21:00 | 2030 Initial | 700 | 0 | -96.69 | -5.68 | 0 | 0 | No
2030-04-26 22:00 | 2030 Initial | 700 | 0 | 203.31 | 179.63 | 0 | 0 | No
2030-04-26 23:00 | 2030 Initial | 700 | 0 | 103.8 | 0 | 0 | 0 | No
2030-04-27 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 02:00 | 2030 Initial | 700 | 0 | 106.81 | 0 | 0 | 0 | No
2030-04-27 03:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 04:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 05:00 | 2030 Initial | 280 | 0 | -210 | -210 | 0 | 0 | No
2030-04-27 06:00 | 2030 Initial | -140 | -300 | -510 | -510 | 0 | 0 | No
2030-04-27 07:00 | 2030 Initial | -245 | -526 | -510 | -510 | 0 | 0 | No
2030-04-27 08:00 | 2030 Initial | 175 | -226 | -510 | -210 | 0 | 0 | No
2030-04-27 09:00 | 2030 Initial | -245 | -526 | -510 | -170.81 | 0 | 0 | No
2030-04-27 10:00 | 2030 Initial | -423.85 | -526 | -510 | -302.24 | 0 | 0 | No
2030-04-27 11:00 | 2030 Initial | -700 | -526 | -510 | -335.19 | 0 | 0 | No
2030-04-27 12:00 | 2030 Initial | -700 | -526 | -510 | -139.01 | 0 | 0 | No
2030-04-27 13:00 | 2030 Initial | -700 | -526 | -510 | -139.01 | 0 | 0 | No
2030-04-27 14:00 | 2030 Initial | -700 | -526 | -510 | -358.33 | 0 | 0 | No
2030-04-27 15:00 | 2030 Initial | -324.13 | -526 | -510 | -319.76 | 0 | 0 | No
2030-04-27 16:00 | 2030 Initial | 95.87 | -526 | -510 | -88.36 | 0 | 0 | No
2030-04-27 17:00 | 2030 Initial | 515.87 | -226 | -388.41 | -210 | 0 | 0 | No
2030-04-27 18:00 | 2030 Initial | 700 | -339.13 | -510 | -510 | 0 | 0 | No
2030-04-27 19:00 | 2030 Initial | 700 | -339.13 | -510 | -510 | 0 | 0 | No
2030-04-27 20:00 | 2030 Initial | 700 | -300 | -300 | -300 | 0 | 0 | No
2030-04-27 21:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 22:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 23:00 | 2030 Initial | 700 | 0 | -221.94 | 0 | 0 | 0 | No
2030-04-28 | 2030 Initial | 700 | 0 | -107.89 | 0 | 0 | 0 | No
2030-04-28 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-28 02:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-28 03:00 | 2030 Initial | 700 | 0 | -127.85 | 0 | 0 | 0 | No
2030-04-28 04:00 | 2030 Initial | 700 | 0 | -264.24 | 0 | 0 | 0 | No
2030-04-28 05:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-28 06:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-28 07:00 | 2030 Initial | 700 | -226 | -510 | 0 | 0 | 0 | No
2030-04-28 08:00 | 2030 Initial | 700 | -526 | -510 | -148 | 0 | 0 | No
2030-04-28 09:00 | 2030 Initial | 700 | -526 | -510 | -204.8 | 0 | 0 | No
2030-04-28 10:00 | 2030 Initial | 700 | -526 | -510 | -257 | 0 | 0 | No
2030-04-28 11:00 | 2030 Initial | 700 | -526 | -510 | -210.8 | 0 | 0 | No
2030-04-28 12:00 | 2030 Initial | 700 | -526 | -510 | -226.38 | 0 | 0 | No
2030-04-28 13:00 | 2030 Initial | 700 | -526 | -510 | -194.73 | 0 | 0 | No
2030-04-28 14:00 | 2030 Initial | 700 | -526 | -510 | -289.15 | 0 | 0 | No
2030-04-28 15:00 | 2030 Initial | 700 | -526 | -510 | -144.25 | 0 | 0 | No
2030-04-28 16:00 | 2030 Initial | 700 | -526 | -510 | -130.5 | 0 | 0 | No
2030-04-28 17:00 | 2030 Initial | 700 | -486.88 | -510 | -2.79 | 0 | 0 | No
2030-04-28 18:00 | 2030 Initial | 700 | -186.88 | -458.31 | 39.33 | 0 | 0 | No
2030-04-28 19:00 | 2030 Initial | 700 | 0 | -211.07 | 64.83 | 0 | 0 | No
2030-04-28 20:00 | 2030 Initial | 700 | 0 | -237.81 | 153.17 | 0 | 0 | No
2030-04-28 21:00 | 2030 Initial | 700 | 0 | -510 | 139.06 | 0 | 0 | No
2030-04-28 22:00 | 2030 Initial | 700 | 0 | -462.53 | 62.96 | 0 | 0 | No
2030-04-28 23:00 | 2030 Initial | 700 | -131.08 | -510 | 0 | 0 | 0 | No
2030-04-29 | 2030 Initial | 700 | -431.08 | -510 | -94.23 | 0 | 0 | No
2030-04-29 01:00 | 2030 Initial | 700 | -526 | -510 | -113.14 | 0 | 0 | No
2030-04-29 02:00 | 2030 Initial | 700 | -526 | -510 | -113.14 | 0 | 0 | No
2030-04-29 03:00 | 2030 Initial | 700 | -526 | -510 | 53.24 | 0 | 0 | No
2030-04-29 04:00 | 2030 Initial | 700 | -526 | -510 | -180.02 | 0 | 0 | No
2030-04-29 05:00 | 2030 Initial | 700 | -526 | -510 | -100.75 | 0 | 0 | No
2030-04-29 06:00 | 2030 Initial | 700 | -526 | -510 | -57.94 | 0 | 0 | No
2030-04-29 07:00 | 2030 Initial | 700 | -526 | -510 | 18.97 | 0 | 0 | No
2030-04-29 08:00 | 2030 Initial | 700 | -526 | -510 | -143.76 | 0 | 0 | No
2030-04-29 09:00 | 2030 Initial | 700 | -526 | -510 | -68.41 | 0 | 0 | No
2030-04-29 10:00 | 2030 Initial | 700 | -526 | -510 | -368.41 | 0 | 0 | No
2030-04-29 11:00 | 2030 Initial | 700 | -380.94 | -390 | -166.33 | 0 | 0 | No
2030-04-29 12:00 | 2030 Initial | 700 | -80.94 | -90 | 133.67 | 0 | 0 | No
2030-04-29 13:00 | 2030 Initial | 700 | 219.06 | 210 | 433.67 | 0 | 0 | No
2030-04-29 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-29 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-29 16:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-29 17:00 | 2030 Initial | 700 | 222.5 | 510 | 510 | 0 | 0 | No
2030-04-29 18:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-29 19:00 | 2030 Initial | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-04-29 20:00 | 2030 Initial | 700 | -95 | -90 | 510 | 0 | 0 | No
2030-04-29 21:00 | 2030 Initial | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-04-29 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-29 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 05:00 | 2030 Initial | 700 | 476.94 | 510 | 510 | 0 | 0 | No
2030-04-30 06:00 | 2030 Initial | 700 | 176.94 | 210 | 210 | 0 | 0 | No
2030-04-30 07:00 | 2030 Initial | 700 | 0 | -45.41 | 0 | 0 | 0 | No
2030-04-30 08:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-04-30 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 14:00 | 2030 Initial | 700 | 374 | 390 | 510 | 0 | 0 | No
2030-04-30 15:00 | 2030 Initial | 700 | 74 | 90 | 510 | 0 | 0 | No
2030-04-30 16:00 | 2030 Initial | 700 | -226 | -210 | 210 | 0 | 0 | No
2030-04-30 17:00 | 2030 Initial | 700 | -526 | -510 | 283.42 | 0 | 0 | No
2030-04-30 18:00 | 2030 Initial | 700 | -226 | -210 | 58.31 | 0 | 0 | No
2030-04-30 19:00 | 2030 Initial | 700 | 0 | 39.35 | 297.22 | 0 | 0 | No
2030-04-30 20:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-04-30 21:00 | 2030 Initial | 700 | 0 | 56.78 | 510 | 0 | 0 | No
2030-04-30 22:00 | 2030 Initial | 700 | 0 | 56.88 | 256.63 | 0 | 0 | No
2030-04-30 23:00 | 2030 Initial | 700 | -76.94 | -90 | 510 | 0 | 0 | No
2030-05-01 | 2030 Initial | 700 | 223.06 | 210 | 510 | 0 | 0 | No
2030-05-01 01:00 | 2030 Initial | 700 | 398.36 | 510 | 510 | 0 | 0 | No
2030-05-01 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-01 03:00 | 2030 Initial | 700 | 505 | 505.64 | 510 | 0 | 0 | No
2030-05-01 04:00 | 2030 Initial | 700 | 205 | 205.64 | 510 | 0 | 0 | No
2030-05-01 05:00 | 2030 Initial | 700 | -95 | -94.36 | 510 | 0 | 0 | No
2030-05-01 06:00 | 2030 Initial | 700 | -395 | -394.36 | 510 | 0 | 0 | No
2030-05-01 07:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-01 08:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-01 09:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-01 10:00 | 2030 Initial | 280 | -226 | -210 | 510 | 0 | 0 | No
2030-05-01 11:00 | 2030 Initial | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-05-01 12:00 | 2030 Initial | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-05-01 13:00 | 2030 Initial | 0 | 0 | -205.95 | 510 | 0 | 0 | No
2030-05-01 14:00 | 2030 Initial | 169.34 | -226 | -329.53 | 453.36 | 0 | 0 | No
2030-05-01 15:00 | 2030 Initial | 589.34 | -526 | -510 | 153.36 | 0 | 0 | No
2030-05-01 16:00 | 2030 Initial | 700 | -526 | -510 | -103.21 | 0 | 0 | No
2030-05-01 17:00 | 2030 Initial | 700 | -526 | -510 | -108.07 | 0 | 0 | No
2030-05-01 18:00 | 2030 Initial | 700 | -300 | -510 | 191.93 | 0 | 0 | No
2030-05-01 19:00 | 2030 Initial | 700 | 0 | -510 | 426.08 | 0 | 0 | No
2030-05-01 20:00 | 2030 Initial | 700 | -38.13 | -510 | 510 | 0 | 0 | No
2030-05-01 21:00 | 2030 Initial | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-05-01 22:00 | 2030 Initial | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-05-01 23:00 | 2030 Initial | 700 | -97.99 | -510 | 438.62 | 0 | 0 | No
2030-05-02 | 2030 Initial | 700 | -37.94 | -210 | 156.89 | 0 | 0 | No
2030-05-02 01:00 | 2030 Initial | 700 | 205 | 90 | 210 | 0 | 0 | No
2030-05-02 02:00 | 2030 Initial | 700 | 505 | 390 | 510 | 0 | 0 | No
2030-05-02 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-02 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-02 05:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-05-02 06:00 | 2030 Initial | 700 | 0 | -90 | 0 | 0 | 0 | No
2030-05-02 07:00 | 2030 Initial | 700 | 0 | -154.99 | 0 | 0 | 0 | No
2030-05-02 08:00 | 2030 Initial | 700 | -226 | -453.28 | 0 | 0 | 0 | No
2030-05-02 09:00 | 2030 Initial | 560 | -526 | -510 | -203.93 | 0 | 0 | No
2030-05-02 10:00 | 2030 Initial | 140 | -526 | -510 | -177.83 | 0 | 0 | No
2030-05-02 11:00 | 2030 Initial | -280 | -526 | -510 | -105.49 | 0 | 0 | No
2030-05-02 12:00 | 2030 Initial | -700 | -526 | -510 | -162.17 | 0 | 0 | No
2030-05-02 13:00 | 2030 Initial | -605.82 | -526 | -510 | -203.85 | 0 | 0 | No
2030-05-02 14:00 | 2030 Initial | -225.99 | -526 | -510 | -172.36 | 0 | 0 | No
2030-05-02 15:00 | 2030 Initial | -104.26 | -526 | -510 | -59.49 | 0 | 0 | No
2030-05-02 16:00 | 2030 Initial | 315.74 | -254.72 | -510 | 24.55 | 0 | 0 | No
2030-05-02 17:00 | 2030 Initial | 700 | 0 | -388.7 | 151.77 | 0 | 0 | No
2030-05-02 18:00 | 2030 Initial | 700 | 0 | -315.55 | 0 | 0 | 0 | No
2030-05-02 19:00 | 2030 Initial | 700 | 0 | -315.55 | 0 | 0 | 0 | No
2030-05-02 20:00 | 2030 Initial | 700 | 0 | -15.55 | 0 | 0 | 0 | No
2030-05-02 21:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-02 22:00 | 2030 Initial | 700 | 0 | 300 | 241.28 | 0 | 0 | No
2030-05-02 23:00 | 2030 Initial | 700 | 0 | 175.31 | 11.54 | 0 | 0 | No
2030-05-03 | 2030 Initial | 700 | 0 | -4.54 | 207.35 | 0 | 0 | No
2030-05-03 01:00 | 2030 Initial | 700 | 0 | -213.83 | 0 | 0 | 0 | No
2030-05-03 02:00 | 2030 Initial | 700 | 0 | -411.72 | 0 | 0 | 0 | No
2030-05-03 03:00 | 2030 Initial | 700 | -13.89 | -510 | 0 | 0 | 0 | No
2030-05-03 04:00 | 2030 Initial | 700 | -74.43 | -510 | 0 | 0 | 0 | No
2030-05-03 05:00 | 2030 Initial | 700 | -187.5 | -510 | 0 | 0 | 0 | No
2030-05-03 06:00 | 2030 Initial | 700 | -75.73 | -510 | 0 | 0 | 0 | No
2030-05-03 07:00 | 2030 Initial | 700 | -75.3 | -510 | 46.25 | 0 | 0 | No
2030-05-03 08:00 | 2030 Initial | 430.87 | -226 | -509.32 | 105.69 | 0 | 0 | No
2030-05-03 09:00 | 2030 Initial | 10.87 | -526 | -510 | 88.03 | 0 | 0 | No
2030-05-03 10:00 | 2030 Initial | -20.59 | -526 | -510 | 38.01 | 0 | 0 | No
2030-05-03 11:00 | 2030 Initial | -440.59 | -526 | -510 | 36.63 | 0 | 0 | No
2030-05-03 12:00 | 2030 Initial | -597.25 | -526 | -510 | 0 | 0 | 0 | No
2030-05-03 13:00 | 2030 Initial | -491.35 | -526 | -510 | 0 | 0 | 0 | No
2030-05-03 14:00 | 2030 Initial | -343.88 | -526 | -510 | 0 | 0 | 0 | No
2030-05-03 15:00 | 2030 Initial | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-05-03 16:00 | 2030 Initial | 320.49 | -526 | -510 | 14.03 | 0 | 0 | No
2030-05-03 17:00 | 2030 Initial | 700 | -349.76 | -510 | -263.46 | 0 | 0 | No
2030-05-03 18:00 | 2030 Initial | 700 | -49.76 | -510 | -475.76 | 0 | 0 | No
2030-05-03 19:00 | 2030 Initial | 700 | 0 | -510 | -175.76 | 0 | 0 | No
2030-05-03 20:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-05-03 21:00 | 2030 Initial | 700 | 0 | -245.95 | 0 | 0 | 0 | No
2030-05-03 22:00 | 2030 Initial | 700 | 0 | 54.05 | 94.72 | 0 | 0 | No
2030-05-03 23:00 | 2030 Initial | 700 | 0 | -245.95 | -53.21 | 0 | 0 | No
2030-05-04 | 2030 Initial | 700 | -79.51 | -510 | -301.07 | 0 | 0 | No
2030-05-04 01:00 | 2030 Initial | 700 | -9.41 | -510 | -425.13 | 0 | 0 | No
2030-05-04 02:00 | 2030 Initial | 700 | -139.95 | -510 | -295.59 | 0 | 0 | No
2030-05-04 03:00 | 2030 Initial | 700 | -423.95 | -510 | -245.74 | 0 | 0 | No
2030-05-04 04:00 | 2030 Initial | 491.88 | -526 | -510 | -232.66 | 0 | 0 | No
2030-05-04 05:00 | 2030 Initial | 321.6 | -526 | -510 | -284.63 | 0 | 0 | No
2030-05-04 06:00 | 2030 Initial | 0 | -526 | -510 | -148.94 | 0 | 0 | No
2030-05-04 07:00 | 2030 Initial | -145.23 | -526 | -510 | 151.06 | 0 | 0 | No
2030-05-04 08:00 | 2030 Initial | 137.86 | -526 | -510 | 53.25 | 0 | 0 | No
2030-05-04 09:00 | 2030 Initial | 557.86 | -526 | -510 | -56.88 | 0 | 0 | No
2030-05-04 10:00 | 2030 Initial | 621.08 | -526 | -510 | -192.2 | 0 | 0 | No
2030-05-04 11:00 | 2030 Initial | 201.08 | -526 | -510 | -173.08 | 0 | 0 | No
2030-05-04 12:00 | 2030 Initial | -149.63 | -526 | -510 | 35.7 | 0 | 0 | No
2030-05-04 13:00 | 2030 Initial | -402.08 | -526 | -510 | -18.28 | 0 | 0 | No
2030-05-04 14:00 | 2030 Initial | -435.51 | -526 | -510 | -77.32 | 0 | 0 | No
2030-05-04 15:00 | 2030 Initial | -122.68 | -526 | -510 | -103.39 | 0 | 0 | No
2030-05-04 16:00 | 2030 Initial | 280 | -526 | -510 | -66 | 0 | 0 | No
2030-05-04 17:00 | 2030 Initial | 700 | -526 | -510 | -115.05 | 0 | 0 | No
2030-05-04 18:00 | 2030 Initial | 700 | -526 | -510 | -54.81 | 0 | 0 | No
2030-05-04 19:00 | 2030 Initial | 700 | -526 | -510 | -30.84 | 0 | 0 | No
2030-05-04 20:00 | 2030 Initial | 700 | -526 | -510 | -7.44 | 0 | 0 | No
2030-05-04 21:00 | 2030 Initial | 700 | -526 | -510 | 16.46 | 0 | 0 | No
2030-05-04 22:00 | 2030 Initial | 700 | -226 | -300 | -167.28 | 0 | 0 | No
2030-05-04 23:00 | 2030 Initial | 700 | 74 | 0 | 132.72 | 0 | 0 | No
2030-05-05 | 2030 Initial | 544.7 | 0 | 234.67 | 113.26 | 0 | 0 | No
2030-05-05 01:00 | 2030 Initial | 572.22 | 0 | 0 | 289.94 | 0 | 0 | No
2030-05-05 02:00 | 2030 Initial | 152.22 | 0 | 225.51 | 91.39 | 0 | 0 | No
2030-05-05 03:00 | 2030 Initial | 0 | 0 | 388.8 | 0 | 0 | 0 | No
2030-05-05 04:00 | 2030 Initial | 0 | 0 | 94.29 | 247.11 | 0 | 0 | No
2030-05-05 05:00 | 2030 Initial | 0 | 0 | -205.71 | 0 | 0 | 0 | No
2030-05-05 06:00 | 2030 Initial | 0 | 0 | -505.71 | -194.51 | 0 | 0 | No
2030-05-05 07:00 | 2030 Initial | -280 | -300 | -510 | -301.84 | 0 | 0 | No
2030-05-05 08:00 | 2030 Initial | -700 | -526 | -510 | -361.29 | 0 | 0 | Yes
2030-05-05 09:00 | 2030 Initial | -700 | -526 | -510 | -222.68 | 0 | 0 | Yes
2030-05-05 10:00 | 2030 Initial | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-05 11:00 | 2030 Initial | -700 | -526 | -510 | -114.25 | 0 | 0 | Yes
2030-05-05 12:00 | 2030 Initial | -700 | -526 | -510 | -23.13 | 0 | 0 | Yes
2030-05-05 13:00 | 2030 Initial | -700 | -526 | -510 | -260.83 | 0 | 0 | Yes
2030-05-05 14:00 | 2030 Initial | -700 | -526 | -510 | -314.38 | 0 | 0 | Yes
2030-05-05 15:00 | 2030 Initial | -700 | -526 | -510 | -316.96 | 0 | 0 | Yes
2030-05-05 16:00 | 2030 Initial | -475.12 | -526 | -510 | -96.16 | 0 | 0 | No
2030-05-05 17:00 | 2030 Initial | -529.19 | -526 | -510 | 169.03 | 0 | 0 | No
2030-05-05 18:00 | 2030 Initial | -700 | -526 | -510 | 298.83 | 0 | 0 | No
2030-05-05 19:00 | 2030 Initial | -280 | -526 | -510 | 157.85 | 0 | 0 | No
2030-05-05 20:00 | 2030 Initial | 0 | -526 | -510 | 333.07 | 0 | 0 | No
2030-05-05 21:00 | 2030 Initial | 400.27 | -526 | -510 | 161.76 | 0 | 0 | No
2030-05-05 22:00 | 2030 Initial | 211.05 | -526 | -510 | 111.4 | 0 | 0 | No
2030-05-05 23:00 | 2030 Initial | 211.05 | -526 | -510 | 118.73 | 0 | 0 | No
2030-05-06 | 2030 Initial | 382.81 | -526 | -510 | 195.57 | 0 | 0 | No
2030-05-06 01:00 | 2030 Initial | 463.45 | -526 | -510 | 18.66 | 0 | 0 | No
2030-05-06 02:00 | 2030 Initial | 346.88 | -526 | -510 | 9.41 | 0 | 0 | No
2030-05-06 03:00 | 2030 Initial | 673.27 | -526 | -510 | 71.71 | 0 | 0 | No
2030-05-06 04:00 | 2030 Initial | 700 | -526 | -510 | -9.99 | 0 | 0 | No
2030-05-06 05:00 | 2030 Initial | 700 | -526 | -510 | -79.18 | 0 | 0 | No
2030-05-06 06:00 | 2030 Initial | 700 | -526 | -510 | -12.95 | 0 | 0 | No
2030-05-06 07:00 | 2030 Initial | 700 | -526 | -510 | -110.02 | 0 | 0 | No
2030-05-06 08:00 | 2030 Initial | 700 | -526 | -510 | -6.32 | 0 | 0 | No
2030-05-06 09:00 | 2030 Initial | 280 | -526 | -510 | -39.89 | 0 | 0 | No
2030-05-06 10:00 | 2030 Initial | -140 | -526 | -510 | 29.39 | 0 | 0 | No
2030-05-06 11:00 | 2030 Initial | -560 | -526 | -510 | -46.81 | 0 | 0 | No
2030-05-06 12:00 | 2030 Initial | -560 | -526 | -510 | -25.29 | 0 | 0 | No
2030-05-06 13:00 | 2030 Initial | -180.41 | -526 | -510 | -10.89 | 0 | 0 | No
2030-05-06 14:00 | 2030 Initial | -108.28 | -526 | -510 | -10.72 | 0 | 0 | No
2030-05-06 15:00 | 2030 Initial | 218.76 | -526 | -510 | 140.12 | 0 | 0 | No
2030-05-06 16:00 | 2030 Initial | 638.76 | -526 | -510 | 289.34 | 0 | 0 | No
2030-05-06 17:00 | 2030 Initial | 700 | -526 | -510 | 403.69 | 0 | 0 | No
2030-05-06 18:00 | 2030 Initial | 280 | -526 | -510 | 474.42 | 0 | 0 | No
2030-05-06 19:00 | 2030 Initial | 574.99 | -526 | -510 | 350.15 | 0 | 0 | No
2030-05-06 20:00 | 2030 Initial | 574.99 | -526 | -510 | 302.17 | 0 | 0 | No
2030-05-06 21:00 | 2030 Initial | 700 | -526 | -510 | 305.62 | 0 | 0 | No
2030-05-06 22:00 | 2030 Initial | 700 | -526 | -510 | 333.85 | 0 | 0 | No
2030-05-06 23:00 | 2030 Initial | 700 | -526 | -510 | 250.3 | 0 | 0 | No
2030-05-07 | 2030 Initial | 291.54 | -526 | -510 | 300.83 | 0 | 0 | No
2030-05-07 01:00 | 2030 Initial | 700 | -526 | -510 | 235.47 | 0 | 0 | No
2030-05-07 02:00 | 2030 Initial | 608.19 | -526 | -510 | 177.65 | 0 | 0 | No
2030-05-07 03:00 | 2030 Initial | 188.19 | -526 | -510 | 229.66 | 0 | 0 | No
2030-05-07 04:00 | 2030 Initial | 188.19 | -526 | -510 | 175.43 | 0 | 0 | No
2030-05-07 05:00 | 2030 Initial | 83.53 | -526 | -510 | 183.41 | 0 | 0 | No
2030-05-07 06:00 | 2030 Initial | -41.43 | -526 | -510 | 210.14 | 0 | 0 | No
2030-05-07 07:00 | 2030 Initial | 314.65 | -526 | -510 | 337.05 | 0 | 0 | No
2030-05-07 08:00 | 2030 Initial | 700 | -526 | -510 | 411.98 | 0 | 0 | No
2030-05-07 09:00 | 2030 Initial | 700 | -526 | -510 | 321.97 | 0 | 0 | No
2030-05-07 10:00 | 2030 Initial | 700 | -526 | -510 | 303.97 | 0 | 0 | No
2030-05-07 11:00 | 2030 Initial | 700 | -526 | -510 | 248.13 | 0 | 0 | No
2030-05-07 12:00 | 2030 Initial | 700 | -526 | -510 | 119.34 | 0 | 0 | No
2030-05-07 13:00 | 2030 Initial | 700 | -526 | -510 | 80.75 | 0 | 0 | No
2030-05-07 14:00 | 2030 Initial | 700 | -526 | -510 | 11.11 | 0 | 0 | No
2030-05-07 15:00 | 2030 Initial | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-07 16:00 | 2030 Initial | 700 | -526 | -510 | 199.93 | 0 | 0 | No
2030-05-07 17:00 | 2030 Initial | 700 | -226 | -210 | 378.63 | 0 | 0 | No
2030-05-07 18:00 | 2030 Initial | 700 | 0 | 90 | 466.46 | 0 | 0 | No
2030-05-07 19:00 | 2030 Initial | 700 | 0 | 259.64 | 510 | 0 | 0 | No
2030-05-07 20:00 | 2030 Initial | 700 | -209.84 | -40.36 | 210 | 0 | 0 | No
2030-05-07 21:00 | 2030 Initial | 700 | 90.16 | 259.64 | 510 | 0 | 0 | No
2030-05-07 22:00 | 2030 Initial | 700 | 367.52 | 510 | 510 | 0 | 0 | No
2030-05-07 23:00 | 2030 Initial | 700 | 67.52 | 428.8 | 293.53 | 0 | 0 | No
2030-05-08 | 2030 Initial | 700 | 0 | 510 | 369.72 | 0 | 0 | No
2030-05-08 01:00 | 2030 Initial | 700 | 0 | 510 | 69.72 | 0 | 0 | No
2030-05-08 02:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-05-08 03:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-05-08 04:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-05-08 05:00 | 2030 Initial | 700 | 0 | 300 | 0 | 0 | 0 | No
2030-05-08 06:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-08 07:00 | 2030 Initial | 700 | -111.71 | -300 | -206.74 | 0 | 0 | No
2030-05-08 08:00 | 2030 Initial | 700 | -226 | -210 | 93.26 | 0 | 0 | No
2030-05-08 09:00 | 2030 Initial | 700 | -526 | -510 | 131.24 | 0 | 0 | No
2030-05-08 10:00 | 2030 Initial | 700 | -526 | -510 | 170.76 | 0 | 0 | No
2030-05-08 11:00 | 2030 Initial | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 12:00 | 2030 Initial | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 13:00 | 2030 Initial | 700 | -526 | -510 | 43.7 | 0 | 0 | No
2030-05-08 14:00 | 2030 Initial | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 15:00 | 2030 Initial | 700 | -526 | -510 | 15.56 | 0 | 0 | No
2030-05-08 16:00 | 2030 Initial | 700 | -526 | -510 | 181.64 | 0 | 0 | No
2030-05-08 17:00 | 2030 Initial | 700 | -300 | -510 | 0 | 0 | 0 | No
2030-05-08 18:00 | 2030 Initial | 700 | 0 | -210 | 0 | 0 | 0 | No
2030-05-08 19:00 | 2030 Initial | 700 | 0 | 75.46 | 0 | 0 | 0 | No
2030-05-08 20:00 | 2030 Initial | 700 | 0 | 117.18 | 0 | 0 | 0 | No
2030-05-08 21:00 | 2030 Initial | 700 | 0 | 417.18 | 0 | 0 | 0 | No
2030-05-08 22:00 | 2030 Initial | 700 | 0 | 117.18 | 0 | 0 | 0 | No
2030-05-08 23:00 | 2030 Initial | 700 | 0 | 300 | 183.64 | 0 | 0 | No
2030-05-09 | 2030 Initial | 700 | 0 | 38.03 | 0 | 0 | 0 | No
2030-05-09 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-09 02:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-09 03:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-09 04:00 | 2030 Initial | 700 | 0 | -44.55 | 0 | 0 | 0 | No
2030-05-09 05:00 | 2030 Initial | 700 | 0 | -191.77 | 0 | 0 | 0 | No
2030-05-09 06:00 | 2030 Initial | 700 | -226 | 0 | 0 | 0 | 0 | No
2030-05-09 07:00 | 2030 Initial | 656.29 | -526 | 0 | -186.89 | 0 | 0 | No
2030-05-09 08:00 | 2030 Initial | 236.29 | -526 | 0 | 110.95 | 0 | 0 | No
2030-05-09 09:00 | 2030 Initial | 136.55 | -526 | 0 | 97.18 | 0 | 0 | No
2030-05-09 10:00 | 2030 Initial | 556.55 | -526 | 0 | 62.7 | 0 | 0 | No
2030-05-09 11:00 | 2030 Initial | 700 | -526 | 0 | 79.14 | 0 | 0 | No
2030-05-09 12:00 | 2030 Initial | 700 | -526 | 0 | 88.52 | 0 | 0 | No
2030-05-09 13:00 | 2030 Initial | 700 | -526 | 0 | 57.72 | 0 | 0 | No
2030-05-09 14:00 | 2030 Initial | 700 | -526 | 0 | 44.89 | 0 | 0 | No
2030-05-09 15:00 | 2030 Initial | 700 | -526 | 0 | 96.87 | 0 | 0 | No
2030-05-09 16:00 | 2030 Initial | 280 | -526 | 0 | 207.32 | 0 | 0 | No
2030-05-09 17:00 | 2030 Initial | 700 | -226 | 0 | 274.28 | 0 | 0 | No
2030-05-09 18:00 | 2030 Initial | 700 | 0 | 0 | 385.36 | 0 | 0 | No
2030-05-09 19:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-05-09 20:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-05-09 21:00 | 2030 Initial | 700 | 0 | 0 | 380.94 | 0 | 0 | No
2030-05-09 22:00 | 2030 Initial | 700 | 0 | 0 | 80.94 | 0 | 0 | No
2030-05-09 23:00 | 2030 Initial | 700 | 0 | 0 | -193.84 | 0 | 0 | No
2030-05-10 | 2030 Initial | 280 | -197.4 | 0 | -300.42 | 0 | 0 | No
2030-05-10 01:00 | 2030 Initial | -140 | -141.88 | 0 | -0.42 | 0 | 0 | No
2030-05-10 02:00 | 2030 Initial | 280 | 158.12 | 0 | 210 | 0 | 0 | No
2030-05-10 03:00 | 2030 Initial | 700 | 458.12 | 0 | 510 | 0 | 0 | No
2030-05-10 04:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 05:00 | 2030 Initial | 700 | 505 | 0 | 488.54 | 0 | 0 | Yes
2030-05-10 06:00 | 2030 Initial | 700 | 505 | 0 | 442.99 | 0 | 0 | Yes
2030-05-10 07:00 | 2030 Initial | 323.53 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 08:00 | 2030 Initial | -96.47 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 09:00 | 2030 Initial | -516.47 | 505 | 0 | 451.15 | 0 | 0 | Yes
2030-05-10 10:00 | 2030 Initial | -700 | 505 | 0 | 326.73 | 0 | 0 | Yes
2030-05-10 11:00 | 2030 Initial | -700 | 505 | 0 | 137.02 | 0 | 0 | Yes
2030-05-10 12:00 | 2030 Initial | -700 | 505 | 0 | 316.72 | 0 | 0 | Yes
2030-05-10 13:00 | 2030 Initial | -700 | 505 | 0 | 276.91 | 0 | 0 | Yes
2030-05-10 14:00 | 2030 Initial | -700 | 505 | 0 | 363.78 | 0 | 0 | Yes
2030-05-10 15:00 | 2030 Initial | -700 | 505 | 0 | 499.79 | 0 | 0 | Yes
2030-05-10 16:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 17:00 | 2030 Initial | -700 | 505 | 0 | 486.78 | 0 | 0 | Yes
2030-05-10 18:00 | 2030 Initial | -411.9 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 19:00 | 2030 Initial | 8.1 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 20:00 | 2030 Initial | 428.1 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 21:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 22:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 23:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 01:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 02:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 03:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 04:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 05:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 06:00 | 2030 Initial | 449.59 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 07:00 | 2030 Initial | 29.59 | 505 | 300 | 510 | 0 | 0 | No
2030-05-11 08:00 | 2030 Initial | -390.41 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 16:00 | 2030 Initial | -280 | 300 | 291.55 | 510 | 0 | 0 | Yes
2030-05-11 17:00 | 2030 Initial | 140 | 0 | -8.45 | 332.48 | 0 | 0 | No
2030-05-11 18:00 | 2030 Initial | 560 | -300 | -308.45 | 32.48 | 0 | 0 | No
2030-05-11 19:00 | 2030 Initial | 700 | 0 | -8.45 | 103.11 | 0 | 0 | No
2030-05-11 20:00 | 2030 Initial | 700 | 0 | 0 | 60.89 | 0 | 0 | No
2030-05-11 21:00 | 2030 Initial | 700 | 0 | 264.07 | 360.89 | 0 | 0 | No
2030-05-11 22:00 | 2030 Initial | 700 | 0 | 486.96 | 130.26 | 0 | 0 | No
2030-05-11 23:00 | 2030 Initial | 700 | 205 | 210 | 400.71 | 0 | 0 | No
2030-05-12 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 08:00 | 2030 Initial | 700 | 205 | 210 | 235.16 | 0 | 0 | No
2030-05-12 09:00 | 2030 Initial | 361.47 | 0 | 0 | 0 | 0 | 0 | No
2030-05-12 10:00 | 2030 Initial | 52.89 | 0 | 0 | 0 | 0 | 0 | No
2030-05-12 11:00 | 2030 Initial | 109.35 | 0 | -300 | -148.87 | 0 | 0 | No
2030-05-12 12:00 | 2030 Initial | 275.48 | 0 | 0 | 0 | 0 | 0 | No
2030-05-12 13:00 | 2030 Initial | 155.77 | 0 | 0 | 0 | 0 | 0 | No
2030-05-12 14:00 | 2030 Initial | 575.77 | -226 | -210 | -126.74 | 0 | 0 | No
2030-05-12 15:00 | 2030 Initial | 700 | -526 | -510 | -426.74 | 0 | 0 | No
2030-05-12 16:00 | 2030 Initial | 700 | -526 | -510 | -356.87 | 0 | 0 | No
2030-05-12 17:00 | 2030 Initial | 700 | -526 | -510 | -404.69 | 0 | 0 | No
2030-05-12 18:00 | 2030 Initial | 700 | -226 | -510 | -104.69 | 0 | 0 | No
2030-05-12 19:00 | 2030 Initial | 700 | 0 | -263.84 | 11.48 | 0 | 0 | No
2030-05-12 20:00 | 2030 Initial | 700 | 0 | -212.95 | 13.68 | 0 | 0 | No
2030-05-12 21:00 | 2030 Initial | 700 | 0 | -67.65 | 0 | 0 | 0 | No
2030-05-12 22:00 | 2030 Initial | 700 | 0 | -67.65 | 0 | 0 | 0 | No
2030-05-12 23:00 | 2030 Initial | 700 | 0 | 187.39 | 210 | 0 | 0 | No
2030-05-13 | 2030 Initial | 700 | 300 | 487.39 | 510 | 0 | 0 | No
2030-05-13 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 08:00 | 2030 Initial | 687.7 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 09:00 | 2030 Initial | 267.7 | 300 | 450.05 | 510 | 0 | 0 | No
2030-05-13 10:00 | 2030 Initial | 44.74 | 0 | 150.05 | 510 | 0 | 0 | No
2030-05-13 11:00 | 2030 Initial | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-05-13 12:00 | 2030 Initial | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-05-13 13:00 | 2030 Initial | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-05-13 14:00 | 2030 Initial | 83.84 | 0 | 0 | 510 | 0 | 0 | No
2030-05-13 15:00 | 2030 Initial | 503.84 | -15.25 | -210 | 510 | 0 | 0 | No
2030-05-13 16:00 | 2030 Initial | 700 | -315.25 | -510 | 454.99 | 0 | 0 | No
2030-05-13 17:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-13 18:00 | 2030 Initial | 700 | -226 | -210 | 510 | 0 | 0 | No
2030-05-13 19:00 | 2030 Initial | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-05-13 20:00 | 2030 Initial | 700 | 0 | 352.73 | 510 | 0 | 0 | No
2030-05-13 21:00 | 2030 Initial | 700 | 0 | 430.48 | 465.89 | 0 | 0 | No
2030-05-13 22:00 | 2030 Initial | 700 | 0 | 130.48 | 510 | 0 | 0 | No
2030-05-13 23:00 | 2030 Initial | 700 | 0 | 0 | 473.74 | 0 | 0 | No
2030-05-14 | 2030 Initial | 700 | 0 | 0 | 173.74 | 0 | 0 | No
2030-05-14 01:00 | 2030 Initial | 700 | 0 | 0 | 116.35 | 0 | 0 | No
2030-05-14 02:00 | 2030 Initial | 700 | 0 | 0 | 95.11 | 0 | 0 | No
2030-05-14 03:00 | 2030 Initial | 700 | 0 | 125.55 | 103.61 | 0 | 0 | No
2030-05-14 04:00 | 2030 Initial | 700 | 0 | 0 | 103.22 | 0 | 0 | No
2030-05-14 05:00 | 2030 Initial | 700 | 0 | 0 | 99.14 | 0 | 0 | No
2030-05-14 06:00 | 2030 Initial | 700 | 0 | -59.14 | 146.97 | 0 | 0 | No
2030-05-14 07:00 | 2030 Initial | 700 | -226 | -237.37 | 212.28 | 0 | 0 | No
2030-05-14 08:00 | 2030 Initial | 700 | -526 | -510 | 320.73 | 0 | 0 | No
2030-05-14 09:00 | 2030 Initial | 700 | -526 | -510 | 329.55 | 0 | 0 | No
2030-05-14 10:00 | 2030 Initial | 700 | -526 | -510 | 269.23 | 0 | 0 | No
2030-05-14 11:00 | 2030 Initial | 700 | -526 | -510 | 264.03 | 0 | 0 | No
2030-05-14 12:00 | 2030 Initial | 700 | -526 | -510 | -35.97 | 0 | 0 | No
2030-05-14 13:00 | 2030 Initial | 700 | -526 | -510 | -112.9 | 0 | 0 | No
2030-05-14 14:00 | 2030 Initial | 700 | -526 | -510 | 85.13 | 0 | 0 | No
2030-05-14 15:00 | 2030 Initial | 700 | -526 | -510 | -36.38 | 0 | 0 | No
2030-05-14 16:00 | 2030 Initial | 700 | -526 | -510 | -200.06 | 0 | 0 | No
2030-05-14 17:00 | 2030 Initial | 700 | -526 | -510 | 82.9 | 0 | 0 | No
2030-05-14 18:00 | 2030 Initial | 700 | -226 | -210 | 0 | 0 | 0 | No
2030-05-14 19:00 | 2030 Initial | 700 | 0 | 90 | 0 | 0 | 0 | No
2030-05-14 20:00 | 2030 Initial | 700 | 0 | 390 | 135.31 | 0 | 0 | No
2030-05-14 21:00 | 2030 Initial | 700 | 0 | 510 | 260.41 | 0 | 0 | No
2030-05-14 22:00 | 2030 Initial | 700 | 0 | 434.74 | 282.14 | 0 | 0 | No
2030-05-14 23:00 | 2030 Initial | 700 | 0 | 510 | 151.24 | 0 | 0 | No
2030-05-15 | 2030 Initial | 700 | 0 | 510 | 181.63 | 0 | 0 | No
2030-05-15 01:00 | 2030 Initial | 700 | 0 | 510 | 181.63 | 0 | 0 | No
2030-05-15 02:00 | 2030 Initial | 700 | 0 | 510 | 253.12 | 0 | 0 | No
2030-05-15 03:00 | 2030 Initial | 700 | 0 | 510 | 316.91 | 0 | 0 | No
2030-05-15 04:00 | 2030 Initial | 700 | 0 | 510 | 82.32 | 0 | 0 | No
2030-05-15 05:00 | 2030 Initial | 700 | 0 | 390 | 371.1 | 0 | 0 | No
2030-05-15 06:00 | 2030 Initial | 700 | 0 | 90 | 71.1 | 0 | 0 | No
2030-05-15 07:00 | 2030 Initial | 700 | -126.84 | -210 | 183.08 | 0 | 0 | No
2030-05-15 08:00 | 2030 Initial | 700 | -426.84 | -510 | 183.08 | 0 | 0 | No
2030-05-15 09:00 | 2030 Initial | 700 | -526 | -510 | -45.13 | 0 | 0 | No
2030-05-15 10:00 | 2030 Initial | 700 | -526 | -510 | -122.06 | 0 | 0 | No
2030-05-15 11:00 | 2030 Initial | 700 | -526 | -510 | -197.2 | 0 | 0 | No
2030-05-15 12:00 | 2030 Initial | 700 | -526 | -510 | -282.27 | 0 | 0 | No
2030-05-15 13:00 | 2030 Initial | 700 | -526 | -510 | -190.4 | 0 | 0 | No
2030-05-15 14:00 | 2030 Initial | 700 | -526 | -510 | -272.92 | 0 | 0 | No
2030-05-15 15:00 | 2030 Initial | 700 | -526 | -510 | -66.8 | 0 | 0 | No
2030-05-15 16:00 | 2030 Initial | 700 | -403.9 | -390 | 67.39 | 0 | 0 | No
2030-05-15 17:00 | 2030 Initial | 700 | -103.9 | -90 | 271.8 | 0 | 0 | No
2030-05-15 18:00 | 2030 Initial | 700 | 58.37 | 210 | 510 | 0 | 0 | No
2030-05-15 19:00 | 2030 Initial | 700 | 58.37 | 510 | 510 | 0 | 0 | No
2030-05-15 20:00 | 2030 Initial | 700 | 301.57 | 510 | 510 | 0 | 0 | No
2030-05-15 21:00 | 2030 Initial | 700 | 1.57 | 510 | 510 | 0 | 0 | No
2030-05-15 22:00 | 2030 Initial | 700 | 260.13 | 510 | 510 | 0 | 0 | No
2030-05-15 23:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-05-16 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-05-16 01:00 | 2030 Initial | 700 | 0 | 510 | 356.99 | 0 | 0 | No
2030-05-16 02:00 | 2030 Initial | 700 | 73.99 | 510 | 510 | 0 | 0 | No
2030-05-16 03:00 | 2030 Initial | 700 | 0 | 510 | 496.96 | 0 | 0 | No
2030-05-16 04:00 | 2030 Initial | 700 | 0 | 510 | 259.48 | 0 | 0 | No
2030-05-16 05:00 | 2030 Initial | 700 | 0 | 456.75 | 0 | 0 | 0 | No
2030-05-16 06:00 | 2030 Initial | 700 | 0 | 265.25 | 0 | 0 | 0 | No
2030-05-16 07:00 | 2030 Initial | 700 | 0 | 67.08 | 143.97 | 0 | 0 | No
2030-05-16 08:00 | 2030 Initial | 700 | -226 | -210 | 296.29 | 0 | 0 | No
2030-05-16 09:00 | 2030 Initial | 700 | -526 | -510 | 249.96 | 0 | 0 | No
2030-05-16 10:00 | 2030 Initial | 700 | -305.92 | -510 | 510 | 0 | 0 | No
2030-05-16 11:00 | 2030 Initial | 700 | -443.02 | -510 | 430.35 | 0 | 0 | No
2030-05-16 12:00 | 2030 Initial | 700 | -472.98 | -510 | 289.56 | 0 | 0 | No
2030-05-16 13:00 | 2030 Initial | 700 | -524.07 | -510 | 206.23 | 0 | 0 | No
2030-05-16 14:00 | 2030 Initial | 700 | -239.9 | -510 | 170.63 | 0 | 0 | No
2030-05-16 15:00 | 2030 Initial | 700 | 0 | -255.5 | 283.84 | 0 | 0 | No
2030-05-16 16:00 | 2030 Initial | 700 | 0 | 44.5 | 384.88 | 0 | 0 | No
2030-05-16 17:00 | 2030 Initial | 700 | 0 | 344.5 | 510 | 0 | 0 | No
2030-05-16 18:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-05-16 19:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-05-16 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-05-16 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-05-16 22:00 | 2030 Initial | 700 | 0 | 510 | 449.27 | 0 | 0 | No
2030-05-16 23:00 | 2030 Initial | 700 | 0 | 510 | 149.27 | 0 | 0 | No
2030-05-17 | 2030 Initial | 700 | 0 | 285.85 | 171.75 | 0 | 0 | No
2030-05-17 01:00 | 2030 Initial | 700 | 0 | -14.15 | 150.68 | 0 | 0 | No
2030-05-17 02:00 | 2030 Initial | 700 | 0 | -314.15 | 145.62 | 0 | 0 | No
2030-05-17 03:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-05-17 04:00 | 2030 Initial | 700 | -27.37 | -510 | 118.28 | 0 | 0 | No
2030-05-17 05:00 | 2030 Initial | 700 | -197.04 | -510 | 99.04 | 0 | 0 | No
2030-05-17 06:00 | 2030 Initial | 700 | -435.89 | -510 | 180.65 | 0 | 0 | No
2030-05-17 07:00 | 2030 Initial | 700 | -157.51 | -510 | 336.34 | 0 | 0 | No
2030-05-17 08:00 | 2030 Initial | 700 | -65.18 | -510 | 440.7 | 0 | 0 | No
2030-05-17 09:00 | 2030 Initial | 700 | -297.43 | -210 | 457.76 | 0 | 0 | No
2030-05-17 10:00 | 2030 Initial | 700 | 2.57 | 90 | 510 | 0 | 0 | No
2030-05-17 11:00 | 2030 Initial | 700 | 302.57 | 390 | 510 | 0 | 0 | No
2030-05-17 12:00 | 2030 Initial | 596.82 | 494.81 | 510 | 510 | 0 | 0 | No
2030-05-17 13:00 | 2030 Initial | 348.19 | 505 | 510 | 510 | 0 | 0 | No
2030-05-17 14:00 | 2030 Initial | 189.83 | 505 | 510 | 510 | 0 | 0 | No
2030-05-17 15:00 | 2030 Initial | 609.83 | 205 | 210 | 510 | 0 | 0 | No
2030-05-17 16:00 | 2030 Initial | 700 | -95 | -90 | 299.85 | 0 | 0 | No
2030-05-17 17:00 | 2030 Initial | 700 | -395 | -390 | 268.55 | 0 | 0 | No
2030-05-17 18:00 | 2030 Initial | 700 | -236.12 | -510 | 164.05 | 0 | 0 | No
2030-05-17 19:00 | 2030 Initial | 700 | -526 | -510 | 430.67 | 0 | 0 | No
2030-05-17 20:00 | 2030 Initial | 700 | -526 | -510 | 287.98 | 0 | 0 | No
2030-05-17 21:00 | 2030 Initial | 700 | -311.95 | -510 | 420.72 | 0 | 0 | No
2030-05-17 22:00 | 2030 Initial | 498.24 | -11.95 | -480.85 | 390.89 | 0 | 0 | No
2030-05-17 23:00 | 2030 Initial | 78.24 | -95 | -180.85 | 195.83 | 0 | 0 | No
2030-05-18 | 2030 Initial | 280 | 122.52 | 119.15 | 448.76 | 0 | 0 | No
2030-05-18 01:00 | 2030 Initial | 700 | 422.52 | 419.15 | 510 | 0 | 0 | No
2030-05-18 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 05:00 | 2030 Initial | 442.59 | 205 | 210 | 510 | 0 | 0 | No
2030-05-18 06:00 | 2030 Initial | 22.59 | -95 | -90 | 295.99 | 0 | 0 | No
2030-05-18 07:00 | 2030 Initial | 442.59 | 205 | 210 | 479.31 | 0 | 0 | No
2030-05-18 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 15:00 | 2030 Initial | 700 | 456.38 | 390 | 510 | 0 | 0 | No
2030-05-18 16:00 | 2030 Initial | 700 | 156.38 | 90 | 271.88 | 0 | 0 | No
2030-05-18 17:00 | 2030 Initial | 700 | -143.62 | -210 | 510 | 0 | 0 | No
2030-05-18 18:00 | 2030 Initial | 700 | -429.2 | -510 | 510 | 0 | 0 | No
2030-05-18 19:00 | 2030 Initial | 700 | -357.72 | -510 | 410.87 | 0 | 0 | No
2030-05-18 20:00 | 2030 Initial | 700 | -150.19 | -510 | 372.95 | 0 | 0 | No
2030-05-18 21:00 | 2030 Initial | 700 | -322.87 | -510 | 510 | 0 | 0 | No
2030-05-18 22:00 | 2030 Initial | 700 | -22.87 | -510 | 426.82 | 0 | 0 | No
2030-05-18 23:00 | 2030 Initial | 700 | -322.87 | -510 | 264.16 | 0 | 0 | No
2030-05-19 | 2030 Initial | 685.67 | -300 | -298.3 | 197.19 | 0 | 0 | No
2030-05-19 01:00 | 2030 Initial | 700 | 0 | 1.7 | 345.81 | 0 | 0 | No
2030-05-19 02:00 | 2030 Initial | 700 | 300 | 301.7 | 510 | 0 | 0 | No
2030-05-19 03:00 | 2030 Initial | 700 | 115.21 | 270.82 | 510 | 0 | 0 | No
2030-05-19 04:00 | 2030 Initial | 700 | 0 | -29.18 | 301.69 | 0 | 0 | No
2030-05-19 05:00 | 2030 Initial | 700 | -190.61 | -329.18 | 1.69 | 0 | 0 | No
2030-05-19 06:00 | 2030 Initial | 700 | -14.68 | -510 | 69.39 | 0 | 0 | No
2030-05-19 07:00 | 2030 Initial | 700 | -279.73 | -510 | -32.04 | 0 | 0 | No
2030-05-19 08:00 | 2030 Initial | 700 | -517.41 | -510 | 4.13 | 0 | 0 | No
2030-05-19 09:00 | 2030 Initial | 700 | -526 | -510 | 142.92 | 0 | 0 | No
2030-05-19 10:00 | 2030 Initial | 700 | -526 | -510 | 142.92 | 0 | 0 | No
2030-05-19 11:00 | 2030 Initial | 700 | -526 | -510 | 200.98 | 0 | 0 | No
2030-05-19 12:00 | 2030 Initial | 700 | -526 | -510 | 232.25 | 0 | 0 | No
2030-05-19 13:00 | 2030 Initial | 700 | -526 | -510 | 294.79 | 0 | 0 | No
2030-05-19 14:00 | 2030 Initial | 700 | -526 | -510 | 343.28 | 0 | 0 | No
2030-05-19 15:00 | 2030 Initial | 700 | -526 | -510 | 330.39 | 0 | 0 | No
2030-05-19 16:00 | 2030 Initial | 700 | -526 | -510 | 330.07 | 0 | 0 | No
2030-05-19 17:00 | 2030 Initial | 700 | -526 | -510 | 216.99 | 0 | 0 | No
2030-05-19 18:00 | 2030 Initial | 700 | -300 | -510 | 192.98 | 0 | 0 | No
2030-05-19 19:00 | 2030 Initial | 700 | 0 | -454.42 | 27.34 | 0 | 0 | No
2030-05-19 20:00 | 2030 Initial | 700 | 0 | -154.42 | 223.14 | 0 | 0 | No
2030-05-19 21:00 | 2030 Initial | 700 | 0 | -26.26 | 185.99 | 0 | 0 | No
2030-05-19 22:00 | 2030 Initial | 700 | 0 | -217.5 | 99.73 | 0 | 0 | No
2030-05-19 23:00 | 2030 Initial | 700 | 0 | -368.36 | 0 | 0 | 0 | No
2030-05-20 | 2030 Initial | 700 | 0 | -444.44 | 55.8 | 0 | 0 | No
2030-05-20 01:00 | 2030 Initial | 700 | -52.51 | -444.44 | 65.39 | 0 | 0 | No
2030-05-20 02:00 | 2030 Initial | 700 | -352.51 | -510 | 102.49 | 0 | 0 | No
2030-05-20 03:00 | 2030 Initial | 700 | -526 | -510 | 39.62 | 0 | 0 | No
2030-05-20 04:00 | 2030 Initial | 700 | -526 | -510 | -62.87 | 0 | 0 | No
2030-05-20 05:00 | 2030 Initial | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-20 06:00 | 2030 Initial | 700 | -526 | -510 | 121.93 | 0 | 0 | No
2030-05-20 07:00 | 2030 Initial | 700 | -526 | -510 | 217.03 | 0 | 0 | No
2030-05-20 08:00 | 2030 Initial | 430.33 | -526 | -510 | 103.77 | 0 | 0 | No
2030-05-20 09:00 | 2030 Initial | 10.33 | -526 | -510 | 0 | 0 | 0 | No
2030-05-20 10:00 | 2030 Initial | -409.67 | -526 | -510 | 182.61 | 0 | 0 | No
2030-05-20 11:00 | 2030 Initial | -700 | -526 | -510 | -117.39 | 0 | 0 | No
2030-05-20 12:00 | 2030 Initial | -700 | -473.72 | -510 | 160.07 | 0 | 0 | No
2030-05-20 13:00 | 2030 Initial | -700 | -526 | -510 | 460.07 | 0 | 0 | No
2030-05-20 14:00 | 2030 Initial | -700 | -526 | -510 | 491.01 | 0 | 0 | No
2030-05-20 15:00 | 2030 Initial | -560 | -526 | -510 | 491.01 | 0 | 0 | No
2030-05-20 16:00 | 2030 Initial | -140 | -357.54 | -510 | 510 | 0 | 0 | No
2030-05-20 17:00 | 2030 Initial | 280 | -57.54 | -304.81 | 510 | 0 | 0 | No
2030-05-20 18:00 | 2030 Initial | 700 | -262.29 | -332.84 | 510 | 0 | 0 | No
2030-05-20 19:00 | 2030 Initial | 700 | 0 | -32.84 | 510 | 0 | 0 | No
2030-05-20 20:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-05-20 21:00 | 2030 Initial | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-05-20 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-20 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-21 | 2030 Initial | 700 | 317.98 | 510 | 510 | 0 | 0 | No
2030-05-21 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-21 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-21 03:00 | 2030 Initial | 700 | 328.13 | 510 | 510 | 0 | 0 | No
2030-05-21 04:00 | 2030 Initial | 700 | 28.13 | 210 | 423.95 | 0 | 0 | No
2030-05-21 05:00 | 2030 Initial | 700 | 0 | 0 | 316.76 | 0 | 0 | No
2030-05-21 06:00 | 2030 Initial | 700 | 0 | 0 | 412.12 | 0 | 0 | No
2030-05-21 07:00 | 2030 Initial | 700 | 0 | -213.34 | 510 | 0 | 0 | No
2030-05-21 08:00 | 2030 Initial | 700 | -226 | -391.23 | 510 | 0 | 0 | No
2030-05-21 09:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-21 10:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-21 11:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-21 12:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-21 13:00 | 2030 Initial | 700 | -526 | -510 | 286.4 | 0 | 0 | No
2030-05-21 14:00 | 2030 Initial | 666.48 | -526 | -510 | 171.01 | 0 | 0 | No
2030-05-21 15:00 | 2030 Initial | 626.28 | -526 | -510 | -128.99 | 0 | 0 | No
2030-05-21 16:00 | 2030 Initial | 700 | -526 | -510 | 23.71 | 0 | 0 | No
2030-05-21 17:00 | 2030 Initial | 700 | -526 | -510 | 128.64 | 0 | 0 | No
2030-05-21 18:00 | 2030 Initial | 700 | -526 | -510 | -171.36 | 0 | 0 | No
2030-05-21 19:00 | 2030 Initial | 700 | -526 | -510 | 8.75 | 0 | 0 | No
2030-05-21 20:00 | 2030 Initial | 347.52 | -526 | -510 | 72 | 0 | 0 | No
2030-05-21 21:00 | 2030 Initial | 140 | -300 | -482.24 | -68.13 | 0 | 0 | No
2030-05-21 22:00 | 2030 Initial | -280 | 0 | -182.24 | -42.52 | 0 | 0 | No
2030-05-21 23:00 | 2030 Initial | -700 | 300 | 117.76 | 257.48 | 0 | 0 | Yes
2030-05-22 | 2030 Initial | -700 | 505 | 417.76 | 347.82 | 0 | 0 | Yes
2030-05-22 01:00 | 2030 Initial | -700 | 505 | 510 | 47.82 | 0 | 0 | Yes
2030-05-22 02:00 | 2030 Initial | -700 | 505 | 510 | 19.11 | 0 | 0 | Yes
2030-05-22 03:00 | 2030 Initial | -700 | 505 | 510 | 165.68 | 0 | 0 | Yes
2030-05-22 04:00 | 2030 Initial | -700 | 505 | 510 | 339.39 | 0 | 0 | Yes
2030-05-22 05:00 | 2030 Initial | -700 | 505 | 510 | 216.89 | 0 | 0 | Yes
2030-05-22 06:00 | 2030 Initial | -700 | 505 | 510 | 134.28 | 0 | 0 | Yes
2030-05-22 07:00 | 2030 Initial | -700 | 505 | 510 | 234.42 | 0 | 0 | Yes
2030-05-22 08:00 | 2030 Initial | -700 | 505 | 510 | 310.44 | 0 | 0 | Yes
2030-05-22 09:00 | 2030 Initial | -700 | 505 | 510 | 292.69 | 0 | 0 | Yes
2030-05-22 10:00 | 2030 Initial | -700 | 505 | 510 | 220.79 | 0 | 0 | Yes
2030-05-22 11:00 | 2030 Initial | -700 | 505 | 510 | 171.78 | 0 | 0 | Yes
2030-05-22 12:00 | 2030 Initial | -700 | 505 | 510 | 161.32 | 0 | 0 | Yes
2030-05-22 13:00 | 2030 Initial | -700 | 505 | 510 | 130.58 | 0 | 0 | Yes
2030-05-22 14:00 | 2030 Initial | -700 | 505 | 510 | 107.93 | 0 | 0 | Yes
2030-05-22 15:00 | 2030 Initial | -700 | 505 | 510 | 128.14 | 0 | 0 | Yes
2030-05-22 16:00 | 2030 Initial | -700 | 505 | 510 | 227.16 | 0 | 0 | Yes
2030-05-22 17:00 | 2030 Initial | -700 | 505 | 510 | 312.05 | 0 | 0 | Yes
2030-05-22 18:00 | 2030 Initial | -700 | 505 | 510 | 338.14 | 0 | 0 | Yes
2030-05-22 19:00 | 2030 Initial | -700 | 505 | 510 | 330.41 | 0 | 0 | Yes
2030-05-22 20:00 | 2030 Initial | -700 | 505 | 510 | 293.59 | 0 | 0 | Yes
2030-05-22 21:00 | 2030 Initial | -700 | 505 | 510 | 505.56 | 0 | 0 | Yes
2030-05-22 22:00 | 2030 Initial | -700 | 505 | 510 | 458.59 | 0 | 0 | Yes
2030-05-22 23:00 | 2030 Initial | -700 | 505 | 510 | 253.2 | 0 | 0 | Yes
2030-05-23 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-23 01:00 | 2030 Initial | -700 | 505 | 510 | 324.21 | 0 | 0 | Yes
2030-05-23 02:00 | 2030 Initial | -700 | 505 | 510 | 42.51 | 0 | 0 | Yes
2030-05-23 03:00 | 2030 Initial | -700 | 505 | 510 | -15.13 | 0 | 0 | Yes
2030-05-23 04:00 | 2030 Initial | -700 | 505 | 510 | 62.24 | 0 | 0 | Yes
2030-05-23 05:00 | 2030 Initial | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-05-23 06:00 | 2030 Initial | -700 | 505 | 510 | 26.5 | 0 | 0 | Yes
2030-05-23 07:00 | 2030 Initial | -700 | 505 | 510 | 150.16 | 0 | 0 | Yes
2030-05-23 08:00 | 2030 Initial | -700 | 505 | 510 | 322.79 | 0 | 0 | Yes
2030-05-23 09:00 | 2030 Initial | -700 | 505 | 510 | 342.19 | 0 | 0 | Yes
2030-05-23 10:00 | 2030 Initial | -700 | 505 | 510 | 341.61 | 0 | 0 | Yes
2030-05-23 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-23 12:00 | 2030 Initial | -700 | 505 | 510 | 302.56 | 0 | 0 | Yes
2030-05-23 13:00 | 2030 Initial | -700 | 505 | 510 | 259.06 | 0 | 0 | Yes
2030-05-23 14:00 | 2030 Initial | -700 | 505 | 510 | 210.98 | 0 | 0 | Yes
2030-05-23 15:00 | 2030 Initial | -700 | 505 | 510 | 374.23 | 0 | 0 | Yes
2030-05-23 16:00 | 2030 Initial | -700 | 505 | 510 | 374.23 | 0 | 0 | Yes
2030-05-23 17:00 | 2030 Initial | -700 | 505 | 510 | 466.49 | 0 | 0 | Yes
2030-05-23 18:00 | 2030 Initial | -280 | 505 | 510 | 497.36 | 0 | 0 | Yes
2030-05-23 19:00 | 2030 Initial | -437.65 | 505 | 510 | 510 | 0 | 0 | No
2030-05-23 20:00 | 2030 Initial | -169.79 | 505 | 510 | 510 | 0 | 0 | No
2030-05-23 21:00 | 2030 Initial | -169.79 | 505 | 510 | 510 | 0 | 0 | No
2030-05-23 22:00 | 2030 Initial | -589.79 | 505 | 510 | 510 | 0 | 0 | No
2030-05-23 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-24 | 2030 Initial | -429.56 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 01:00 | 2030 Initial | -260.42 | 505 | 510 | 474.79 | 0 | 0 | Yes
2030-05-24 02:00 | 2030 Initial | -680.42 | 505 | 510 | 507.93 | 0 | 0 | Yes
2030-05-24 03:00 | 2030 Initial | -497.41 | 505 | 510 | 438.36 | 0 | 0 | Yes
2030-05-24 04:00 | 2030 Initial | -91.97 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 05:00 | 2030 Initial | -91.97 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 06:00 | 2030 Initial | -230.05 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 07:00 | 2030 Initial | -425.68 | 505 | 510 | 510 | 0 | 0 | No
2030-05-24 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-24 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 15:00 | 2030 Initial | -700 | 505 | 489.93 | 510 | 0 | 0 | Yes
2030-05-24 16:00 | 2030 Initial | -280 | 300 | 189.93 | 510 | 0 | 0 | No
2030-05-24 17:00 | 2030 Initial | 140 | 0 | -110.07 | 494.13 | 0 | 0 | No
2030-05-24 18:00 | 2030 Initial | 176.77 | -300 | -410.07 | 510 | 0 | 0 | No
2030-05-24 19:00 | 2030 Initial | 596.77 | 0 | -483.8 | 510 | 0 | 0 | No
2030-05-24 20:00 | 2030 Initial | 700 | 0 | -183.8 | 488.07 | 0 | 0 | No
2030-05-24 21:00 | 2030 Initial | 700 | 0 | -210 | 510 | 0 | 0 | No
2030-05-24 22:00 | 2030 Initial | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-05-24 23:00 | 2030 Initial | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-05-25 | 2030 Initial | 700 | -296.48 | -510 | 390.79 | 0 | 0 | No
2030-05-25 01:00 | 2030 Initial | 700 | -211.06 | -510 | 403.28 | 0 | 0 | No
2030-05-25 02:00 | 2030 Initial | 469.43 | -511.06 | 0 | 394.65 | 0 | 0 | No
2030-05-25 03:00 | 2030 Initial | 622.28 | -526 | 0 | 329.21 | 0 | 0 | No
2030-05-25 04:00 | 2030 Initial | 302.13 | -526 | 0 | 342.42 | 0 | 0 | No
2030-05-25 05:00 | 2030 Initial | -117.87 | -526 | 0 | 314.33 | 0 | 0 | No
2030-05-25 06:00 | 2030 Initial | -537.87 | -526 | 0 | 348.8 | 0 | 0 | No
2030-05-25 07:00 | 2030 Initial | -700 | -526 | 0 | 172.78 | 0 | 0 | No
2030-05-25 08:00 | 2030 Initial | -700 | -526 | 0 | -12.66 | 0 | 0 | No
2030-05-25 09:00 | 2030 Initial | -700 | -526 | 0 | 82.83 | 0 | 0 | Yes
2030-05-25 10:00 | 2030 Initial | -700 | -526 | 0 | -108.3 | 0 | 0 | Yes
2030-05-25 11:00 | 2030 Initial | -700 | -526 | 0 | -334.1 | 0 | 0 | Yes
2030-05-25 12:00 | 2030 Initial | -700 | -526 | 0 | -313.48 | 0 | 0 | Yes
2030-05-25 13:00 | 2030 Initial | -700 | -526 | 0 | -80.03 | 0 | 0 | Yes
2030-05-25 14:00 | 2030 Initial | -700 | -526 | 0 | -124.45 | 0 | 0 | Yes
2030-05-25 15:00 | 2030 Initial | -280 | -526 | 0 | 175.55 | 0 | 0 | No
2030-05-25 16:00 | 2030 Initial | 140 | -526 | 0 | 319.58 | 0 | 0 | No
2030-05-25 17:00 | 2030 Initial | 560 | -526 | 0 | 213.12 | 0 | 0 | No
2030-05-25 18:00 | 2030 Initial | 700 | -526 | 0 | 43.47 | 0 | 0 | No
2030-05-25 19:00 | 2030 Initial | 700 | -226 | 0 | 343.47 | 0 | 0 | No
2030-05-25 20:00 | 2030 Initial | 700 | 0 | 0 | 383.17 | 0 | 0 | No
2030-05-25 21:00 | 2030 Initial | 700 | 0 | 0 | 83.17 | 0 | 0 | No
2030-05-25 22:00 | 2030 Initial | 700 | 0 | 0 | 383.17 | 0 | 0 | No
2030-05-25 23:00 | 2030 Initial | 700 | 0 | 0 | 353.16 | 0 | 0 | No
2030-05-26 | 2030 Initial | 700 | 0 | 0 | 53.16 | 0 | 0 | No
2030-05-26 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-26 02:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-26 03:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-26 04:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-26 05:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-26 06:00 | 2030 Initial | 700 | -226 | 0 | 0 | 0 | 0 | No
2030-05-26 07:00 | 2030 Initial | 700 | -526 | 0 | 34.58 | 0 | 0 | No
2030-05-26 08:00 | 2030 Initial | 700 | -526 | 0 | 38.86 | 0 | 0 | No
2030-05-26 09:00 | 2030 Initial | 700 | -526 | 0 | 0 | 0 | 0 | No
2030-05-26 10:00 | 2030 Initial | 700 | -526 | 0 | 48.43 | 0 | 0 | No
2030-05-26 11:00 | 2030 Initial | 700 | -526 | 0 | 110.3 | 0 | 0 | No
2030-05-26 12:00 | 2030 Initial | 700 | -526 | 0 | 131.14 | 0 | 0 | No
2030-05-26 13:00 | 2030 Initial | 700 | -526 | 0 | 112.64 | 0 | 0 | No
2030-05-26 14:00 | 2030 Initial | 700 | -526 | 0 | 68.79 | 0 | 0 | No
2030-05-26 15:00 | 2030 Initial | 700 | -526 | 0 | 104.22 | 0 | 0 | No
2030-05-26 16:00 | 2030 Initial | 700 | -526 | 0 | 173.74 | 0 | 0 | No
2030-05-26 17:00 | 2030 Initial | 700 | -526 | 0 | 17.44 | 0 | 0 | No
2030-05-26 18:00 | 2030 Initial | 700 | -226 | 0 | 125.71 | 0 | 0 | No
2030-05-26 19:00 | 2030 Initial | 700 | 0 | 0 | 165.12 | 0 | 0 | No
2030-05-26 20:00 | 2030 Initial | 700 | 0 | 0 | 465.12 | 0 | 0 | No
2030-05-26 21:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-05-26 22:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-05-26 23:00 | 2030 Initial | 700 | 0 | 0 | 453.66 | 0 | 0 | No
2030-05-27 | 2030 Initial | 700 | 0 | 0 | 153.66 | 0 | 0 | No
2030-05-27 01:00 | 2030 Initial | 700 | 0 | 0 | 142.81 | 0 | 0 | No
2030-05-27 02:00 | 2030 Initial | 700 | 0 | 300 | 48.41 | 0 | 0 | No
2030-05-27 03:00 | 2030 Initial | 700 | 0 | 482.79 | 33.22 | 0 | 0 | No
2030-05-27 04:00 | 2030 Initial | 700 | 0 | 182.79 | 0 | 0 | 0 | No
2030-05-27 05:00 | 2030 Initial | 700 | 0 | 32.35 | 0 | 0 | 0 | No
2030-05-27 06:00 | 2030 Initial | 700 | 0 | 103.71 | 44.35 | 0 | 0 | No
2030-05-27 07:00 | 2030 Initial | 700 | 0 | -6.72 | 122.25 | 0 | 0 | No
2030-05-27 08:00 | 2030 Initial | 700 | -226 | -218.44 | 160.04 | 0 | 0 | No
2030-05-27 09:00 | 2030 Initial | 700 | -526 | -510 | 140.1 | 0 | 0 | No
2030-05-27 10:00 | 2030 Initial | 700 | -526 | -510 | 24.07 | 0 | 0 | No
2030-05-27 11:00 | 2030 Initial | 700 | -526 | -510 | 4.6 | 0 | 0 | No
2030-05-27 12:00 | 2030 Initial | 700 | -526 | -510 | -90.02 | 0 | 0 | No
2030-05-27 13:00 | 2030 Initial | 700 | -526 | -510 | -136.41 | 0 | 0 | No
2030-05-27 14:00 | 2030 Initial | 700 | -526 | -510 | -125.34 | 0 | 0 | No
2030-05-27 15:00 | 2030 Initial | 700 | -526 | -510 | -114.99 | 0 | 0 | No
2030-05-27 16:00 | 2030 Initial | 700 | -526 | -510 | 26.4 | 0 | 0 | No
2030-05-27 17:00 | 2030 Initial | 700 | -234.93 | -300 | 26.47 | 0 | 0 | No
2030-05-27 18:00 | 2030 Initial | 700 | 0 | 0 | 122.94 | 0 | 0 | No
2030-05-27 19:00 | 2030 Initial | 700 | 0 | 300 | 89.17 | 0 | 0 | No
2030-05-27 20:00 | 2030 Initial | 700 | 0 | 300 | 20.7 | 0 | 0 | No
2030-05-27 21:00 | 2030 Initial | 700 | 0 | 72.04 | 201.63 | 0 | 0 | No
2030-05-27 22:00 | 2030 Initial | 700 | 0 | 246.1 | 177.97 | 0 | 0 | No
2030-05-27 23:00 | 2030 Initial | 700 | 0 | 0 | 102 | 0 | 0 | No
2030-05-28 | 2030 Initial | 700 | 0 | -117.2 | 108.59 | 0 | 0 | No
2030-05-28 01:00 | 2030 Initial | 700 | 0 | -225.08 | 125.38 | 0 | 0 | No
2030-05-28 02:00 | 2030 Initial | 700 | 0 | -392.31 | 126.05 | 0 | 0 | No
2030-05-28 03:00 | 2030 Initial | 700 | -252.36 | -510 | 110.59 | 0 | 0 | No
2030-05-28 04:00 | 2030 Initial | 700 | -382.27 | -510 | 68.78 | 0 | 0 | No
2030-05-28 05:00 | 2030 Initial | 700 | -526 | -510 | 60.33 | 0 | 0 | No
2030-05-28 06:00 | 2030 Initial | 700 | -526 | -510 | 121.36 | 0 | 0 | No
2030-05-28 07:00 | 2030 Initial | 700 | -526 | -510 | 177.25 | 0 | 0 | No
2030-05-28 08:00 | 2030 Initial | 700 | -526 | -510 | 265.7 | 0 | 0 | No
2030-05-28 09:00 | 2030 Initial | 700 | -526 | -510 | 208.39 | 0 | 0 | No
2030-05-28 10:00 | 2030 Initial | 700 | -526 | -510 | 162.73 | 0 | 0 | No
2030-05-28 11:00 | 2030 Initial | 700 | -526 | -510 | 145.92 | 0 | 0 | No
2030-05-28 12:00 | 2030 Initial | 484.21 | -526 | -510 | 82.55 | 0 | 0 | No
2030-05-28 13:00 | 2030 Initial | 700 | -526 | -510 | -15.47 | 0 | 0 | No
2030-05-28 14:00 | 2030 Initial | 620.07 | -526 | -510 | -58.75 | 0 | 0 | No
2030-05-28 15:00 | 2030 Initial | 700 | -526 | -510 | 43.23 | 0 | 0 | No
2030-05-28 16:00 | 2030 Initial | 700 | -526 | -510 | 90.06 | 0 | 0 | No
2030-05-28 17:00 | 2030 Initial | 700 | -526 | -510 | 184.97 | 0 | 0 | No
2030-05-28 18:00 | 2030 Initial | 700 | -526 | -510 | 173.25 | 0 | 0 | No
2030-05-28 19:00 | 2030 Initial | 700 | -526 | -510 | 164.61 | 0 | 0 | No
2030-05-28 20:00 | 2030 Initial | 700 | -526 | -510 | 198.53 | 0 | 0 | No
2030-05-28 21:00 | 2030 Initial | 700 | -526 | -510 | 234.46 | 0 | 0 | No
2030-05-28 22:00 | 2030 Initial | 700 | -526 | -510 | 172.96 | 0 | 0 | No
2030-05-28 23:00 | 2030 Initial | 700 | -526 | -510 | 59.27 | 0 | 0 | No
2030-05-29 | 2030 Initial | 700 | -526 | -510 | -48.3 | 0 | 0 | No
2030-05-29 01:00 | 2030 Initial | 700 | -526 | -510 | 32.96 | 0 | 0 | No
2030-05-29 02:00 | 2030 Initial | 700 | -526 | -510 | -34.26 | 0 | 0 | No
2030-05-29 03:00 | 2030 Initial | 700 | -526 | -510 | 5.85 | 0 | 0 | No
2030-05-29 04:00 | 2030 Initial | 700 | -526 | -510 | -72.94 | 0 | 0 | No
2030-05-29 05:00 | 2030 Initial | 700 | -526 | -510 | -92.53 | 0 | 0 | No
2030-05-29 06:00 | 2030 Initial | 700 | -526 | -510 | 48.57 | 0 | 0 | No
2030-05-29 07:00 | 2030 Initial | 390.49 | -526 | -510 | -11.22 | 0 | 0 | No
2030-05-29 08:00 | 2030 Initial | -29.51 | -526 | -510 | -103.96 | 0 | 0 | No
2030-05-29 09:00 | 2030 Initial | -449.51 | -526 | -510 | -318.53 | 0 | 0 | Yes
2030-05-29 10:00 | 2030 Initial | -700 | -526 | -510 | -455.03 | 0 | 0 | Yes
2030-05-29 11:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 12:00 | 2030 Initial | -700 | -526 | -510 | -504.38 | 0 | 0 | Yes
2030-05-29 13:00 | 2030 Initial | -700 | -526 | -510 | -376.29 | 0 | 0 | Yes
2030-05-29 14:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 15:00 | 2030 Initial | -404.59 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 16:00 | 2030 Initial | 15.41 | -526 | -510 | -281.84 | 0 | 0 | No
2030-05-29 17:00 | 2030 Initial | 435.41 | -526 | -510 | -92.95 | 0 | 0 | No
2030-05-29 18:00 | 2030 Initial | 700 | -526 | -510 | 27.66 | 0 | 0 | No
2030-05-29 19:00 | 2030 Initial | 700 | -526 | -510 | 226.2 | 0 | 0 | No
2030-05-29 20:00 | 2030 Initial | 700 | -526 | -510 | 351.16 | 0 | 0 | No
2030-05-29 21:00 | 2030 Initial | 583.1 | -526 | -510 | 340.98 | 0 | 0 | No
2030-05-29 22:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-29 23:00 | 2030 Initial | 700 | -526 | -510 | 477.05 | 0 | 0 | No
2030-05-30 | 2030 Initial | 700 | -526 | -510 | 337.13 | 0 | 0 | No
2030-05-30 01:00 | 2030 Initial | 700 | -526 | -510 | 364.07 | 0 | 0 | No
2030-05-30 02:00 | 2030 Initial | 700 | -526 | -510 | 305.64 | 0 | 0 | No
2030-05-30 03:00 | 2030 Initial | 700 | -226 | -250.23 | 510 | 0 | 0 | No
2030-05-30 04:00 | 2030 Initial | 700 | -427.72 | -510 | 384.26 | 0 | 0 | No
2030-05-30 05:00 | 2030 Initial | 700 | -526 | -510 | 291.28 | 0 | 0 | No
2030-05-30 06:00 | 2030 Initial | 280 | -526 | -510 | 137.3 | 0 | 0 | No
2030-05-30 07:00 | 2030 Initial | 700 | -526 | -510 | 391.58 | 0 | 0 | No
2030-05-30 08:00 | 2030 Initial | 700 | -526 | -510 | 408.42 | 0 | 0 | No
2030-05-30 09:00 | 2030 Initial | 700 | -526 | -510 | 277.83 | 0 | 0 | No
2030-05-30 10:00 | 2030 Initial | 280 | -485.06 | -510 | 290.42 | 0 | 0 | No
2030-05-30 11:00 | 2030 Initial | -51.44 | -185.06 | -430.7 | 489.23 | 0 | 0 | No
2030-05-30 12:00 | 2030 Initial | -206.81 | 0 | -130.7 | 510 | 0 | 0 | No
2030-05-30 13:00 | 2030 Initial | 0 | -59.69 | -430.7 | 351.44 | 0 | 0 | No
2030-05-30 14:00 | 2030 Initial | 0 | -359.69 | -510 | 80.99 | 0 | 0 | No
2030-05-30 15:00 | 2030 Initial | 280 | -526 | -510 | 168.34 | 0 | 0 | No
2030-05-30 16:00 | 2030 Initial | 700 | -526 | -510 | 143.03 | 0 | 0 | No
2030-05-30 17:00 | 2030 Initial | 700 | -496.22 | -510 | 295.15 | 0 | 0 | No
2030-05-30 18:00 | 2030 Initial | 700 | -196.22 | -210 | 295.15 | 0 | 0 | No
2030-05-30 19:00 | 2030 Initial | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-05-30 20:00 | 2030 Initial | 700 | 0 | 390 | 294.84 | 0 | 0 | No
2030-05-30 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-05-30 22:00 | 2030 Initial | 700 | 289.64 | 510 | 510 | 0 | 0 | No
2030-05-30 23:00 | 2030 Initial | 700 | 505 | 510 | 421.99 | 0 | 0 | No
2030-05-31 | 2030 Initial | 700 | 505 | 510 | 366.1 | 0 | 0 | No
2030-05-31 01:00 | 2030 Initial | 700 | 505 | 510 | 66.1 | 0 | 0 | No
2030-05-31 02:00 | 2030 Initial | 700 | 505 | 510 | 49.3 | 0 | 0 | No
2030-05-31 03:00 | 2030 Initial | 700 | 505 | 510 | 342.44 | 0 | 0 | No
2030-05-31 04:00 | 2030 Initial | 700 | 505 | 510 | 253.98 | 0 | 0 | No
2030-05-31 05:00 | 2030 Initial | 700 | 205 | 210 | -46.02 | 0 | 0 | No
2030-05-31 06:00 | 2030 Initial | 700 | -95 | -90 | -2.1 | 0 | 0 | No
2030-05-31 07:00 | 2030 Initial | 700 | -180.77 | -390 | -302.1 | 0 | 0 | No
2030-05-31 08:00 | 2030 Initial | 700 | -468.73 | -510 | -210.54 | 0 | 0 | No
2030-05-31 09:00 | 2030 Initial | 700 | -526 | -510 | -32.57 | 0 | 0 | No
2030-05-31 10:00 | 2030 Initial | 700 | -526 | -510 | -223.1 | 0 | 0 | No
2030-05-31 11:00 | 2030 Initial | 700 | -526 | -510 | -117.13 | 0 | 0 | No
2030-05-31 12:00 | 2030 Initial | 700 | -526 | -510 | 143.59 | 0 | 0 | No
2030-05-31 13:00 | 2030 Initial | 700 | -526 | -510 | 75.47 | 0 | 0 | No
2030-05-31 14:00 | 2030 Initial | 700 | -526 | -510 | 168.07 | 0 | 0 | No
2030-05-31 15:00 | 2030 Initial | 700 | -526 | -510 | 78.32 | 0 | 0 | No
2030-05-31 16:00 | 2030 Initial | 700 | -526 | -510 | 217.07 | 0 | 0 | No
2030-05-31 17:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-31 18:00 | 2030 Initial | 700 | -505.09 | -510 | 330.58 | 0 | 0 | No
2030-05-31 19:00 | 2030 Initial | 700 | -205.09 | -263.43 | 480.75 | 0 | 0 | No
2030-05-31 20:00 | 2030 Initial | 700 | 0 | -33.2 | 510 | 0 | 0 | No
2030-05-31 21:00 | 2030 Initial | 700 | 0 | -60.54 | 510 | 0 | 0 | No
2030-05-31 22:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-05-31 23:00 | 2030 Initial | 700 | 0 | 0 | 508.36 | 0 | 0 | No
2030-06-01 | 2030 Initial | 700 | 0 | -81.62 | 208.36 | 0 | 0 | No
2030-06-01 01:00 | 2030 Initial | 700 | 0 | 82.45 | 0 | 0 | 0 | No
2030-06-01 02:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-01 03:00 | 2030 Initial | 700 | 0 | -4.42 | 0 | 0 | 0 | No
2030-06-01 04:00 | 2030 Initial | 700 | 0 | -133.89 | 0 | 0 | 0 | No
2030-06-01 05:00 | 2030 Initial | 700 | 0 | -224.69 | 0 | 0 | 0 | No
2030-06-01 06:00 | 2030 Initial | 700 | -124.24 | -302.23 | 0 | 0 | 0 | No
2030-06-01 07:00 | 2030 Initial | 700 | -424.24 | -510 | -20.33 | 0 | 0 | No
2030-06-01 08:00 | 2030 Initial | 700 | -526 | -510 | -27.75 | 0 | 0 | No
2030-06-01 09:00 | 2030 Initial | 700 | -526 | -510 | -25.18 | 0 | 0 | No
2030-06-01 10:00 | 2030 Initial | 700 | -526 | -510 | -42.48 | 0 | 0 | No
2030-06-01 11:00 | 2030 Initial | 700 | -526 | -510 | -7.73 | 0 | 0 | No
2030-06-01 12:00 | 2030 Initial | 700 | -526 | -510 | -6.28 | 0 | 0 | No
2030-06-01 13:00 | 2030 Initial | 700 | -526 | -510 | -52.93 | 0 | 0 | No
2030-06-01 14:00 | 2030 Initial | 700 | -526 | -510 | -51.4 | 0 | 0 | No
2030-06-01 15:00 | 2030 Initial | 700 | -526 | -510 | -35.82 | 0 | 0 | No
2030-06-01 16:00 | 2030 Initial | 700 | -526 | -510 | 54.68 | 0 | 0 | No
2030-06-01 17:00 | 2030 Initial | 700 | -526 | -510 | 136.05 | 0 | 0 | No
2030-06-01 18:00 | 2030 Initial | 700 | -226 | -273.85 | 167.12 | 0 | 0 | No
2030-06-01 19:00 | 2030 Initial | 700 | 0 | 0 | 240.14 | 0 | 0 | No
2030-06-01 20:00 | 2030 Initial | 700 | 0 | 210 | 262.34 | 0 | 0 | No
2030-06-01 21:00 | 2030 Initial | 700 | 0 | 510 | 270.18 | 0 | 0 | No
2030-06-01 22:00 | 2030 Initial | 700 | 0 | 510 | 266.13 | 0 | 0 | No
2030-06-01 23:00 | 2030 Initial | 700 | 0 | 493.61 | 217.44 | 0 | 0 | No
2030-06-02 | 2030 Initial | 700 | 0 | 233.71 | 127.6 | 0 | 0 | No
2030-06-02 01:00 | 2030 Initial | 700 | 0 | 291.72 | 163.82 | 0 | 0 | No
2030-06-02 02:00 | 2030 Initial | 700 | 0 | 42.68 | 150.68 | 0 | 0 | No
2030-06-02 03:00 | 2030 Initial | 700 | 0 | 42.68 | 122.96 | 0 | 0 | No
2030-06-02 04:00 | 2030 Initial | 700 | 0 | 42.68 | 92.76 | 0 | 0 | No
2030-06-02 05:00 | 2030 Initial | 700 | 0 | 90 | 56.44 | 0 | 0 | No
2030-06-02 06:00 | 2030 Initial | 700 | -226 | -210 | 58.54 | 0 | 0 | No
2030-06-02 07:00 | 2030 Initial | 700 | -526 | -510 | 39.9 | 0 | 0 | No
2030-06-02 08:00 | 2030 Initial | 700 | -526 | -510 | -20.89 | 0 | 0 | No
2030-06-02 09:00 | 2030 Initial | 700 | -526 | -510 | -69.97 | 0 | 0 | No
2030-06-02 10:00 | 2030 Initial | 700 | -526 | -510 | -47.09 | 0 | 0 | No
2030-06-02 11:00 | 2030 Initial | 700 | -526 | -510 | -17.08 | 0 | 0 | No
2030-06-02 12:00 | 2030 Initial | 700 | -526 | -510 | -11.9 | 0 | 0 | No
2030-06-02 13:00 | 2030 Initial | 700 | -526 | -510 | -4.56 | 0 | 0 | No
2030-06-02 14:00 | 2030 Initial | 700 | -526 | -510 | -10.44 | 0 | 0 | No
2030-06-02 15:00 | 2030 Initial | 700 | -526 | -510 | -59.64 | 0 | 0 | No
2030-06-02 16:00 | 2030 Initial | 700 | -526 | -510 | 0.43 | 0 | 0 | No
2030-06-02 17:00 | 2030 Initial | 700 | -526 | -510 | -193.2 | 0 | 0 | No
2030-06-02 18:00 | 2030 Initial | 700 | -526 | -510 | -493.2 | 0 | 0 | No
2030-06-02 19:00 | 2030 Initial | 700 | -244.5 | -510 | -358.64 | 0 | 0 | No
2030-06-02 20:00 | 2030 Initial | 700 | 0 | -510 | -255.9 | 0 | 0 | No
2030-06-02 21:00 | 2030 Initial | 700 | 0 | -510 | 37.77 | 0 | 0 | No
2030-06-02 22:00 | 2030 Initial | 700 | 0 | -510 | 163 | 0 | 0 | No
2030-06-02 23:00 | 2030 Initial | 700 | -141.81 | -510 | 46.75 | 0 | 0 | No
2030-06-03 | 2030 Initial | 700 | -394.18 | -510 | -154.39 | 0 | 0 | No
2030-06-03 01:00 | 2030 Initial | 700 | -147.22 | -210 | -28.31 | 0 | 0 | No
2030-06-03 02:00 | 2030 Initial | 700 | 152.78 | 90 | 18.42 | 0 | 0 | No
2030-06-03 03:00 | 2030 Initial | 453.22 | 452.78 | 390 | 250.57 | 0 | 0 | No
2030-06-03 04:00 | 2030 Initial | 33.22 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 05:00 | 2030 Initial | -386.78 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-03 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 14:00 | 2030 Initial | -700 | 479.8 | 210 | 210 | 0 | 0 | Yes
2030-06-03 15:00 | 2030 Initial | -700 | 179.8 | -90 | -90 | 0 | 0 | Yes
2030-06-03 16:00 | 2030 Initial | -700 | -120.2 | -390 | -390 | 0 | 0 | Yes
2030-06-03 17:00 | 2030 Initial | -560 | -275.79 | -390 | -390 | 0 | 0 | No
2030-06-03 18:00 | 2030 Initial | -140 | -38.96 | -90 | -90 | 0 | 0 | No
2030-06-03 19:00 | 2030 Initial | 280 | 261.04 | 210 | 210 | 0 | 0 | No
2030-06-03 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-03 21:00 | 2030 Initial | 700 | 505 | 510 | 471.48 | 0 | 0 | No
2030-06-03 22:00 | 2030 Initial | 700 | 505 | 510 | 348.63 | 0 | 0 | No
2030-06-03 23:00 | 2030 Initial | 700 | 505 | 510 | 218.79 | 0 | 0 | No
2030-06-04 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-04 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-04 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-04 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-04 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-04 05:00 | 2030 Initial | 700 | 300 | 309.77 | 510 | 0 | 0 | No
2030-06-04 06:00 | 2030 Initial | 700 | 0 | 9.77 | 221.48 | 0 | 0 | No
2030-06-04 07:00 | 2030 Initial | 700 | -300 | -290.23 | 293.88 | 0 | 0 | No
2030-06-04 08:00 | 2030 Initial | 700 | -526 | -510 | 293.88 | 0 | 0 | No
2030-06-04 09:00 | 2030 Initial | 700 | -526 | -510 | 415.11 | 0 | 0 | No
2030-06-04 10:00 | 2030 Initial | 700 | -526 | -510 | 220.48 | 0 | 0 | No
2030-06-04 11:00 | 2030 Initial | 700 | -526 | -510 | 30.84 | 0 | 0 | No
2030-06-04 12:00 | 2030 Initial | 700 | -526 | -510 | 30.84 | 0 | 0 | No
2030-06-04 13:00 | 2030 Initial | 700 | -526 | -510 | 98.63 | 0 | 0 | No
2030-06-04 14:00 | 2030 Initial | 700 | -526 | -510 | -153.59 | 0 | 0 | No
2030-06-04 15:00 | 2030 Initial | 700 | -526 | -510 | -273.76 | 0 | 0 | No
2030-06-04 16:00 | 2030 Initial | 700 | -526 | -510 | -93.14 | 0 | 0 | No
2030-06-04 17:00 | 2030 Initial | 700 | -526 | -510 | -78.59 | 0 | 0 | No
2030-06-04 18:00 | 2030 Initial | 700 | -526 | -510 | -43.93 | 0 | 0 | No
2030-06-04 19:00 | 2030 Initial | 700 | -526 | -510 | -343.93 | 0 | 0 | No
2030-06-04 20:00 | 2030 Initial | 700 | -526 | -510 | -110.91 | 0 | 0 | No
2030-06-04 21:00 | 2030 Initial | 606.27 | -526 | -510 | -178.24 | 0 | 0 | No
2030-06-04 22:00 | 2030 Initial | 700 | -526 | -510 | -135.9 | 0 | 0 | No
2030-06-04 23:00 | 2030 Initial | 700 | -395 | -390 | -3.69 | 0 | 0 | No
2030-06-05 | 2030 Initial | 700 | -95 | -90 | 80.66 | 0 | 0 | No
2030-06-05 01:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-06-05 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-05 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-05 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-05 05:00 | 2030 Initial | 700 | 505 | 510 | 505.56 | 0 | 0 | No
2030-06-05 06:00 | 2030 Initial | 472.94 | 505 | 510 | 205.56 | 0 | 0 | No
2030-06-05 07:00 | 2030 Initial | 52.94 | 505 | 510 | 197.32 | 0 | 0 | No
2030-06-05 08:00 | 2030 Initial | -367.06 | 505 | 510 | 474.55 | 0 | 0 | Yes
2030-06-05 09:00 | 2030 Initial | -700 | 505 | 510 | 255.34 | 0 | 0 | Yes
2030-06-05 10:00 | 2030 Initial | -700 | 505 | 510 | 176.75 | 0 | 0 | Yes
2030-06-05 11:00 | 2030 Initial | -700 | 505 | 510 | 90.51 | 0 | 0 | Yes
2030-06-05 12:00 | 2030 Initial | -700 | 505 | 510 | 219.3 | 0 | 0 | Yes
2030-06-05 13:00 | 2030 Initial | -700 | 505 | 510 | 113.67 | 0 | 0 | Yes
2030-06-05 14:00 | 2030 Initial | -700 | 505 | 510 | 69.69 | 0 | 0 | Yes
2030-06-05 15:00 | 2030 Initial | -700 | 505 | 510 | 74.62 | 0 | 0 | Yes
2030-06-05 16:00 | 2030 Initial | -700 | 505 | 510 | 180.64 | 0 | 0 | Yes
2030-06-05 17:00 | 2030 Initial | -700 | 505 | 510 | 315.16 | 0 | 0 | Yes
2030-06-05 18:00 | 2030 Initial | -700 | 505 | 510 | 241.44 | 0 | 0 | Yes
2030-06-05 19:00 | 2030 Initial | -700 | 505 | 510 | 210.42 | 0 | 0 | Yes
2030-06-05 20:00 | 2030 Initial | -700 | 505 | 510 | 217.42 | 0 | 0 | Yes
2030-06-05 21:00 | 2030 Initial | -700 | 505 | 510 | 205.48 | 0 | 0 | Yes
2030-06-05 22:00 | 2030 Initial | -700 | 505 | 510 | 71.56 | 0 | 0 | Yes
2030-06-05 23:00 | 2030 Initial | -700 | 505 | 510 | -0.69 | 0 | 0 | Yes
2030-06-06 | 2030 Initial | -700 | 505 | 510 | 294.41 | 0 | 0 | Yes
2030-06-06 01:00 | 2030 Initial | -700 | 505 | 510 | 14.55 | 0 | 0 | Yes
2030-06-06 02:00 | 2030 Initial | -700 | 505 | 510 | 88.32 | 0 | 0 | Yes
2030-06-06 03:00 | 2030 Initial | -700 | 505 | 510 | -103.49 | 0 | 0 | Yes
2030-06-06 04:00 | 2030 Initial | -700 | 505 | 510 | -84.49 | 0 | 0 | Yes
2030-06-06 05:00 | 2030 Initial | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-06 06:00 | 2030 Initial | -700 | 505 | 510 | 287.21 | 0 | 0 | Yes
2030-06-06 07:00 | 2030 Initial | -700 | 505 | 510 | 123.45 | 0 | 0 | Yes
2030-06-06 08:00 | 2030 Initial | -700 | 505 | 510 | 242.74 | 0 | 0 | Yes
2030-06-06 09:00 | 2030 Initial | -700 | 505 | 510 | 242.74 | 0 | 0 | Yes
2030-06-06 10:00 | 2030 Initial | -700 | 505 | 510 | 303.35 | 0 | 0 | Yes
2030-06-06 11:00 | 2030 Initial | -700 | 505 | 510 | 362.85 | 0 | 0 | Yes
2030-06-06 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-06 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-06 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-06 15:00 | 2030 Initial | -700 | 505 | 510 | 414.54 | 0 | 0 | Yes
2030-06-06 16:00 | 2030 Initial | -503.83 | 505 | 283.74 | 510 | 0 | 0 | Yes
2030-06-06 17:00 | 2030 Initial | -83.83 | 205 | -16.26 | 392.44 | 0 | 0 | No
2030-06-06 18:00 | 2030 Initial | 336.17 | -95 | -316.26 | 92.44 | 0 | 0 | No
2030-06-06 19:00 | 2030 Initial | 700 | -395 | -510 | -190.71 | 0 | 0 | No
2030-06-06 20:00 | 2030 Initial | 700 | -395.38 | -510 | -463.08 | 0 | 0 | No
2030-06-06 21:00 | 2030 Initial | 700 | -136.43 | -210 | -510 | 0 | 0 | No
2030-06-06 22:00 | 2030 Initial | 700 | 151.23 | 90 | -339.53 | 0 | 0 | No
2030-06-06 23:00 | 2030 Initial | 280 | 451.23 | 390 | -39.53 | 0 | 0 | No
2030-06-07 | 2030 Initial | 700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-07 01:00 | 2030 Initial | 700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-06-07 02:00 | 2030 Initial | 505.34 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-07 03:00 | 2030 Initial | 590.2 | 505 | 510 | 261.37 | 0 | 0 | Yes
2030-06-07 04:00 | 2030 Initial | 170.2 | 505 | 510 | 369.23 | 0 | 0 | Yes
2030-06-07 05:00 | 2030 Initial | 374.86 | 443.68 | 510 | 314.92 | 0 | 0 | No
2030-06-07 06:00 | 2030 Initial | 700 | 143.68 | 210 | 14.92 | 0 | 0 | No
2030-06-07 07:00 | 2030 Initial | 280 | -156.32 | -90 | -285.08 | 0 | 0 | No
2030-06-07 08:00 | 2030 Initial | 682.44 | 0 | 0 | -233.45 | 0 | 0 | No
2030-06-07 09:00 | 2030 Initial | 262.44 | 0 | -26.94 | -133.53 | 0 | 0 | No
2030-06-07 10:00 | 2030 Initial | 0 | 0 | -150.9 | -275.19 | 0 | 0 | No
2030-06-07 11:00 | 2030 Initial | 0 | 0 | -264.91 | 0 | 0 | 0 | No
2030-06-07 12:00 | 2030 Initial | 0 | 0 | 0 | -174.35 | 0 | 0 | No
2030-06-07 13:00 | 2030 Initial | 0 | 115.73 | 300 | 125.65 | 0 | 0 | No
2030-06-07 14:00 | 2030 Initial | 0 | 115.91 | 177.98 | 0 | 0 | 0 | No
2030-06-07 15:00 | 2030 Initial | 280 | 0 | -122.02 | -300 | 0 | 0 | No
2030-06-07 16:00 | 2030 Initial | 700 | -226 | -422.02 | -510 | 0 | 0 | No
2030-06-07 17:00 | 2030 Initial | 537.43 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 18:00 | 2030 Initial | 159.1 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 19:00 | 2030 Initial | 579.1 | -226 | -510 | -336.82 | 0 | 0 | No
2030-06-07 20:00 | 2030 Initial | 700 | 0 | -415.77 | -36.82 | 0 | 0 | No
2030-06-07 21:00 | 2030 Initial | 700 | 0 | -170.24 | 0 | 0 | 0 | No
2030-06-07 22:00 | 2030 Initial | 700 | 0 | -298.82 | 0 | 0 | 0 | No
2030-06-07 23:00 | 2030 Initial | 700 | 0 | -322.57 | 0 | 0 | 0 | No
2030-06-08 | 2030 Initial | 700 | 0 | -190.42 | 0 | 0 | 0 | No
2030-06-08 01:00 | 2030 Initial | 700 | 0 | -78.03 | 0 | 0 | 0 | No
2030-06-08 02:00 | 2030 Initial | 700 | 0 | -96.33 | 0 | 0 | 0 | No
2030-06-08 03:00 | 2030 Initial | 700 | 0 | -65.86 | 0 | 0 | 0 | No
2030-06-08 04:00 | 2030 Initial | 700 | 0 | -134.21 | 0 | 0 | 0 | No
2030-06-08 05:00 | 2030 Initial | 700 | 0 | -434.21 | 0 | 0 | 0 | No
2030-06-08 06:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-08 07:00 | 2030 Initial | 452.66 | -300 | -510 | -49.31 | 0 | 0 | No
2030-06-08 08:00 | 2030 Initial | 700 | -526 | -510 | -58.98 | 0 | 0 | No
2030-06-08 09:00 | 2030 Initial | 700 | -526 | -510 | -44.88 | 0 | 0 | No
2030-06-08 10:00 | 2030 Initial | 700 | -526 | -510 | 2.1 | 0 | 0 | No
2030-06-08 11:00 | 2030 Initial | 700 | -526 | -510 | 19.7 | 0 | 0 | No
2030-06-08 12:00 | 2030 Initial | 700 | -526 | -510 | -1.1 | 0 | 0 | No
2030-06-08 13:00 | 2030 Initial | 700 | -526 | -510 | -8.77 | 0 | 0 | No
2030-06-08 14:00 | 2030 Initial | 700 | -526 | -510 | -66.33 | 0 | 0 | No
2030-06-08 15:00 | 2030 Initial | 700 | -526 | -510 | -84.49 | 0 | 0 | No
2030-06-08 16:00 | 2030 Initial | 700 | -526 | -510 | -18.92 | 0 | 0 | No
2030-06-08 17:00 | 2030 Initial | 700 | -526 | -510 | 78.54 | 0 | 0 | No
2030-06-08 18:00 | 2030 Initial | 700 | -526 | -510 | -221.46 | 0 | 0 | No
2030-06-08 19:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-08 20:00 | 2030 Initial | 700 | -526 | -510 | -382.05 | 0 | 0 | No
2030-06-08 21:00 | 2030 Initial | 700 | -317.41 | -510 | -82.05 | 0 | 0 | No
2030-06-08 22:00 | 2030 Initial | 700 | -17.41 | -210 | 217.95 | 0 | 0 | No
2030-06-08 23:00 | 2030 Initial | 700 | 0 | 77.62 | 0 | 0 | 0 | No
2030-06-09 | 2030 Initial | 700 | 0 | -8.16 | 0 | 0 | 0 | No
2030-06-09 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-09 02:00 | 2030 Initial | 700 | 0 | -78.8 | 0 | 0 | 0 | No
2030-06-09 03:00 | 2030 Initial | 700 | 0 | -164.84 | 0 | 0 | 0 | No
2030-06-09 04:00 | 2030 Initial | 700 | 0 | -115.75 | 0 | 0 | 0 | No
2030-06-09 05:00 | 2030 Initial | 700 | 0 | -311.31 | 0 | 0 | 0 | No
2030-06-09 06:00 | 2030 Initial | 700 | 0 | -97.23 | 0 | 0 | 0 | No
2030-06-09 07:00 | 2030 Initial | 700 | 0 | -397.23 | 1.02 | 0 | 0 | No
2030-06-09 08:00 | 2030 Initial | 700 | -226 | -502.48 | 0 | 0 | 0 | No
2030-06-09 09:00 | 2030 Initial | 700 | -526 | -510 | -2.56 | 0 | 0 | No
2030-06-09 10:00 | 2030 Initial | 700 | -526 | -510 | 14.75 | 0 | 0 | No
2030-06-09 11:00 | 2030 Initial | 700 | -526 | -510 | 56.88 | 0 | 0 | No
2030-06-09 12:00 | 2030 Initial | 700 | -526 | -510 | 80.49 | 0 | 0 | No
2030-06-09 13:00 | 2030 Initial | 700 | -526 | -510 | 87.87 | 0 | 0 | No
2030-06-09 14:00 | 2030 Initial | 700 | -526 | -510 | 58.95 | 0 | 0 | No
2030-06-09 15:00 | 2030 Initial | 700 | -526 | -510 | 107.98 | 0 | 0 | No
2030-06-09 16:00 | 2030 Initial | 700 | -526 | -510 | 165.67 | 0 | 0 | No
2030-06-09 17:00 | 2030 Initial | 700 | -226 | -510 | 190.04 | 0 | 0 | No
2030-06-09 18:00 | 2030 Initial | 700 | 0 | -217.36 | 123.73 | 0 | 0 | No
2030-06-09 19:00 | 2030 Initial | 700 | 0 | 0 | 72.14 | 0 | 0 | No
2030-06-09 20:00 | 2030 Initial | 700 | 0 | 0 | 18.39 | 0 | 0 | No
2030-06-09 21:00 | 2030 Initial | 700 | 0 | 0 | 64.93 | 0 | 0 | No
2030-06-09 22:00 | 2030 Initial | 700 | 0 | -4.14 | 22.68 | 0 | 0 | No
2030-06-09 23:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-10 | 2030 Initial | 700 | 0 | -24.98 | 26.29 | 0 | 0 | No
2030-06-10 01:00 | 2030 Initial | 700 | 0 | -324.98 | 20.97 | 0 | 0 | No
2030-06-10 02:00 | 2030 Initial | 700 | 0 | -330.45 | 0 | 0 | 0 | No
2030-06-10 03:00 | 2030 Initial | 700 | 0 | -366.33 | 0 | 0 | 0 | No
2030-06-10 04:00 | 2030 Initial | 700 | 0 | -339.88 | 0 | 0 | 0 | No
2030-06-10 05:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-10 06:00 | 2030 Initial | 700 | 0 | -510 | 75.42 | 0 | 0 | No
2030-06-10 07:00 | 2030 Initial | 700 | 0 | -406.58 | 199.09 | 0 | 0 | No
2030-06-10 08:00 | 2030 Initial | 700 | -226 | -510 | 279.28 | 0 | 0 | No
2030-06-10 09:00 | 2030 Initial | 700 | -526 | -510 | 197.78 | 0 | 0 | No
2030-06-10 10:00 | 2030 Initial | 700 | -526 | -510 | 262.86 | 0 | 0 | No
2030-06-10 11:00 | 2030 Initial | 700 | -526 | -510 | 267.78 | 0 | 0 | No
2030-06-10 12:00 | 2030 Initial | 700 | -526 | -510 | 167.15 | 0 | 0 | No
2030-06-10 13:00 | 2030 Initial | 700 | -526 | -510 | 180.96 | 0 | 0 | No
2030-06-10 14:00 | 2030 Initial | 700 | -526 | -510 | 218.9 | 0 | 0 | No
2030-06-10 15:00 | 2030 Initial | 700 | -526 | -510 | 234.94 | 0 | 0 | No
2030-06-10 16:00 | 2030 Initial | 700 | -526 | -510 | 305.49 | 0 | 0 | No
2030-06-10 17:00 | 2030 Initial | 700 | -526 | -510 | 258.89 | 0 | 0 | No
2030-06-10 18:00 | 2030 Initial | 700 | -493.26 | -510 | 103.07 | 0 | 0 | No
2030-06-10 19:00 | 2030 Initial | 700 | -205.26 | -510 | -4.59 | 0 | 0 | No
2030-06-10 20:00 | 2030 Initial | 700 | 0 | -390 | -35.4 | 0 | 0 | No
2030-06-10 21:00 | 2030 Initial | 700 | -95 | -90 | -127.61 | 0 | 0 | No
2030-06-10 22:00 | 2030 Initial | 700 | 205 | 210 | -316.49 | 0 | 0 | No
2030-06-10 23:00 | 2030 Initial | 552.37 | 505 | 510 | -16.49 | 0 | 0 | Yes
2030-06-11 | 2030 Initial | 138.03 | 505 | 510 | 115.96 | 0 | 0 | Yes
2030-06-11 01:00 | 2030 Initial | -281.97 | 505 | 510 | 384.74 | 0 | 0 | Yes
2030-06-11 02:00 | 2030 Initial | -700 | 505 | 510 | 115.83 | 0 | 0 | Yes
2030-06-11 03:00 | 2030 Initial | -700 | 505 | 510 | -64.16 | 0 | 0 | Yes
2030-06-11 04:00 | 2030 Initial | -700 | 505 | 510 | -3.5 | 0 | 0 | Yes
2030-06-11 05:00 | 2030 Initial | -700 | 505 | 510 | -62.35 | 0 | 0 | Yes
2030-06-11 06:00 | 2030 Initial | -700 | 505 | 510 | 7.47 | 0 | 0 | Yes
2030-06-11 07:00 | 2030 Initial | -700 | 505 | 510 | 124.31 | 0 | 0 | Yes
2030-06-11 08:00 | 2030 Initial | -700 | 505 | 510 | 277.24 | 0 | 0 | Yes
2030-06-11 09:00 | 2030 Initial | -700 | 505 | 510 | 100.96 | 0 | 0 | Yes
2030-06-11 10:00 | 2030 Initial | -700 | 505 | 510 | 167.37 | 0 | 0 | Yes
2030-06-11 11:00 | 2030 Initial | -700 | 505 | 510 | 132.24 | 0 | 0 | Yes
2030-06-11 12:00 | 2030 Initial | -700 | 505 | 510 | 432.24 | 0 | 0 | Yes
2030-06-11 13:00 | 2030 Initial | -700 | 505 | 510 | 318.5 | 0 | 0 | Yes
2030-06-11 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 16:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 17:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-06-11 18:00 | 2030 Initial | 102.57 | 505 | 510 | 510 | 0 | 0 | No
2030-06-11 19:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-06-11 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 21:00 | 2030 Initial | 700 | 505 | 510 | 417.25 | 0 | 0 | Yes
2030-06-11 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 23:00 | 2030 Initial | 700 | 505 | 510 | 439.64 | 0 | 0 | Yes
2030-06-12 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-12 01:00 | 2030 Initial | 700 | 505 | 510 | 344.99 | 0 | 0 | Yes
2030-06-12 02:00 | 2030 Initial | 280 | 505 | 510 | 122.07 | 0 | 0 | Yes
2030-06-12 03:00 | 2030 Initial | 167.74 | 505 | 510 | 363.82 | 0 | 0 | Yes
2030-06-12 04:00 | 2030 Initial | 0 | 505 | 510 | 70.78 | 0 | 0 | Yes
2030-06-12 05:00 | 2030 Initial | -66.98 | 505 | 510 | 1.51 | 0 | 0 | Yes
2030-06-12 06:00 | 2030 Initial | -159.87 | 505 | 510 | 192.62 | 0 | 0 | Yes
2030-06-12 07:00 | 2030 Initial | 0 | 505 | 510 | 158.81 | 0 | 0 | Yes
2030-06-12 08:00 | 2030 Initial | -280 | 505 | 510 | -141.19 | 0 | 0 | No
2030-06-12 09:00 | 2030 Initial | -700 | 505 | 510 | 158.81 | 0 | 0 | Yes
2030-06-12 10:00 | 2030 Initial | -700 | 505 | 510 | 355.04 | 0 | 0 | Yes
2030-06-12 11:00 | 2030 Initial | -700 | 505 | 510 | 331.11 | 0 | 0 | Yes
2030-06-12 12:00 | 2030 Initial | -700 | 505 | 510 | 233.77 | 0 | 0 | Yes
2030-06-12 13:00 | 2030 Initial | -700 | 505 | 510 | 367.52 | 0 | 0 | Yes
2030-06-12 14:00 | 2030 Initial | -700 | 505 | 510 | 394.66 | 0 | 0 | Yes
2030-06-12 15:00 | 2030 Initial | -280 | 300 | 464.88 | 250.03 | 0 | 0 | Yes
2030-06-12 16:00 | 2030 Initial | 140 | 0 | 164.88 | -49.97 | 0 | 0 | No
2030-06-12 17:00 | 2030 Initial | 560 | 105.63 | 0 | 250.03 | 0 | 0 | No
2030-06-12 18:00 | 2030 Initial | 700 | -194.37 | -300 | -49.97 | 0 | 0 | No
2030-06-12 19:00 | 2030 Initial | 700 | 0 | -510 | -349.97 | 0 | 0 | No
2030-06-12 20:00 | 2030 Initial | 700 | 0 | -510 | -510 | 0 | 0 | No
2030-06-12 21:00 | 2030 Initial | 700 | 0 | -422.41 | -343.7 | 0 | 0 | No
2030-06-12 22:00 | 2030 Initial | 700 | 0 | -122.41 | -175.47 | 0 | 0 | No
2030-06-12 23:00 | 2030 Initial | 700 | 0 | 177.59 | 124.53 | 0 | 0 | No
2030-06-13 | 2030 Initial | 700 | 0 | 300 | 346.12 | 0 | 0 | No
2030-06-13 01:00 | 2030 Initial | 700 | 25.59 | 0 | 384.67 | 0 | 0 | No
2030-06-13 02:00 | 2030 Initial | 700 | 0 | -300 | 84.67 | 0 | 0 | No
2030-06-13 03:00 | 2030 Initial | 700 | 0 | -510 | 177.86 | 0 | 0 | No
2030-06-13 04:00 | 2030 Initial | 700 | 0 | -510 | 193.17 | 0 | 0 | No
2030-06-13 05:00 | 2030 Initial | 700 | -34.21 | -510 | -55.49 | 0 | 0 | No
2030-06-13 06:00 | 2030 Initial | 700 | 0 | -510 | -30.86 | 0 | 0 | No
2030-06-13 07:00 | 2030 Initial | 700 | 0 | -510 | -169.18 | 0 | 0 | No
2030-06-13 08:00 | 2030 Initial | 700 | -226 | -510 | 0 | 0 | 0 | No
2030-06-13 09:00 | 2030 Initial | 700 | -526 | -510 | 37.4 | 0 | 0 | No
2030-06-13 10:00 | 2030 Initial | 700 | -526 | -510 | 337.4 | 0 | 0 | No
2030-06-13 11:00 | 2030 Initial | 700 | -526 | -510 | 139.66 | 0 | 0 | No
2030-06-13 12:00 | 2030 Initial | 700 | -526 | -510 | 111.55 | 0 | 0 | No
2030-06-13 13:00 | 2030 Initial | 700 | -526 | -510 | 207.45 | 0 | 0 | No
2030-06-13 14:00 | 2030 Initial | 700 | -526 | -510 | -92.55 | 0 | 0 | No
2030-06-13 15:00 | 2030 Initial | 700 | -526 | -510 | 25.65 | 0 | 0 | No
2030-06-13 16:00 | 2030 Initial | 700 | -526 | -510 | -39.95 | 0 | 0 | No
2030-06-13 17:00 | 2030 Initial | 700 | -297.46 | -381.13 | 260.05 | 0 | 0 | No
2030-06-13 18:00 | 2030 Initial | 700 | 0 | -81.13 | 21.63 | 0 | 0 | No
2030-06-13 19:00 | 2030 Initial | 700 | 0 | 218.87 | 149.47 | 0 | 0 | No
2030-06-13 20:00 | 2030 Initial | 700 | 0 | 247.58 | 0 | 0 | 0 | No
2030-06-13 21:00 | 2030 Initial | 700 | 0 | 510 | 300 | 0 | 0 | No
2030-06-13 22:00 | 2030 Initial | 700 | 0 | 416.17 | 300 | 0 | 0 | No
2030-06-13 23:00 | 2030 Initial | 700 | 0 | 116.17 | 0 | 0 | 0 | No
2030-06-14 | 2030 Initial | 700 | 0 | -138.8 | 0 | 0 | 0 | No
2030-06-14 01:00 | 2030 Initial | 700 | 0 | -438.8 | -22.14 | 0 | 0 | No
2030-06-14 02:00 | 2030 Initial | 700 | 0 | -151.24 | 0 | 0 | 0 | No
2030-06-14 03:00 | 2030 Initial | 700 | 0 | 21.24 | 0 | 0 | 0 | No
2030-06-14 04:00 | 2030 Initial | 700 | 0 | -278.76 | 0 | 0 | 0 | No
2030-06-14 05:00 | 2030 Initial | 700 | 0 | -510 | -132.3 | 0 | 0 | No
2030-06-14 06:00 | 2030 Initial | 700 | 0 | -510 | -254.11 | 0 | 0 | No
2030-06-14 07:00 | 2030 Initial | 700 | -226 | -510 | 0 | 0 | 0 | No
2030-06-14 08:00 | 2030 Initial | 700 | -526 | -510 | -20.94 | 0 | 0 | No
2030-06-14 09:00 | 2030 Initial | 700 | -526 | -510 | 6.99 | 0 | 0 | No
2030-06-14 10:00 | 2030 Initial | 700 | -526 | -510 | -185.45 | 0 | 0 | No
2030-06-14 11:00 | 2030 Initial | 700 | -526 | -510 | -325 | 0 | 0 | No
2030-06-14 12:00 | 2030 Initial | 700 | -526 | -510 | -332.46 | 0 | 0 | No
2030-06-14 13:00 | 2030 Initial | 700 | -526 | -510 | -212.25 | 0 | 0 | No
2030-06-14 14:00 | 2030 Initial | 700 | -526 | -510 | -124.75 | 0 | 0 | No
2030-06-14 15:00 | 2030 Initial | 700 | -526 | -510 | 49.87 | 0 | 0 | No
2030-06-14 16:00 | 2030 Initial | 700 | -526 | -510 | -85.51 | 0 | 0 | No
2030-06-14 17:00 | 2030 Initial | 700 | -370.15 | -510 | -154.7 | 0 | 0 | No
2030-06-14 18:00 | 2030 Initial | 700 | -70.15 | -510 | -110.48 | 0 | 0 | No
2030-06-14 19:00 | 2030 Initial | 700 | 0 | -510 | -410.48 | 0 | 0 | No
2030-06-14 20:00 | 2030 Initial | 700 | 0 | -466.56 | -151.71 | 0 | 0 | No
2030-06-14 21:00 | 2030 Initial | 700 | 0 | -166.56 | 0 | 0 | 0 | No
2030-06-14 22:00 | 2030 Initial | 700 | 0 | 133.44 | 300 | 0 | 0 | No
2030-06-14 23:00 | 2030 Initial | 700 | 0 | 286.29 | 0 | 0 | 0 | No
2030-06-15 | 2030 Initial | 700 | 0 | -13.71 | 0 | 0 | 0 | No
2030-06-15 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-15 02:00 | 2030 Initial | 700 | 0 | -225.13 | 0 | 0 | 0 | No
2030-06-15 03:00 | 2030 Initial | 700 | 0 | -203.83 | 0 | 0 | 0 | No
2030-06-15 04:00 | 2030 Initial | 700 | 0 | -503.83 | 0 | 0 | 0 | No
2030-06-15 05:00 | 2030 Initial | 700 | 0 | -418.83 | 0 | 0 | 0 | No
2030-06-15 06:00 | 2030 Initial | 700 | -226 | -510 | -210 | 0 | 0 | No
2030-06-15 07:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 08:00 | 2030 Initial | 280 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 09:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 10:00 | 2030 Initial | 700 | -526 | -510 | -399.1 | 0 | 0 | No
2030-06-15 11:00 | 2030 Initial | 700 | -526 | -510 | -320.11 | 0 | 0 | No
2030-06-15 12:00 | 2030 Initial | 700 | -526 | -510 | -138.75 | 0 | 0 | No
2030-06-15 13:00 | 2030 Initial | 700 | -526 | -510 | -267.76 | 0 | 0 | No
2030-06-15 14:00 | 2030 Initial | 700 | -526 | -510 | -184.91 | 0 | 0 | No
2030-06-15 15:00 | 2030 Initial | 700 | -526 | -510 | -151.49 | 0 | 0 | No
2030-06-15 16:00 | 2030 Initial | 700 | -526 | -510 | -259.58 | 0 | 0 | No
2030-06-15 17:00 | 2030 Initial | 280 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 18:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 19:00 | 2030 Initial | 700 | -483.92 | -510 | -510 | 0 | 0 | No
2030-06-15 20:00 | 2030 Initial | 700 | -183.92 | -510 | -510 | 0 | 0 | No
2030-06-15 21:00 | 2030 Initial | 700 | -300 | -396.92 | -300 | 0 | 0 | No
2030-06-15 22:00 | 2030 Initial | 700 | 0 | -96.92 | 0 | 0 | 0 | No
2030-06-15 23:00 | 2030 Initial | 700 | 0 | -131.65 | 0 | 0 | 0 | No
2030-06-16 | 2030 Initial | 700 | 0 | -354.99 | 0 | 0 | 0 | No
2030-06-16 01:00 | 2030 Initial | 700 | 0 | -385.69 | 0 | 0 | 0 | No
2030-06-16 02:00 | 2030 Initial | 700 | 0 | -499.02 | 0 | 0 | 0 | No
2030-06-16 03:00 | 2030 Initial | 700 | 0 | -510 | -71.83 | 0 | 0 | No
2030-06-16 04:00 | 2030 Initial | 700 | 0 | -510 | -37.75 | 0 | 0 | No
2030-06-16 05:00 | 2030 Initial | 700 | 0 | -510 | -22.87 | 0 | 0 | No
2030-06-16 06:00 | 2030 Initial | 700 | -168.31 | -510 | 0 | 0 | 0 | No
2030-06-16 07:00 | 2030 Initial | 700 | -468.31 | -510 | 12.79 | 0 | 0 | No
2030-06-16 08:00 | 2030 Initial | 700 | -526 | -510 | -7.71 | 0 | 0 | No
2030-06-16 09:00 | 2030 Initial | 700 | -526 | -510 | -31.64 | 0 | 0 | No
2030-06-16 10:00 | 2030 Initial | 700 | -526 | -510 | -32.74 | 0 | 0 | No
2030-06-16 11:00 | 2030 Initial | 700 | -526 | -510 | -13.94 | 0 | 0 | No
2030-06-16 12:00 | 2030 Initial | 700 | -526 | -510 | 8.28 | 0 | 0 | No
2030-06-16 13:00 | 2030 Initial | 700 | -526 | -510 | 22.53 | 0 | 0 | No
2030-06-16 14:00 | 2030 Initial | 700 | -526 | -510 | -25.23 | 0 | 0 | No
2030-06-16 15:00 | 2030 Initial | 700 | -526 | -510 | -71.28 | 0 | 0 | No
2030-06-16 16:00 | 2030 Initial | 700 | -526 | -510 | -31.05 | 0 | 0 | No
2030-06-16 17:00 | 2030 Initial | 700 | -494.85 | -510 | -63.46 | 0 | 0 | No
2030-06-16 18:00 | 2030 Initial | 700 | -194.85 | -210 | 55.13 | 0 | 0 | No
2030-06-16 19:00 | 2030 Initial | 700 | 0 | 0 | 30.03 | 0 | 0 | No
2030-06-16 20:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-16 21:00 | 2030 Initial | 700 | 0 | -57.89 | 0 | 0 | 0 | No
2030-06-16 22:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-16 23:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-17 | 2030 Initial | 700 | 0 | 122.54 | 0 | 0 | 0 | No
2030-06-17 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-17 02:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-17 03:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-17 04:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-17 05:00 | 2030 Initial | 700 | 0 | -79.14 | 0 | 0 | 0 | No
2030-06-17 06:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-17 07:00 | 2030 Initial | 700 | 0 | -86.56 | 104.67 | 0 | 0 | No
2030-06-17 08:00 | 2030 Initial | 700 | -7.87 | -271.14 | 264.55 | 0 | 0 | No
2030-06-17 09:00 | 2030 Initial | 700 | -307.87 | -510 | 310.63 | 0 | 0 | No
2030-06-17 10:00 | 2030 Initial | 700 | -526 | -510 | 297.82 | 0 | 0 | No
2030-06-17 11:00 | 2030 Initial | 700 | -478.59 | -510 | 335.8 | 0 | 0 | No
2030-06-17 12:00 | 2030 Initial | 700 | -526 | -510 | 307.92 | 0 | 0 | No
2030-06-17 13:00 | 2030 Initial | 700 | -526 | -510 | 233.86 | 0 | 0 | No
2030-06-17 14:00 | 2030 Initial | 700 | -526 | -510 | 264.82 | 0 | 0 | No
2030-06-17 15:00 | 2030 Initial | 700 | -526 | -510 | 271.07 | 0 | 0 | No
2030-06-17 16:00 | 2030 Initial | 700 | -317.44 | -510 | 326.67 | 0 | 0 | No
2030-06-17 17:00 | 2030 Initial | 700 | -17.44 | -210 | 411.12 | 0 | 0 | No
2030-06-17 18:00 | 2030 Initial | 700 | 0 | 90 | 431.77 | 0 | 0 | No
2030-06-17 19:00 | 2030 Initial | 700 | 0 | 390 | 510 | 0 | 0 | No
2030-06-17 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-06-17 21:00 | 2030 Initial | 700 | 0 | 510 | 500.47 | 0 | 0 | No
2030-06-17 22:00 | 2030 Initial | 700 | 0 | 510 | 500.47 | 0 | 0 | No
2030-06-17 23:00 | 2030 Initial | 700 | 0 | 510 | 388.44 | 0 | 0 | No
2030-06-18 | 2030 Initial | 700 | 0 | 510 | 88.44 | 0 | 0 | No
2030-06-18 01:00 | 2030 Initial | 700 | 0 | 398.36 | 92.03 | 0 | 0 | No
2030-06-18 02:00 | 2030 Initial | 700 | 0 | 194.78 | 98.92 | 0 | 0 | No
2030-06-18 03:00 | 2030 Initial | 700 | 0 | 283.68 | 88.78 | 0 | 0 | No
2030-06-18 04:00 | 2030 Initial | 700 | 0 | 338.86 | 56.4 | 0 | 0 | No
2030-06-18 05:00 | 2030 Initial | 700 | 0 | 62.61 | 32.48 | 0 | 0 | No
2030-06-18 06:00 | 2030 Initial | 700 | 0 | 269.17 | 95.24 | 0 | 0 | No
2030-06-18 07:00 | 2030 Initial | 700 | 0 | 9.99 | 226.21 | 0 | 0 | No
2030-06-18 08:00 | 2030 Initial | 700 | 0 | -271.39 | 256.87 | 0 | 0 | No
2030-06-18 09:00 | 2030 Initial | 586.91 | -300 | -510 | 259.24 | 0 | 0 | No
2030-06-18 10:00 | 2030 Initial | 455.46 | -526 | -510 | 220.57 | 0 | 0 | No
2030-06-18 11:00 | 2030 Initial | 545.01 | -526 | -510 | 241.87 | 0 | 0 | No
2030-06-18 12:00 | 2030 Initial | 700 | -518.46 | -510 | 246.24 | 0 | 0 | No
2030-06-18 13:00 | 2030 Initial | 700 | -393.43 | -510 | 196.71 | 0 | 0 | No
2030-06-18 14:00 | 2030 Initial | 700 | -295.42 | -510 | 200.58 | 0 | 0 | No
2030-06-18 15:00 | 2030 Initial | 700 | -160.11 | -300 | 191.49 | 0 | 0 | No
2030-06-18 16:00 | 2030 Initial | 700 | 0 | 0 | 232.12 | 0 | 0 | No
2030-06-18 17:00 | 2030 Initial | 700 | 0 | 300 | 187.76 | 0 | 0 | No
2030-06-18 18:00 | 2030 Initial | 700 | 0 | 510 | 238.02 | 0 | 0 | No
2030-06-18 19:00 | 2030 Initial | 700 | 0 | 375.48 | 0 | 0 | 0 | No
2030-06-18 20:00 | 2030 Initial | 700 | 0 | 75.48 | 0 | 0 | 0 | No
2030-06-18 21:00 | 2030 Initial | 700 | 0 | -13.72 | 0 | 0 | 0 | No
2030-06-18 22:00 | 2030 Initial | 700 | 0 | 189.4 | 0 | 0 | 0 | No
2030-06-18 23:00 | 2030 Initial | 700 | 0 | 202.68 | 0 | 0 | 0 | No
2030-06-19 | 2030 Initial | 700 | 0 | 38.52 | 0 | 0 | 0 | No
2030-06-19 01:00 | 2030 Initial | 700 | 0 | -29.41 | 0 | 0 | 0 | No
2030-06-19 02:00 | 2030 Initial | 700 | 0 | -202.05 | 0 | 0 | 0 | No
2030-06-19 03:00 | 2030 Initial | 700 | 0 | -276.16 | 0 | 0 | 0 | No
2030-06-19 04:00 | 2030 Initial | 700 | 0 | -312.51 | 0 | 0 | 0 | No
2030-06-19 05:00 | 2030 Initial | 700 | 0 | -323.48 | 0 | 0 | 0 | No
2030-06-19 06:00 | 2030 Initial | 700 | 0 | -370.2 | 0 | 0 | 0 | No
2030-06-19 07:00 | 2030 Initial | 700 | 0 | -70.2 | 119.46 | 0 | 0 | No
2030-06-19 08:00 | 2030 Initial | 700 | 0 | 0 | 132.9 | 0 | 0 | No
2030-06-19 09:00 | 2030 Initial | 700 | 0 | -264.68 | 256.6 | 0 | 0 | No
2030-06-19 10:00 | 2030 Initial | 700 | 0 | -270.96 | 127.62 | 0 | 0 | No
2030-06-19 11:00 | 2030 Initial | 645.27 | -300 | -510 | 295.22 | 0 | 0 | No
2030-06-19 12:00 | 2030 Initial | 465.38 | -408.05 | -510 | 250.39 | 0 | 0 | No
2030-06-19 13:00 | 2030 Initial | 45.38 | -526 | -510 | 223.6 | 0 | 0 | No
2030-06-19 14:00 | 2030 Initial | -176.44 | -526 | -510 | 224.88 | 0 | 0 | No
2030-06-19 15:00 | 2030 Initial | 109.16 | -526 | -510 | 236.12 | 0 | 0 | No
2030-06-19 16:00 | 2030 Initial | 529.16 | -426.95 | -510 | 63.2 | 0 | 0 | No
2030-06-19 17:00 | 2030 Initial | 678.21 | -300 | -357.9 | 12.92 | 0 | 0 | No
2030-06-19 18:00 | 2030 Initial | 700 | 0 | -57.9 | 100.04 | 0 | 0 | No
2030-06-19 19:00 | 2030 Initial | 700 | 0 | 154.83 | 215.8 | 0 | 0 | No
2030-06-19 20:00 | 2030 Initial | 700 | 0 | 377.77 | 259.41 | 0 | 0 | No
2030-06-19 21:00 | 2030 Initial | 700 | 0 | 510 | 292.65 | 0 | 0 | No
2030-06-19 22:00 | 2030 Initial | 700 | 0 | 510 | 164.14 | 0 | 0 | No
2030-06-19 23:00 | 2030 Initial | 700 | 0 | 347.96 | 141.53 | 0 | 0 | No
2030-06-20 | 2030 Initial | 700 | 0 | 68.11 | 68.48 | 0 | 0 | No
2030-06-20 01:00 | 2030 Initial | 700 | 0 | -152.39 | 137.52 | 0 | 0 | No
2030-06-20 02:00 | 2030 Initial | 700 | -3.34 | -452.39 | 127.39 | 0 | 0 | No
2030-06-20 03:00 | 2030 Initial | 700 | -284.49 | -510 | 79.28 | 0 | 0 | No
2030-06-20 04:00 | 2030 Initial | 671.96 | -340.62 | -510 | 63.21 | 0 | 0 | No
2030-06-20 05:00 | 2030 Initial | 251.96 | -353.39 | -510 | -13.33 | 0 | 0 | No
2030-06-20 06:00 | 2030 Initial | -168.04 | -526 | -510 | 42.94 | 0 | 0 | No
2030-06-20 07:00 | 2030 Initial | -588.04 | -526 | -510 | 128.89 | 0 | 0 | No
2030-06-20 08:00 | 2030 Initial | -700 | -526 | -510 | 57.5 | 0 | 0 | No
2030-06-20 09:00 | 2030 Initial | -700 | -526 | -510 | -100.93 | 0 | 0 | Yes
2030-06-20 10:00 | 2030 Initial | -700 | -526 | -510 | -56.91 | 0 | 0 | Yes
2030-06-20 11:00 | 2030 Initial | -700 | -526 | -510 | -259.83 | 0 | 0 | Yes
2030-06-20 12:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 13:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 14:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 15:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 16:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-20 17:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-20 18:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-20 19:00 | 2030 Initial | -700 | -395 | -505.01 | -510 | 0 | 0 | No
2030-06-20 20:00 | 2030 Initial | -700 | -95 | -205.01 | -510 | 0 | 0 | No
2030-06-20 21:00 | 2030 Initial | -700 | 205 | 94.99 | -510 | 0 | 0 | No
2030-06-20 22:00 | 2030 Initial | -496.98 | 505 | 394.99 | -210 | 0 | 0 | Yes
2030-06-20 23:00 | 2030 Initial | -76.98 | 505 | 510 | 90 | 0 | 0 | Yes
2030-06-21 | 2030 Initial | 67.09 | 505 | 510 | 390 | 0 | 0 | Yes
2030-06-21 01:00 | 2030 Initial | -254.1 | 505 | 510 | 410.05 | 0 | 0 | Yes
2030-06-21 02:00 | 2030 Initial | -476.18 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 03:00 | 2030 Initial | -342.06 | 505 | 510 | 510 | 0 | 0 | No
2030-06-21 04:00 | 2030 Initial | -475.94 | 505 | 510 | 510 | 0 | 0 | No
2030-06-21 05:00 | 2030 Initial | -675.18 | 505 | 510 | 510 | 0 | 0 | No
2030-06-21 06:00 | 2030 Initial | -392.87 | 505 | 510 | 510 | 0 | 0 | No
2030-06-21 07:00 | 2030 Initial | -388.51 | 505 | 510 | 510 | 0 | 0 | No
2030-06-21 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-21 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 16:00 | 2030 Initial | -700 | 364.95 | 300 | 510 | 0 | 0 | Yes
2030-06-21 17:00 | 2030 Initial | -280 | 64.95 | 0 | 448.02 | 0 | 0 | No
2030-06-21 18:00 | 2030 Initial | 140 | -235.05 | -300 | 148.02 | 0 | 0 | No
2030-06-21 19:00 | 2030 Initial | 560 | 0 | -479.19 | 237.66 | 0 | 0 | No
2030-06-21 20:00 | 2030 Initial | 700 | 0 | -179.19 | 510 | 0 | 0 | No
2030-06-21 21:00 | 2030 Initial | 700 | 0 | -79.43 | 510 | 0 | 0 | No
2030-06-21 22:00 | 2030 Initial | 700 | 0 | -149.23 | 510 | 0 | 0 | No
2030-06-21 23:00 | 2030 Initial | 700 | -86.01 | -449.23 | 294.24 | 0 | 0 | No
2030-06-22 | 2030 Initial | 280 | -386.01 | -510 | 295.65 | 0 | 0 | No
2030-06-22 01:00 | 2030 Initial | 462.36 | -86.01 | -210 | 289.69 | 0 | 0 | No
2030-06-22 02:00 | 2030 Initial | 420 | 0 | 0 | 282.46 | 0 | 0 | No
2030-06-22 03:00 | 2030 Initial | 0 | 0 | -121.12 | 411.16 | 0 | 0 | No
2030-06-22 04:00 | 2030 Initial | -15.17 | -226 | -210 | 111.16 | 0 | 0 | No
2030-06-22 05:00 | 2030 Initial | -435.17 | -526 | -510 | -188.84 | 0 | 0 | No
2030-06-22 06:00 | 2030 Initial | -700 | -526 | -510 | -488.84 | 0 | 0 | No
2030-06-22 07:00 | 2030 Initial | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-06-22 08:00 | 2030 Initial | 140 | -226 | -304.92 | -390 | 0 | 0 | No
2030-06-22 09:00 | 2030 Initial | -280 | 74 | -4.92 | -90 | 0 | 0 | No
2030-06-22 10:00 | 2030 Initial | -700 | 374 | 295.08 | 210 | 0 | 0 | Yes
2030-06-22 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-22 15:00 | 2030 Initial | -700 | 505 | 510 | 390 | 0 | 0 | Yes
2030-06-22 16:00 | 2030 Initial | -700 | 505 | 510 | 90 | 0 | 0 | Yes
2030-06-22 17:00 | 2030 Initial | -700 | 505 | 510 | -210 | 0 | 0 | Yes
2030-06-22 18:00 | 2030 Initial | -349.28 | 205 | 210 | -510 | 0 | 0 | No
2030-06-22 19:00 | 2030 Initial | -284.29 | 505 | 510 | -210 | 0 | 0 | No
2030-06-22 20:00 | 2030 Initial | 135.71 | 505 | 510 | 90 | 0 | 0 | Yes
2030-06-22 21:00 | 2030 Initial | 515.79 | 505 | 510 | 390 | 0 | 0 | Yes
2030-06-22 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-22 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 06:00 | 2030 Initial | 700 | 205 | 210 | 245.97 | 0 | 0 | No
2030-06-23 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 09:00 | 2030 Initial | 700 | 205 | 213.3 | 252.09 | 0 | 0 | No
2030-06-23 10:00 | 2030 Initial | 700 | 0 | 276.28 | 385.11 | 0 | 0 | No
2030-06-23 11:00 | 2030 Initial | 700 | 205 | 393.89 | 367.61 | 0 | 0 | No
2030-06-23 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 14:00 | 2030 Initial | 700 | 225.06 | 210 | 510 | 0 | 0 | No
2030-06-23 15:00 | 2030 Initial | 700 | -74.94 | -90 | 510 | 0 | 0 | No
2030-06-23 16:00 | 2030 Initial | 700 | -374.94 | -390 | 357.11 | 0 | 0 | No
2030-06-23 17:00 | 2030 Initial | 700 | -526 | -510 | 57.11 | 0 | 0 | No
2030-06-23 18:00 | 2030 Initial | 700 | -226 | -210 | 149.98 | 0 | 0 | No
2030-06-23 19:00 | 2030 Initial | 700 | 0 | 0 | 149.98 | 0 | 0 | No
2030-06-23 20:00 | 2030 Initial | 700 | 0 | 0 | 292.9 | 0 | 0 | No
2030-06-23 21:00 | 2030 Initial | 700 | 0 | 102.74 | 134.01 | 0 | 0 | No
2030-06-23 22:00 | 2030 Initial | 700 | 0 | 363.39 | 80.33 | 0 | 0 | No
2030-06-23 23:00 | 2030 Initial | 700 | 0 | 63.39 | 219.54 | 0 | 0 | No
2030-06-24 | 2030 Initial | 700 | 0 | 315.25 | 290.32 | 0 | 0 | No
2030-06-24 01:00 | 2030 Initial | 700 | 0 | 118.54 | 362.95 | 0 | 0 | No
2030-06-24 02:00 | 2030 Initial | 700 | 190.84 | 377.36 | 339.58 | 0 | 0 | No
2030-06-24 03:00 | 2030 Initial | 700 | 490.84 | 510 | 510 | 0 | 0 | No
2030-06-24 04:00 | 2030 Initial | 700 | 479.39 | 510 | 510 | 0 | 0 | No
2030-06-24 05:00 | 2030 Initial | 700 | 179.39 | 210 | 338.82 | 0 | 0 | No
2030-06-24 06:00 | 2030 Initial | 700 | 0 | 260.31 | 479.24 | 0 | 0 | No
2030-06-24 07:00 | 2030 Initial | 700 | 267.57 | 449.14 | 510 | 0 | 0 | No
2030-06-24 08:00 | 2030 Initial | 700 | 300 | 149.14 | 510 | 0 | 0 | No
2030-06-24 09:00 | 2030 Initial | 700 | 0 | -150.86 | 510 | 0 | 0 | No
2030-06-24 10:00 | 2030 Initial | 700 | -300 | -450.86 | 392.88 | 0 | 0 | No
2030-06-24 11:00 | 2030 Initial | 700 | -526 | -510 | 460.14 | 0 | 0 | No
2030-06-24 12:00 | 2030 Initial | 700 | -526 | -510 | 431.39 | 0 | 0 | No
2030-06-24 13:00 | 2030 Initial | 700 | -526 | -510 | 401.01 | 0 | 0 | No
2030-06-24 14:00 | 2030 Initial | 700 | -526 | -510 | 453.25 | 0 | 0 | No
2030-06-24 15:00 | 2030 Initial | 700 | -526 | -510 | 317.3 | 0 | 0 | No
2030-06-24 16:00 | 2030 Initial | 700 | -358.74 | -510 | 485.33 | 0 | 0 | No
2030-06-24 17:00 | 2030 Initial | 700 | -58.74 | -210 | 510 | 0 | 0 | No
2030-06-24 18:00 | 2030 Initial | 700 | 0 | 90 | 425.87 | 0 | 0 | No
2030-06-24 19:00 | 2030 Initial | 700 | 0 | 390 | 425.87 | 0 | 0 | No
2030-06-24 20:00 | 2030 Initial | 700 | 0 | 510 | 436.71 | 0 | 0 | No
2030-06-24 21:00 | 2030 Initial | 700 | 0 | 510 | 436.71 | 0 | 0 | No
2030-06-24 22:00 | 2030 Initial | 700 | 16.83 | 510 | 327 | 0 | 0 | No
2030-06-24 23:00 | 2030 Initial | 700 | 316.83 | 510 | 510 | 0 | 0 | No
2030-06-25 | 2030 Initial | 700 | 16.83 | 510 | 346.05 | 0 | 0 | No
2030-06-25 01:00 | 2030 Initial | 700 | 0 | 510 | 290.61 | 0 | 0 | No
2030-06-25 02:00 | 2030 Initial | 700 | 0 | 469.08 | 321.58 | 0 | 0 | No
2030-06-25 03:00 | 2030 Initial | 700 | 0 | 492.74 | 265 | 0 | 0 | No
2030-06-25 04:00 | 2030 Initial | 700 | 0 | 294.87 | 293.9 | 0 | 0 | No
2030-06-25 05:00 | 2030 Initial | 700 | 0 | 192.86 | 280.05 | 0 | 0 | No
2030-06-25 06:00 | 2030 Initial | 700 | 0 | -82.78 | 332.78 | 0 | 0 | No
2030-06-25 07:00 | 2030 Initial | 700 | -226 | -232.64 | 405.4 | 0 | 0 | No
2030-06-25 08:00 | 2030 Initial | 700 | -526 | -510 | 456.66 | 0 | 0 | No
2030-06-25 09:00 | 2030 Initial | 700 | -526 | -510 | 462.79 | 0 | 0 | No
2030-06-25 10:00 | 2030 Initial | 700 | -526 | -510 | 332.8 | 0 | 0 | No
2030-06-25 11:00 | 2030 Initial | 700 | -300 | -300 | 210 | 0 | 0 | No
2030-06-25 12:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-06-25 13:00 | 2030 Initial | 700 | 300 | 300 | 510 | 0 | 0 | No
2030-06-25 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-25 15:00 | 2030 Initial | 700 | 205 | 289.62 | 510 | 0 | 0 | No
2030-06-25 16:00 | 2030 Initial | 700 | -95 | -10.38 | 409.06 | 0 | 0 | No
2030-06-25 17:00 | 2030 Initial | 700 | 32.87 | 289.62 | 510 | 0 | 0 | No
2030-06-25 18:00 | 2030 Initial | 700 | 32.87 | 510 | 510 | 0 | 0 | No
2030-06-25 19:00 | 2030 Initial | 700 | 332.87 | 510 | 510 | 0 | 0 | No
2030-06-25 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-25 21:00 | 2030 Initial | 700 | 435.63 | 510 | 510 | 0 | 0 | No
2030-06-25 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-25 23:00 | 2030 Initial | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-06-26 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-06-26 01:00 | 2030 Initial | 700 | 0 | 510 | 332.36 | 0 | 0 | No
2030-06-26 02:00 | 2030 Initial | 700 | 0 | 432.3 | 271.99 | 0 | 0 | No
2030-06-26 03:00 | 2030 Initial | 700 | 0 | 510 | 290.43 | 0 | 0 | No
2030-06-26 04:00 | 2030 Initial | 700 | 0 | 269.18 | 102.72 | 0 | 0 | No
2030-06-26 05:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-26 06:00 | 2030 Initial | 700 | 0 | 0 | 65.1 | 0 | 0 | No
2030-06-26 07:00 | 2030 Initial | 700 | 0 | -58.22 | 302.65 | 0 | 0 | No
2030-06-26 08:00 | 2030 Initial | 518.95 | -300 | -358.22 | 333.35 | 0 | 0 | No
2030-06-26 09:00 | 2030 Initial | 428.14 | -526 | -510 | 280.73 | 0 | 0 | No
2030-06-26 10:00 | 2030 Initial | 8.14 | -526 | -510 | 156.52 | 0 | 0 | No
2030-06-26 11:00 | 2030 Initial | 0 | -226 | -243.22 | 456.52 | 0 | 0 | No
2030-06-26 12:00 | 2030 Initial | 0 | 0 | -367.91 | 510 | 0 | 0 | No
2030-06-26 13:00 | 2030 Initial | 280 | -211.41 | -300 | 354.35 | 0 | 0 | No
2030-06-26 14:00 | 2030 Initial | 700 | 88.59 | 0 | 510 | 0 | 0 | No
2030-06-26 15:00 | 2030 Initial | 700 | 300 | 127.24 | 510 | 0 | 0 | No
2030-06-26 16:00 | 2030 Initial | 280 | 0 | -172.76 | 210 | 0 | 0 | No
2030-06-26 17:00 | 2030 Initial | 487.5 | -300 | -472.76 | 424.41 | 0 | 0 | No
2030-06-26 18:00 | 2030 Initial | 700 | -36.99 | -510 | 360.68 | 0 | 0 | No
2030-06-26 19:00 | 2030 Initial | 700 | 0 | -264.97 | 473.13 | 0 | 0 | No
2030-06-26 20:00 | 2030 Initial | 700 | 0 | -333.92 | 429.13 | 0 | 0 | No
2030-06-26 21:00 | 2030 Initial | 700 | 0 | -33.92 | 294.05 | 0 | 0 | No
2030-06-26 22:00 | 2030 Initial | 700 | 0 | 0 | 272.49 | 0 | 0 | No
2030-06-26 23:00 | 2030 Initial | 700 | 0 | 0 | 81.96 | 0 | 0 | No
2030-06-27 | 2030 Initial | 402.57 | 205 | 210 | 354.3 | 0 | 0 | No
2030-06-27 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 05:00 | 2030 Initial | 700 | 289.47 | 210 | 481.61 | 0 | 0 | No
2030-06-27 06:00 | 2030 Initial | 700 | -10.53 | -90 | 181.61 | 0 | 0 | No
2030-06-27 07:00 | 2030 Initial | 700 | -91.86 | -90 | 135.96 | 0 | 0 | No
2030-06-27 08:00 | 2030 Initial | 700 | 175.91 | 210 | 210 | 0 | 0 | No
2030-06-27 09:00 | 2030 Initial | 700 | 475.91 | 510 | 510 | 0 | 0 | No
2030-06-27 10:00 | 2030 Initial | 651.47 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 11:00 | 2030 Initial | 231.47 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 12:00 | 2030 Initial | -188.53 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 13:00 | 2030 Initial | -608.53 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 16:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 17:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 18:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 19:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 20:00 | 2030 Initial | -700 | 505 | 510 | 473.08 | 0 | 0 | Yes
2030-06-27 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 02:00 | 2030 Initial | -700 | 505 | 510 | 456.63 | 0 | 0 | Yes
2030-06-28 03:00 | 2030 Initial | -700 | 505 | 510 | 436.63 | 0 | 0 | Yes
2030-06-28 04:00 | 2030 Initial | -700 | 505 | 510 | 192.51 | 0 | 0 | Yes
2030-06-28 05:00 | 2030 Initial | -700 | 505 | 510 | 160.33 | 0 | 0 | Yes
2030-06-28 06:00 | 2030 Initial | -700 | 505 | 510 | 249.64 | 0 | 0 | Yes
2030-06-28 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 13:00 | 2030 Initial | -700 | 505 | 510 | 438.79 | 0 | 0 | Yes
2030-06-28 14:00 | 2030 Initial | -700 | 505 | 510 | 420.51 | 0 | 0 | Yes
2030-06-28 15:00 | 2030 Initial | -700 | 505 | 510 | 343.51 | 0 | 0 | Yes
2030-06-28 16:00 | 2030 Initial | -700 | 505 | 510 | 389.16 | 0 | 0 | Yes
2030-06-28 17:00 | 2030 Initial | -700 | 505 | 510 | 414.34 | 0 | 0 | Yes
2030-06-28 18:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 19:00 | 2030 Initial | -700 | 505 | 510 | 424.36 | 0 | 0 | Yes
2030-06-28 20:00 | 2030 Initial | -700 | 505 | 510 | 465.55 | 0 | 0 | Yes
2030-06-28 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 23:00 | 2030 Initial | -700 | 505 | 510 | 489.31 | 0 | 0 | Yes
2030-06-29 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 16:00 | 2030 Initial | -678.16 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 17:00 | 2030 Initial | -258.16 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 18:00 | 2030 Initial | 161.84 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 19:00 | 2030 Initial | 581.84 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 21:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 10:00 | 2030 Initial | 700 | 205 | 381.34 | 510 | 0 | 0 | No
2030-06-30 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 13:00 | 2030 Initial | 700 | 254.32 | 210 | 510 | 0 | 0 | No
2030-06-30 14:00 | 2030 Initial | 700 | -45.68 | -90 | 510 | 0 | 0 | No
2030-06-30 15:00 | 2030 Initial | 700 | -122.84 | -206.54 | 510 | 0 | 0 | No
2030-06-30 16:00 | 2030 Initial | 700 | 0 | 93.46 | 510 | 0 | 0 | No
2030-06-30 17:00 | 2030 Initial | 700 | 0 | 393.46 | 510 | 0 | 0 | No
2030-06-30 18:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-06-30 19:00 | 2030 Initial | 700 | 84.92 | 510 | 510 | 0 | 0 | No
2030-06-30 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-06-30 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-06-30 22:00 | 2030 Initial | 700 | 3.64 | 510 | 510 | 0 | 0 | No
2030-06-30 23:00 | 2030 Initial | 700 | 52.39 | 510 | 510 | 0 | 0 | No
2030-07-01 | 2030 Initial | 700 | 0 | 510 | 210 | 0 | 0 | No
2030-07-01 01:00 | 2030 Initial | 700 | 0 | 439.37 | 140.22 | 0 | 0 | No
2030-07-01 02:00 | 2030 Initial | 700 | 0 | 510 | 130.86 | 0 | 0 | No
2030-07-01 03:00 | 2030 Initial | 700 | 0 | 469.95 | 110.16 | 0 | 0 | No
2030-07-01 04:00 | 2030 Initial | 700 | 0 | 216.44 | 15.71 | 0 | 0 | No
2030-07-01 05:00 | 2030 Initial | 700 | 0 | 103.1 | 0 | 0 | 0 | No
2030-07-01 06:00 | 2030 Initial | 700 | 0 | 163.01 | 4.49 | 0 | 0 | No
2030-07-01 07:00 | 2030 Initial | 700 | 0 | 463.01 | 158.9 | 0 | 0 | No
2030-07-01 08:00 | 2030 Initial | 700 | 0 | 245.52 | 252.27 | 0 | 0 | No
2030-07-01 09:00 | 2030 Initial | 700 | 0 | 0 | 304.54 | 0 | 0 | No
2030-07-01 10:00 | 2030 Initial | 700 | 0 | -60.26 | 259.74 | 0 | 0 | No
2030-07-01 11:00 | 2030 Initial | 700 | 0 | -170.24 | 295.38 | 0 | 0 | No
2030-07-01 12:00 | 2030 Initial | 700 | 0 | -371.13 | 245.2 | 0 | 0 | No
2030-07-01 13:00 | 2030 Initial | 700 | 0 | -161.72 | 184.86 | 0 | 0 | No
2030-07-01 14:00 | 2030 Initial | 700 | -224.87 | -461.72 | 168.43 | 0 | 0 | No
2030-07-01 15:00 | 2030 Initial | 700 | -8.66 | -510 | 144.86 | 0 | 0 | No
2030-07-01 16:00 | 2030 Initial | 700 | -36.33 | -510 | 120.09 | 0 | 0 | No
2030-07-01 17:00 | 2030 Initial | 700 | -184.47 | -300 | 143.75 | 0 | 0 | No
2030-07-01 18:00 | 2030 Initial | 700 | 0 | 0 | 197.79 | 0 | 0 | No
2030-07-01 19:00 | 2030 Initial | 700 | 0 | 260.21 | 185.18 | 0 | 0 | No
2030-07-01 20:00 | 2030 Initial | 700 | 0 | 260.21 | 159.09 | 0 | 0 | No
2030-07-01 21:00 | 2030 Initial | 700 | 0 | 344.27 | 146.54 | 0 | 0 | No
2030-07-01 22:00 | 2030 Initial | 700 | 0 | 396.09 | 218.98 | 0 | 0 | No
2030-07-01 23:00 | 2030 Initial | 700 | 0 | 190.41 | 172.47 | 0 | 0 | No
2030-07-02 | 2030 Initial | 700 | 0 | 140.86 | 171.74 | 0 | 0 | No
2030-07-02 01:00 | 2030 Initial | 700 | 0 | -159.14 | 111.19 | 0 | 0 | No
2030-07-02 02:00 | 2030 Initial | 700 | 0 | -459.14 | 95.21 | 0 | 0 | No
2030-07-02 03:00 | 2030 Initial | 700 | 0 | -510 | 85.87 | 0 | 0 | No
2030-07-02 04:00 | 2030 Initial | 700 | -16.59 | -510 | 72.71 | 0 | 0 | No
2030-07-02 05:00 | 2030 Initial | 700 | -112.09 | -510 | 41.06 | 0 | 0 | No
2030-07-02 06:00 | 2030 Initial | 700 | 0 | -269.29 | 68.65 | 0 | 0 | No
2030-07-02 07:00 | 2030 Initial | 700 | 0 | -203.55 | 143.32 | 0 | 0 | No
2030-07-02 08:00 | 2030 Initial | 505.2 | -110.94 | -503.55 | 154.99 | 0 | 0 | No
2030-07-02 09:00 | 2030 Initial | 85.2 | -410.94 | -510 | -0.29 | 0 | 0 | No
2030-07-02 10:00 | 2030 Initial | -334.8 | -526 | -510 | -174.84 | 0 | 0 | No
2030-07-02 11:00 | 2030 Initial | -350.7 | -526 | -510 | -125.96 | 0 | 0 | No
2030-07-02 12:00 | 2030 Initial | -408.33 | -526 | -510 | 94.81 | 0 | 0 | No
2030-07-02 13:00 | 2030 Initial | -140 | -526 | -510 | 16.9 | 0 | 0 | No
2030-07-02 14:00 | 2030 Initial | 280 | -526 | -510 | 64.19 | 0 | 0 | No
2030-07-02 15:00 | 2030 Initial | 700 | -526 | -510 | 84.74 | 0 | 0 | No
2030-07-02 16:00 | 2030 Initial | 280 | -300 | -222.08 | 215.67 | 0 | 0 | No
2030-07-02 17:00 | 2030 Initial | 700 | 0 | 77.92 | 510 | 0 | 0 | No
2030-07-02 18:00 | 2030 Initial | 700 | 291.83 | 377.92 | 510 | 0 | 0 | No
2030-07-02 19:00 | 2030 Initial | 700 | 0 | 407.29 | 331.85 | 0 | 0 | No
2030-07-02 20:00 | 2030 Initial | 700 | 99.94 | 510 | 510 | 0 | 0 | No
2030-07-02 21:00 | 2030 Initial | 700 | 111.28 | 210 | 510 | 0 | 0 | No
2030-07-02 22:00 | 2030 Initial | 700 | -14.13 | -90 | 438.51 | 0 | 0 | No
2030-07-02 23:00 | 2030 Initial | 280 | -314.13 | -390 | 138.51 | 0 | 0 | No
2030-07-03 | 2030 Initial | 242.74 | -526 | -510 | -28.53 | 0 | 0 | No
2030-07-03 01:00 | 2030 Initial | 662.74 | -526 | -510 | 36.2 | 0 | 0 | No
2030-07-03 02:00 | 2030 Initial | 242.74 | -226 | -300 | -136.31 | 0 | 0 | No
2030-07-03 03:00 | 2030 Initial | 166.82 | 0 | 0 | 0 | 0 | 0 | No
2030-07-03 04:00 | 2030 Initial | 0 | 0 | 22.57 | 0 | 0 | 0 | No
2030-07-03 05:00 | 2030 Initial | 0 | 0 | 312.89 | 0 | 0 | 0 | No
2030-07-03 06:00 | 2030 Initial | 0 | 0 | 293.95 | 0 | 0 | 0 | No
2030-07-03 07:00 | 2030 Initial | 0 | 0 | 492.91 | 210 | 0 | 0 | No
2030-07-03 08:00 | 2030 Initial | 0 | 233.16 | 510 | 510 | 0 | 0 | No
2030-07-03 09:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 10:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 11:00 | 2030 Initial | 270.17 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 12:00 | 2030 Initial | -149.83 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 13:00 | 2030 Initial | -26.86 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 14:00 | 2030 Initial | 393.14 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 16:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 17:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 18:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 21:00 | 2030 Initial | 280 | 205 | 210 | 510 | 0 | 0 | No
2030-07-03 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 06:00 | 2030 Initial | 700 | 205 | 210 | 499.24 | 0 | 0 | No
2030-07-04 07:00 | 2030 Initial | 700 | 0 | -68.05 | 510 | 0 | 0 | No
2030-07-04 08:00 | 2030 Initial | 700 | 0 | -59.58 | 510 | 0 | 0 | No
2030-07-04 09:00 | 2030 Initial | 700 | 2.2 | 210 | 510 | 0 | 0 | No
2030-07-04 10:00 | 2030 Initial | 700 | 302.2 | 510 | 510 | 0 | 0 | No
2030-07-04 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 14:00 | 2030 Initial | 700 | 226.19 | 210 | 510 | 0 | 0 | No
2030-07-04 15:00 | 2030 Initial | 700 | -73.81 | -90 | 510 | 0 | 0 | No
2030-07-04 16:00 | 2030 Initial | 700 | -373.81 | -390 | 508.83 | 0 | 0 | No
2030-07-04 17:00 | 2030 Initial | 700 | -526 | -510 | 485.85 | 0 | 0 | No
2030-07-04 18:00 | 2030 Initial | 700 | -526 | -510 | 185.85 | 0 | 0 | No
2030-07-04 19:00 | 2030 Initial | 560 | -526 | -510 | -114.15 | 0 | 0 | No
2030-07-04 20:00 | 2030 Initial | 140 | -226 | -241.52 | -205.34 | 0 | 0 | No
2030-07-04 21:00 | 2030 Initial | -280 | 74 | 58.48 | 94.66 | 0 | 0 | No
2030-07-04 22:00 | 2030 Initial | -700 | 374 | 358.48 | 394.66 | 0 | 0 | Yes
2030-07-04 23:00 | 2030 Initial | -700 | 505 | 510 | 201.05 | 0 | 0 | Yes
2030-07-05 | 2030 Initial | -700 | 505 | 510 | 56.54 | 0 | 0 | Yes
2030-07-05 01:00 | 2030 Initial | -700 | 505 | 510 | 84.64 | 0 | 0 | Yes
2030-07-05 02:00 | 2030 Initial | -700 | 505 | 510 | -10.63 | 0 | 0 | Yes
2030-07-05 03:00 | 2030 Initial | -700 | 505 | 510 | 227.16 | 0 | 0 | Yes
2030-07-05 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 05:00 | 2030 Initial | -700 | 505 | 510 | 272.46 | 0 | 0 | Yes
2030-07-05 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 10:00 | 2030 Initial | -700 | 505 | 510 | 490.03 | 0 | 0 | Yes
2030-07-05 11:00 | 2030 Initial | -700 | 505 | 510 | 328.49 | 0 | 0 | Yes
2030-07-05 12:00 | 2030 Initial | -700 | 505 | 510 | 28.49 | 0 | 0 | Yes
2030-07-05 13:00 | 2030 Initial | -700 | 505 | 510 | 55.16 | 0 | 0 | Yes
2030-07-05 14:00 | 2030 Initial | -700 | 505 | 411.43 | 186.39 | 0 | 0 | Yes
2030-07-05 15:00 | 2030 Initial | -700 | 505 | 394.13 | 116.87 | 0 | 0 | Yes
2030-07-05 16:00 | 2030 Initial | -700 | 505 | 510 | 116.87 | 0 | 0 | Yes
2030-07-05 17:00 | 2030 Initial | -700 | 505 | 510 | 275.25 | 0 | 0 | Yes
2030-07-05 18:00 | 2030 Initial | -700 | 505 | 510 | 203.14 | 0 | 0 | Yes
2030-07-05 19:00 | 2030 Initial | -700 | 505 | 510 | 282.25 | 0 | 0 | Yes
2030-07-05 20:00 | 2030 Initial | -700 | 505 | 510 | 446.95 | 0 | 0 | Yes
2030-07-05 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 22:00 | 2030 Initial | -700 | 505 | 510 | 363.65 | 0 | 0 | Yes
2030-07-05 23:00 | 2030 Initial | -700 | 505 | 510 | 499.44 | 0 | 0 | Yes
2030-07-06 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 02:00 | 2030 Initial | -700 | 505 | 510 | 343.62 | 0 | 0 | Yes
2030-07-06 03:00 | 2030 Initial | -700 | 505 | 510 | 296.63 | 0 | 0 | Yes
2030-07-06 04:00 | 2030 Initial | -584.35 | 505 | 510 | 135.19 | 0 | 0 | Yes
2030-07-06 05:00 | 2030 Initial | -309.09 | 505 | 510 | 180.3 | 0 | 0 | Yes
2030-07-06 06:00 | 2030 Initial | -592.31 | 505 | 510 | 331.15 | 0 | 0 | Yes
2030-07-06 07:00 | 2030 Initial | -491.87 | 505 | 510 | 497.69 | 0 | 0 | Yes
2030-07-06 08:00 | 2030 Initial | -700 | 505 | 510 | 378.58 | 0 | 0 | Yes
2030-07-06 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 11:00 | 2030 Initial | -700 | 505 | 510 | 477.39 | 0 | 0 | Yes
2030-07-06 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 13:00 | 2030 Initial | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-07-06 14:00 | 2030 Initial | -280 | 74 | 90 | 510 | 0 | 0 | Yes
2030-07-06 15:00 | 2030 Initial | 140 | -226 | -210 | 374.62 | 0 | 0 | No
2030-07-06 16:00 | 2030 Initial | 560 | -526 | -510 | 192.45 | 0 | 0 | No
2030-07-06 17:00 | 2030 Initial | 700 | -526 | -510 | 58.21 | 0 | 0 | No
2030-07-06 18:00 | 2030 Initial | 700 | -280.1 | -510 | 74.31 | 0 | 0 | No
2030-07-06 19:00 | 2030 Initial | 700 | 0 | -257.09 | 366.89 | 0 | 0 | No
2030-07-06 20:00 | 2030 Initial | 700 | 0 | 42.91 | 395.22 | 0 | 0 | No
2030-07-06 21:00 | 2030 Initial | 700 | 0 | 215.99 | 310.33 | 0 | 0 | No
2030-07-06 22:00 | 2030 Initial | 700 | 0 | 0 | 10.33 | 0 | 0 | No
2030-07-06 23:00 | 2030 Initial | 700 | 0 | 43.15 | 309.99 | 0 | 0 | No
2030-07-07 | 2030 Initial | 700 | 205 | 312.19 | 349.22 | 0 | 0 | No
2030-07-07 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-07 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-07 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-07 04:00 | 2030 Initial | 700 | 410.17 | 390 | 510 | 0 | 0 | No
2030-07-07 05:00 | 2030 Initial | 700 | 110.17 | 90 | 210 | 0 | 0 | No
2030-07-07 06:00 | 2030 Initial | 700 | -36.7 | -210 | -16.59 | 0 | 0 | No
2030-07-07 07:00 | 2030 Initial | 700 | -336.7 | -510 | -127.45 | 0 | 0 | No
2030-07-07 08:00 | 2030 Initial | 700 | -526 | -510 | -80.33 | 0 | 0 | No
2030-07-07 09:00 | 2030 Initial | 700 | -526 | -510 | 187.31 | 0 | 0 | No
2030-07-07 10:00 | 2030 Initial | 700 | -526 | -510 | 266.15 | 0 | 0 | No
2030-07-07 11:00 | 2030 Initial | 700 | -526 | -510 | 369.21 | 0 | 0 | No
2030-07-07 12:00 | 2030 Initial | 700 | -526 | -510 | 450.04 | 0 | 0 | No
2030-07-07 13:00 | 2030 Initial | 700 | -526 | -510 | 485.19 | 0 | 0 | No
2030-07-07 14:00 | 2030 Initial | 700 | -526 | -510 | 395.36 | 0 | 0 | No
2030-07-07 15:00 | 2030 Initial | 700 | -526 | -510 | 374.4 | 0 | 0 | No
2030-07-07 16:00 | 2030 Initial | 700 | -526 | -510 | 374.19 | 0 | 0 | No
2030-07-07 17:00 | 2030 Initial | 700 | -226 | -423.55 | 187.63 | 0 | 0 | No
2030-07-07 18:00 | 2030 Initial | 700 | 0 | -126.09 | 96.01 | 0 | 0 | No
2030-07-07 19:00 | 2030 Initial | 700 | 0 | 0 | 165.28 | 0 | 0 | No
2030-07-07 20:00 | 2030 Initial | 700 | 0 | 8.01 | 61.17 | 0 | 0 | No
2030-07-07 21:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-07 22:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-07 23:00 | 2030 Initial | 700 | 0 | 39.62 | 0 | 0 | 0 | No
2030-07-08 | 2030 Initial | 700 | 0 | 339.62 | 32.41 | 0 | 0 | No
2030-07-08 01:00 | 2030 Initial | 700 | 0 | 362.54 | 19.72 | 0 | 0 | No
2030-07-08 02:00 | 2030 Initial | 700 | 0 | 287.1 | 15.61 | 0 | 0 | No
2030-07-08 03:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-07-08 04:00 | 2030 Initial | 700 | 0 | 275.84 | 5.26 | 0 | 0 | No
2030-07-08 05:00 | 2030 Initial | 700 | 0 | 203.19 | 0 | 0 | 0 | No
2030-07-08 06:00 | 2030 Initial | 700 | 0 | 364.63 | 14.97 | 0 | 0 | No
2030-07-08 07:00 | 2030 Initial | 700 | 0 | 143.97 | 131.93 | 0 | 0 | No
2030-07-08 08:00 | 2030 Initial | 700 | 0 | 0 | 165.93 | 0 | 0 | No
2030-07-08 09:00 | 2030 Initial | 700 | 0 | -170.81 | 188.7 | 0 | 0 | No
2030-07-08 10:00 | 2030 Initial | 700 | 0 | -217.65 | 184.9 | 0 | 0 | No
2030-07-08 11:00 | 2030 Initial | 700 | 0 | -225.74 | 207.37 | 0 | 0 | No
2030-07-08 12:00 | 2030 Initial | 700 | -50.93 | -510 | 236.08 | 0 | 0 | No
2030-07-08 13:00 | 2030 Initial | 700 | -214.16 | -510 | 215.21 | 0 | 0 | No
2030-07-08 14:00 | 2030 Initial | 700 | -237.93 | -510 | 232.82 | 0 | 0 | No
2030-07-08 15:00 | 2030 Initial | 700 | -459.03 | -510 | 250.33 | 0 | 0 | No
2030-07-08 16:00 | 2030 Initial | 700 | -159.03 | -210 | 306.55 | 0 | 0 | No
2030-07-08 17:00 | 2030 Initial | 700 | 0 | -1.25 | 391.54 | 0 | 0 | No
2030-07-08 18:00 | 2030 Initial | 700 | 0 | 175.05 | 318.23 | 0 | 0 | No
2030-07-08 19:00 | 2030 Initial | 700 | 0 | 282.28 | 264.36 | 0 | 0 | No
2030-07-08 20:00 | 2030 Initial | 700 | 0 | 0 | 85.33 | 0 | 0 | No
2030-07-08 21:00 | 2030 Initial | 700 | 0 | 300 | 0 | 0 | 0 | No
2030-07-08 22:00 | 2030 Initial | 700 | 0 | 0 | 12.26 | 0 | 0 | No
2030-07-08 23:00 | 2030 Initial | 700 | 0 | 273.36 | 0 | 0 | 0 | No
2030-07-09 | 2030 Initial | 700 | 0 | 210 | 210 | 0 | 0 | No
2030-07-09 01:00 | 2030 Initial | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-07-09 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-09 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-09 04:00 | 2030 Initial | 700 | 460.03 | 390 | 510 | 0 | 0 | No
2030-07-09 05:00 | 2030 Initial | 280 | 160.03 | 90 | 245.79 | 0 | 0 | No
2030-07-09 06:00 | 2030 Initial | 280 | -139.97 | -210 | 300.12 | 0 | 0 | No
2030-07-09 07:00 | 2030 Initial | 585.83 | -439.97 | -510 | 415.55 | 0 | 0 | No
2030-07-09 08:00 | 2030 Initial | 700 | -526 | -510 | 441.85 | 0 | 0 | No
2030-07-09 09:00 | 2030 Initial | 700 | -526 | -510 | 351.41 | 0 | 0 | No
2030-07-09 10:00 | 2030 Initial | 700 | -526 | -510 | 65.85 | 0 | 0 | No
2030-07-09 11:00 | 2030 Initial | 700 | -526 | -510 | -188.61 | 0 | 0 | No
2030-07-09 12:00 | 2030 Initial | 700 | -526 | -510 | -320.08 | 0 | 0 | No
2030-07-09 13:00 | 2030 Initial | 700 | -526 | -510 | -237.37 | 0 | 0 | No
2030-07-09 14:00 | 2030 Initial | 700 | -526 | -510 | -244.6 | 0 | 0 | No
2030-07-09 15:00 | 2030 Initial | 700 | -526 | -510 | -135.71 | 0 | 0 | No
2030-07-09 16:00 | 2030 Initial | 700 | -526 | -510 | -239.58 | 0 | 0 | No
2030-07-09 17:00 | 2030 Initial | 700 | -526 | -510 | -116.07 | 0 | 0 | No
2030-07-09 18:00 | 2030 Initial | 700 | -526 | -510 | -97.48 | 0 | 0 | No
2030-07-09 19:00 | 2030 Initial | 700 | -226 | -510 | 202.52 | 0 | 0 | No
2030-07-09 20:00 | 2030 Initial | 700 | -105.92 | -510 | 343.67 | 0 | 0 | No
2030-07-09 21:00 | 2030 Initial | 700 | 0 | -510 | 375.98 | 0 | 0 | No
2030-07-09 22:00 | 2030 Initial | 700 | 0 | -510 | 390.08 | 0 | 0 | No
2030-07-09 23:00 | 2030 Initial | 700 | 0 | -510 | 361.14 | 0 | 0 | No
2030-07-10 | 2030 Initial | 700 | -53.08 | -510 | 252.35 | 0 | 0 | No
2030-07-10 01:00 | 2030 Initial | 700 | 0 | -510 | 348.24 | 0 | 0 | No
2030-07-10 02:00 | 2030 Initial | 700 | 0 | -362.19 | 311.8 | 0 | 0 | No
2030-07-10 03:00 | 2030 Initial | 700 | 0 | -454.32 | 338.08 | 0 | 0 | No
2030-07-10 04:00 | 2030 Initial | 700 | 0 | -475.09 | 65.9 | 0 | 0 | No
2030-07-10 05:00 | 2030 Initial | 700 | 0 | -435.33 | 253.08 | 0 | 0 | No
2030-07-10 06:00 | 2030 Initial | 700 | -144.43 | -223.62 | 355.8 | 0 | 0 | No
2030-07-10 07:00 | 2030 Initial | 700 | -444.43 | -510 | 345.64 | 0 | 0 | No
2030-07-10 08:00 | 2030 Initial | 700 | -526 | -510 | 300.1 | 0 | 0 | No
2030-07-10 09:00 | 2030 Initial | 700 | -526 | -510 | 55.28 | 0 | 0 | No
2030-07-10 10:00 | 2030 Initial | 280 | -526 | -510 | 42.5 | 0 | 0 | No
2030-07-10 11:00 | 2030 Initial | -140 | -526 | -510 | -256.73 | 0 | 0 | No
2030-07-10 12:00 | 2030 Initial | -560 | -526 | -510 | -169.57 | 0 | 0 | No
2030-07-10 13:00 | 2030 Initial | -140 | -526 | -510 | -155.72 | 0 | 0 | No
2030-07-10 14:00 | 2030 Initial | 280 | -526 | -510 | -354.86 | 0 | 0 | No
2030-07-10 15:00 | 2030 Initial | 700 | -526 | -510 | -463.02 | 0 | 0 | No
2030-07-10 16:00 | 2030 Initial | 700 | -526 | -510 | -492.11 | 0 | 0 | No
2030-07-10 17:00 | 2030 Initial | 700 | -526 | -510 | -192.11 | 0 | 0 | No
2030-07-10 18:00 | 2030 Initial | 700 | -226 | -210 | 0 | 0 | 0 | No
2030-07-10 19:00 | 2030 Initial | 700 | 0 | 0 | 100.98 | 0 | 0 | No
2030-07-10 20:00 | 2030 Initial | 700 | 0 | 210 | 142 | 0 | 0 | No
2030-07-10 21:00 | 2030 Initial | 700 | 0 | 510 | 441.17 | 0 | 0 | No
2030-07-10 22:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-10 23:00 | 2030 Initial | 700 | 0 | 510 | 353.56 | 0 | 0 | No
2030-07-11 | 2030 Initial | 700 | 0 | 510 | 150.72 | 0 | 0 | No
2030-07-11 01:00 | 2030 Initial | 700 | 0 | 510 | 109 | 0 | 0 | No
2030-07-11 02:00 | 2030 Initial | 700 | 0 | 510 | 34.13 | 0 | 0 | No
2030-07-11 03:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-07-11 04:00 | 2030 Initial | 700 | 0 | 510 | 4.65 | 0 | 0 | No
2030-07-11 05:00 | 2030 Initial | 700 | 0 | 390 | 41.25 | 0 | 0 | No
2030-07-11 06:00 | 2030 Initial | 700 | 0 | 90 | 0 | 0 | 0 | No
2030-07-11 07:00 | 2030 Initial | 700 | -213 | -210 | 0 | 0 | 0 | No
2030-07-11 08:00 | 2030 Initial | 700 | -513 | -510 | 32.91 | 0 | 0 | No
2030-07-11 09:00 | 2030 Initial | 700 | -526 | -510 | 22.73 | 0 | 0 | No
2030-07-11 10:00 | 2030 Initial | 700 | -526 | -510 | -17.62 | 0 | 0 | No
2030-07-11 11:00 | 2030 Initial | 700 | -526 | -510 | 10.02 | 0 | 0 | No
2030-07-11 12:00 | 2030 Initial | 700 | -526 | -510 | 113.45 | 0 | 0 | No
2030-07-11 13:00 | 2030 Initial | 700 | -526 | -510 | 86.37 | 0 | 0 | No
2030-07-11 14:00 | 2030 Initial | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-11 15:00 | 2030 Initial | 700 | -526 | -510 | 152.58 | 0 | 0 | No
2030-07-11 16:00 | 2030 Initial | 700 | -526 | -510 | 175.64 | 0 | 0 | No
2030-07-11 17:00 | 2030 Initial | 700 | -226 | -210 | 262.4 | 0 | 0 | No
2030-07-11 18:00 | 2030 Initial | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-07-11 19:00 | 2030 Initial | 700 | 0 | 390 | 406.46 | 0 | 0 | No
2030-07-11 20:00 | 2030 Initial | 700 | 0 | 428.6 | 112.5 | 0 | 0 | No
2030-07-11 21:00 | 2030 Initial | 700 | 0 | 510 | 399.56 | 0 | 0 | No
2030-07-11 22:00 | 2030 Initial | 700 | 0 | 510 | 246.14 | 0 | 0 | No
2030-07-11 23:00 | 2030 Initial | 700 | 0 | 510 | 156.72 | 0 | 0 | No
2030-07-12 | 2030 Initial | 700 | 0 | 464.11 | 27.33 | 0 | 0 | No
2030-07-12 01:00 | 2030 Initial | 700 | 0 | 164.11 | 259.9 | 0 | 0 | No
2030-07-12 02:00 | 2030 Initial | 700 | 0 | -135.89 | 33.42 | 0 | 0 | No
2030-07-12 03:00 | 2030 Initial | 700 | 0 | -273.95 | 25.78 | 0 | 0 | No
2030-07-12 04:00 | 2030 Initial | 700 | 0 | -510 | 10.49 | 0 | 0 | No
2030-07-12 05:00 | 2030 Initial | 700 | -247.2 | -510 | -26.45 | 0 | 0 | No
2030-07-12 06:00 | 2030 Initial | 700 | -233.69 | -510 | -17.98 | 0 | 0 | No
2030-07-12 07:00 | 2030 Initial | 700 | -526 | -510 | -13.86 | 0 | 0 | No
2030-07-12 08:00 | 2030 Initial | 700 | -526 | -510 | -85.79 | 0 | 0 | No
2030-07-12 09:00 | 2030 Initial | 700 | -526 | -510 | 24.05 | 0 | 0 | No
2030-07-12 10:00 | 2030 Initial | 700 | -526 | -510 | -124.36 | 0 | 0 | No
2030-07-12 11:00 | 2030 Initial | 700 | -526 | -510 | -190.42 | 0 | 0 | No
2030-07-12 12:00 | 2030 Initial | 700 | -526 | -510 | -145.06 | 0 | 0 | No
2030-07-12 13:00 | 2030 Initial | 700 | -526 | -510 | -350.14 | 0 | 0 | No
2030-07-12 14:00 | 2030 Initial | 700 | -526 | -510 | -313.1 | 0 | 0 | No
2030-07-12 15:00 | 2030 Initial | 700 | -526 | -510 | -368.75 | 0 | 0 | No
2030-07-12 16:00 | 2030 Initial | 700 | -526 | -510 | -302.39 | 0 | 0 | No
2030-07-12 17:00 | 2030 Initial | 700 | -526 | -510 | -160.67 | 0 | 0 | No
2030-07-12 18:00 | 2030 Initial | 700 | -518.68 | -510 | 27.09 | 0 | 0 | No
2030-07-12 19:00 | 2030 Initial | 700 | -300 | -510 | 69.03 | 0 | 0 | No
2030-07-12 20:00 | 2030 Initial | 700 | 0 | -510 | -66 | 0 | 0 | No
2030-07-12 21:00 | 2030 Initial | 700 | -162.09 | -510 | 3.67 | 0 | 0 | No
2030-07-12 22:00 | 2030 Initial | 700 | -340.01 | -510 | -1.61 | 0 | 0 | No
2030-07-12 23:00 | 2030 Initial | 700 | -300 | -324.37 | -69.87 | 0 | 0 | No
2030-07-13 | 2030 Initial | 368.77 | 0 | -24.37 | 199.1 | 0 | 0 | No
2030-07-13 01:00 | 2030 Initial | 700 | 300 | 275.63 | 499.1 | 0 | 0 | No
2030-07-13 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-13 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-13 04:00 | 2030 Initial | 700 | 300 | 371.59 | 510 | 0 | 0 | No
2030-07-13 05:00 | 2030 Initial | 700 | 0 | 71.59 | 210 | 0 | 0 | No
2030-07-13 06:00 | 2030 Initial | 700 | -190.65 | -228.41 | -71.52 | 0 | 0 | No
2030-07-13 07:00 | 2030 Initial | 700 | -52.56 | -510 | -344.65 | 0 | 0 | No
2030-07-13 08:00 | 2030 Initial | 700 | -352.56 | -510 | -381.07 | 0 | 0 | No
2030-07-13 09:00 | 2030 Initial | 700 | -300 | -510 | -81.07 | 0 | 0 | No
2030-07-13 10:00 | 2030 Initial | 700 | 0 | -210 | 218.93 | 0 | 0 | No
2030-07-13 11:00 | 2030 Initial | 700 | 228.78 | 90 | 510 | 0 | 0 | No
2030-07-13 12:00 | 2030 Initial | 700 | 205 | 390 | 510 | 0 | 0 | No
2030-07-13 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-13 14:00 | 2030 Initial | 700 | 205 | 224.96 | 510 | 0 | 0 | No
2030-07-13 15:00 | 2030 Initial | 700 | 0 | -75.04 | 243.58 | 0 | 0 | No
2030-07-13 16:00 | 2030 Initial | 700 | -300 | -375.04 | -56.42 | 0 | 0 | No
2030-07-13 17:00 | 2030 Initial | 700 | -335.77 | -510 | 0 | 0 | 0 | No
2030-07-13 18:00 | 2030 Initial | 700 | -35.77 | -485.34 | 43.58 | 0 | 0 | No
2030-07-13 19:00 | 2030 Initial | 700 | 0 | -394.77 | 170.9 | 0 | 0 | No
2030-07-13 20:00 | 2030 Initial | 700 | 0 | -298.75 | 114.63 | 0 | 0 | No
2030-07-13 21:00 | 2030 Initial | 700 | 0 | -186.44 | 201.99 | 0 | 0 | No
2030-07-13 22:00 | 2030 Initial | 700 | 0 | -49 | 52.77 | 0 | 0 | No
2030-07-13 23:00 | 2030 Initial | 700 | 0 | -214.76 | 142.59 | 0 | 0 | No
2030-07-14 | 2030 Initial | 700 | 0 | 0 | 315.17 | 0 | 0 | No
2030-07-14 01:00 | 2030 Initial | 700 | 0 | 116.5 | 288.86 | 0 | 0 | No
2030-07-14 02:00 | 2030 Initial | 700 | 300 | 416.5 | 510 | 0 | 0 | No
2030-07-14 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-14 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-14 05:00 | 2030 Initial | 700 | 442.97 | 390 | 510 | 0 | 0 | No
2030-07-14 06:00 | 2030 Initial | 700 | 142.97 | 90 | 210 | 0 | 0 | No
2030-07-14 07:00 | 2030 Initial | 700 | -145.78 | -210 | 278.02 | 0 | 0 | No
2030-07-14 08:00 | 2030 Initial | 700 | -445.78 | -510 | -21.98 | 0 | 0 | No
2030-07-14 09:00 | 2030 Initial | 700 | -526 | -510 | 20.06 | 0 | 0 | No
2030-07-14 10:00 | 2030 Initial | 700 | -526 | -510 | 125.5 | 0 | 0 | No
2030-07-14 11:00 | 2030 Initial | 700 | -526 | -510 | 289.76 | 0 | 0 | No
2030-07-14 12:00 | 2030 Initial | 700 | -526 | -510 | 289.76 | 0 | 0 | No
2030-07-14 13:00 | 2030 Initial | 700 | -526 | -510 | 18.67 | 0 | 0 | No
2030-07-14 14:00 | 2030 Initial | 700 | -526 | -510 | 130.72 | 0 | 0 | No
2030-07-14 15:00 | 2030 Initial | 700 | -526 | -510 | 187.56 | 0 | 0 | No
2030-07-14 16:00 | 2030 Initial | 700 | -526 | -510 | 183.73 | 0 | 0 | No
2030-07-14 17:00 | 2030 Initial | 700 | -526 | -510 | 211.43 | 0 | 0 | No
2030-07-14 18:00 | 2030 Initial | 280 | -526 | -510 | 217.93 | 0 | 0 | No
2030-07-14 19:00 | 2030 Initial | 700 | -526 | -510 | 50.81 | 0 | 0 | No
2030-07-14 20:00 | 2030 Initial | 532.66 | -526 | -510 | 50.81 | 0 | 0 | No
2030-07-14 21:00 | 2030 Initial | 360.46 | -526 | -510 | 129.56 | 0 | 0 | No
2030-07-14 22:00 | 2030 Initial | 339.84 | -526 | -510 | 72.02 | 0 | 0 | No
2030-07-14 23:00 | 2030 Initial | 0 | -526 | -510 | 73.81 | 0 | 0 | No
2030-07-15 | 2030 Initial | 375.35 | -526 | -510 | 39.71 | 0 | 0 | No
2030-07-15 01:00 | 2030 Initial | 41.6 | -526 | -510 | 163.63 | 0 | 0 | No
2030-07-15 02:00 | 2030 Initial | 84.01 | -526 | -510 | 67.3 | 0 | 0 | No
2030-07-15 03:00 | 2030 Initial | 194.59 | -526 | -510 | 60.09 | 0 | 0 | No
2030-07-15 04:00 | 2030 Initial | 614.59 | -526 | -510 | -57.06 | 0 | 0 | No
2030-07-15 05:00 | 2030 Initial | 700 | -526 | -510 | 108.21 | 0 | 0 | No
2030-07-15 06:00 | 2030 Initial | 700 | -526 | -510 | -48.85 | 0 | 0 | No
2030-07-15 07:00 | 2030 Initial | 560 | -526 | -510 | 64.77 | 0 | 0 | No
2030-07-15 08:00 | 2030 Initial | 140 | -526 | -510 | -13.63 | 0 | 0 | No
2030-07-15 09:00 | 2030 Initial | -280 | -526 | -510 | -80.76 | 0 | 0 | No
2030-07-15 10:00 | 2030 Initial | -700 | -526 | -510 | -191.85 | 0 | 0 | No
2030-07-15 11:00 | 2030 Initial | -700 | -526 | -510 | -119.05 | 0 | 0 | No
2030-07-15 12:00 | 2030 Initial | -700 | -526 | -510 | -154.24 | 0 | 0 | No
2030-07-15 13:00 | 2030 Initial | -442.71 | -526 | -510 | -334.93 | 0 | 0 | No
2030-07-15 14:00 | 2030 Initial | -22.71 | -526 | -510 | -173.74 | 0 | 0 | No
2030-07-15 15:00 | 2030 Initial | 0 | -526 | -510 | 10.62 | 0 | 0 | No
2030-07-15 16:00 | 2030 Initial | -420 | -526 | -510 | -47.02 | 0 | 0 | No
2030-07-15 17:00 | 2030 Initial | -167.65 | -526 | -510 | 32.88 | 0 | 0 | No
2030-07-15 18:00 | 2030 Initial | 252.35 | -460.09 | -510 | -111.37 | 0 | 0 | No
2030-07-15 19:00 | 2030 Initial | 672.35 | -330.4 | -510 | -83.39 | 0 | 0 | No
2030-07-15 20:00 | 2030 Initial | 700 | -272.28 | -510 | 149.62 | 0 | 0 | No
2030-07-15 21:00 | 2030 Initial | 700 | -137.86 | -510 | 111.05 | 0 | 0 | No
2030-07-15 22:00 | 2030 Initial | 700 | -95.53 | -510 | 48.9 | 0 | 0 | No
2030-07-15 23:00 | 2030 Initial | 700 | -300 | -397.6 | 51.21 | 0 | 0 | No
2030-07-16 | 2030 Initial | 523.67 | 0 | -97.6 | 210 | 0 | 0 | No
2030-07-16 01:00 | 2030 Initial | 700 | 300 | 202.4 | 510 | 0 | 0 | No
2030-07-16 02:00 | 2030 Initial | 700 | 0 | 125.91 | 510 | 0 | 0 | No
2030-07-16 03:00 | 2030 Initial | 700 | 0 | 0 | 210 | 0 | 0 | No
2030-07-16 04:00 | 2030 Initial | 700 | 0 | 0 | 267.97 | 0 | 0 | No
2030-07-16 05:00 | 2030 Initial | 700 | 0 | 0 | 292.15 | 0 | 0 | No
2030-07-16 06:00 | 2030 Initial | 700 | 0 | -31.51 | 382.11 | 0 | 0 | No
2030-07-16 07:00 | 2030 Initial | 700 | 0 | -196.55 | 510 | 0 | 0 | No
2030-07-16 08:00 | 2030 Initial | 700 | 0 | -60.32 | 510 | 0 | 0 | No
2030-07-16 09:00 | 2030 Initial | 280 | 0 | -318.18 | 510 | 0 | 0 | No
2030-07-16 10:00 | 2030 Initial | -140 | 0 | -510 | 491.67 | 0 | 0 | No
2030-07-16 11:00 | 2030 Initial | -560 | -226 | -510 | 393.35 | 0 | 0 | No
2030-07-16 12:00 | 2030 Initial | -700 | -526 | -510 | 177.74 | 0 | 0 | No
2030-07-16 13:00 | 2030 Initial | -700 | -526 | -510 | 27.88 | 0 | 0 | No
2030-07-16 14:00 | 2030 Initial | -700 | -526 | -510 | -154.04 | 0 | 0 | No
2030-07-16 15:00 | 2030 Initial | -700 | -526 | -510 | -454.04 | 0 | 0 | No
2030-07-16 16:00 | 2030 Initial | -699.79 | -526 | -510 | -154.04 | 0 | 0 | No
2030-07-16 17:00 | 2030 Initial | -279.79 | -226 | -510 | 145.96 | 0 | 0 | No
2030-07-16 18:00 | 2030 Initial | 140.21 | 0 | -510 | 27.18 | 0 | 0 | No
2030-07-16 19:00 | 2030 Initial | 560.21 | 0 | -244.07 | 314.45 | 0 | 0 | No
2030-07-16 20:00 | 2030 Initial | 700 | 0 | -52.01 | 383.35 | 0 | 0 | No
2030-07-16 21:00 | 2030 Initial | 280 | 0 | 0 | 329.74 | 0 | 0 | No
2030-07-16 22:00 | 2030 Initial | 700 | 0 | -300 | 405.91 | 0 | 0 | No
2030-07-16 23:00 | 2030 Initial | 700 | 0 | -510 | 240.76 | 0 | 0 | No
2030-07-17 | 2030 Initial | 700 | 0 | -483.43 | 267.69 | 0 | 0 | No
2030-07-17 01:00 | 2030 Initial | 467.03 | 0 | -183.43 | 73.73 | 0 | 0 | No
2030-07-17 02:00 | 2030 Initial | 356.98 | 0 | 0 | 248 | 0 | 0 | No
2030-07-17 03:00 | 2030 Initial | 494.89 | 0 | 0 | 141.96 | 0 | 0 | No
2030-07-17 04:00 | 2030 Initial | 520.79 | 0 | -210 | 0 | 0 | 0 | No
2030-07-17 05:00 | 2030 Initial | 700 | -185.5 | -510 | 0 | 0 | 0 | No
2030-07-17 06:00 | 2030 Initial | 700 | -250.7 | -510 | -16.09 | 0 | 0 | No
2030-07-17 07:00 | 2030 Initial | 700 | -225.25 | -510 | 190.05 | 0 | 0 | No
2030-07-17 08:00 | 2030 Initial | 686.75 | -525.25 | -510 | 476.75 | 0 | 0 | No
2030-07-17 09:00 | 2030 Initial | 347.57 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 10:00 | 2030 Initial | 58.8 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 11:00 | 2030 Initial | -81.7 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 12:00 | 2030 Initial | -144.52 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 13:00 | 2030 Initial | 0 | -479.22 | -510 | 490.66 | 0 | 0 | No
2030-07-17 14:00 | 2030 Initial | 20.06 | -526 | -510 | 466.78 | 0 | 0 | No
2030-07-17 15:00 | 2030 Initial | 440.06 | -521.68 | -510 | 478 | 0 | 0 | No
2030-07-17 16:00 | 2030 Initial | 652.21 | -350.86 | -468.19 | 510 | 0 | 0 | No
2030-07-17 17:00 | 2030 Initial | 700 | -50.86 | -168.19 | 510 | 0 | 0 | No
2030-07-17 18:00 | 2030 Initial | 700 | 0 | 131.81 | 510 | 0 | 0 | No
2030-07-17 19:00 | 2030 Initial | 700 | 33.66 | 431.81 | 510 | 0 | 0 | No
2030-07-17 20:00 | 2030 Initial | 700 | 275.27 | 510 | 510 | 0 | 0 | No
2030-07-17 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-17 22:00 | 2030 Initial | 700 | 235.54 | 510 | 510 | 0 | 0 | No
2030-07-17 23:00 | 2030 Initial | 700 | 0 | 510 | 398.01 | 0 | 0 | No
2030-07-18 | 2030 Initial | 700 | 0 | 510 | 318.12 | 0 | 0 | No
2030-07-18 01:00 | 2030 Initial | 700 | 0 | 510 | 253.4 | 0 | 0 | No
2030-07-18 02:00 | 2030 Initial | 700 | 0 | 232.85 | 231.89 | 0 | 0 | No
2030-07-18 03:00 | 2030 Initial | 700 | 0 | 424.03 | 177.24 | 0 | 0 | No
2030-07-18 04:00 | 2030 Initial | 700 | 0 | 198.76 | 145.61 | 0 | 0 | No
2030-07-18 05:00 | 2030 Initial | 700 | 0 | 193.92 | 43.06 | 0 | 0 | No
2030-07-18 06:00 | 2030 Initial | 700 | 0 | 323.94 | 121.42 | 0 | 0 | No
2030-07-18 07:00 | 2030 Initial | 700 | 0 | 68.85 | 228.52 | 0 | 0 | No
2030-07-18 08:00 | 2030 Initial | 700 | 0 | 0 | 195.67 | 0 | 0 | No
2030-07-18 09:00 | 2030 Initial | 700 | -226 | -287.14 | 2.22 | 0 | 0 | No
2030-07-18 10:00 | 2030 Initial | 700 | -526 | -510 | 231.3 | 0 | 0 | No
2030-07-18 11:00 | 2030 Initial | 700 | -526 | -510 | 95.45 | 0 | 0 | No
2030-07-18 12:00 | 2030 Initial | 700 | -526 | -510 | -192.41 | 0 | 0 | No
2030-07-18 13:00 | 2030 Initial | 700 | -526 | -510 | -159.23 | 0 | 0 | No
2030-07-18 14:00 | 2030 Initial | 700 | -526 | -510 | -25.73 | 0 | 0 | No
2030-07-18 15:00 | 2030 Initial | 700 | -526 | -510 | -189.38 | 0 | 0 | No
2030-07-18 16:00 | 2030 Initial | 700 | -526 | -510 | 110.62 | 0 | 0 | No
2030-07-18 17:00 | 2030 Initial | 700 | -300 | -458.3 | 127.07 | 0 | 0 | No
2030-07-18 18:00 | 2030 Initial | 700 | 0 | -158.3 | 147.98 | 0 | 0 | No
2030-07-18 19:00 | 2030 Initial | 700 | 0 | 141.7 | 317.72 | 0 | 0 | No
2030-07-18 20:00 | 2030 Initial | 700 | 0 | 12.05 | 198.17 | 0 | 0 | No
2030-07-18 21:00 | 2030 Initial | 700 | 0 | 312.05 | 263.52 | 0 | 0 | No
2030-07-18 22:00 | 2030 Initial | 700 | 0 | 312.05 | 317.9 | 0 | 0 | No
2030-07-18 23:00 | 2030 Initial | 700 | 0 | 300 | 240.03 | 0 | 0 | No
2030-07-19 | 2030 Initial | 700 | 0 | 88.44 | 124.51 | 0 | 0 | No
2030-07-19 01:00 | 2030 Initial | 700 | 0 | 75.83 | 97.08 | 0 | 0 | No
2030-07-19 02:00 | 2030 Initial | 700 | 0 | 0 | 69.18 | 0 | 0 | No
2030-07-19 03:00 | 2030 Initial | 700 | 0 | 34 | 142.42 | 0 | 0 | No
2030-07-19 04:00 | 2030 Initial | 700 | 0 | 45.43 | 113.28 | 0 | 0 | No
2030-07-19 05:00 | 2030 Initial | 700 | 0 | -18.52 | 71.04 | 0 | 0 | No
2030-07-19 06:00 | 2030 Initial | 700 | 0 | -211.52 | 167.08 | 0 | 0 | No
2030-07-19 07:00 | 2030 Initial | 700 | -226 | -459.57 | 151.87 | 0 | 0 | No
2030-07-19 08:00 | 2030 Initial | 700 | -526 | -510 | -148.13 | 0 | 0 | No
2030-07-19 09:00 | 2030 Initial | 700 | -526 | -510 | -139.6 | 0 | 0 | No
2030-07-19 10:00 | 2030 Initial | 700 | -526 | -510 | 82.57 | 0 | 0 | No
2030-07-19 11:00 | 2030 Initial | 700 | -526 | -510 | -217.43 | 0 | 0 | No
2030-07-19 12:00 | 2030 Initial | 700 | -526 | -510 | -210 | 0 | 0 | No
2030-07-19 13:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-07-19 14:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-07-19 15:00 | 2030 Initial | 700 | -526 | -510 | -455.72 | 0 | 0 | No
2030-07-19 16:00 | 2030 Initial | 700 | -526 | -510 | -232.98 | 0 | 0 | No
2030-07-19 17:00 | 2030 Initial | 700 | -497.36 | -510 | -209.61 | 0 | 0 | No
2030-07-19 18:00 | 2030 Initial | 700 | -197.36 | -210 | 0 | 0 | 0 | No
2030-07-19 19:00 | 2030 Initial | 700 | 0 | 0 | 218.04 | 0 | 0 | No
2030-07-19 20:00 | 2030 Initial | 700 | 0 | 266.9 | 247.29 | 0 | 0 | No
2030-07-19 21:00 | 2030 Initial | 700 | 0 | 103.98 | 294.76 | 0 | 0 | No
2030-07-19 22:00 | 2030 Initial | 700 | 0 | 403.98 | 136.96 | 0 | 0 | No
2030-07-19 23:00 | 2030 Initial | 700 | 0 | 478.18 | 127.13 | 0 | 0 | No
2030-07-20 | 2030 Initial | 700 | 0 | 510 | 73.69 | 0 | 0 | No
2030-07-20 01:00 | 2030 Initial | 700 | 0 | 510 | 142.93 | 0 | 0 | No
2030-07-20 02:00 | 2030 Initial | 700 | 0 | 510 | 111.03 | 0 | 0 | No
2030-07-20 03:00 | 2030 Initial | 700 | 0 | 510 | 62.49 | 0 | 0 | No
2030-07-20 04:00 | 2030 Initial | 700 | 0 | 431.45 | 128.97 | 0 | 0 | No
2030-07-20 05:00 | 2030 Initial | 700 | 0 | 131.45 | 109.23 | 0 | 0 | No
2030-07-20 06:00 | 2030 Initial | 700 | 0 | -168.55 | 0 | 0 | 0 | No
2030-07-20 07:00 | 2030 Initial | 700 | -300 | -468.55 | 16.26 | 0 | 0 | No
2030-07-20 08:00 | 2030 Initial | 700 | -526 | -510 | -80.22 | 0 | 0 | No
2030-07-20 09:00 | 2030 Initial | 700 | -526 | -510 | -101.69 | 0 | 0 | No
2030-07-20 10:00 | 2030 Initial | 700 | -526 | -510 | -159.96 | 0 | 0 | No
2030-07-20 11:00 | 2030 Initial | 700 | -526 | -510 | -133.02 | 0 | 0 | No
2030-07-20 12:00 | 2030 Initial | 700 | -526 | -510 | -60 | 0 | 0 | No
2030-07-20 13:00 | 2030 Initial | 700 | -526 | -510 | -39.65 | 0 | 0 | No
2030-07-20 14:00 | 2030 Initial | 700 | -526 | -510 | -214.6 | 0 | 0 | No
2030-07-20 15:00 | 2030 Initial | 700 | -526 | -510 | -180.64 | 0 | 0 | No
2030-07-20 16:00 | 2030 Initial | 700 | -526 | -510 | -20.57 | 0 | 0 | No
2030-07-20 17:00 | 2030 Initial | 700 | -300 | -325.53 | 20.23 | 0 | 0 | No
2030-07-20 18:00 | 2030 Initial | 700 | 0 | -25.53 | 132.16 | 0 | 0 | No
2030-07-20 19:00 | 2030 Initial | 700 | 0 | 274.47 | 135.93 | 0 | 0 | No
2030-07-20 20:00 | 2030 Initial | 700 | 0 | 510 | 194.82 | 0 | 0 | No
2030-07-20 21:00 | 2030 Initial | 700 | 0 | 510 | 209.54 | 0 | 0 | No
2030-07-20 22:00 | 2030 Initial | 700 | 0 | 510 | 265.76 | 0 | 0 | No
2030-07-20 23:00 | 2030 Initial | 700 | 0 | 510 | 235.01 | 0 | 0 | No
2030-07-21 | 2030 Initial | 700 | 0 | 401.28 | 0 | 0 | 0 | No
2030-07-21 01:00 | 2030 Initial | 700 | 0 | 510 | 2.78 | 0 | 0 | No
2030-07-21 02:00 | 2030 Initial | 700 | 0 | 410.13 | 0 | 0 | 0 | No
2030-07-21 03:00 | 2030 Initial | 700 | 0 | 354.89 | 0 | 0 | 0 | No
2030-07-21 04:00 | 2030 Initial | 700 | 0 | 189.37 | 0 | 0 | 0 | No
2030-07-21 05:00 | 2030 Initial | 700 | 0 | 11.61 | 0 | 0 | 0 | No
2030-07-21 06:00 | 2030 Initial | 700 | 0 | -208.6 | 0 | 0 | 0 | No
2030-07-21 07:00 | 2030 Initial | 700 | -300 | -508.6 | -101.93 | 0 | 0 | No
2030-07-21 08:00 | 2030 Initial | 700 | -526 | -510 | 29.56 | 0 | 0 | No
2030-07-21 09:00 | 2030 Initial | 700 | -526 | -510 | 39.64 | 0 | 0 | No
2030-07-21 10:00 | 2030 Initial | 700 | -526 | -510 | 76.52 | 0 | 0 | No
2030-07-21 11:00 | 2030 Initial | 700 | -526 | -510 | 78.54 | 0 | 0 | No
2030-07-21 12:00 | 2030 Initial | 700 | -526 | -510 | 141.17 | 0 | 0 | No
2030-07-21 13:00 | 2030 Initial | 700 | -526 | -510 | 127.96 | 0 | 0 | No
2030-07-21 14:00 | 2030 Initial | 700 | -526 | -510 | 70.78 | 0 | 0 | No
2030-07-21 15:00 | 2030 Initial | 700 | -526 | -510 | 67.65 | 0 | 0 | No
2030-07-21 16:00 | 2030 Initial | 700 | -526 | -510 | 181.85 | 0 | 0 | No
2030-07-21 17:00 | 2030 Initial | 700 | -323.17 | -510 | 50.54 | 0 | 0 | No
2030-07-21 18:00 | 2030 Initial | 700 | -23.17 | -210 | 112.39 | 0 | 0 | No
2030-07-21 19:00 | 2030 Initial | 700 | 0 | 0 | 125.12 | 0 | 0 | No
2030-07-21 20:00 | 2030 Initial | 700 | 0 | 0 | 103.65 | 0 | 0 | No
2030-07-21 21:00 | 2030 Initial | 700 | 0 | 0 | 46.33 | 0 | 0 | No
2030-07-21 22:00 | 2030 Initial | 700 | 0 | 0 | 33.92 | 0 | 0 | No
2030-07-21 23:00 | 2030 Initial | 700 | 0 | -71.45 | 0 | 0 | 0 | No
2030-07-22 | 2030 Initial | 700 | 0 | -371.45 | -50.45 | 0 | 0 | No
2030-07-22 01:00 | 2030 Initial | 700 | -6.67 | -398.62 | 0 | 0 | 0 | No
2030-07-22 02:00 | 2030 Initial | 700 | -306.67 | -510 | -204.58 | 0 | 0 | No
2030-07-22 03:00 | 2030 Initial | 700 | -526 | -510 | -311.14 | 0 | 0 | No
2030-07-22 04:00 | 2030 Initial | 700 | -526 | -510 | -426.21 | 0 | 0 | No
2030-07-22 05:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-07-22 06:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-07-22 07:00 | 2030 Initial | 700 | -526 | -510 | -210 | 0 | 0 | No
2030-07-22 08:00 | 2030 Initial | 700 | -526 | -510 | -427.22 | 0 | 0 | No
2030-07-22 09:00 | 2030 Initial | 700 | -526 | -510 | -157.83 | 0 | 0 | No
2030-07-22 10:00 | 2030 Initial | 700 | -526 | -510 | 23.28 | 0 | 0 | No
2030-07-22 11:00 | 2030 Initial | 700 | -526 | -510 | 11.83 | 0 | 0 | No
2030-07-22 12:00 | 2030 Initial | 700 | -526 | -510 | -98.25 | 0 | 0 | No
2030-07-22 13:00 | 2030 Initial | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-22 14:00 | 2030 Initial | 700 | -526 | -510 | -129.97 | 0 | 0 | No
2030-07-22 15:00 | 2030 Initial | 700 | -526 | -510 | -20.58 | 0 | 0 | No
2030-07-22 16:00 | 2030 Initial | 700 | -526 | -510 | 220.63 | 0 | 0 | No
2030-07-22 17:00 | 2030 Initial | 700 | -226 | -510 | 312.1 | 0 | 0 | No
2030-07-22 18:00 | 2030 Initial | 700 | 0 | -412.19 | 318.55 | 0 | 0 | No
2030-07-22 19:00 | 2030 Initial | 700 | 0 | -112.19 | 283.94 | 0 | 0 | No
2030-07-22 20:00 | 2030 Initial | 700 | 0 | -108.59 | 156.94 | 0 | 0 | No
2030-07-22 21:00 | 2030 Initial | 700 | 0 | -408.59 | 212.51 | 0 | 0 | No
2030-07-22 22:00 | 2030 Initial | 700 | 0 | -249.17 | 0 | 0 | 0 | No
2030-07-22 23:00 | 2030 Initial | 700 | 0 | -108.86 | 0 | 0 | 0 | No
2030-07-23 | 2030 Initial | 700 | 0 | -220.19 | 0 | 0 | 0 | No
2030-07-23 01:00 | 2030 Initial | 700 | 0 | -301.81 | 0 | 0 | 0 | No
2030-07-23 02:00 | 2030 Initial | 700 | 0 | -190.74 | 0 | 0 | 0 | No
2030-07-23 03:00 | 2030 Initial | 700 | 0 | 26.22 | 0 | 0 | 0 | No
2030-07-23 04:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-23 05:00 | 2030 Initial | 700 | 0 | -16.04 | 0 | 0 | 0 | No
2030-07-23 06:00 | 2030 Initial | 700 | 0 | 231.47 | 157.49 | 0 | 0 | No
2030-07-23 07:00 | 2030 Initial | 700 | 0 | 296.28 | 293.41 | 0 | 0 | No
2030-07-23 08:00 | 2030 Initial | 700 | 6.32 | 372.74 | 510 | 0 | 0 | No
2030-07-23 09:00 | 2030 Initial | 700 | 0 | 72.74 | 333.79 | 0 | 0 | No
2030-07-23 10:00 | 2030 Initial | 700 | -300 | -227.26 | 279.19 | 0 | 0 | No
2030-07-23 11:00 | 2030 Initial | 547.52 | -526 | -510 | 282.45 | 0 | 0 | No
2030-07-23 12:00 | 2030 Initial | 290.72 | -526 | -510 | 312.01 | 0 | 0 | No
2030-07-23 13:00 | 2030 Initial | 280 | -526 | -510 | 291.88 | 0 | 0 | No
2030-07-23 14:00 | 2030 Initial | 700 | -526 | -510 | 261.93 | 0 | 0 | No
2030-07-23 15:00 | 2030 Initial | 700 | -520.15 | -510 | 147.8 | 0 | 0 | No
2030-07-23 16:00 | 2030 Initial | 700 | -300 | -385.41 | 262.55 | 0 | 0 | No
2030-07-23 17:00 | 2030 Initial | 700 | 0 | -85.41 | 510 | 0 | 0 | No
2030-07-23 18:00 | 2030 Initial | 700 | 300 | 214.59 | 510 | 0 | 0 | No
2030-07-23 19:00 | 2030 Initial | 700 | 492.74 | 510 | 510 | 0 | 0 | No
2030-07-23 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-23 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-23 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-23 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-24 | 2030 Initial | 700 | 208.32 | 510 | 510 | 0 | 0 | No
2030-07-24 01:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-24 02:00 | 2030 Initial | 700 | 6.55 | 510 | 510 | 0 | 0 | No
2030-07-24 03:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-24 04:00 | 2030 Initial | 700 | 0 | 510 | 479.81 | 0 | 0 | No
2030-07-24 05:00 | 2030 Initial | 700 | 0 | 510 | 468.07 | 0 | 0 | No
2030-07-24 06:00 | 2030 Initial | 700 | 0 | 390 | 437.75 | 0 | 0 | No
2030-07-24 07:00 | 2030 Initial | 700 | 0 | 90 | 508.73 | 0 | 0 | No
2030-07-24 08:00 | 2030 Initial | 700 | -226 | -210 | 422.53 | 0 | 0 | No
2030-07-24 09:00 | 2030 Initial | 700 | -526 | -510 | 413.4 | 0 | 0 | No
2030-07-24 10:00 | 2030 Initial | 280 | -526 | -510 | 333.22 | 0 | 0 | No
2030-07-24 11:00 | 2030 Initial | 262.57 | -526 | -510 | 403.91 | 0 | 0 | No
2030-07-24 12:00 | 2030 Initial | -157.43 | -526 | -510 | 298.14 | 0 | 0 | No
2030-07-24 13:00 | 2030 Initial | 262.57 | -526 | -510 | 171.54 | 0 | 0 | No
2030-07-24 14:00 | 2030 Initial | 682.57 | -526 | -510 | 0 | 0 | 0 | No
2030-07-24 15:00 | 2030 Initial | 700 | -226 | -510 | 172.69 | 0 | 0 | No
2030-07-24 16:00 | 2030 Initial | 700 | -325.97 | -510 | 303.73 | 0 | 0 | No
2030-07-24 17:00 | 2030 Initial | 700 | -25.97 | -210 | 510 | 0 | 0 | No
2030-07-24 18:00 | 2030 Initial | 700 | 0 | -108.07 | 400.37 | 0 | 0 | No
2030-07-24 19:00 | 2030 Initial | 700 | 0 | -408.07 | 344.19 | 0 | 0 | No
2030-07-24 20:00 | 2030 Initial | 700 | 0 | -345.24 | 46.69 | 0 | 0 | No
2030-07-24 21:00 | 2030 Initial | 700 | 0 | -45.24 | 0 | 0 | 0 | No
2030-07-24 22:00 | 2030 Initial | 539.34 | 205 | 210 | 210 | 0 | 0 | No
2030-07-24 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 07:00 | 2030 Initial | 700 | 205 | 386.28 | 510 | 0 | 0 | No
2030-07-25 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 15:00 | 2030 Initial | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-07-25 16:00 | 2030 Initial | 700 | 0 | 40.85 | 510 | 0 | 0 | No
2030-07-25 17:00 | 2030 Initial | 700 | 0 | -17.7 | 510 | 0 | 0 | No
2030-07-25 18:00 | 2030 Initial | 700 | 0 | -92.21 | 249.09 | 0 | 0 | No
2030-07-25 19:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-07-25 20:00 | 2030 Initial | 700 | 0 | 50.22 | 510 | 0 | 0 | No
2030-07-25 21:00 | 2030 Initial | 700 | 0 | 350.22 | 486.51 | 0 | 0 | No
2030-07-25 22:00 | 2030 Initial | 700 | 0 | 50.22 | 465.69 | 0 | 0 | No
2030-07-25 23:00 | 2030 Initial | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-07-26 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 05:00 | 2030 Initial | 700 | 293.31 | 510 | 510 | 0 | 0 | No
2030-07-26 06:00 | 2030 Initial | 700 | 216.4 | 510 | 510 | 0 | 0 | No
2030-07-26 07:00 | 2030 Initial | 700 | 205 | 510 | 367.85 | 0 | 0 | No
2030-07-26 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 11:00 | 2030 Initial | 365.09 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 12:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 13:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 14:00 | 2030 Initial | 106.93 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 15:00 | 2030 Initial | 289.59 | 389.45 | 510 | 510 | 0 | 0 | No
2030-07-26 16:00 | 2030 Initial | 700 | 89.45 | 210 | 274.83 | 0 | 0 | No
2030-07-26 17:00 | 2030 Initial | 280 | -210.55 | -90 | 510 | 0 | 0 | No
2030-07-26 18:00 | 2030 Initial | 700 | 0 | 18.44 | 510 | 0 | 0 | No
2030-07-26 19:00 | 2030 Initial | 700 | 0 | 93.82 | 510 | 0 | 0 | No
2030-07-26 20:00 | 2030 Initial | 700 | 0 | 375.39 | 510 | 0 | 0 | No
2030-07-26 21:00 | 2030 Initial | 700 | 0 | 75.39 | 510 | 0 | 0 | No
2030-07-26 22:00 | 2030 Initial | 700 | 205 | 279.59 | 510 | 0 | 0 | No
2030-07-26 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 07:00 | 2030 Initial | 409.58 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 08:00 | 2030 Initial | -10.42 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 09:00 | 2030 Initial | -430.42 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 11:00 | 2030 Initial | -700 | 505 | 510 | 280.74 | 0 | 0 | Yes
2030-07-27 12:00 | 2030 Initial | -700 | 505 | 510 | 118.84 | 0 | 0 | Yes
2030-07-27 13:00 | 2030 Initial | -700 | 505 | 510 | 114.31 | 0 | 0 | Yes
2030-07-27 14:00 | 2030 Initial | -700 | 505 | 510 | 229.68 | 0 | 0 | Yes
2030-07-27 15:00 | 2030 Initial | -700 | 505 | 510 | 392.27 | 0 | 0 | Yes
2030-07-27 16:00 | 2030 Initial | -700 | 505 | 510 | 392.26 | 0 | 0 | Yes
2030-07-27 17:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 18:00 | 2030 Initial | -529.19 | 505 | 510 | 296.7 | 0 | 0 | Yes
2030-07-27 19:00 | 2030 Initial | -109.19 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 20:00 | 2030 Initial | 310.81 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 22:00 | 2030 Initial | 700 | 505 | 510 | 506.57 | 0 | 0 | Yes
2030-07-27 23:00 | 2030 Initial | 700 | 505 | 510 | 347.28 | 0 | 0 | Yes
2030-07-28 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 04:00 | 2030 Initial | 700 | 505 | 510 | 463.53 | 0 | 0 | Yes
2030-07-28 05:00 | 2030 Initial | 576.95 | 505 | 510 | 329.46 | 0 | 0 | Yes
2030-07-28 06:00 | 2030 Initial | 156.95 | 505 | 510 | 302.73 | 0 | 0 | Yes
2030-07-28 07:00 | 2030 Initial | -263.05 | 505 | 510 | 183.62 | 0 | 0 | Yes
2030-07-28 08:00 | 2030 Initial | -683.05 | 505 | 510 | 99.94 | 0 | 0 | Yes
2030-07-28 09:00 | 2030 Initial | -700 | 505 | 510 | 224.29 | 0 | 0 | Yes
2030-07-28 10:00 | 2030 Initial | -700 | 505 | 510 | 3.19 | 0 | 0 | Yes
2030-07-28 11:00 | 2030 Initial | -700 | 505 | 510 | 55.04 | 0 | 0 | Yes
2030-07-28 12:00 | 2030 Initial | -700 | 505 | 510 | 240.38 | 0 | 0 | Yes
2030-07-28 13:00 | 2030 Initial | -700 | 505 | 510 | 360.16 | 0 | 0 | Yes
2030-07-28 14:00 | 2030 Initial | -700 | 505 | 510 | 432.06 | 0 | 0 | Yes
2030-07-28 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 16:00 | 2030 Initial | -528.03 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 17:00 | 2030 Initial | -108.03 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 18:00 | 2030 Initial | 311.97 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 09:00 | 2030 Initial | 700 | 300 | 255.1 | 510 | 0 | 0 | No
2030-07-29 10:00 | 2030 Initial | 700 | 0 | -44.9 | 402.54 | 0 | 0 | No
2030-07-29 11:00 | 2030 Initial | 700 | -224.58 | -344.9 | 448.77 | 0 | 0 | No
2030-07-29 12:00 | 2030 Initial | 700 | 0 | -509.16 | 509.11 | 0 | 0 | No
2030-07-29 13:00 | 2030 Initial | 700 | 0 | -230.81 | 473.49 | 0 | 0 | No
2030-07-29 14:00 | 2030 Initial | 700 | 0 | -36.34 | 461.11 | 0 | 0 | No
2030-07-29 15:00 | 2030 Initial | 700 | 0 | 0 | 320.62 | 0 | 0 | No
2030-07-29 16:00 | 2030 Initial | 700 | 0 | 46.12 | 407.65 | 0 | 0 | No
2030-07-29 17:00 | 2030 Initial | 700 | 0 | 4.21 | 510 | 0 | 0 | No
2030-07-29 18:00 | 2030 Initial | 700 | 0 | 0 | 468.93 | 0 | 0 | No
2030-07-29 19:00 | 2030 Initial | 700 | 0 | 103.23 | 461.97 | 0 | 0 | No
2030-07-29 20:00 | 2030 Initial | 700 | 0 | 51.46 | 374.2 | 0 | 0 | No
2030-07-29 21:00 | 2030 Initial | 700 | 0 | 0 | 398.18 | 0 | 0 | No
2030-07-29 22:00 | 2030 Initial | 700 | 0 | -144.7 | 191.98 | 0 | 0 | No
2030-07-29 23:00 | 2030 Initial | 700 | -91.96 | -444.7 | 98.25 | 0 | 0 | No
2030-07-30 | 2030 Initial | 700 | 0 | -510 | 58.51 | 0 | 0 | No
2030-07-30 01:00 | 2030 Initial | 700 | -1.5 | -510 | -1.03 | 0 | 0 | No
2030-07-30 02:00 | 2030 Initial | 700 | 0 | -510 | -104.63 | 0 | 0 | No
2030-07-30 03:00 | 2030 Initial | 700 | -1.08 | -510 | -96.32 | 0 | 0 | No
2030-07-30 04:00 | 2030 Initial | 700 | -221.61 | -510 | -121.54 | 0 | 0 | No
2030-07-30 05:00 | 2030 Initial | 700 | -125.15 | -510 | 17.94 | 0 | 0 | No
2030-07-30 06:00 | 2030 Initial | 700 | -175.92 | -510 | 103.34 | 0 | 0 | No
2030-07-30 07:00 | 2030 Initial | 700 | -64.53 | -510 | 170.4 | 0 | 0 | No
2030-07-30 08:00 | 2030 Initial | 700 | -262.24 | -510 | 238.43 | 0 | 0 | No
2030-07-30 09:00 | 2030 Initial | 700 | -526 | -510 | 201.07 | 0 | 0 | No
2030-07-30 10:00 | 2030 Initial | 700 | -526 | -510 | 166.22 | 0 | 0 | No
2030-07-30 11:00 | 2030 Initial | 700 | -526 | -510 | 39.12 | 0 | 0 | No
2030-07-30 12:00 | 2030 Initial | 700 | -526 | -510 | 165.93 | 0 | 0 | No
2030-07-30 13:00 | 2030 Initial | 700 | -526 | -510 | 160.26 | 0 | 0 | No
2030-07-30 14:00 | 2030 Initial | 700 | -526 | -510 | 290.4 | 0 | 0 | No
2030-07-30 15:00 | 2030 Initial | 700 | -526 | -510 | 227.94 | 0 | 0 | No
2030-07-30 16:00 | 2030 Initial | 700 | -526 | -510 | 112.46 | 0 | 0 | No
2030-07-30 17:00 | 2030 Initial | 700 | -526 | -510 | -78.24 | 0 | 0 | No
2030-07-30 18:00 | 2030 Initial | 700 | -441.32 | -510 | -319.41 | 0 | 0 | No
2030-07-30 19:00 | 2030 Initial | 700 | -141.32 | -510 | -19.41 | 0 | 0 | No
2030-07-30 20:00 | 2030 Initial | 700 | 0 | -510 | -303.38 | 0 | 0 | No
2030-07-30 21:00 | 2030 Initial | 700 | 0 | -510 | -300 | 0 | 0 | No
2030-07-30 22:00 | 2030 Initial | 700 | -262.7 | -210 | 0 | 0 | 0 | No
2030-07-30 23:00 | 2030 Initial | 700 | 37.3 | 90 | 210 | 0 | 0 | No
2030-07-31 | 2030 Initial | 700 | 337.3 | 390 | 510 | 0 | 0 | No
2030-07-31 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 16:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 17:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 18:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 19:00 | 2030 Initial | 700 | 357.68 | 510 | 510 | 0 | 0 | No
2030-07-31 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 05:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-08-01 06:00 | 2030 Initial | 700 | -13.66 | -90 | 236.75 | 0 | 0 | No
2030-08-01 07:00 | 2030 Initial | 700 | -24.09 | -390 | 318.16 | 0 | 0 | No
2030-08-01 08:00 | 2030 Initial | 700 | -261.73 | -510 | 318.16 | 0 | 0 | No
2030-08-01 09:00 | 2030 Initial | 700 | -526 | -510 | 394.96 | 0 | 0 | No
2030-08-01 10:00 | 2030 Initial | 700 | -526 | -510 | 375.64 | 0 | 0 | No
2030-08-01 11:00 | 2030 Initial | 700 | -526 | -510 | 422.24 | 0 | 0 | No
2030-08-01 12:00 | 2030 Initial | 700 | -526 | -510 | 365.98 | 0 | 0 | No
2030-08-01 13:00 | 2030 Initial | 700 | -526 | -510 | 352.38 | 0 | 0 | No
2030-08-01 14:00 | 2030 Initial | 700 | -526 | -510 | 468.06 | 0 | 0 | No
2030-08-01 15:00 | 2030 Initial | 700 | -322.31 | -510 | 440.05 | 0 | 0 | No
2030-08-01 16:00 | 2030 Initial | 700 | -64.44 | -318.63 | 361.52 | 0 | 0 | No
2030-08-01 17:00 | 2030 Initial | 700 | 0 | -18.63 | 449.6 | 0 | 0 | No
2030-08-01 18:00 | 2030 Initial | 700 | 0 | 223.32 | 494.65 | 0 | 0 | No
2030-08-01 19:00 | 2030 Initial | 700 | 0 | 510 | 494.48 | 0 | 0 | No
2030-08-01 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-01 21:00 | 2030 Initial | 700 | 0 | 510 | 413.35 | 0 | 0 | No
2030-08-01 22:00 | 2030 Initial | 700 | 0 | 510 | 499.27 | 0 | 0 | No
2030-08-01 23:00 | 2030 Initial | 700 | 0 | 406.15 | 372.91 | 0 | 0 | No
2030-08-02 | 2030 Initial | 700 | 0 | 341.49 | 272.67 | 0 | 0 | No
2030-08-02 01:00 | 2030 Initial | 700 | 0 | 290.23 | 213.59 | 0 | 0 | No
2030-08-02 02:00 | 2030 Initial | 700 | 0 | 74.91 | 174.79 | 0 | 0 | No
2030-08-02 03:00 | 2030 Initial | 700 | 0 | 130.75 | 181.01 | 0 | 0 | No
2030-08-02 04:00 | 2030 Initial | 700 | 0 | 0 | 141.75 | 0 | 0 | No
2030-08-02 05:00 | 2030 Initial | 700 | 0 | 282.21 | 172.52 | 0 | 0 | No
2030-08-02 06:00 | 2030 Initial | 700 | 0 | 20.49 | 241.59 | 0 | 0 | No
2030-08-02 07:00 | 2030 Initial | 700 | 0 | 0 | 327.74 | 0 | 0 | No
2030-08-02 08:00 | 2030 Initial | 700 | -226 | -210 | 414.24 | 0 | 0 | No
2030-08-02 09:00 | 2030 Initial | 700 | -526 | -510 | 415.54 | 0 | 0 | No
2030-08-02 10:00 | 2030 Initial | 700 | -526 | -510 | 296.38 | 0 | 0 | No
2030-08-02 11:00 | 2030 Initial | 700 | -526 | -510 | 341.26 | 0 | 0 | No
2030-08-02 12:00 | 2030 Initial | 700 | -526 | -510 | 316.48 | 0 | 0 | No
2030-08-02 13:00 | 2030 Initial | 700 | -526 | -510 | 329.62 | 0 | 0 | No
2030-08-02 14:00 | 2030 Initial | 700 | -526 | -510 | 273.1 | 0 | 0 | No
2030-08-02 15:00 | 2030 Initial | 700 | -526 | -510 | 350.25 | 0 | 0 | No
2030-08-02 16:00 | 2030 Initial | 700 | -526 | -510 | 386.63 | 0 | 0 | No
2030-08-02 17:00 | 2030 Initial | 700 | -226 | -408.88 | 355.79 | 0 | 0 | No
2030-08-02 18:00 | 2030 Initial | 700 | -240.28 | -124.32 | 448.68 | 0 | 0 | No
2030-08-02 19:00 | 2030 Initial | 700 | 0 | 175.68 | 510 | 0 | 0 | No
2030-08-02 20:00 | 2030 Initial | 700 | -227.95 | -90 | 267.75 | 0 | 0 | No
2030-08-02 21:00 | 2030 Initial | 700 | 72.05 | 210 | 510 | 0 | 0 | No
2030-08-02 22:00 | 2030 Initial | 700 | 161.45 | 510 | 510 | 0 | 0 | No
2030-08-02 23:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-03 | 2030 Initial | 700 | 0 | 510 | 252.48 | 0 | 0 | No
2030-08-03 01:00 | 2030 Initial | 700 | 0 | 510 | 268.34 | 0 | 0 | No
2030-08-03 02:00 | 2030 Initial | 700 | 0 | 433.39 | 238.98 | 0 | 0 | No
2030-08-03 03:00 | 2030 Initial | 700 | 0 | 452.23 | 178.5 | 0 | 0 | No
2030-08-03 04:00 | 2030 Initial | 700 | 0 | 167.03 | 195.31 | 0 | 0 | No
2030-08-03 05:00 | 2030 Initial | 700 | 0 | 8.02 | 195.85 | 0 | 0 | No
2030-08-03 06:00 | 2030 Initial | 700 | 0 | 0 | 201.92 | 0 | 0 | No
2030-08-03 07:00 | 2030 Initial | 700 | 0 | -228.31 | 218.54 | 0 | 0 | No
2030-08-03 08:00 | 2030 Initial | 356.6 | -300 | -510 | 89.07 | 0 | 0 | No
2030-08-03 09:00 | 2030 Initial | 368.18 | -526 | -510 | 82.97 | 0 | 0 | No
2030-08-03 10:00 | 2030 Initial | 700 | -526 | -510 | 165.43 | 0 | 0 | No
2030-08-03 11:00 | 2030 Initial | 280 | -526 | -510 | 86.06 | 0 | 0 | No
2030-08-03 12:00 | 2030 Initial | 700 | -526 | -510 | 178.78 | 0 | 0 | No
2030-08-03 13:00 | 2030 Initial | 700 | -526 | -510 | 134.38 | 0 | 0 | No
2030-08-03 14:00 | 2030 Initial | 700 | -526 | -510 | 111.34 | 0 | 0 | No
2030-08-03 15:00 | 2030 Initial | 700 | -526 | -510 | 193.53 | 0 | 0 | No
2030-08-03 16:00 | 2030 Initial | 700 | -526 | -510 | 257.77 | 0 | 0 | No
2030-08-03 17:00 | 2030 Initial | 700 | -300 | -317.88 | 356.8 | 0 | 0 | No
2030-08-03 18:00 | 2030 Initial | 700 | 0 | -17.88 | 396.09 | 0 | 0 | No
2030-08-03 19:00 | 2030 Initial | 700 | 0 | 282.12 | 413.02 | 0 | 0 | No
2030-08-03 20:00 | 2030 Initial | 700 | 0 | 317.53 | 387.65 | 0 | 0 | No
2030-08-03 21:00 | 2030 Initial | 700 | 0 | 17.53 | 398.91 | 0 | 0 | No
2030-08-03 22:00 | 2030 Initial | 700 | 0 | 90 | 349.36 | 0 | 0 | No
2030-08-03 23:00 | 2030 Initial | 422.9 | -226 | -210 | 215.66 | 0 | 0 | No
2030-08-04 | 2030 Initial | 414.41 | -526 | -510 | 122.37 | 0 | 0 | No
2030-08-04 01:00 | 2030 Initial | -5.59 | -385.63 | -510 | 2.45 | 0 | 0 | No
2030-08-04 02:00 | 2030 Initial | -425.59 | -526 | -510 | 50.75 | 0 | 0 | No
2030-08-04 03:00 | 2030 Initial | -140 | -526 | -510 | 10.76 | 0 | 0 | No
2030-08-04 04:00 | 2030 Initial | 280 | -526 | -510 | -289.24 | 0 | 0 | No
2030-08-04 05:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-04 06:00 | 2030 Initial | 420 | -526 | -510 | -510 | 0 | 0 | No
2030-08-04 07:00 | 2030 Initial | 0 | -226 | -210 | -274.95 | 0 | 0 | No
2030-08-04 08:00 | 2030 Initial | -420 | 74 | 90 | 25.05 | 0 | 0 | Yes
2030-08-04 09:00 | 2030 Initial | -700 | 374 | 390 | 279.32 | 0 | 0 | Yes
2030-08-04 10:00 | 2030 Initial | -700 | 505 | 510 | 412.19 | 0 | 0 | Yes
2030-08-04 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 15:00 | 2030 Initial | -700 | 505 | 510 | 444.91 | 0 | 0 | Yes
2030-08-04 16:00 | 2030 Initial | -700 | 505 | 510 | 405.67 | 0 | 0 | Yes
2030-08-04 17:00 | 2030 Initial | -700 | 505 | 510 | 322.68 | 0 | 0 | Yes
2030-08-04 18:00 | 2030 Initial | -700 | 505 | 510 | 459.18 | 0 | 0 | Yes
2030-08-04 19:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 20:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 21:00 | 2030 Initial | -700 | 505 | 510 | 451.16 | 0 | 0 | Yes
2030-08-04 22:00 | 2030 Initial | -420.42 | 505 | 510 | 510 | 0 | 0 | No
2030-08-04 23:00 | 2030 Initial | -384.6 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-05 | 2030 Initial | 35.4 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 01:00 | 2030 Initial | 455.4 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 02:00 | 2030 Initial | 578.76 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 03:00 | 2030 Initial | 628.71 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 05:00 | 2030 Initial | 675.79 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 06:00 | 2030 Initial | 675.79 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 08:00 | 2030 Initial | 676.15 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 13:00 | 2030 Initial | 354.7 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 14:00 | 2030 Initial | 657.27 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 16:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 17:00 | 2030 Initial | 700 | 205 | 427.16 | 510 | 0 | 0 | No
2030-08-05 18:00 | 2030 Initial | 700 | 0 | 230.35 | 510 | 0 | 0 | No
2030-08-05 19:00 | 2030 Initial | 700 | 58.02 | 510 | 510 | 0 | 0 | No
2030-08-05 20:00 | 2030 Initial | 700 | 58.02 | 510 | 510 | 0 | 0 | No
2030-08-05 21:00 | 2030 Initial | 700 | 270.73 | 510 | 510 | 0 | 0 | No
2030-08-05 22:00 | 2030 Initial | 700 | 60.07 | 510 | 510 | 0 | 0 | No
2030-08-05 23:00 | 2030 Initial | 700 | 41.32 | 510 | 510 | 0 | 0 | No
2030-08-06 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-06 01:00 | 2030 Initial | 700 | 0 | 510 | 389.79 | 0 | 0 | No
2030-08-06 02:00 | 2030 Initial | 700 | 0 | 313.72 | 266.41 | 0 | 0 | No
2030-08-06 03:00 | 2030 Initial | 700 | 0 | 56.3 | 323.14 | 0 | 0 | No
2030-08-06 04:00 | 2030 Initial | 700 | 0 | -243.7 | 212.38 | 0 | 0 | No
2030-08-06 05:00 | 2030 Initial | 700 | 0 | -328.79 | 185.61 | 0 | 0 | No
2030-08-06 06:00 | 2030 Initial | 700 | 0 | -450.75 | 163.69 | 0 | 0 | No
2030-08-06 07:00 | 2030 Initial | 700 | -195.96 | -510 | 129.31 | 0 | 0 | No
2030-08-06 08:00 | 2030 Initial | 700 | -430.05 | -510 | 11.53 | 0 | 0 | No
2030-08-06 09:00 | 2030 Initial | 700 | -526 | -510 | -70.98 | 0 | 0 | No
2030-08-06 10:00 | 2030 Initial | 700 | -526 | -510 | 62.76 | 0 | 0 | No
2030-08-06 11:00 | 2030 Initial | 700 | -526 | -510 | -237.24 | 0 | 0 | No
2030-08-06 12:00 | 2030 Initial | 700 | -526 | -510 | -504.25 | 0 | 0 | No
2030-08-06 13:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-06 14:00 | 2030 Initial | 700 | -526 | -510 | -317.83 | 0 | 0 | No
2030-08-06 15:00 | 2030 Initial | 700 | -526 | -510 | -88.6 | 0 | 0 | No
2030-08-06 16:00 | 2030 Initial | 700 | -526 | -510 | 177.7 | 0 | 0 | No
2030-08-06 17:00 | 2030 Initial | 700 | -526 | -510 | 274.84 | 0 | 0 | No
2030-08-06 18:00 | 2030 Initial | 531.41 | -526 | -510 | 439.08 | 0 | 0 | No
2030-08-06 19:00 | 2030 Initial | 700 | -226 | -510 | 412.13 | 0 | 0 | No
2030-08-06 20:00 | 2030 Initial | 700 | 0 | -510 | 444.66 | 0 | 0 | No
2030-08-06 21:00 | 2030 Initial | 700 | -119.48 | -510 | 419.68 | 0 | 0 | No
2030-08-06 22:00 | 2030 Initial | 700 | -419.48 | -510 | 325.95 | 0 | 0 | No
2030-08-06 23:00 | 2030 Initial | 700 | -526 | -510 | 209.23 | 0 | 0 | No
2030-08-07 | 2030 Initial | 700 | -526 | -510 | 87.77 | 0 | 0 | No
2030-08-07 01:00 | 2030 Initial | 700 | -526 | -510 | -83.94 | 0 | 0 | No
2030-08-07 02:00 | 2030 Initial | 700 | -526 | -510 | -34.19 | 0 | 0 | No
2030-08-07 03:00 | 2030 Initial | 700 | -526 | -510 | -85.53 | 0 | 0 | No
2030-08-07 04:00 | 2030 Initial | 700 | -526 | -510 | -35.89 | 0 | 0 | No
2030-08-07 05:00 | 2030 Initial | 700 | -526 | -510 | -119.1 | 0 | 0 | No
2030-08-07 06:00 | 2030 Initial | 700 | -526 | -510 | -34.46 | 0 | 0 | No
2030-08-07 07:00 | 2030 Initial | 700 | -526 | -510 | -69.29 | 0 | 0 | No
2030-08-07 08:00 | 2030 Initial | 700 | -526 | -510 | 52.25 | 0 | 0 | No
2030-08-07 09:00 | 2030 Initial | 700 | -526 | -510 | -66.98 | 0 | 0 | No
2030-08-07 10:00 | 2030 Initial | 700 | -526 | -510 | -141.36 | 0 | 0 | No
2030-08-07 11:00 | 2030 Initial | 700 | -526 | -510 | 110.65 | 0 | 0 | No
2030-08-07 12:00 | 2030 Initial | 700 | -526 | -510 | 227.69 | 0 | 0 | No
2030-08-07 13:00 | 2030 Initial | 700 | -526 | -510 | -18.2 | 0 | 0 | No
2030-08-07 14:00 | 2030 Initial | 700 | -526 | -510 | 3.5 | 0 | 0 | No
2030-08-07 15:00 | 2030 Initial | 700 | -488.9 | -510 | 201.09 | 0 | 0 | No
2030-08-07 16:00 | 2030 Initial | 700 | -246.31 | -300 | 320.36 | 0 | 0 | No
2030-08-07 17:00 | 2030 Initial | 700 | 0 | 0 | 236.7 | 0 | 0 | No
2030-08-07 18:00 | 2030 Initial | 700 | 0 | 300 | 456.64 | 0 | 0 | No
2030-08-07 19:00 | 2030 Initial | 700 | 0 | 510 | 499.09 | 0 | 0 | No
2030-08-07 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-07 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-07 22:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-07 23:00 | 2030 Initial | 700 | 0 | 510 | 399.95 | 0 | 0 | No
2030-08-08 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-08 01:00 | 2030 Initial | 700 | 0 | 510 | 399.13 | 0 | 0 | No
2030-08-08 02:00 | 2030 Initial | 700 | 0 | 510 | 99.13 | 0 | 0 | No
2030-08-08 03:00 | 2030 Initial | 700 | 0 | 510 | 204 | 0 | 0 | No
2030-08-08 04:00 | 2030 Initial | 700 | 0 | 510 | 265.49 | 0 | 0 | No
2030-08-08 05:00 | 2030 Initial | 700 | 0 | 510 | 27.46 | 0 | 0 | No
2030-08-08 06:00 | 2030 Initial | 700 | 0 | 300 | 118.95 | 0 | 0 | No
2030-08-08 07:00 | 2030 Initial | 700 | 0 | 0 | 410.5 | 0 | 0 | No
2030-08-08 08:00 | 2030 Initial | 700 | -294.08 | -300 | 253.42 | 0 | 0 | No
2030-08-08 09:00 | 2030 Initial | 700 | -526 | -510 | 222.38 | 0 | 0 | No
2030-08-08 10:00 | 2030 Initial | 700 | -526 | -510 | 174.95 | 0 | 0 | No
2030-08-08 11:00 | 2030 Initial | 700 | -526 | -510 | 175.72 | 0 | 0 | No
2030-08-08 12:00 | 2030 Initial | 700 | -526 | -510 | 166.24 | 0 | 0 | No
2030-08-08 13:00 | 2030 Initial | 700 | -526 | -510 | 113.11 | 0 | 0 | No
2030-08-08 14:00 | 2030 Initial | 700 | -526 | -510 | 75.8 | 0 | 0 | No
2030-08-08 15:00 | 2030 Initial | 700 | -526 | -510 | 63.65 | 0 | 0 | No
2030-08-08 16:00 | 2030 Initial | 700 | -348.27 | -475.34 | 162.97 | 0 | 0 | No
2030-08-08 17:00 | 2030 Initial | 700 | -48.27 | -175.34 | 250.78 | 0 | 0 | No
2030-08-08 18:00 | 2030 Initial | 700 | 0 | 124.66 | 510 | 0 | 0 | No
2030-08-08 19:00 | 2030 Initial | 700 | 0 | 424.66 | 510 | 0 | 0 | No
2030-08-08 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-08 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-08 22:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-08 23:00 | 2030 Initial | 700 | 0 | 510 | 476.62 | 0 | 0 | No
2030-08-09 | 2030 Initial | 700 | 0 | 510 | 369.73 | 0 | 0 | No
2030-08-09 01:00 | 2030 Initial | 700 | 0 | 276.34 | 69.73 | 0 | 0 | No
2030-08-09 02:00 | 2030 Initial | 700 | 66.62 | 351.32 | 168.87 | 0 | 0 | No
2030-08-09 03:00 | 2030 Initial | 700 | 366.62 | 510 | 468.87 | 0 | 0 | No
2030-08-09 04:00 | 2030 Initial | 700 | 162.67 | 295.67 | 168.87 | 0 | 0 | No
2030-08-09 05:00 | 2030 Initial | 700 | 0 | -4.33 | -131.13 | 0 | 0 | No
2030-08-09 06:00 | 2030 Initial | 700 | 0 | -279.17 | -272.4 | 0 | 0 | No
2030-08-09 07:00 | 2030 Initial | 700 | 0 | -389.39 | 0 | 0 | 0 | No
2030-08-09 08:00 | 2030 Initial | 700 | -226 | -471.74 | 0 | 0 | 0 | No
2030-08-09 09:00 | 2030 Initial | 700 | -526 | -510 | 175.3 | 0 | 0 | No
2030-08-09 10:00 | 2030 Initial | 700 | -526 | -510 | 126.06 | 0 | 0 | No
2030-08-09 11:00 | 2030 Initial | 700 | -526 | -510 | 67.2 | 0 | 0 | No
2030-08-09 12:00 | 2030 Initial | 700 | -526 | -510 | 58.55 | 0 | 0 | No
2030-08-09 13:00 | 2030 Initial | 700 | -526 | -510 | 96.72 | 0 | 0 | No
2030-08-09 14:00 | 2030 Initial | 700 | -526 | -510 | 92.82 | 0 | 0 | No
2030-08-09 15:00 | 2030 Initial | 700 | -526 | -510 | 136.31 | 0 | 0 | No
2030-08-09 16:00 | 2030 Initial | 700 | -460.77 | -498.51 | 239.67 | 0 | 0 | No
2030-08-09 17:00 | 2030 Initial | 700 | -160.77 | -198.51 | 510 | 0 | 0 | No
2030-08-09 18:00 | 2030 Initial | 700 | 0 | 101.49 | 510 | 0 | 0 | No
2030-08-09 19:00 | 2030 Initial | 700 | 0 | 401.49 | 510 | 0 | 0 | No
2030-08-09 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-09 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-09 22:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-09 23:00 | 2030 Initial | 700 | 0 | 510 | 420.9 | 0 | 0 | No
2030-08-10 | 2030 Initial | 700 | 0 | 210 | 120.9 | 0 | 0 | No
2030-08-10 01:00 | 2030 Initial | 700 | 0 | 4.08 | -179.1 | 0 | 0 | No
2030-08-10 02:00 | 2030 Initial | 700 | 0 | 36.91 | 0 | 0 | 0 | No
2030-08-10 03:00 | 2030 Initial | 700 | 0 | -81.4 | 0 | 0 | 0 | No
2030-08-10 04:00 | 2030 Initial | 700 | 0 | -53.67 | 0 | 0 | 0 | No
2030-08-10 05:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-10 06:00 | 2030 Initial | 700 | 0 | -90.83 | 0 | 0 | 0 | No
2030-08-10 07:00 | 2030 Initial | 700 | 0 | -145.95 | 0 | 0 | 0 | No
2030-08-10 08:00 | 2030 Initial | 700 | -226 | -332.14 | 75.42 | 0 | 0 | No
2030-08-10 09:00 | 2030 Initial | 700 | -526 | -510 | 119.26 | 0 | 0 | No
2030-08-10 10:00 | 2030 Initial | 700 | -526 | -510 | 59.82 | 0 | 0 | No
2030-08-10 11:00 | 2030 Initial | 700 | -526 | -510 | 144.61 | 0 | 0 | No
2030-08-10 12:00 | 2030 Initial | 700 | -526 | -510 | 199.19 | 0 | 0 | No
2030-08-10 13:00 | 2030 Initial | 700 | -455.82 | -510 | 119.66 | 0 | 0 | No
2030-08-10 14:00 | 2030 Initial | 700 | -427.13 | -510 | 119.87 | 0 | 0 | No
2030-08-10 15:00 | 2030 Initial | 700 | -287.19 | -510 | 139.39 | 0 | 0 | No
2030-08-10 16:00 | 2030 Initial | 700 | -23.99 | -459.08 | 184.36 | 0 | 0 | No
2030-08-10 17:00 | 2030 Initial | 700 | 0 | -159.08 | 84.96 | 0 | 0 | No
2030-08-10 18:00 | 2030 Initial | 700 | 0 | 140.92 | 171.7 | 0 | 0 | No
2030-08-10 19:00 | 2030 Initial | 700 | 0 | 360.99 | 0 | 0 | 0 | No
2030-08-10 20:00 | 2030 Initial | 700 | 0 | 510 | 161.54 | 0 | 0 | No
2030-08-10 21:00 | 2030 Initial | 700 | 0 | 500.46 | 179.18 | 0 | 0 | No
2030-08-10 22:00 | 2030 Initial | 700 | 0 | 306.03 | 0 | 0 | 0 | No
2030-08-10 23:00 | 2030 Initial | 700 | 0 | 332.51 | 89.24 | 0 | 0 | No
2030-08-11 | 2030 Initial | 700 | 0 | 227.85 | 0 | 0 | 0 | No
2030-08-11 01:00 | 2030 Initial | 700 | 0 | 184.75 | 37.86 | 0 | 0 | No
2030-08-11 02:00 | 2030 Initial | 700 | 0 | 29.5 | 20.32 | 0 | 0 | No
2030-08-11 03:00 | 2030 Initial | 700 | 0 | 14.09 | 4.3 | 0 | 0 | No
2030-08-11 04:00 | 2030 Initial | 700 | 0 | 0 | 15.67 | 0 | 0 | No
2030-08-11 05:00 | 2030 Initial | 700 | 0 | -107.22 | 0 | 0 | 0 | No
2030-08-11 06:00 | 2030 Initial | 700 | 0 | -407.22 | 0 | 0 | 0 | No
2030-08-11 07:00 | 2030 Initial | 700 | -226 | -460.07 | 0 | 0 | 0 | No
2030-08-11 08:00 | 2030 Initial | 700 | -526 | -510 | -66.96 | 0 | 0 | No
2030-08-11 09:00 | 2030 Initial | 700 | -526 | -510 | -120.33 | 0 | 0 | No
2030-08-11 10:00 | 2030 Initial | 700 | -526 | -510 | -179.66 | 0 | 0 | No
2030-08-11 11:00 | 2030 Initial | 700 | -526 | -510 | -160.87 | 0 | 0 | No
2030-08-11 12:00 | 2030 Initial | 700 | -526 | -510 | -129.49 | 0 | 0 | No
2030-08-11 13:00 | 2030 Initial | 700 | -526 | -510 | -26.43 | 0 | 0 | No
2030-08-11 14:00 | 2030 Initial | 700 | -526 | -510 | -33.2 | 0 | 0 | No
2030-08-11 15:00 | 2030 Initial | 700 | -526 | -510 | -34.38 | 0 | 0 | No
2030-08-11 16:00 | 2030 Initial | 700 | -526 | -510 | 40.1 | 0 | 0 | No
2030-08-11 17:00 | 2030 Initial | 700 | -226 | -210 | 126.63 | 0 | 0 | No
2030-08-11 18:00 | 2030 Initial | 700 | 0 | 90 | 160.8 | 0 | 0 | No
2030-08-11 19:00 | 2030 Initial | 700 | 0 | 210 | 164.23 | 0 | 0 | No
2030-08-11 20:00 | 2030 Initial | 700 | 0 | 510 | 169.92 | 0 | 0 | No
2030-08-11 21:00 | 2030 Initial | 700 | 0 | 510 | 204.35 | 0 | 0 | No
2030-08-11 22:00 | 2030 Initial | 700 | 0 | 510 | 155.16 | 0 | 0 | No
2030-08-11 23:00 | 2030 Initial | 700 | 0 | 510 | 54.92 | 0 | 0 | No
2030-08-12 | 2030 Initial | 700 | 0 | 372.22 | 38.96 | 0 | 0 | No
2030-08-12 01:00 | 2030 Initial | 700 | 0 | 72.22 | 0 | 0 | 0 | No
2030-08-12 02:00 | 2030 Initial | 700 | 0 | 152.62 | 0 | 0 | 0 | No
2030-08-12 03:00 | 2030 Initial | 700 | 0 | 14.34 | 0 | 0 | 0 | No
2030-08-12 04:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-12 05:00 | 2030 Initial | 700 | 0 | 4.44 | 0 | 0 | 0 | No
2030-08-12 06:00 | 2030 Initial | 700 | 0 | 0 | 2.87 | 0 | 0 | No
2030-08-12 07:00 | 2030 Initial | 700 | 0 | 0 | 93.94 | 0 | 0 | No
2030-08-12 08:00 | 2030 Initial | 700 | -226 | -295.91 | 184.93 | 0 | 0 | No
2030-08-12 09:00 | 2030 Initial | 700 | -526 | -510 | 133.3 | 0 | 0 | No
2030-08-12 10:00 | 2030 Initial | 700 | -526 | -510 | -16.87 | 0 | 0 | No
2030-08-12 11:00 | 2030 Initial | 700 | -526 | -510 | -24.89 | 0 | 0 | No
2030-08-12 12:00 | 2030 Initial | 700 | -526 | -510 | -41.97 | 0 | 0 | No
2030-08-12 13:00 | 2030 Initial | 700 | -526 | -510 | -32.2 | 0 | 0 | No
2030-08-12 14:00 | 2030 Initial | 700 | -526 | -510 | -28.74 | 0 | 0 | No
2030-08-12 15:00 | 2030 Initial | 700 | -526 | -510 | -68.36 | 0 | 0 | No
2030-08-12 16:00 | 2030 Initial | 700 | -389.48 | -510 | 90.17 | 0 | 0 | No
2030-08-12 17:00 | 2030 Initial | 700 | -89.48 | -210 | 132.12 | 0 | 0 | No
2030-08-12 18:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-12 19:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-12 20:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-12 21:00 | 2030 Initial | 700 | 0 | 22.46 | 0 | 0 | 0 | No
2030-08-12 22:00 | 2030 Initial | 700 | 0 | 5.97 | 0 | 0 | 0 | No
2030-08-12 23:00 | 2030 Initial | 700 | 0 | -81.46 | 22.09 | 0 | 0 | No
2030-08-13 | 2030 Initial | 700 | 0 | 0 | 89.81 | 0 | 0 | No
2030-08-13 01:00 | 2030 Initial | 700 | -33.46 | -300 | 15.63 | 0 | 0 | No
2030-08-13 02:00 | 2030 Initial | 700 | 0 | -446.95 | 58.06 | 0 | 0 | No
2030-08-13 03:00 | 2030 Initial | 700 | 0 | -504.53 | 1.86 | 0 | 0 | No
2030-08-13 04:00 | 2030 Initial | 700 | -45.84 | -510 | -23.81 | 0 | 0 | No
2030-08-13 05:00 | 2030 Initial | 700 | -295.04 | -510 | -214.32 | 0 | 0 | No
2030-08-13 06:00 | 2030 Initial | 608.09 | -300 | -510 | -150.23 | 0 | 0 | No
2030-08-13 07:00 | 2030 Initial | 700 | 0 | -459.9 | 149.77 | 0 | 0 | No
2030-08-13 08:00 | 2030 Initial | 700 | -36.57 | -478.24 | 212.3 | 0 | 0 | No
2030-08-13 09:00 | 2030 Initial | 700 | -336.57 | -510 | 122.22 | 0 | 0 | No
2030-08-13 10:00 | 2030 Initial | 441.37 | -526 | -510 | 83.65 | 0 | 0 | No
2030-08-13 11:00 | 2030 Initial | 423.94 | -526 | -510 | 157.45 | 0 | 0 | No
2030-08-13 12:00 | 2030 Initial | 471.77 | -526 | -510 | 72.06 | 0 | 0 | No
2030-08-13 13:00 | 2030 Initial | 255.85 | -526 | -510 | -40.6 | 0 | 0 | No
2030-08-13 14:00 | 2030 Initial | 280 | -526 | -510 | -171.3 | 0 | 0 | No
2030-08-13 15:00 | 2030 Initial | 700 | -526 | -510 | -307.06 | 0 | 0 | No
2030-08-13 16:00 | 2030 Initial | 700 | -375.15 | -458.22 | -134.2 | 0 | 0 | No
2030-08-13 17:00 | 2030 Initial | 700 | -75.15 | -158.22 | 165.8 | 0 | 0 | No
2030-08-13 18:00 | 2030 Initial | 700 | 0 | 141.78 | 465.8 | 0 | 0 | No
2030-08-13 19:00 | 2030 Initial | 700 | 0 | 441.78 | 510 | 0 | 0 | No
2030-08-13 20:00 | 2030 Initial | 700 | 0 | 510 | 486.13 | 0 | 0 | No
2030-08-13 21:00 | 2030 Initial | 700 | 0 | 510 | 296.5 | 0 | 0 | No
2030-08-13 22:00 | 2030 Initial | 700 | 0 | 510 | 293.64 | 0 | 0 | No
2030-08-13 23:00 | 2030 Initial | 700 | 0 | 300 | 40.31 | 0 | 0 | No
2030-08-14 | 2030 Initial | 700 | 0 | 0 | -61.28 | 0 | 0 | No
2030-08-14 01:00 | 2030 Initial | 700 | 0 | -290.98 | 0 | 0 | 0 | No
2030-08-14 02:00 | 2030 Initial | 700 | 0 | -148.25 | 0 | 0 | 0 | No
2030-08-14 03:00 | 2030 Initial | 700 | 0 | -443.81 | 0 | 0 | 0 | No
2030-08-14 04:00 | 2030 Initial | 700 | 0 | -143.81 | 0 | 0 | 0 | No
2030-08-14 05:00 | 2030 Initial | 700 | 0 | -127.71 | 0 | 0 | 0 | No
2030-08-14 06:00 | 2030 Initial | 700 | 0 | -6.09 | 0 | 0 | 0 | No
2030-08-14 07:00 | 2030 Initial | 700 | 0 | -193.96 | 7.2 | 0 | 0 | No
2030-08-14 08:00 | 2030 Initial | 700 | -226 | -210 | 307.2 | 0 | 0 | No
2030-08-14 09:00 | 2030 Initial | 700 | -526 | -510 | 245.98 | 0 | 0 | No
2030-08-14 10:00 | 2030 Initial | 700 | -526 | -510 | 183.18 | 0 | 0 | No
2030-08-14 11:00 | 2030 Initial | 700 | -526 | -510 | 180.98 | 0 | 0 | No
2030-08-14 12:00 | 2030 Initial | 700 | -526 | -510 | 159.3 | 0 | 0 | No
2030-08-14 13:00 | 2030 Initial | 700 | -526 | -510 | 117.78 | 0 | 0 | No
2030-08-14 14:00 | 2030 Initial | 700 | -526 | -510 | 127.27 | 0 | 0 | No
2030-08-14 15:00 | 2030 Initial | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-08-14 16:00 | 2030 Initial | 700 | -300 | -370.76 | -107.94 | 0 | 0 | No
2030-08-14 17:00 | 2030 Initial | 700 | 0 | -70.76 | 183.68 | 0 | 0 | No
2030-08-14 18:00 | 2030 Initial | 700 | 300 | 210 | 260.04 | 0 | 0 | No
2030-08-14 19:00 | 2030 Initial | 700 | 0 | -90 | -39.96 | 0 | 0 | No
2030-08-14 20:00 | 2030 Initial | 700 | 0 | 210 | 145.78 | 0 | 0 | No
2030-08-14 21:00 | 2030 Initial | 700 | 300 | 510 | 445.78 | 0 | 0 | No
2030-08-14 22:00 | 2030 Initial | 700 | 258.49 | 510 | 488.8 | 0 | 0 | No
2030-08-14 23:00 | 2030 Initial | 700 | 32.18 | 510 | 222.03 | 0 | 0 | No
2030-08-15 | 2030 Initial | 700 | 0 | 345.59 | 0 | 0 | 0 | No
2030-08-15 01:00 | 2030 Initial | 700 | 0 | 272.18 | 0 | 0 | 0 | No
2030-08-15 02:00 | 2030 Initial | 700 | 0 | 67.62 | 0 | 0 | 0 | No
2030-08-15 03:00 | 2030 Initial | 700 | 0 | 180.11 | 0 | 0 | 0 | No
2030-08-15 04:00 | 2030 Initial | 700 | 0 | 38.07 | 0 | 0 | 0 | No
2030-08-15 05:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-15 06:00 | 2030 Initial | 700 | 0 | 209.2 | 0 | 0 | 0 | No
2030-08-15 07:00 | 2030 Initial | 700 | 0 | 242.94 | 0 | 0 | 0 | No
2030-08-15 08:00 | 2030 Initial | 700 | 0 | -57.06 | 0 | 0 | 0 | No
2030-08-15 09:00 | 2030 Initial | 700 | 0 | -357.06 | -3.15 | 0 | 0 | No
2030-08-15 10:00 | 2030 Initial | 700 | -107.38 | -510 | -138.4 | 0 | 0 | No
2030-08-15 11:00 | 2030 Initial | 700 | -398.08 | -510 | -85.5 | 0 | 0 | No
2030-08-15 12:00 | 2030 Initial | 700 | -98.08 | -510 | -169.33 | 0 | 0 | No
2030-08-15 13:00 | 2030 Initial | 700 | -252.52 | -510 | -169.33 | 0 | 0 | No
2030-08-15 14:00 | 2030 Initial | 700 | -254.92 | -510 | 0 | 0 | 0 | No
2030-08-15 15:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-15 16:00 | 2030 Initial | 700 | 0 | -300 | -72.62 | 0 | 0 | No
2030-08-15 17:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-15 18:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-15 19:00 | 2030 Initial | 700 | 0 | 287.64 | 0 | 0 | 0 | No
2030-08-15 20:00 | 2030 Initial | 700 | 205 | 287.64 | 89.37 | 0 | 0 | No
2030-08-15 21:00 | 2030 Initial | 700 | 505 | 510 | 389.37 | 0 | 0 | No
2030-08-15 22:00 | 2030 Initial | 700 | 505 | 510 | 208.01 | 0 | 0 | No
2030-08-15 23:00 | 2030 Initial | 700 | 205 | 426.17 | -91.99 | 0 | 0 | No
2030-08-16 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-08-16 01:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-08-16 02:00 | 2030 Initial | 700 | 0 | 381.76 | 0 | 0 | 0 | No
2030-08-16 03:00 | 2030 Initial | 700 | 0 | 489.21 | 0 | 0 | 0 | No
2030-08-16 04:00 | 2030 Initial | 700 | 0 | 189.21 | 0 | 0 | 0 | No
2030-08-16 05:00 | 2030 Initial | 700 | 0 | 146.48 | 0 | 0 | 0 | No
2030-08-16 06:00 | 2030 Initial | 700 | 0 | 258.41 | 0 | 0 | 0 | No
2030-08-16 07:00 | 2030 Initial | 700 | 0 | 383.77 | 0 | 0 | 0 | No
2030-08-16 08:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-08-16 09:00 | 2030 Initial | 700 | 0 | 510 | 72.48 | 0 | 0 | No
2030-08-16 10:00 | 2030 Initial | 700 | 0 | 509.95 | 0 | 0 | 0 | No
2030-08-16 11:00 | 2030 Initial | 700 | 0 | 330.84 | 0 | 0 | 0 | No
2030-08-16 12:00 | 2030 Initial | 700 | 0 | 44.48 | 0 | 0 | 0 | No
2030-08-16 13:00 | 2030 Initial | 700 | 0 | 210.98 | 0 | 0 | 0 | No
2030-08-16 14:00 | 2030 Initial | 700 | 0 | 402.17 | 0 | 0 | 0 | No
2030-08-16 15:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-08-16 16:00 | 2030 Initial | 700 | 0 | 510 | 117.49 | 0 | 0 | No
2030-08-16 17:00 | 2030 Initial | 700 | 0 | 510 | 21.89 | 0 | 0 | No
2030-08-16 18:00 | 2030 Initial | 700 | 0 | 510 | 211.31 | 0 | 0 | No
2030-08-16 19:00 | 2030 Initial | 700 | 0 | 510 | 59.96 | 0 | 0 | No
2030-08-16 20:00 | 2030 Initial | 700 | 205 | 510 | 59.96 | 0 | 0 | No
2030-08-16 21:00 | 2030 Initial | 700 | 505 | 510 | 147.22 | 0 | 0 | No
2030-08-16 22:00 | 2030 Initial | 700 | 505 | 510 | 325.83 | 0 | 0 | No
2030-08-16 23:00 | 2030 Initial | 700 | 494.17 | 510 | 261.15 | 0 | 0 | No
2030-08-17 | 2030 Initial | 700 | 218.82 | 510 | 4.76 | 0 | 0 | No
2030-08-17 01:00 | 2030 Initial | 700 | 0 | 510 | -99.78 | 0 | 0 | No
2030-08-17 02:00 | 2030 Initial | 700 | 0 | 510 | -21.82 | 0 | 0 | No
2030-08-17 03:00 | 2030 Initial | 700 | 0 | 510 | -131.55 | 0 | 0 | No
2030-08-17 04:00 | 2030 Initial | 700 | 0 | 510 | -80.65 | 0 | 0 | No
2030-08-17 05:00 | 2030 Initial | 700 | 0 | 510 | -210 | 0 | 0 | No
2030-08-17 06:00 | 2030 Initial | 700 | 0 | 287.6 | -510 | 0 | 0 | No
2030-08-17 07:00 | 2030 Initial | 700 | 0 | 460.68 | -210 | 0 | 0 | No
2030-08-17 08:00 | 2030 Initial | 700 | 0 | 274.05 | 0 | 0 | 0 | No
2030-08-17 09:00 | 2030 Initial | 700 | 0 | 503.32 | 0 | 0 | 0 | No
2030-08-17 10:00 | 2030 Initial | 700 | 0 | 453.81 | 0 | 0 | 0 | No
2030-08-17 11:00 | 2030 Initial | 700 | 0 | 465.58 | 0 | 0 | 0 | No
2030-08-17 12:00 | 2030 Initial | 700 | 0 | 366.95 | 0 | 0 | 0 | No
2030-08-17 13:00 | 2030 Initial | 700 | 0 | 163.81 | 0 | 0 | 0 | No
2030-08-17 14:00 | 2030 Initial | 700 | 0 | -37.35 | 0 | 0 | 0 | No
2030-08-17 15:00 | 2030 Initial | 700 | 0 | -137.93 | 0 | 0 | 0 | No
2030-08-17 16:00 | 2030 Initial | 700 | 0 | 10.38 | 0 | 0 | 0 | No
2030-08-17 17:00 | 2030 Initial | 700 | 0 | 310.38 | 205.78 | 0 | 0 | No
2030-08-17 18:00 | 2030 Initial | 700 | 0 | 510 | 278.57 | 0 | 0 | No
2030-08-17 19:00 | 2030 Initial | 700 | 0 | 510 | 337.96 | 0 | 0 | No
2030-08-17 20:00 | 2030 Initial | 700 | 0 | 510 | 137.61 | 0 | 0 | No
2030-08-17 21:00 | 2030 Initial | 700 | 0 | 510 | 224.11 | 0 | 0 | No
2030-08-17 22:00 | 2030 Initial | 700 | 0 | 510 | 16.04 | 0 | 0 | No
2030-08-17 23:00 | 2030 Initial | 700 | 0 | 300 | 42.94 | 0 | 0 | No
2030-08-18 | 2030 Initial | 700 | 0 | 182.89 | 0 | 0 | 0 | No
2030-08-18 01:00 | 2030 Initial | 700 | 0 | 136.73 | 0 | 0 | 0 | No
2030-08-18 02:00 | 2030 Initial | 700 | 0 | 107.77 | 0 | 0 | 0 | No
2030-08-18 03:00 | 2030 Initial | 700 | 0 | 211.11 | 0 | 0 | 0 | No
2030-08-18 04:00 | 2030 Initial | 700 | 0 | 26.47 | 0 | 0 | 0 | No
2030-08-18 05:00 | 2030 Initial | 700 | 0 | 160.06 | 0 | 0 | 0 | No
2030-08-18 06:00 | 2030 Initial | 700 | 0 | -35.57 | 0 | 0 | 0 | No
2030-08-18 07:00 | 2030 Initial | 700 | 0 | -99.46 | 0 | 0 | 0 | No
2030-08-18 08:00 | 2030 Initial | 700 | 0 | -399.46 | -27.05 | 0 | 0 | No
2030-08-18 09:00 | 2030 Initial | 700 | -109.44 | -510 | -239.35 | 0 | 0 | No
2030-08-18 10:00 | 2030 Initial | 700 | -409.44 | -510 | -225.37 | 0 | 0 | No
2030-08-18 11:00 | 2030 Initial | 700 | -526 | -510 | -200.88 | 0 | 0 | No
2030-08-18 12:00 | 2030 Initial | 700 | -526 | -510 | -93.72 | 0 | 0 | No
2030-08-18 13:00 | 2030 Initial | 700 | -526 | -510 | -120.37 | 0 | 0 | No
2030-08-18 14:00 | 2030 Initial | 700 | -526 | -510 | -133.2 | 0 | 0 | No
2030-08-18 15:00 | 2030 Initial | 700 | -526 | -510 | -146.97 | 0 | 0 | No
2030-08-18 16:00 | 2030 Initial | 700 | -441.36 | -510 | -118.35 | 0 | 0 | No
2030-08-18 17:00 | 2030 Initial | 700 | -141.36 | -225.14 | 0 | 0 | 0 | No
2030-08-18 18:00 | 2030 Initial | 700 | 0 | 74.86 | 0 | 0 | 0 | No
2030-08-18 19:00 | 2030 Initial | 700 | 0 | 350.86 | 0 | 0 | 0 | No
2030-08-18 20:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-08-18 21:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-08-18 22:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-08-18 23:00 | 2030 Initial | 700 | 0 | 338.4 | 0 | 0 | 0 | No
2030-08-19 | 2030 Initial | 700 | 0 | 300 | 0 | 0 | 0 | No
2030-08-19 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-19 02:00 | 2030 Initial | 700 | 0 | -68.2 | 0 | 0 | 0 | No
2030-08-19 03:00 | 2030 Initial | 700 | 0 | -165.3 | 0 | 0 | 0 | No
2030-08-19 04:00 | 2030 Initial | 700 | 0 | -325.59 | 0 | 0 | 0 | No
2030-08-19 05:00 | 2030 Initial | 700 | 0 | -267.53 | 0 | 0 | 0 | No
2030-08-19 06:00 | 2030 Initial | 700 | 0 | -72.72 | 0 | 0 | 0 | No
2030-08-19 07:00 | 2030 Initial | 700 | 0 | -265.62 | 78.99 | 0 | 0 | No
2030-08-19 08:00 | 2030 Initial | 700 | 0 | -299.57 | 0 | 0 | 0 | No
2030-08-19 09:00 | 2030 Initial | 700 | -189.53 | -510 | 5.93 | 0 | 0 | No
2030-08-19 10:00 | 2030 Initial | 700 | -279.57 | -210 | 129.41 | 0 | 0 | No
2030-08-19 11:00 | 2030 Initial | 700 | 20.43 | 90 | 210 | 0 | 0 | No
2030-08-19 12:00 | 2030 Initial | 700 | 320.43 | 390 | 510 | 0 | 0 | No
2030-08-19 13:00 | 2030 Initial | 700 | 505 | 510 | 456.93 | 0 | 0 | Yes
2030-08-19 14:00 | 2030 Initial | 700 | 505 | 510 | 273.72 | 0 | 0 | Yes
2030-08-19 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-19 16:00 | 2030 Initial | 700 | 505 | 510 | 428.17 | 0 | 0 | Yes
2030-08-19 17:00 | 2030 Initial | 700 | 505 | 510 | 343.37 | 0 | 0 | Yes
2030-08-19 18:00 | 2030 Initial | 280 | 505 | 510 | 213.19 | 0 | 0 | Yes
2030-08-19 19:00 | 2030 Initial | -140 | 505 | 510 | 185.44 | 0 | 0 | Yes
2030-08-19 20:00 | 2030 Initial | -560 | 505 | 510 | 147.82 | 0 | 0 | Yes
2030-08-19 21:00 | 2030 Initial | -700 | 505 | 510 | 301.5 | 0 | 0 | Yes
2030-08-19 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-19 23:00 | 2030 Initial | -700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-08-20 | 2030 Initial | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-20 01:00 | 2030 Initial | -700 | 505 | 510 | -62.85 | 0 | 0 | Yes
2030-08-20 02:00 | 2030 Initial | -700 | 505 | 510 | -80.31 | 0 | 0 | Yes
2030-08-20 03:00 | 2030 Initial | -700 | 505 | 510 | -124.94 | 0 | 0 | Yes
2030-08-20 04:00 | 2030 Initial | -700 | 505 | 510 | -95.25 | 0 | 0 | Yes
2030-08-20 05:00 | 2030 Initial | -700 | 505 | 510 | 51.58 | 0 | 0 | Yes
2030-08-20 06:00 | 2030 Initial | -700 | 505 | 510 | 69.37 | 0 | 0 | Yes
2030-08-20 07:00 | 2030 Initial | -700 | 505 | 510 | 121.38 | 0 | 0 | Yes
2030-08-20 08:00 | 2030 Initial | -700 | 505 | 510 | 215.74 | 0 | 0 | Yes
2030-08-20 09:00 | 2030 Initial | -700 | 505 | 510 | 214.55 | 0 | 0 | Yes
2030-08-20 10:00 | 2030 Initial | -700 | 505 | 510 | 167.39 | 0 | 0 | Yes
2030-08-20 11:00 | 2030 Initial | -700 | 505 | 510 | 181.38 | 0 | 0 | Yes
2030-08-20 12:00 | 2030 Initial | -700 | 505 | 510 | 369.63 | 0 | 0 | Yes
2030-08-20 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-20 14:00 | 2030 Initial | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-08-20 15:00 | 2030 Initial | -700 | 505 | 510 | 88.8 | 0 | 0 | Yes
2030-08-20 16:00 | 2030 Initial | -700 | 505 | 510 | 257.96 | 0 | 0 | Yes
2030-08-20 17:00 | 2030 Initial | -700 | 505 | 510 | 284.44 | 0 | 0 | Yes
2030-08-20 18:00 | 2030 Initial | -700 | 505 | 510 | 20.08 | 0 | 0 | Yes
2030-08-20 19:00 | 2030 Initial | -700 | 205 | 220.65 | -279.92 | 0 | 0 | No
2030-08-20 20:00 | 2030 Initial | -700 | 505 | 510 | 20.08 | 0 | 0 | Yes
2030-08-20 21:00 | 2030 Initial | -700 | 505 | 510 | 169.73 | 0 | 0 | Yes
2030-08-20 22:00 | 2030 Initial | -700 | 505 | 510 | 46.21 | 0 | 0 | Yes
2030-08-20 23:00 | 2030 Initial | -700 | 505 | 510 | -62.17 | 0 | 0 | Yes
2030-08-21 | 2030 Initial | -700 | 505 | 510 | 54.08 | 0 | 0 | Yes
2030-08-21 01:00 | 2030 Initial | -700 | 505 | 510 | 98.88 | 0 | 0 | Yes
2030-08-21 02:00 | 2030 Initial | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-21 03:00 | 2030 Initial | -700 | 505 | 510 | 169.16 | 0 | 0 | Yes
2030-08-21 04:00 | 2030 Initial | -700 | 505 | 510 | 469.16 | 0 | 0 | Yes
2030-08-21 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 16:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 17:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 18:00 | 2030 Initial | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 23:00 | 2030 Initial | 559.17 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 07:00 | 2030 Initial | 418.53 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 08:00 | 2030 Initial | 233.08 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 09:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 10:00 | 2030 Initial | -420 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 11:00 | 2030 Initial | -268.12 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 12:00 | 2030 Initial | -304.97 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 13:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 14:00 | 2030 Initial | -139.39 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 15:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 16:00 | 2030 Initial | 167.25 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 17:00 | 2030 Initial | 587.25 | 490.61 | 510 | 510 | 0 | 0 | No
2030-08-22 18:00 | 2030 Initial | 700 | 190.61 | 210 | 210 | 0 | 0 | No
2030-08-22 19:00 | 2030 Initial | 517.39 | -109.39 | -90 | 244.32 | 0 | 0 | No
2030-08-22 20:00 | 2030 Initial | 700 | -167.83 | -90 | 116.55 | 0 | 0 | No
2030-08-22 21:00 | 2030 Initial | 700 | 132.17 | 210 | 385.71 | 0 | 0 | No
2030-08-22 22:00 | 2030 Initial | 700 | 432.17 | 510 | 510 | 0 | 0 | No
2030-08-22 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 06:00 | 2030 Initial | 700 | 205 | 210 | 413.04 | 0 | 0 | No
2030-08-23 07:00 | 2030 Initial | 700 | -95 | -90 | 346.45 | 0 | 0 | No
2030-08-23 08:00 | 2030 Initial | 700 | -395 | -390 | 251.65 | 0 | 0 | No
2030-08-23 09:00 | 2030 Initial | 700 | -526 | -510 | 209.96 | 0 | 0 | No
2030-08-23 10:00 | 2030 Initial | 700 | -526 | -510 | 362.16 | 0 | 0 | No
2030-08-23 11:00 | 2030 Initial | 700 | -526 | -510 | 354.15 | 0 | 0 | No
2030-08-23 12:00 | 2030 Initial | 700 | -526 | -510 | 395.91 | 0 | 0 | No
2030-08-23 13:00 | 2030 Initial | 700 | -526 | -510 | 363.64 | 0 | 0 | No
2030-08-23 14:00 | 2030 Initial | 700 | -526 | -510 | 318.11 | 0 | 0 | No
2030-08-23 15:00 | 2030 Initial | 700 | -526 | -510 | 322.39 | 0 | 0 | No
2030-08-23 16:00 | 2030 Initial | 700 | -526 | -510 | 186.47 | 0 | 0 | No
2030-08-23 17:00 | 2030 Initial | 700 | -226 | -210 | 289.51 | 0 | 0 | No
2030-08-23 18:00 | 2030 Initial | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-08-23 19:00 | 2030 Initial | 700 | 0 | 390 | 510 | 0 | 0 | No
2030-08-23 20:00 | 2030 Initial | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-08-23 21:00 | 2030 Initial | 700 | 135.21 | 510 | 510 | 0 | 0 | No
2030-08-23 22:00 | 2030 Initial | 700 | 135.21 | 510 | 510 | 0 | 0 | No
2030-08-23 23:00 | 2030 Initial | 700 | 135.21 | 510 | 510 | 0 | 0 | No
2030-08-24 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-24 01:00 | 2030 Initial | 700 | 27.06 | 510 | 510 | 0 | 0 | No
2030-08-24 02:00 | 2030 Initial | 700 | 29.43 | 510 | 510 | 0 | 0 | No
2030-08-24 03:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-24 04:00 | 2030 Initial | 700 | 0 | 510 | 480.9 | 0 | 0 | No
2030-08-24 05:00 | 2030 Initial | 700 | 0 | 510 | 180.9 | 0 | 0 | No
2030-08-24 06:00 | 2030 Initial | 700 | 0 | 510 | 328.47 | 0 | 0 | No
2030-08-24 07:00 | 2030 Initial | 700 | 0 | 289.53 | 410.4 | 0 | 0 | No
2030-08-24 08:00 | 2030 Initial | 700 | 0 | -10.47 | 212.67 | 0 | 0 | No
2030-08-24 09:00 | 2030 Initial | 700 | -300 | -310.47 | 49.8 | 0 | 0 | No
2030-08-24 10:00 | 2030 Initial | 700 | -526 | -510 | 29.06 | 0 | 0 | No
2030-08-24 11:00 | 2030 Initial | 672.61 | -526 | -510 | 32.97 | 0 | 0 | No
2030-08-24 12:00 | 2030 Initial | 700 | -526 | -510 | 37.84 | 0 | 0 | No
2030-08-24 13:00 | 2030 Initial | 591.19 | -526 | -510 | 0.28 | 0 | 0 | No
2030-08-24 14:00 | 2030 Initial | 700 | -526 | -510 | 42.12 | 0 | 0 | No
2030-08-24 15:00 | 2030 Initial | 700 | -526 | -510 | 82.38 | 0 | 0 | No
2030-08-24 16:00 | 2030 Initial | 700 | -371.29 | -510 | 61.47 | 0 | 0 | No
2030-08-24 17:00 | 2030 Initial | 700 | -424.55 | -510 | -238.53 | 0 | 0 | No
2030-08-24 18:00 | 2030 Initial | 700 | -526 | -510 | -469.96 | 0 | 0 | No
2030-08-24 19:00 | 2030 Initial | 700 | -336.38 | -510 | -221.49 | 0 | 0 | No
2030-08-24 20:00 | 2030 Initial | 613.02 | -503.91 | -510 | -112.29 | 0 | 0 | No
2030-08-24 21:00 | 2030 Initial | 193.02 | -226 | -510 | -252.99 | 0 | 0 | No
2030-08-24 22:00 | 2030 Initial | -226.98 | -526 | -510 | -250.2 | 0 | 0 | No
2030-08-24 23:00 | 2030 Initial | -646.98 | -526 | -510 | -510 | 0 | 0 | No
2030-08-25 | 2030 Initial | -226.98 | -423.14 | -510 | -510 | 0 | 0 | No
2030-08-25 01:00 | 2030 Initial | -646.98 | -123.14 | -210 | -210 | 0 | 0 | No
2030-08-25 02:00 | 2030 Initial | -700 | 176.86 | 90 | 90 | 0 | 0 | Yes
2030-08-25 03:00 | 2030 Initial | -700 | 476.86 | 390 | 46.25 | 0 | 0 | Yes
2030-08-25 04:00 | 2030 Initial | -700 | 505 | 510 | -177.2 | 0 | 0 | Yes
2030-08-25 05:00 | 2030 Initial | -700 | 505 | 510 | -124.69 | 0 | 0 | Yes
2030-08-25 06:00 | 2030 Initial | -700 | 505 | 510 | -146.86 | 0 | 0 | Yes
2030-08-25 07:00 | 2030 Initial | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 08:00 | 2030 Initial | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 09:00 | 2030 Initial | -700 | 505 | 510 | -131.98 | 0 | 0 | Yes
2030-08-25 10:00 | 2030 Initial | -700 | 505 | 510 | -82.37 | 0 | 0 | Yes
2030-08-25 11:00 | 2030 Initial | -700 | 505 | 510 | -46.01 | 0 | 0 | Yes
2030-08-25 12:00 | 2030 Initial | -700 | 505 | 510 | -22.45 | 0 | 0 | Yes
2030-08-25 13:00 | 2030 Initial | -700 | 505 | 510 | -22.46 | 0 | 0 | Yes
2030-08-25 14:00 | 2030 Initial | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 15:00 | 2030 Initial | -700 | 505 | 510 | 264.61 | 0 | 0 | Yes
2030-08-25 16:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 17:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 18:00 | 2030 Initial | -700 | 505 | 510 | 455.16 | 0 | 0 | Yes
2030-08-25 19:00 | 2030 Initial | -700 | 505 | 510 | 276.75 | 0 | 0 | Yes
2030-08-25 20:00 | 2030 Initial | -515.87 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 21:00 | 2030 Initial | -407.12 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 22:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 23:00 | 2030 Initial | -248.46 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-26 | 2030 Initial | 171.54 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 01:00 | 2030 Initial | 591.54 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 15:00 | 2030 Initial | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-08-26 16:00 | 2030 Initial | 700 | -40.65 | -90 | 510 | 0 | 0 | No
2030-08-26 17:00 | 2030 Initial | 700 | 0 | 208.84 | 510 | 0 | 0 | No
2030-08-26 18:00 | 2030 Initial | 700 | 7.96 | 508.84 | 510 | 0 | 0 | No
2030-08-26 19:00 | 2030 Initial | 700 | 212.41 | 510 | 510 | 0 | 0 | No
2030-08-26 20:00 | 2030 Initial | 700 | 403.89 | 510 | 510 | 0 | 0 | No
2030-08-26 21:00 | 2030 Initial | 700 | 103.89 | 510 | 510 | 0 | 0 | No
2030-08-26 22:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-26 23:00 | 2030 Initial | 700 | 0 | 510 | 435.43 | 0 | 0 | No
2030-08-27 | 2030 Initial | 700 | 0 | 210 | 135.43 | 0 | 0 | No
2030-08-27 01:00 | 2030 Initial | 700 | 0 | 214.35 | 55.52 | 0 | 0 | No
2030-08-27 02:00 | 2030 Initial | 700 | 0 | 20.44 | 24.34 | 0 | 0 | No
2030-08-27 03:00 | 2030 Initial | 700 | 0 | -246.36 | 26.07 | 0 | 0 | No
2030-08-27 04:00 | 2030 Initial | 700 | 0 | -499.54 | 12.77 | 0 | 0 | No
2030-08-27 05:00 | 2030 Initial | 700 | 0 | -316.44 | 30.28 | 0 | 0 | No
2030-08-27 06:00 | 2030 Initial | 700 | 0 | -263.56 | 99.74 | 0 | 0 | No
2030-08-27 07:00 | 2030 Initial | 700 | 0 | 0 | 169.51 | 0 | 0 | No
2030-08-27 08:00 | 2030 Initial | 700 | 0 | 300 | 402.59 | 0 | 0 | No
2030-08-27 09:00 | 2030 Initial | 700 | 0 | 510 | 410.47 | 0 | 0 | No
2030-08-27 10:00 | 2030 Initial | 700 | 0 | 510 | 353.52 | 0 | 0 | No
2030-08-27 11:00 | 2030 Initial | 700 | 0 | 475.68 | 268.28 | 0 | 0 | No
2030-08-27 12:00 | 2030 Initial | 700 | 0 | 360.29 | 267.77 | 0 | 0 | No
2030-08-27 13:00 | 2030 Initial | 700 | 0 | 292.56 | 214.39 | 0 | 0 | No
2030-08-27 14:00 | 2030 Initial | 700 | 0 | -7.44 | 383.19 | 0 | 0 | No
2030-08-27 15:00 | 2030 Initial | 700 | 0 | 252.27 | 364.08 | 0 | 0 | No
2030-08-27 16:00 | 2030 Initial | 700 | 0 | 341.95 | 418.97 | 0 | 0 | No
2030-08-27 17:00 | 2030 Initial | 700 | 29.86 | 510 | 510 | 0 | 0 | No
2030-08-27 18:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-27 19:00 | 2030 Initial | 700 | 0 | 510 | 422.45 | 0 | 0 | No
2030-08-27 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-27 21:00 | 2030 Initial | 700 | 0 | 510 | 411.08 | 0 | 0 | No
2030-08-27 22:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-08-27 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 01:00 | 2030 Initial | 700 | 505 | 510 | 395.95 | 0 | 0 | No
2030-08-28 02:00 | 2030 Initial | 700 | 505 | 510 | 266.76 | 0 | 0 | Yes
2030-08-28 03:00 | 2030 Initial | 700 | 505 | 510 | 207.26 | 0 | 0 | Yes
2030-08-28 04:00 | 2030 Initial | 700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-28 05:00 | 2030 Initial | 700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-28 06:00 | 2030 Initial | 700 | 505 | 510 | 100.79 | 0 | 0 | Yes
2030-08-28 07:00 | 2030 Initial | 629.52 | 505 | 510 | 400.79 | 0 | 0 | Yes
2030-08-28 08:00 | 2030 Initial | 209.52 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 09:00 | 2030 Initial | -210.48 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 10:00 | 2030 Initial | -630.48 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 16:00 | 2030 Initial | -453.56 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 17:00 | 2030 Initial | -33.56 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 18:00 | 2030 Initial | 386.44 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 19:00 | 2030 Initial | 0 | 205 | 510 | 231.14 | 0 | 0 | No
2030-08-28 20:00 | 2030 Initial | 182.04 | 205 | 210 | 210 | 0 | 0 | No
2030-08-28 21:00 | 2030 Initial | 360.61 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 07:00 | 2030 Initial | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 08:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 09:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 15:00 | 2030 Initial | -568.32 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 16:00 | 2030 Initial | -148.32 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 17:00 | 2030 Initial | 271.68 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 18:00 | 2030 Initial | 691.68 | 205 | 278.6 | 245.83 | 0 | 0 | No
2030-08-29 19:00 | 2030 Initial | 700 | 0 | 403.39 | 105.61 | 0 | 0 | No
2030-08-29 20:00 | 2030 Initial | 700 | 179.18 | 510 | 210 | 0 | 0 | No
2030-08-29 21:00 | 2030 Initial | 700 | 479.18 | 510 | 510 | 0 | 0 | No
2030-08-29 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 06:00 | 2030 Initial | 700 | 205 | 478.66 | 210 | 0 | 0 | No
2030-08-30 07:00 | 2030 Initial | 700 | 131.34 | 363 | 510 | 0 | 0 | No
2030-08-30 08:00 | 2030 Initial | 700 | 0 | 63 | 489.93 | 0 | 0 | No
2030-08-30 09:00 | 2030 Initial | 700 | -300 | -237 | 189.93 | 0 | 0 | No
2030-08-30 10:00 | 2030 Initial | 700 | -526 | -510 | -110.07 | 0 | 0 | No
2030-08-30 11:00 | 2030 Initial | 347.94 | -526 | -510 | -40.43 | 0 | 0 | No
2030-08-30 12:00 | 2030 Initial | 700 | -411.28 | -510 | -39.1 | 0 | 0 | No
2030-08-30 13:00 | 2030 Initial | 700 | -111.28 | -510 | -70.71 | 0 | 0 | No
2030-08-30 14:00 | 2030 Initial | 700 | 0 | -376.31 | 0 | 0 | 0 | No
2030-08-30 15:00 | 2030 Initial | 700 | 0 | -90 | -24.96 | 0 | 0 | No
2030-08-30 16:00 | 2030 Initial | 700 | 0 | 210 | 117.52 | 0 | 0 | No
2030-08-30 17:00 | 2030 Initial | 700 | 140.88 | 510 | 417.52 | 0 | 0 | No
2030-08-30 18:00 | 2030 Initial | 700 | 80.38 | 510 | 321.23 | 0 | 0 | No
2030-08-30 19:00 | 2030 Initial | 700 | 0 | 510 | 145.37 | 0 | 0 | No
2030-08-30 20:00 | 2030 Initial | 700 | 0 | 510 | 19.56 | 0 | 0 | No
2030-08-30 21:00 | 2030 Initial | 700 | 275.32 | 510 | 224.1 | 0 | 0 | No
2030-08-30 22:00 | 2030 Initial | 700 | 505 | 510 | 426.88 | 0 | 0 | No
2030-08-30 23:00 | 2030 Initial | 700 | 300 | 510 | 329.46 | 0 | 0 | No
2030-08-31 | 2030 Initial | 700 | 0 | 467.64 | 29.46 | 0 | 0 | No
2030-08-31 01:00 | 2030 Initial | 700 | 0 | 332.31 | 59.84 | 0 | 0 | No
2030-08-31 02:00 | 2030 Initial | 700 | 0 | 32.31 | 0 | 0 | 0 | No
2030-08-31 03:00 | 2030 Initial | 700 | 0 | -134.42 | 0 | 0 | 0 | No
2030-08-31 04:00 | 2030 Initial | 700 | 0 | -194.35 | 0 | 0 | 0 | No
2030-08-31 05:00 | 2030 Initial | 700 | 0 | -417.95 | 0 | 0 | 0 | No
2030-08-31 06:00 | 2030 Initial | 700 | 0 | -224.48 | 0 | 0 | 0 | No
2030-08-31 07:00 | 2030 Initial | 480.92 | -72.94 | -282.15 | -210 | 0 | 0 | No
2030-08-31 08:00 | 2030 Initial | 60.92 | -372.94 | -510 | -510 | 0 | 0 | No
2030-08-31 09:00 | 2030 Initial | -359.08 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 10:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 11:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 12:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 13:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 14:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 15:00 | 2030 Initial | -385.2 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 16:00 | 2030 Initial | 34.8 | -502.11 | -510 | -503.34 | 0 | 0 | No
2030-08-31 17:00 | 2030 Initial | 454.8 | -226 | -510 | -298.93 | 0 | 0 | No
2030-08-31 18:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 19:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 20:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 21:00 | 2030 Initial | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-08-31 22:00 | 2030 Initial | 700 | 0 | -165.39 | 0 | 0 | 0 | No
2030-08-31 23:00 | 2030 Initial | 700 | 0 | -465.39 | -21.01 | 0 | 0 | No
2030-09-01 | 2030 Initial | 700 | 0 | -510 | -75.81 | 0 | 0 | No
2030-09-01 01:00 | 2030 Initial | 700 | 0 | -510 | -81.68 | 0 | 0 | No
2030-09-01 02:00 | 2030 Initial | 700 | 0 | -510 | -62.07 | 0 | 0 | No
2030-09-01 03:00 | 2030 Initial | 700 | -174.77 | -510 | -90.71 | 0 | 0 | No
2030-09-01 04:00 | 2030 Initial | 700 | 0 | -507.16 | 0 | 0 | 0 | No
2030-09-01 05:00 | 2030 Initial | 700 | 0 | -510 | -61.55 | 0 | 0 | No
2030-09-01 06:00 | 2030 Initial | 700 | 0 | -510 | 46.49 | 0 | 0 | No
2030-09-01 07:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-01 08:00 | 2030 Initial | 700 | -226 | -510 | -17.56 | 0 | 0 | No
2030-09-01 09:00 | 2030 Initial | 700 | -526 | -510 | -72.94 | 0 | 0 | No
2030-09-01 10:00 | 2030 Initial | 700 | -526 | -510 | -86.83 | 0 | 0 | No
2030-09-01 11:00 | 2030 Initial | 700 | -526 | -510 | -151.31 | 0 | 0 | No
2030-09-01 12:00 | 2030 Initial | 700 | -526 | -510 | -44.33 | 0 | 0 | No
2030-09-01 13:00 | 2030 Initial | 700 | -526 | -510 | -129.96 | 0 | 0 | No
2030-09-01 14:00 | 2030 Initial | 700 | -526 | -510 | -42.96 | 0 | 0 | No
2030-09-01 15:00 | 2030 Initial | 700 | -526 | -510 | -211.62 | 0 | 0 | No
2030-09-01 16:00 | 2030 Initial | 700 | -526 | -510 | 58.05 | 0 | 0 | No
2030-09-01 17:00 | 2030 Initial | 700 | -374.38 | -510 | 215.29 | 0 | 0 | No
2030-09-01 18:00 | 2030 Initial | 700 | -74.38 | -510 | 169.56 | 0 | 0 | No
2030-09-01 19:00 | 2030 Initial | 700 | -314.26 | -510 | 104.73 | 0 | 0 | No
2030-09-01 20:00 | 2030 Initial | 700 | -526 | -510 | 50.77 | 0 | 0 | No
2030-09-01 21:00 | 2030 Initial | 700 | -526 | -510 | -86.34 | 0 | 0 | No
2030-09-01 22:00 | 2030 Initial | 331.86 | -526 | -510 | -218.8 | 0 | 0 | No
2030-09-01 23:00 | 2030 Initial | 412.7 | -526 | -510 | -233.05 | 0 | 0 | No
2030-09-02 | 2030 Initial | -7.3 | -526 | -510 | -372.22 | 0 | 0 | No
2030-09-02 01:00 | 2030 Initial | 0 | -226 | -280.77 | -72.22 | 0 | 0 | No
2030-09-02 02:00 | 2030 Initial | 0 | 0 | -300 | -117.85 | 0 | 0 | No
2030-09-02 03:00 | 2030 Initial | -344.11 | 0 | 0 | 0 | 0 | 0 | No
2030-09-02 04:00 | 2030 Initial | -700 | 0 | -12.51 | 0 | 0 | 0 | No
2030-09-02 05:00 | 2030 Initial | -700 | 0 | -240.85 | 0 | 0 | 0 | No
2030-09-02 06:00 | 2030 Initial | -700 | 0 | 59.15 | 0 | 0 | 0 | No
2030-09-02 07:00 | 2030 Initial | -700 | 300 | 359.15 | 300 | 0 | 0 | No
2030-09-02 08:00 | 2030 Initial | -414.38 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 09:00 | 2030 Initial | -3.25 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 10:00 | 2030 Initial | 89 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 11:00 | 2030 Initial | -190.22 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 12:00 | 2030 Initial | -190.53 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 13:00 | 2030 Initial | -7.37 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 14:00 | 2030 Initial | -424.08 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 15:00 | 2030 Initial | -209.11 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 16:00 | 2030 Initial | -58.81 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 17:00 | 2030 Initial | 304.72 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 18:00 | 2030 Initial | 481.15 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 19:00 | 2030 Initial | 498.72 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 20:00 | 2030 Initial | 399.74 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 21:00 | 2030 Initial | 204.84 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 22:00 | 2030 Initial | 624.84 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 23:00 | 2030 Initial | 463.94 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 08:00 | 2030 Initial | 523.29 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 09:00 | 2030 Initial | 103.29 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 10:00 | 2030 Initial | -316.71 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 16:00 | 2030 Initial | -572.31 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 17:00 | 2030 Initial | -152.31 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 18:00 | 2030 Initial | 267.69 | 205 | 510 | 359.38 | 0 | 0 | No
2030-09-03 19:00 | 2030 Initial | 687.69 | 0 | 510 | 206.21 | 0 | 0 | No
2030-09-03 20:00 | 2030 Initial | 700 | 0 | 510 | 506.21 | 0 | 0 | No
2030-09-03 21:00 | 2030 Initial | 700 | 205 | 510 | 299.03 | 0 | 0 | No
2030-09-03 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 05:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 06:00 | 2030 Initial | 57.58 | 205 | 210 | 210 | 0 | 0 | No
2030-09-04 07:00 | 2030 Initial | 16.97 | 0 | 49.82 | 0 | 0 | 0 | No
2030-09-04 08:00 | 2030 Initial | 280 | 260.06 | 349.82 | 300 | 0 | 0 | No
2030-09-04 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 10:00 | 2030 Initial | 280 | 282.56 | 510 | 419.41 | 0 | 0 | No
2030-09-04 11:00 | 2030 Initial | -140 | 205 | 435.95 | 210 | 0 | 0 | No
2030-09-04 12:00 | 2030 Initial | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 15:00 | 2030 Initial | -581.21 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 16:00 | 2030 Initial | -161.21 | 300 | 424.27 | 300 | 0 | 0 | No
2030-09-04 17:00 | 2030 Initial | -121.7 | 0 | 124.27 | 0 | 0 | 0 | No
2030-09-04 18:00 | 2030 Initial | 298.3 | 0 | 0 | 0 | 0 | 0 | No
2030-09-04 19:00 | 2030 Initial | 700 | 0 | 264.24 | 0 | 0 | 0 | No
2030-09-04 20:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-09-04 21:00 | 2030 Initial | 700 | 205 | 510 | 210 | 0 | 0 | No
2030-09-04 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 06:00 | 2030 Initial | 299.72 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 07:00 | 2030 Initial | 280 | 205 | 210 | 210 | 0 | 0 | No
2030-09-05 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 09:00 | 2030 Initial | 674.24 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 10:00 | 2030 Initial | 254.24 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 11:00 | 2030 Initial | 0 | 205 | 510 | 353.72 | 0 | 0 | No
2030-09-05 12:00 | 2030 Initial | 0 | 205 | 510 | 426.69 | 0 | 0 | No
2030-09-05 13:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 14:00 | 2030 Initial | 280 | 491.13 | 405.37 | 510 | 0 | 0 | No
2030-09-05 15:00 | 2030 Initial | 700 | 191.13 | 105.37 | 510 | 0 | 0 | No
2030-09-05 16:00 | 2030 Initial | 280 | -108.87 | -194.63 | 510 | 0 | 0 | No
2030-09-05 17:00 | 2030 Initial | 700 | -157.92 | -494.63 | 510 | 0 | 0 | No
2030-09-05 18:00 | 2030 Initial | 700 | 0 | -194.63 | 510 | 0 | 0 | No
2030-09-05 19:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-09-05 20:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-09-05 21:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-09-05 22:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-09-05 23:00 | 2030 Initial | 700 | 0 | -97.24 | 470.53 | 0 | 0 | No
2030-09-06 | 2030 Initial | 700 | 0 | 0 | 170.53 | 0 | 0 | No
2030-09-06 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-06 02:00 | 2030 Initial | 700 | 0 | -165.26 | 0 | 0 | 0 | No
2030-09-06 03:00 | 2030 Initial | 700 | 0 | -208.66 | 0 | 0 | 0 | No
2030-09-06 04:00 | 2030 Initial | 700 | 0 | -312.1 | 0 | 0 | 0 | No
2030-09-06 05:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-06 06:00 | 2030 Initial | 700 | 0 | -424.64 | 0 | 0 | 0 | No
2030-09-06 07:00 | 2030 Initial | 700 | 0 | -124.64 | 0 | 0 | 0 | No
2030-09-06 08:00 | 2030 Initial | 700 | 0 | 175.36 | 62.01 | 0 | 0 | No
2030-09-06 09:00 | 2030 Initial | 700 | 0 | -96.23 | 0 | 0 | 0 | No
2030-09-06 10:00 | 2030 Initial | 700 | -116.75 | -396.23 | -117.23 | 0 | 0 | No
2030-09-06 11:00 | 2030 Initial | 700 | -277.95 | -510 | 0 | 0 | 0 | No
2030-09-06 12:00 | 2030 Initial | 700 | -526 | -510 | -60.04 | 0 | 0 | No
2030-09-06 13:00 | 2030 Initial | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-09-06 14:00 | 2030 Initial | 700 | -351.5 | -510 | -100.77 | 0 | 0 | No
2030-09-06 15:00 | 2030 Initial | 700 | -110.69 | -510 | -100.77 | 0 | 0 | No
2030-09-06 16:00 | 2030 Initial | 700 | -211.66 | -300 | -257.49 | 0 | 0 | No
2030-09-06 17:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-06 18:00 | 2030 Initial | 700 | 0 | 124.35 | 0 | 0 | 0 | No
2030-09-06 19:00 | 2030 Initial | 700 | 0 | 155.04 | 0 | 0 | 0 | No
2030-09-06 20:00 | 2030 Initial | 700 | 0 | 155.04 | 0 | 0 | 0 | No
2030-09-06 21:00 | 2030 Initial | 700 | 0 | 189.11 | 0 | 0 | 0 | No
2030-09-06 22:00 | 2030 Initial | 700 | 0 | 90 | 288.84 | 0 | 0 | No
2030-09-06 23:00 | 2030 Initial | 700 | -175.65 | -210 | -11.16 | 0 | 0 | No
2030-09-07 | 2030 Initial | 700 | -280.57 | -510 | -18.68 | 0 | 0 | No
2030-09-07 01:00 | 2030 Initial | 700 | -211.04 | -510 | 24.1 | 0 | 0 | No
2030-09-07 02:00 | 2030 Initial | 700 | -370.44 | -510 | -44.18 | 0 | 0 | No
2030-09-07 03:00 | 2030 Initial | 634.59 | -526 | -510 | -13.1 | 0 | 0 | No
2030-09-07 04:00 | 2030 Initial | 214.59 | -526 | -510 | -223.6 | 0 | 0 | No
2030-09-07 05:00 | 2030 Initial | 299.4 | -526 | -510 | -173.5 | 0 | 0 | No
2030-09-07 06:00 | 2030 Initial | 124.06 | -526 | -510 | -172.88 | 0 | 0 | No
2030-09-07 07:00 | 2030 Initial | 68 | -526 | -510 | 56.91 | 0 | 0 | No
2030-09-07 08:00 | 2030 Initial | 68 | -526 | -510 | 149.74 | 0 | 0 | No
2030-09-07 09:00 | 2030 Initial | -335.63 | -300 | -300 | 102.61 | 0 | 0 | No
2030-09-07 10:00 | 2030 Initial | 0 | 0 | 0 | 219.23 | 0 | 0 | No
2030-09-07 11:00 | 2030 Initial | -234.62 | 300 | 300 | 510 | 0 | 0 | No
2030-09-07 12:00 | 2030 Initial | -654.62 | 505 | 510 | 510 | 0 | 0 | No
2030-09-07 13:00 | 2030 Initial | -654.62 | 505 | 510 | 510 | 0 | 0 | No
2030-09-07 14:00 | 2030 Initial | -244.05 | 505 | 510 | 510 | 0 | 0 | No
2030-09-07 15:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-07 16:00 | 2030 Initial | -169.7 | 205 | 478.11 | 387.32 | 0 | 0 | No
2030-09-07 17:00 | 2030 Initial | 176.53 | 85.06 | 300 | 374.67 | 0 | 0 | No
2030-09-07 18:00 | 2030 Initial | 596.53 | 0 | 0 | 74.67 | 0 | 0 | No
2030-09-07 19:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-07 20:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-09-07 21:00 | 2030 Initial | 607.61 | 505 | 510 | 510 | 0 | 0 | No
2030-09-07 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-07 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 06:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-09-08 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 10:00 | 2030 Initial | 700 | 205 | 231.43 | 510 | 0 | 0 | No
2030-09-08 11:00 | 2030 Initial | 700 | 85.9 | 510 | 510 | 0 | 0 | No
2030-09-08 12:00 | 2030 Initial | 700 | 205 | 316.78 | 510 | 0 | 0 | No
2030-09-08 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 16:00 | 2030 Initial | 700 | 222.09 | 510 | 510 | 0 | 0 | No
2030-09-08 17:00 | 2030 Initial | 700 | 391.35 | 510 | 510 | 0 | 0 | No
2030-09-08 18:00 | 2030 Initial | 280 | 91.35 | 210 | 210 | 0 | 0 | No
2030-09-08 19:00 | 2030 Initial | 280 | 205 | 210 | 210 | 0 | 0 | No
2030-09-08 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 07:00 | 2030 Initial | 691.46 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 08:00 | 2030 Initial | 271.46 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 09:00 | 2030 Initial | -148.54 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 10:00 | 2030 Initial | -568.54 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 14:00 | 2030 Initial | -444.77 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 15:00 | 2030 Initial | -24.77 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 16:00 | 2030 Initial | 395.23 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 17:00 | 2030 Initial | 700 | 205 | 210 | 427.24 | 0 | 0 | No
2030-09-09 18:00 | 2030 Initial | 700 | 146.31 | 510 | 510 | 0 | 0 | No
2030-09-09 19:00 | 2030 Initial | 700 | 446.31 | 510 | 510 | 0 | 0 | No
2030-09-09 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 23:00 | 2030 Initial | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-09-10 | 2030 Initial | 700 | 65.22 | 510 | 510 | 0 | 0 | No
2030-09-10 01:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-10 02:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-10 03:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-10 04:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-10 05:00 | 2030 Initial | 700 | 0 | 478.87 | 510 | 0 | 0 | No
2030-09-10 06:00 | 2030 Initial | 700 | 0 | 178.87 | 498.85 | 0 | 0 | No
2030-09-10 07:00 | 2030 Initial | 700 | -272.1 | -121.13 | 198.85 | 0 | 0 | No
2030-09-10 08:00 | 2030 Initial | 700 | 27.44 | 90 | 498.85 | 0 | 0 | No
2030-09-10 09:00 | 2030 Initial | 627.69 | -272.56 | -210 | 510 | 0 | 0 | No
2030-09-10 10:00 | 2030 Initial | 644.93 | -526 | -510 | 389.18 | 0 | 0 | No
2030-09-10 11:00 | 2030 Initial | 499.55 | -526 | -510 | 365.14 | 0 | 0 | No
2030-09-10 12:00 | 2030 Initial | 177.81 | -526 | -510 | 180.05 | 0 | 0 | No
2030-09-10 13:00 | 2030 Initial | -62.08 | -526 | -510 | 192.27 | 0 | 0 | No
2030-09-10 14:00 | 2030 Initial | 16.76 | -526 | -510 | 220.72 | 0 | 0 | No
2030-09-10 15:00 | 2030 Initial | 436.76 | -526 | -510 | 297.07 | 0 | 0 | No
2030-09-10 16:00 | 2030 Initial | 564.95 | -300 | -510 | 494.23 | 0 | 0 | No
2030-09-10 17:00 | 2030 Initial | 700 | 0 | -297.31 | 466.63 | 0 | 0 | No
2030-09-10 18:00 | 2030 Initial | 700 | 0 | -32.43 | 510 | 0 | 0 | No
2030-09-10 19:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-09-10 20:00 | 2030 Initial | 700 | 0 | 0 | 398.6 | 0 | 0 | No
2030-09-10 21:00 | 2030 Initial | 700 | 0 | -79.54 | 395.03 | 0 | 0 | No
2030-09-10 22:00 | 2030 Initial | 689.24 | -184.74 | -90 | 281.43 | 0 | 0 | No
2030-09-10 23:00 | 2030 Initial | 700 | 115.26 | 210 | 210 | 0 | 0 | No
2030-09-11 | 2030 Initial | 700 | 415.26 | 510 | 510 | 0 | 0 | No
2030-09-11 01:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 02:00 | 2030 Initial | 17.05 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 03:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 04:00 | 2030 Initial | -247.27 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 05:00 | 2030 Initial | -346.49 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 07:00 | 2030 Initial | -389.74 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 08:00 | 2030 Initial | 30.26 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 09:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 10:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 11:00 | 2030 Initial | -9.87 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 12:00 | 2030 Initial | -170.63 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 13:00 | 2030 Initial | -170.63 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 14:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 15:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 16:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 17:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 18:00 | 2030 Initial | 700 | 205 | 510 | 332.99 | 0 | 0 | No
2030-09-11 19:00 | 2030 Initial | 700 | 0 | 510 | 247.11 | 0 | 0 | No
2030-09-11 20:00 | 2030 Initial | 700 | 0 | 510 | 314.3 | 0 | 0 | No
2030-09-11 21:00 | 2030 Initial | 700 | 205 | 510 | 210 | 0 | 0 | No
2030-09-11 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 08:00 | 2030 Initial | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 09:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 10:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 13:00 | 2030 Initial | -700 | 505 | 453.76 | 510 | 0 | 0 | No
2030-09-12 14:00 | 2030 Initial | -700 | 374 | 153.76 | 510 | 0 | 0 | No
2030-09-12 15:00 | 2030 Initial | -700 | 74 | -146.24 | 510 | 0 | 0 | No
2030-09-12 16:00 | 2030 Initial | -280 | -226 | -446.24 | 298.66 | 0 | 0 | No
2030-09-12 17:00 | 2030 Initial | -280 | -526 | -510 | 231.87 | 0 | 0 | No
2030-09-12 18:00 | 2030 Initial | -168.78 | -526 | -510 | 0 | 0 | 0 | No
2030-09-12 19:00 | 2030 Initial | -284.5 | -300 | -413.22 | -275.35 | 0 | 0 | No
2030-09-12 20:00 | 2030 Initial | -475.54 | 0 | -113.22 | -135.57 | 0 | 0 | No
2030-09-12 21:00 | 2030 Initial | -700 | 300 | 186.78 | 164.43 | 0 | 0 | No
2030-09-12 22:00 | 2030 Initial | -700 | 505 | 486.78 | 464.43 | 0 | 0 | Yes
2030-09-12 23:00 | 2030 Initial | -700 | 505 | 510 | 377.34 | 0 | 0 | Yes
2030-09-13 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-13 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-13 02:00 | 2030 Initial | -700 | 505 | 300 | 510 | 0 | 0 | Yes
2030-09-13 03:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 04:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 05:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 06:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 07:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-09-13 08:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-09-13 09:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 10:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 11:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 12:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 13:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 14:00 | 2030 Initial | -700 | 437.19 | 0 | 510 | 0 | 0 | Yes
2030-09-13 15:00 | 2030 Initial | -700 | 137.19 | 0 | 510 | 0 | 0 | Yes
2030-09-13 16:00 | 2030 Initial | -323.1 | -162.81 | 0 | 510 | 0 | 0 | No
2030-09-13 17:00 | 2030 Initial | -448.4 | -462.81 | 0 | 261.17 | 0 | 0 | No
2030-09-13 18:00 | 2030 Initial | -28.4 | -162.81 | 0 | 454.2 | 0 | 0 | No
2030-09-13 19:00 | 2030 Initial | 391.6 | 0 | 0 | 510 | 0 | 0 | No
2030-09-13 20:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-09-13 21:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-09-13 22:00 | 2030 Initial | 700 | 0 | 0 | 370.95 | 0 | 0 | No
2030-09-13 23:00 | 2030 Initial | 700 | 0 | 0 | 199.16 | 0 | 0 | No
2030-09-14 | 2030 Initial | 622.8 | 0 | 0 | 210 | 0 | 0 | No
2030-09-14 01:00 | 2030 Initial | 700 | 272.58 | 0 | 510 | 0 | 0 | No
2030-09-14 02:00 | 2030 Initial | 700 | -27.42 | 0 | 210 | 0 | 0 | No
2030-09-14 03:00 | 2030 Initial | 700 | -327.42 | 0 | -71.05 | 0 | 0 | No
2030-09-14 04:00 | 2030 Initial | 700 | -526 | 0 | -18.03 | 0 | 0 | No
2030-09-14 05:00 | 2030 Initial | 683.56 | -526 | 0 | 14.82 | 0 | 0 | No
2030-09-14 06:00 | 2030 Initial | 557.97 | -462.1 | 0 | 46.93 | 0 | 0 | No
2030-09-14 07:00 | 2030 Initial | 700 | -162.1 | 0 | 140.73 | 0 | 0 | No
2030-09-14 08:00 | 2030 Initial | 695.1 | -462.1 | 0 | 174.47 | 0 | 0 | No
2030-09-14 09:00 | 2030 Initial | 700 | -517.37 | 0 | 204 | 0 | 0 | No
2030-09-14 10:00 | 2030 Initial | 700 | -526 | 0 | 229.1 | 0 | 0 | No
2030-09-14 11:00 | 2030 Initial | 700 | -526 | 0 | 232.48 | 0 | 0 | No
2030-09-14 12:00 | 2030 Initial | 700 | -526 | 0 | 228.23 | 0 | 0 | No
2030-09-14 13:00 | 2030 Initial | 700 | -526 | 0 | 172.69 | 0 | 0 | No
2030-09-14 14:00 | 2030 Initial | 700 | -526 | 0 | 151.11 | 0 | 0 | No
2030-09-14 15:00 | 2030 Initial | 700 | -526 | 0 | 167.2 | 0 | 0 | No
2030-09-14 16:00 | 2030 Initial | 700 | -526 | 0 | 180.77 | 0 | 0 | No
2030-09-14 17:00 | 2030 Initial | 518.67 | -526 | 0 | -74.91 | 0 | 0 | No
2030-09-14 18:00 | 2030 Initial | 700 | -526 | 0 | -222.91 | 0 | 0 | No
2030-09-14 19:00 | 2030 Initial | 700 | -526 | 0 | -54.59 | 0 | 0 | No
2030-09-14 20:00 | 2030 Initial | 526.12 | -526 | 0 | -54.59 | 0 | 0 | No
2030-09-14 21:00 | 2030 Initial | 691.17 | -526 | 0 | 195.9 | 0 | 0 | No
2030-09-14 22:00 | 2030 Initial | 700 | -346.22 | 0 | 131.06 | 0 | 0 | No
2030-09-14 23:00 | 2030 Initial | 700 | -246.57 | 0 | -143.27 | 0 | 0 | No
2030-09-15 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-15 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-15 02:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-15 03:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-15 04:00 | 2030 Initial | 700 | 0 | -187.23 | 0 | 0 | 0 | No
2030-09-15 05:00 | 2030 Initial | 700 | -40.44 | -300 | 0 | 0 | 0 | No
2030-09-15 06:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-15 07:00 | 2030 Initial | 700 | 0 | 0 | 9.97 | 0 | 0 | No
2030-09-15 08:00 | 2030 Initial | 700 | -94.29 | -210 | 0 | 0 | 0 | No
2030-09-15 09:00 | 2030 Initial | 700 | -394.29 | -510 | 32.28 | 0 | 0 | No
2030-09-15 10:00 | 2030 Initial | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-09-15 11:00 | 2030 Initial | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-09-15 12:00 | 2030 Initial | 700 | -526 | -510 | 48.47 | 0 | 0 | No
2030-09-15 13:00 | 2030 Initial | 700 | -526 | -510 | 68.08 | 0 | 0 | No
2030-09-15 14:00 | 2030 Initial | 700 | -526 | -510 | 76.97 | 0 | 0 | No
2030-09-15 15:00 | 2030 Initial | 700 | -485.8 | -510 | 97.35 | 0 | 0 | No
2030-09-15 16:00 | 2030 Initial | 700 | -300 | -347.42 | 168.76 | 0 | 0 | No
2030-09-15 17:00 | 2030 Initial | 700 | 0 | -47.42 | 321.84 | 0 | 0 | No
2030-09-15 18:00 | 2030 Initial | 700 | -300 | -333.52 | 21.84 | 0 | 0 | No
2030-09-15 19:00 | 2030 Initial | 700 | 0 | -33.52 | 210 | 0 | 0 | No
2030-09-15 20:00 | 2030 Initial | 700 | 300 | 266.48 | 510 | 0 | 0 | No
2030-09-15 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-15 22:00 | 2030 Initial | 700 | 291.92 | 510 | 510 | 0 | 0 | No
2030-09-15 23:00 | 2030 Initial | 700 | 0 | 510 | 343.37 | 0 | 0 | No
2030-09-16 | 2030 Initial | 700 | 64.11 | 510 | 510 | 0 | 0 | No
2030-09-16 01:00 | 2030 Initial | 700 | 0 | 510 | 321.24 | 0 | 0 | No
2030-09-16 02:00 | 2030 Initial | 700 | 0 | 510 | 268.77 | 0 | 0 | No
2030-09-16 03:00 | 2030 Initial | 700 | 0 | 510 | 399.14 | 0 | 0 | No
2030-09-16 04:00 | 2030 Initial | 700 | 0 | 510 | 110.02 | 0 | 0 | No
2030-09-16 05:00 | 2030 Initial | 700 | 0 | 510 | 211.52 | 0 | 0 | No
2030-09-16 06:00 | 2030 Initial | 700 | 0 | 510 | 437.54 | 0 | 0 | No
2030-09-16 07:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-16 08:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-16 09:00 | 2030 Initial | 700 | 205 | 510 | 503.87 | 0 | 0 | No
2030-09-16 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-16 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-16 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-16 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-16 14:00 | 2030 Initial | 700 | 352.26 | 510 | 510 | 0 | 0 | No
2030-09-16 15:00 | 2030 Initial | 700 | 52.26 | 210 | 372.05 | 0 | 0 | No
2030-09-16 16:00 | 2030 Initial | 700 | 0 | 465.93 | 445.4 | 0 | 0 | No
2030-09-16 17:00 | 2030 Initial | 700 | 278.44 | 510 | 510 | 0 | 0 | No
2030-09-16 18:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-16 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-16 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-16 21:00 | 2030 Initial | 700 | 474.54 | 510 | 510 | 0 | 0 | No
2030-09-16 22:00 | 2030 Initial | 700 | 174.54 | 510 | 510 | 0 | 0 | No
2030-09-16 23:00 | 2030 Initial | 700 | 0 | 510 | 358.67 | 0 | 0 | No
2030-09-17 | 2030 Initial | 700 | 0 | 435.71 | 58.67 | 0 | 0 | No
2030-09-17 01:00 | 2030 Initial | 700 | 0 | 507.21 | 0 | 0 | 0 | No
2030-09-17 02:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-09-17 03:00 | 2030 Initial | 700 | 0 | 434.29 | 0 | 0 | 0 | No
2030-09-17 04:00 | 2030 Initial | 700 | 0 | 466.58 | 0 | 0 | 0 | No
2030-09-17 05:00 | 2030 Initial | 700 | 0 | 466.04 | 0 | 0 | 0 | No
2030-09-17 06:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-09-17 07:00 | 2030 Initial | 700 | 0 | 332.04 | 155.11 | 0 | 0 | No
2030-09-17 08:00 | 2030 Initial | 700 | 0 | 90 | 305.9 | 0 | 0 | No
2030-09-17 09:00 | 2030 Initial | 700 | -198.78 | -210 | 309.79 | 0 | 0 | No
2030-09-17 10:00 | 2030 Initial | 700 | -498.78 | -510 | 244.14 | 0 | 0 | No
2030-09-17 11:00 | 2030 Initial | 700 | -526 | -510 | 263.02 | 0 | 0 | No
2030-09-17 12:00 | 2030 Initial | 700 | -526 | -510 | 178.31 | 0 | 0 | No
2030-09-17 13:00 | 2030 Initial | 700 | -526 | -510 | 220.14 | 0 | 0 | No
2030-09-17 14:00 | 2030 Initial | 700 | -526 | -510 | 250.28 | 0 | 0 | No
2030-09-17 15:00 | 2030 Initial | 700 | -526 | -428.59 | 254.5 | 0 | 0 | No
2030-09-17 16:00 | 2030 Initial | 700 | -226 | -128.59 | 408.27 | 0 | 0 | No
2030-09-17 17:00 | 2030 Initial | 700 | 38.94 | 171.41 | 510 | 0 | 0 | No
2030-09-17 18:00 | 2030 Initial | 700 | 338.94 | 471.41 | 510 | 0 | 0 | No
2030-09-17 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-17 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-17 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-17 22:00 | 2030 Initial | 700 | 247.88 | 368.71 | 406.67 | 0 | 0 | No
2030-09-17 23:00 | 2030 Initial | 700 | 0 | 68.71 | 106.67 | 0 | 0 | No
2030-09-18 | 2030 Initial | 700 | 0 | -124.11 | 406.67 | 0 | 0 | No
2030-09-18 01:00 | 2030 Initial | 700 | 0 | -171.37 | 206.51 | 0 | 0 | No
2030-09-18 02:00 | 2030 Initial | 700 | 0 | -377.77 | 163.58 | 0 | 0 | No
2030-09-18 03:00 | 2030 Initial | 700 | 0 | -77.77 | 106.31 | 0 | 0 | No
2030-09-18 04:00 | 2030 Initial | 700 | 0 | -158.7 | 20.84 | 0 | 0 | No
2030-09-18 05:00 | 2030 Initial | 700 | 0 | -236.72 | 84.43 | 0 | 0 | No
2030-09-18 06:00 | 2030 Initial | 700 | 0 | -207.29 | 141.54 | 0 | 0 | No
2030-09-18 07:00 | 2030 Initial | 700 | 0 | -90.42 | 389.91 | 0 | 0 | No
2030-09-18 08:00 | 2030 Initial | 700 | 0 | -234.24 | 464.69 | 0 | 0 | No
2030-09-18 09:00 | 2030 Initial | 700 | -226 | -404.25 | 400.07 | 0 | 0 | No
2030-09-18 10:00 | 2030 Initial | 700 | -526 | -510 | 257.75 | 0 | 0 | No
2030-09-18 11:00 | 2030 Initial | 700 | -526 | -510 | 282.54 | 0 | 0 | No
2030-09-18 12:00 | 2030 Initial | 700 | -526 | -510 | 263.03 | 0 | 0 | No
2030-09-18 13:00 | 2030 Initial | 700 | -526 | -510 | 260.79 | 0 | 0 | No
2030-09-18 14:00 | 2030 Initial | 700 | -526 | -510 | 122.83 | 0 | 0 | No
2030-09-18 15:00 | 2030 Initial | 700 | -526 | -510 | 83.4 | 0 | 0 | No
2030-09-18 16:00 | 2030 Initial | 700 | -526 | -510 | 352 | 0 | 0 | No
2030-09-18 17:00 | 2030 Initial | 699.56 | -300 | -300 | 457.11 | 0 | 0 | No
2030-09-18 18:00 | 2030 Initial | 700 | 0 | 0 | 366.74 | 0 | 0 | No
2030-09-18 19:00 | 2030 Initial | 700 | 0 | 288.56 | 318.41 | 0 | 0 | No
2030-09-18 20:00 | 2030 Initial | 700 | 0 | 510 | 194.18 | 0 | 0 | No
2030-09-18 21:00 | 2030 Initial | 700 | 205 | 510 | 237.44 | 0 | 0 | No
2030-09-18 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-18 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 04:00 | 2030 Initial | 700 | 434.32 | 510 | 510 | 0 | 0 | No
2030-09-19 05:00 | 2030 Initial | 280 | 134.32 | 210 | 210 | 0 | 0 | No
2030-09-19 06:00 | 2030 Initial | 700 | 0 | 0 | 214.16 | 0 | 0 | No
2030-09-19 07:00 | 2030 Initial | 700 | 0 | 0 | 432.33 | 0 | 0 | No
2030-09-19 08:00 | 2030 Initial | 700 | 0 | -129.92 | 192.9 | 0 | 0 | No
2030-09-19 09:00 | 2030 Initial | 700 | 0 | -429.92 | 338.78 | 0 | 0 | No
2030-09-19 10:00 | 2030 Initial | 374.92 | -300 | -510 | 510 | 0 | 0 | No
2030-09-19 11:00 | 2030 Initial | 0 | -509 | -510 | 510 | 0 | 0 | No
2030-09-19 12:00 | 2030 Initial | 305.34 | -209 | -210 | 510 | 0 | 0 | No
2030-09-19 13:00 | 2030 Initial | 336.22 | 0 | 0 | 510 | 0 | 0 | No
2030-09-19 14:00 | 2030 Initial | 700 | 79.45 | 0 | 510 | 0 | 0 | No
2030-09-19 15:00 | 2030 Initial | 280 | -220.55 | -300 | 510 | 0 | 0 | No
2030-09-19 16:00 | 2030 Initial | 408.12 | -300 | -97.57 | 510 | 0 | 0 | No
2030-09-19 17:00 | 2030 Initial | 700 | 0 | 202.43 | 510 | 0 | 0 | No
2030-09-19 18:00 | 2030 Initial | 700 | 86.3 | 502.43 | 510 | 0 | 0 | No
2030-09-19 19:00 | 2030 Initial | 700 | 386.3 | 510 | 510 | 0 | 0 | No
2030-09-19 20:00 | 2030 Initial | 700 | 117.63 | 510 | 510 | 0 | 0 | No
2030-09-19 21:00 | 2030 Initial | 700 | 63.91 | 510 | 510 | 0 | 0 | No
2030-09-19 22:00 | 2030 Initial | 700 | 63.91 | 510 | 510 | 0 | 0 | No
2030-09-19 23:00 | 2030 Initial | 700 | 0 | 510 | 279.36 | 0 | 0 | No
2030-09-20 | 2030 Initial | 700 | 0 | 510 | 246.48 | 0 | 0 | No
2030-09-20 01:00 | 2030 Initial | 700 | 0 | 510 | 220.75 | 0 | 0 | No
2030-09-20 02:00 | 2030 Initial | 700 | 0 | 510 | 231.4 | 0 | 0 | No
2030-09-20 03:00 | 2030 Initial | 700 | 43.39 | 510 | 510 | 0 | 0 | No
2030-09-20 04:00 | 2030 Initial | 700 | 197.6 | 351.56 | 510 | 0 | 0 | No
2030-09-20 05:00 | 2030 Initial | 700 | 0 | 51.56 | 210 | 0 | 0 | No
2030-09-20 06:00 | 2030 Initial | 700 | 0 | 88.34 | 0 | 0 | 0 | No
2030-09-20 07:00 | 2030 Initial | 700 | 0 | 376.95 | 0 | 0 | 0 | No
2030-09-20 08:00 | 2030 Initial | 700 | 49.21 | 90 | 300 | 0 | 0 | No
2030-09-20 09:00 | 2030 Initial | 700 | -15.8 | -210 | 0 | 0 | 0 | No
2030-09-20 10:00 | 2030 Initial | 633.42 | -315.8 | -510 | -101.34 | 0 | 0 | No
2030-09-20 11:00 | 2030 Initial | 614.2 | -526 | -510 | -127.21 | 0 | 0 | No
2030-09-20 12:00 | 2030 Initial | 700 | -526 | -510 | -127.21 | 0 | 0 | No
2030-09-20 13:00 | 2030 Initial | 477.23 | -526 | -510 | -183.85 | 0 | 0 | No
2030-09-20 14:00 | 2030 Initial | 700 | -526 | -510 | -53.65 | 0 | 0 | No
2030-09-20 15:00 | 2030 Initial | 700 | -357.97 | -430.81 | -5.55 | 0 | 0 | No
2030-09-20 16:00 | 2030 Initial | 700 | -57.97 | -130.81 | -88.06 | 0 | 0 | No
2030-09-20 17:00 | 2030 Initial | 700 | 156.61 | 169.19 | 210 | 0 | 0 | No
2030-09-20 18:00 | 2030 Initial | 700 | -143.39 | -90 | -90 | 0 | 0 | No
2030-09-20 19:00 | 2030 Initial | 700 | 156.61 | 210 | 210 | 0 | 0 | No
2030-09-20 20:00 | 2030 Initial | 700 | 456.61 | 510 | 510 | 0 | 0 | No
2030-09-20 21:00 | 2030 Initial | 700 | 505 | 510 | 457.94 | 0 | 0 | No
2030-09-20 22:00 | 2030 Initial | 700 | 425.55 | 510 | 372.26 | 0 | 0 | No
2030-09-20 23:00 | 2030 Initial | 700 | 125.55 | 510 | 276.06 | 0 | 0 | No
2030-09-21 | 2030 Initial | 700 | 0 | 510 | 19.74 | 0 | 0 | No
2030-09-21 01:00 | 2030 Initial | 700 | 0 | 510 | 147.07 | 0 | 0 | No
2030-09-21 02:00 | 2030 Initial | 700 | 0 | 510 | 34.49 | 0 | 0 | No
2030-09-21 03:00 | 2030 Initial | 700 | 0 | 474.68 | 0 | 0 | 0 | No
2030-09-21 04:00 | 2030 Initial | 700 | 0 | 361.8 | 0 | 0 | 0 | No
2030-09-21 05:00 | 2030 Initial | 700 | 0 | 174.34 | 0 | 0 | 0 | No
2030-09-21 06:00 | 2030 Initial | 700 | 0 | 226.9 | 0 | 0 | 0 | No
2030-09-21 07:00 | 2030 Initial | 700 | 0 | 234.36 | 0 | 0 | 0 | No
2030-09-21 08:00 | 2030 Initial | 700 | 0 | -65.64 | 0 | 0 | 0 | No
2030-09-21 09:00 | 2030 Initial | 553.13 | -300 | -365.64 | -300 | 0 | 0 | No
2030-09-21 10:00 | 2030 Initial | 427.96 | -526 | -510 | -292.9 | 0 | 0 | No
2030-09-21 11:00 | 2030 Initial | 280 | -526 | -510 | -261.57 | 0 | 0 | No
2030-09-21 12:00 | 2030 Initial | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-09-21 13:00 | 2030 Initial | 700 | -526 | -510 | -221.95 | 0 | 0 | No
2030-09-21 14:00 | 2030 Initial | 700 | -526 | -510 | -463.89 | 0 | 0 | No
2030-09-21 15:00 | 2030 Initial | 700 | -526 | -510 | -402.29 | 0 | 0 | No
2030-09-21 16:00 | 2030 Initial | 700 | -297.23 | -510 | -159.21 | 0 | 0 | No
2030-09-21 17:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-21 18:00 | 2030 Initial | 700 | 0 | -354.47 | 0 | 0 | 0 | No
2030-09-21 19:00 | 2030 Initial | 700 | 0 | -54.47 | 0 | 0 | 0 | No
2030-09-21 20:00 | 2030 Initial | 700 | 0 | 210 | 16.23 | 0 | 0 | No
2030-09-21 21:00 | 2030 Initial | 700 | 300 | 510 | 316.23 | 0 | 0 | No
2030-09-21 22:00 | 2030 Initial | 700 | 0 | 510 | 335.69 | 0 | 0 | No
2030-09-21 23:00 | 2030 Initial | 700 | 0 | 300 | 57.53 | 0 | 0 | No
2030-09-22 | 2030 Initial | 700 | -110.39 | 0 | -242.47 | 0 | 0 | No
2030-09-22 01:00 | 2030 Initial | 700 | 0 | -190.48 | 0 | 0 | 0 | No
2030-09-22 02:00 | 2030 Initial | 700 | 0 | -490.48 | -10.46 | 0 | 0 | No
2030-09-22 03:00 | 2030 Initial | 700 | -22.86 | -510 | -126.64 | 0 | 0 | No
2030-09-22 04:00 | 2030 Initial | 700 | -275.92 | -510 | -170.85 | 0 | 0 | No
2030-09-22 05:00 | 2030 Initial | 700 | -469.85 | -510 | -236.23 | 0 | 0 | No
2030-09-22 06:00 | 2030 Initial | 293.34 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 07:00 | 2030 Initial | 439.08 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 08:00 | 2030 Initial | 427.37 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 09:00 | 2030 Initial | 94.24 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 10:00 | 2030 Initial | -325.76 | -226 | -210 | -210 | 0 | 0 | No
2030-09-22 11:00 | 2030 Initial | -700 | 74 | 90 | 90 | 0 | 0 | No
2030-09-22 12:00 | 2030 Initial | -700 | 374 | 390 | 390 | 0 | 0 | No
2030-09-22 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-22 15:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-22 16:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 17:00 | 2030 Initial | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 18:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 05:00 | 2030 Initial | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-09-23 06:00 | 2030 Initial | 700 | 0 | 169.46 | 210 | 0 | 0 | No
2030-09-23 07:00 | 2030 Initial | 700 | 0 | 469.46 | 504.72 | 0 | 0 | No
2030-09-23 08:00 | 2030 Initial | 700 | 145.33 | 510 | 510 | 0 | 0 | No
2030-09-23 09:00 | 2030 Initial | 700 | 10.52 | 510 | 510 | 0 | 0 | No
2030-09-23 10:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-23 11:00 | 2030 Initial | 700 | 0 | 479.9 | 210 | 0 | 0 | No
2030-09-23 12:00 | 2030 Initial | 700 | 0 | 424.76 | 69.08 | 0 | 0 | No
2030-09-23 13:00 | 2030 Initial | 700 | 0 | 282.96 | 0 | 0 | 0 | No
2030-09-23 14:00 | 2030 Initial | 700 | 0 | 219.59 | 0 | 0 | 0 | No
2030-09-23 15:00 | 2030 Initial | 700 | 0 | 502.99 | 210 | 0 | 0 | No
2030-09-23 16:00 | 2030 Initial | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-09-23 17:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 18:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 19:00 | 2030 Initial | 700 | 382.36 | 510 | 510 | 0 | 0 | No
2030-09-23 20:00 | 2030 Initial | 700 | 277.89 | 510 | 510 | 0 | 0 | No
2030-09-23 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-23 22:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-09-23 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 01:00 | 2030 Initial | 692.42 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 02:00 | 2030 Initial | 515.8 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 03:00 | 2030 Initial | 366.11 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 04:00 | 2030 Initial | 366.11 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 06:00 | 2030 Initial | 700 | 300 | 228.54 | 349.56 | 0 | 0 | No
2030-09-24 07:00 | 2030 Initial | 700 | 0 | -71.46 | 49.56 | 0 | 0 | No
2030-09-24 08:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-24 09:00 | 2030 Initial | 700 | 0 | 31.15 | 0 | 0 | 0 | No
2030-09-24 10:00 | 2030 Initial | 700 | 256 | 331.15 | 300 | 0 | 0 | No
2030-09-24 11:00 | 2030 Initial | 700 | 300 | 367.26 | 458.82 | 0 | 0 | No
2030-09-24 12:00 | 2030 Initial | 700 | 0 | 67.26 | 158.82 | 0 | 0 | No
2030-09-24 13:00 | 2030 Initial | 428.79 | 0 | 0 | 36.61 | 0 | 0 | No
2030-09-24 14:00 | 2030 Initial | 453.37 | -226 | -210 | 2.88 | 0 | 0 | No
2030-09-24 15:00 | 2030 Initial | 700 | -526 | -510 | 121.43 | 0 | 0 | No
2030-09-24 16:00 | 2030 Initial | 700 | -526 | -510 | 210 | 0 | 0 | No
2030-09-24 17:00 | 2030 Initial | 700 | -226 | -308.22 | 510 | 0 | 0 | No
2030-09-24 18:00 | 2030 Initial | 700 | 0 | -13.52 | 510 | 0 | 0 | No
2030-09-24 19:00 | 2030 Initial | 700 | 0 | 286.48 | 510 | 0 | 0 | No
2030-09-24 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-24 21:00 | 2030 Initial | 700 | 0 | 293.76 | 510 | 0 | 0 | No
2030-09-24 22:00 | 2030 Initial | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-09-24 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 | 2030 Initial | 542.74 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 01:00 | 2030 Initial | 247.21 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 02:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 03:00 | 2030 Initial | -137.38 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 04:00 | 2030 Initial | -406.08 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 05:00 | 2030 Initial | -393.01 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 06:00 | 2030 Initial | -181.47 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 07:00 | 2030 Initial | 238.53 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 08:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 09:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 13:00 | 2030 Initial | -700 | 505 | 510 | 462.31 | 0 | 0 | Yes
2030-09-25 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 15:00 | 2030 Initial | -522.73 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 16:00 | 2030 Initial | -102.73 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 17:00 | 2030 Initial | 317.27 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 18:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 16:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 17:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 18:00 | 2030 Initial | 700 | 396.58 | 510 | 510 | 0 | 0 | No
2030-09-26 19:00 | 2030 Initial | 700 | 396.58 | 510 | 367.9 | 0 | 0 | No
2030-09-26 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 07:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-09-27 08:00 | 2030 Initial | 700 | 495.59 | 510 | 510 | 0 | 0 | No
2030-09-27 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 11:00 | 2030 Initial | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-09-27 12:00 | 2030 Initial | 700 | -95 | -90 | 228.79 | 0 | 0 | No
2030-09-27 13:00 | 2030 Initial | 700 | -315.85 | -390 | 189.64 | 0 | 0 | No
2030-09-27 14:00 | 2030 Initial | 700 | -40.44 | -451.19 | 185.89 | 0 | 0 | No
2030-09-27 15:00 | 2030 Initial | 700 | 0 | -151.19 | 222.01 | 0 | 0 | No
2030-09-27 16:00 | 2030 Initial | 700 | 0 | 95.35 | 317.71 | 0 | 0 | No
2030-09-27 17:00 | 2030 Initial | 700 | 0 | 395.35 | 427.95 | 0 | 0 | No
2030-09-27 18:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-27 19:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-27 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-27 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-27 22:00 | 2030 Initial | 700 | 0 | 368.35 | 210 | 0 | 0 | No
2030-09-27 23:00 | 2030 Initial | 700 | 0 | 68.35 | 22.46 | 0 | 0 | No
2030-09-28 | 2030 Initial | 700 | -147.43 | -231.65 | -76.32 | 0 | 0 | No
2030-09-28 01:00 | 2030 Initial | 700 | -226 | -434.74 | 0 | 0 | 0 | No
2030-09-28 02:00 | 2030 Initial | 700 | -526 | -510 | -89.27 | 0 | 0 | No
2030-09-28 03:00 | 2030 Initial | 700 | -226 | -510 | 0 | 0 | 0 | No
2030-09-28 04:00 | 2030 Initial | 700 | 0 | -347.68 | 0 | 0 | 0 | No
2030-09-28 05:00 | 2030 Initial | 700 | 0 | -259.77 | 0 | 0 | 0 | No
2030-09-28 06:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-28 07:00 | 2030 Initial | 700 | 0 | -227.61 | 0 | 0 | 0 | No
2030-09-28 08:00 | 2030 Initial | 700 | 0 | -312.72 | 102.62 | 0 | 0 | No
2030-09-28 09:00 | 2030 Initial | 700 | -232.72 | -510 | 157.57 | 0 | 0 | No
2030-09-28 10:00 | 2030 Initial | 502.2 | -361.29 | -510 | 125.83 | 0 | 0 | No
2030-09-28 11:00 | 2030 Initial | 82.2 | -293.61 | -510 | 129.9 | 0 | 0 | No
2030-09-28 12:00 | 2030 Initial | -337.8 | -526 | -510 | 91.98 | 0 | 0 | No
2030-09-28 13:00 | 2030 Initial | 82.2 | -526 | -510 | -83.26 | 0 | 0 | No
2030-09-28 14:00 | 2030 Initial | 502.2 | -526 | -510 | -383.26 | 0 | 0 | No
2030-09-28 15:00 | 2030 Initial | 700 | -526 | -510 | -373.85 | 0 | 0 | No
2030-09-28 16:00 | 2030 Initial | 700 | -465.52 | -510 | -115.68 | 0 | 0 | No
2030-09-28 17:00 | 2030 Initial | 700 | -165.52 | -210 | 184.32 | 0 | 0 | No
2030-09-28 18:00 | 2030 Initial | 700 | 0 | 90 | 164.29 | 0 | 0 | No
2030-09-28 19:00 | 2030 Initial | 700 | 0 | 237.55 | 210 | 0 | 0 | No
2030-09-28 20:00 | 2030 Initial | 700 | 261.74 | 510 | 510 | 0 | 0 | No
2030-09-28 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-28 22:00 | 2030 Initial | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-09-28 23:00 | 2030 Initial | 700 | 0 | 510 | 489.43 | 0 | 0 | No
2030-09-29 | 2030 Initial | 700 | 0 | 510 | 361.48 | 0 | 0 | No
2030-09-29 01:00 | 2030 Initial | 700 | 0 | 510 | 361.48 | 0 | 0 | No
2030-09-29 02:00 | 2030 Initial | 700 | 0 | 510 | 324.98 | 0 | 0 | No
2030-09-29 03:00 | 2030 Initial | 700 | 0 | 510 | 142.35 | 0 | 0 | No
2030-09-29 04:00 | 2030 Initial | 700 | 0 | 510 | 43.36 | 0 | 0 | No
2030-09-29 05:00 | 2030 Initial | 700 | 0 | 510 | 22.45 | 0 | 0 | No
2030-09-29 06:00 | 2030 Initial | 700 | 0 | 390.45 | 52.68 | 0 | 0 | No
2030-09-29 07:00 | 2030 Initial | 700 | 0 | 183.22 | 114.35 | 0 | 0 | No
2030-09-29 08:00 | 2030 Initial | 700 | 0 | -116.78 | 95.74 | 0 | 0 | No
2030-09-29 09:00 | 2030 Initial | 317.78 | -300 | -416.78 | 71.4 | 0 | 0 | No
2030-09-29 10:00 | 2030 Initial | 86.61 | -526 | -510 | 41.57 | 0 | 0 | No
2030-09-29 11:00 | 2030 Initial | -22.23 | -526 | -510 | -47.03 | 0 | 0 | No
2030-09-29 12:00 | 2030 Initial | -108.15 | -526 | -510 | -22.79 | 0 | 0 | No
2030-09-29 13:00 | 2030 Initial | 280 | -526 | -510 | -58.29 | 0 | 0 | No
2030-09-29 14:00 | 2030 Initial | 700 | -526 | -510 | -143.77 | 0 | 0 | No
2030-09-29 15:00 | 2030 Initial | 700 | -526 | -510 | -144.13 | 0 | 0 | No
2030-09-29 16:00 | 2030 Initial | 280 | -526 | -510 | 66.72 | 0 | 0 | No
2030-09-29 17:00 | 2030 Initial | 425.82 | -526 | -510 | 14.97 | 0 | 0 | No
2030-09-29 18:00 | 2030 Initial | 185.24 | -526 | -510 | -4.78 | 0 | 0 | No
2030-09-29 19:00 | 2030 Initial | 93.17 | -526 | -510 | 31.21 | 0 | 0 | No
2030-09-29 20:00 | 2030 Initial | -128.5 | -526 | -510 | -80.84 | 0 | 0 | No
2030-09-29 21:00 | 2030 Initial | -546.61 | -526 | -510 | -247.78 | 0 | 0 | No
2030-09-29 22:00 | 2030 Initial | -700 | -526 | -510 | -276.19 | 0 | 0 | No
2030-09-29 23:00 | 2030 Initial | -280 | -226 | -250.9 | -224.42 | 0 | 0 | No
2030-09-30 | 2030 Initial | -257.33 | 74 | 49.1 | 75.58 | 0 | 0 | No
2030-09-30 01:00 | 2030 Initial | -140 | 374 | 349.1 | 375.58 | 0 | 0 | Yes
2030-09-30 02:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-30 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-30 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-30 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 16:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 17:00 | 2030 Initial | 700 | 351.59 | 510 | 510 | 0 | 0 | No
2030-09-30 18:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 05:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-10-01 06:00 | 2030 Initial | 700 | 0 | 70.09 | 0 | 0 | 0 | No
2030-10-01 07:00 | 2030 Initial | 700 | 0 | 370.09 | 92.34 | 0 | 0 | No
2030-10-01 08:00 | 2030 Initial | 700 | 0 | 510 | 162.57 | 0 | 0 | No
2030-10-01 09:00 | 2030 Initial | 700 | 0 | 288.08 | 140.93 | 0 | 0 | No
2030-10-01 10:00 | 2030 Initial | 700 | 0 | -11.92 | 85.24 | 0 | 0 | No
2030-10-01 11:00 | 2030 Initial | 700 | 0 | -311.92 | 0 | 0 | 0 | No
2030-10-01 12:00 | 2030 Initial | 700 | 0 | -169.14 | 0 | 0 | 0 | No
2030-10-01 13:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-01 14:00 | 2030 Initial | 700 | 0 | 79.06 | 0 | 0 | 0 | No
2030-10-01 15:00 | 2030 Initial | 700 | 0 | 379.06 | 263.83 | 0 | 0 | No
2030-10-01 16:00 | 2030 Initial | 700 | 0 | 510 | 159.66 | 0 | 0 | No
2030-10-01 17:00 | 2030 Initial | 700 | 205 | 289.07 | 210 | 0 | 0 | No
2030-10-01 18:00 | 2030 Initial | 700 | -95 | -10.93 | -90 | 0 | 0 | No
2030-10-01 19:00 | 2030 Initial | 700 | 205 | 289.07 | 210 | 0 | 0 | No
2030-10-01 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 21:00 | 2030 Initial | 700 | 414.01 | 510 | 510 | 0 | 0 | No
2030-10-01 22:00 | 2030 Initial | 700 | 114.01 | 236.79 | 287.52 | 0 | 0 | No
2030-10-01 23:00 | 2030 Initial | 700 | -70.05 | -63.21 | -12.48 | 0 | 0 | No
2030-10-02 | 2030 Initial | 700 | 0 | -324.98 | 0 | 0 | 0 | No
2030-10-02 01:00 | 2030 Initial | 700 | -176.02 | -90 | 7.91 | 0 | 0 | No
2030-10-02 02:00 | 2030 Initial | 700 | 123.98 | 210 | 264.11 | 0 | 0 | No
2030-10-02 03:00 | 2030 Initial | 700 | 423.98 | 510 | 510 | 0 | 0 | No
2030-10-02 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-02 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-02 06:00 | 2030 Initial | 700 | 205 | 210 | 346.87 | 0 | 0 | No
2030-10-02 07:00 | 2030 Initial | 700 | 0 | 144.14 | 510 | 0 | 0 | No
2030-10-02 08:00 | 2030 Initial | 700 | 300 | 444.14 | 510 | 0 | 0 | No
2030-10-02 09:00 | 2030 Initial | 700 | 0 | 221.64 | 510 | 0 | 0 | No
2030-10-02 10:00 | 2030 Initial | 280 | 166.49 | 390 | 510 | 0 | 0 | No
2030-10-02 11:00 | 2030 Initial | -37.04 | 95.27 | 90 | 510 | 0 | 0 | No
2030-10-02 12:00 | 2030 Initial | -457.04 | -14.08 | -210 | 510 | 0 | 0 | No
2030-10-02 13:00 | 2030 Initial | -700 | -314.08 | -510 | 510 | 0 | 0 | No
2030-10-02 14:00 | 2030 Initial | -700 | -235.94 | -510 | 510 | 0 | 0 | No
2030-10-02 15:00 | 2030 Initial | -571.74 | -526 | -510 | 466.07 | 0 | 0 | No
2030-10-02 16:00 | 2030 Initial | -151.74 | -273.49 | -300 | 510 | 0 | 0 | No
2030-10-02 17:00 | 2030 Initial | 268.26 | 0 | 0 | 510 | 0 | 0 | No
2030-10-02 18:00 | 2030 Initial | 688.26 | 0 | 0 | 510 | 0 | 0 | No
2030-10-02 19:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-10-02 20:00 | 2030 Initial | 700 | 0 | 155.01 | 510 | 0 | 0 | No
2030-10-02 21:00 | 2030 Initial | 700 | 205 | 364.65 | 381.73 | 0 | 0 | No
2030-10-02 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-02 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 06:00 | 2030 Initial | 281.87 | 205 | 210 | 458.72 | 0 | 0 | No
2030-10-03 07:00 | 2030 Initial | 700 | 0 | 165.7 | 399.56 | 0 | 0 | No
2030-10-03 08:00 | 2030 Initial | 700 | 107.6 | 465.7 | 510 | 0 | 0 | No
2030-10-03 09:00 | 2030 Initial | 700 | 206.61 | 300 | 510 | 0 | 0 | No
2030-10-03 10:00 | 2030 Initial | 374.82 | 0 | 0 | 262.71 | 0 | 0 | No
2030-10-03 11:00 | 2030 Initial | 0 | -280.6 | -300 | -37.29 | 0 | 0 | No
2030-10-03 12:00 | 2030 Initial | 0 | 0 | -303.45 | 0 | 0 | 0 | No
2030-10-03 13:00 | 2030 Initial | 0 | 0 | -81.88 | 0 | 0 | 0 | No
2030-10-03 14:00 | 2030 Initial | 259.52 | 0 | 0 | 0 | 0 | 0 | No
2030-10-03 15:00 | 2030 Initial | 492.79 | 0 | 0 | 92.76 | 0 | 0 | No
2030-10-03 16:00 | 2030 Initial | 700 | 0 | 300 | 136.08 | 0 | 0 | No
2030-10-03 17:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-10-03 18:00 | 2030 Initial | 700 | 0 | 510 | 263.44 | 0 | 0 | No
2030-10-03 19:00 | 2030 Initial | 700 | 205 | 510 | 466.8 | 0 | 0 | No
2030-10-03 20:00 | 2030 Initial | 700 | 505 | 510 | 405.27 | 0 | 0 | No
2030-10-03 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 22:00 | 2030 Initial | 560 | 505 | 510 | 368.32 | 0 | 0 | Yes
2030-10-03 23:00 | 2030 Initial | 140 | 505 | 510 | 83.15 | 0 | 0 | Yes
2030-10-04 | 2030 Initial | -236.46 | 505 | 510 | -1.36 | 0 | 0 | Yes
2030-10-04 01:00 | 2030 Initial | -656.46 | 505 | 510 | 130.89 | 0 | 0 | Yes
2030-10-04 02:00 | 2030 Initial | -580.3 | 505 | 510 | 167.83 | 0 | 0 | Yes
2030-10-04 03:00 | 2030 Initial | -700 | 505 | 510 | -2.25 | 0 | 0 | Yes
2030-10-04 04:00 | 2030 Initial | -700 | 505 | 510 | 202.56 | 0 | 0 | Yes
2030-10-04 05:00 | 2030 Initial | -700 | 505 | 300 | 256.55 | 0 | 0 | Yes
2030-10-04 06:00 | 2030 Initial | -700 | 292.72 | 0 | 0 | 0 | 0 | Yes
2030-10-04 07:00 | 2030 Initial | -700 | -7.28 | -300 | -300 | 0 | 0 | No
2030-10-04 08:00 | 2030 Initial | -424.58 | 0 | 0 | 0 | 0 | 0 | No
2030-10-04 09:00 | 2030 Initial | -466.38 | 0 | 0 | 137.55 | 0 | 0 | No
2030-10-04 10:00 | 2030 Initial | -634.2 | 0 | 0 | 210 | 0 | 0 | No
2030-10-04 11:00 | 2030 Initial | -214.2 | -139.02 | -300 | 510 | 0 | 0 | No
2030-10-04 12:00 | 2030 Initial | -544.11 | 0 | 0 | 510 | 0 | 0 | No
2030-10-04 13:00 | 2030 Initial | -341.27 | 0 | 0 | 510 | 0 | 0 | No
2030-10-04 14:00 | 2030 Initial | -4.46 | 0 | -275.47 | 510 | 0 | 0 | No
2030-10-04 15:00 | 2030 Initial | 280 | -226 | -253.21 | 510 | 0 | 0 | No
2030-10-04 16:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-04 17:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-04 18:00 | 2030 Initial | 700 | -517.76 | -510 | 510 | 0 | 0 | No
2030-10-04 19:00 | 2030 Initial | 700 | -217.76 | -510 | 510 | 0 | 0 | No
2030-10-04 20:00 | 2030 Initial | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-10-04 21:00 | 2030 Initial | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-10-04 22:00 | 2030 Initial | 700 | -210.11 | -510 | 410.21 | 0 | 0 | No
2030-10-04 23:00 | 2030 Initial | 700 | -151.3 | -395.81 | 458.17 | 0 | 0 | No
2030-10-05 | 2030 Initial | 700 | 0 | -95.81 | 291.68 | 0 | 0 | No
2030-10-05 01:00 | 2030 Initial | 700 | 0 | 195.14 | 385.27 | 0 | 0 | No
2030-10-05 02:00 | 2030 Initial | 700 | 0 | 384.78 | 510 | 0 | 0 | No
2030-10-05 03:00 | 2030 Initial | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-10-05 04:00 | 2030 Initial | 700 | -226 | -210 | 210 | 0 | 0 | No
2030-10-05 05:00 | 2030 Initial | 700 | -526 | -510 | 52.58 | 0 | 0 | No
2030-10-05 06:00 | 2030 Initial | 700 | -526 | -510 | 250.42 | 0 | 0 | No
2030-10-05 07:00 | 2030 Initial | 700 | -526 | -510 | 80.08 | 0 | 0 | No
2030-10-05 08:00 | 2030 Initial | 700 | -526 | -510 | 258.47 | 0 | 0 | No
2030-10-05 09:00 | 2030 Initial | 700 | -526 | -510 | 499.39 | 0 | 0 | No
2030-10-05 10:00 | 2030 Initial | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-05 11:00 | 2030 Initial | 700 | -526 | -510 | 433.93 | 0 | 0 | No
2030-10-05 12:00 | 2030 Initial | 700 | -526 | -510 | 234.11 | 0 | 0 | No
2030-10-05 13:00 | 2030 Initial | 700 | -526 | -510 | -65.89 | 0 | 0 | No
2030-10-05 14:00 | 2030 Initial | 700 | -360.24 | -510 | -152.63 | 0 | 0 | No
2030-10-05 15:00 | 2030 Initial | 700 | -60.24 | -413.36 | 139.25 | 0 | 0 | No
2030-10-05 16:00 | 2030 Initial | 700 | 0 | -510 | 245.22 | 0 | 0 | No
2030-10-05 17:00 | 2030 Initial | 700 | 0 | -455.15 | 314.35 | 0 | 0 | No
2030-10-05 18:00 | 2030 Initial | 700 | 0 | -155.15 | 63.35 | 0 | 0 | No
2030-10-05 19:00 | 2030 Initial | 700 | 0 | 0 | 363.35 | 0 | 0 | No
2030-10-05 20:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-10-05 21:00 | 2030 Initial | 700 | 0 | -49.35 | 510 | 0 | 0 | No
2030-10-05 22:00 | 2030 Initial | 700 | 185.87 | 210 | 457.11 | 0 | 0 | No
2030-10-05 23:00 | 2030 Initial | 700 | 485.87 | 510 | 510 | 0 | 0 | No
2030-10-06 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-06 01:00 | 2030 Initial | 382 | 505 | 510 | 510 | 0 | 0 | No
2030-10-06 02:00 | 2030 Initial | 6.69 | 505 | 510 | 510 | 0 | 0 | No
2030-10-06 03:00 | 2030 Initial | 75.53 | 505 | 510 | 510 | 0 | 0 | No
2030-10-06 04:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-10-06 05:00 | 2030 Initial | 192.69 | 205 | 210 | 510 | 0 | 0 | No
2030-10-06 06:00 | 2030 Initial | 513.43 | -95 | -90 | 387.16 | 0 | 0 | No
2030-10-06 07:00 | 2030 Initial | 700 | -395 | -390 | 510 | 0 | 0 | No
2030-10-06 08:00 | 2030 Initial | 700 | -95 | -90 | 510 | 0 | 0 | No
2030-10-06 09:00 | 2030 Initial | 362.78 | 0 | 0 | 442.1 | 0 | 0 | No
2030-10-06 10:00 | 2030 Initial | 369.98 | 0 | 0 | 360.74 | 0 | 0 | No
2030-10-06 11:00 | 2030 Initial | 46.31 | 0 | 0 | 185.93 | 0 | 0 | No
2030-10-06 12:00 | 2030 Initial | -358.49 | 0 | 0 | 468.61 | 0 | 0 | No
2030-10-06 13:00 | 2030 Initial | -560 | 0 | 0 | 323.88 | 0 | 0 | No
2030-10-06 14:00 | 2030 Initial | -140 | 0 | -13.35 | 217.93 | 0 | 0 | No
2030-10-06 15:00 | 2030 Initial | 280 | -300 | -313.35 | -82.07 | 0 | 0 | No
2030-10-06 16:00 | 2030 Initial | 700 | -526 | -510 | -382.07 | 0 | 0 | No
2030-10-06 17:00 | 2030 Initial | 700 | -422.02 | -510 | -510 | 0 | 0 | No
2030-10-06 18:00 | 2030 Initial | 700 | -122.02 | -210 | -210 | 0 | 0 | No
2030-10-06 19:00 | 2030 Initial | 700 | 177.98 | 90 | 90 | 0 | 0 | No
2030-10-06 20:00 | 2030 Initial | 700 | 477.98 | 390 | 390 | 0 | 0 | No
2030-10-06 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-06 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-06 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 16:00 | 2030 Initial | 700 | 219.14 | 510 | 510 | 0 | 0 | No
2030-10-07 17:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-10-07 18:00 | 2030 Initial | 700 | 44.11 | 510 | 510 | 0 | 0 | No
2030-10-07 19:00 | 2030 Initial | 700 | 94.69 | 510 | 510 | 0 | 0 | No
2030-10-07 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-10-07 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-10-07 22:00 | 2030 Initial | 700 | 0 | 210 | 421.27 | 0 | 0 | No
2030-10-07 23:00 | 2030 Initial | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-10-08 | 2030 Initial | 700 | 237.3 | 510 | 510 | 0 | 0 | No
2030-10-08 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 07:00 | 2030 Initial | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-10-08 08:00 | 2030 Initial | 700 | 0 | 218.82 | 510 | 0 | 0 | No
2030-10-08 09:00 | 2030 Initial | 700 | 205 | 391.83 | 510 | 0 | 0 | No
2030-10-08 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 14:00 | 2030 Initial | 700 | 205 | 210 | 486.34 | 0 | 0 | No
2030-10-08 15:00 | 2030 Initial | 700 | -95 | -90 | 186.34 | 0 | 0 | No
2030-10-08 16:00 | 2030 Initial | 700 | 0 | -256.48 | 425.29 | 0 | 0 | No
2030-10-08 17:00 | 2030 Initial | 700 | 71.2 | 14.08 | 510 | 0 | 0 | No
2030-10-08 18:00 | 2030 Initial | 700 | 0 | -285.92 | 510 | 0 | 0 | No
2030-10-08 19:00 | 2030 Initial | 700 | 0 | -228.16 | 510 | 0 | 0 | No
2030-10-08 20:00 | 2030 Initial | 700 | 138.9 | 71.84 | 510 | 0 | 0 | No
2030-10-08 21:00 | 2030 Initial | 700 | -126.54 | -228.16 | 266.64 | 0 | 0 | No
2030-10-08 22:00 | 2030 Initial | 700 | -55.82 | -454.17 | -33.36 | 0 | 0 | No
2030-10-08 23:00 | 2030 Initial | 700 | -95 | -154.17 | 19.67 | 0 | 0 | No
2030-10-09 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-09 01:00 | 2030 Initial | 700 | 300 | 300 | 300 | 0 | 0 | No
2030-10-09 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 04:00 | 2030 Initial | 446 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 05:00 | 2030 Initial | 26 | 205 | 210 | 210 | 0 | 0 | No
2030-10-09 06:00 | 2030 Initial | 446 | 0 | 63.37 | 0 | 0 | 0 | No
2030-10-09 07:00 | 2030 Initial | 700 | 0 | 63.37 | 0 | 0 | 0 | No
2030-10-09 08:00 | 2030 Initial | 700 | 0 | 178.78 | 0 | 0 | 0 | No
2030-10-09 09:00 | 2030 Initial | 420 | 0 | 478.78 | 165.42 | 0 | 0 | No
2030-10-09 10:00 | 2030 Initial | 0 | 205 | 510 | 465.42 | 0 | 0 | No
2030-10-09 11:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 15:00 | 2030 Initial | -310.89 | 275.73 | 300 | 510 | 0 | 0 | No
2030-10-09 16:00 | 2030 Initial | 109.11 | 0 | 0 | 324.98 | 0 | 0 | No
2030-10-09 17:00 | 2030 Initial | 529.11 | 0 | -64.42 | 510 | 0 | 0 | No
2030-10-09 18:00 | 2030 Initial | 700 | 0 | 69.49 | 510 | 0 | 0 | No
2030-10-09 19:00 | 2030 Initial | 700 | 0 | 62.8 | 510 | 0 | 0 | No
2030-10-09 20:00 | 2030 Initial | 700 | 0 | 332.75 | 510 | 0 | 0 | No
2030-10-09 21:00 | 2030 Initial | 700 | 292.64 | 510 | 510 | 0 | 0 | No
2030-10-09 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 02:00 | 2030 Initial | 332.02 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 03:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 04:00 | 2030 Initial | 115.53 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 05:00 | 2030 Initial | 224.35 | 300 | 229.5 | 300 | 0 | 0 | No
2030-10-10 06:00 | 2030 Initial | -195.65 | 0 | -70.5 | 0 | 0 | 0 | No
2030-10-10 07:00 | 2030 Initial | 224.35 | 0 | 0 | 0 | 0 | 0 | No
2030-10-10 08:00 | 2030 Initial | 644.35 | 0 | 0 | 109.32 | 0 | 0 | No
2030-10-10 09:00 | 2030 Initial | 700 | 109.42 | 300 | 409.32 | 0 | 0 | No
2030-10-10 10:00 | 2030 Initial | 566.62 | 409.42 | 510 | 510 | 0 | 0 | No
2030-10-10 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 13:00 | 2030 Initial | 700 | 265.8 | 510 | 510 | 0 | 0 | No
2030-10-10 14:00 | 2030 Initial | 700 | 36.24 | 510 | 510 | 0 | 0 | No
2030-10-10 15:00 | 2030 Initial | 700 | 236.31 | 210 | 510 | 0 | 0 | No
2030-10-10 16:00 | 2030 Initial | 280 | -63.69 | -90 | 214.41 | 0 | 0 | No
2030-10-10 17:00 | 2030 Initial | 700 | 0 | 0 | 421.32 | 0 | 0 | No
2030-10-10 18:00 | 2030 Initial | 700 | 0 | 118.95 | 510 | 0 | 0 | No
2030-10-10 19:00 | 2030 Initial | 700 | 0 | 98.35 | 510 | 0 | 0 | No
2030-10-10 20:00 | 2030 Initial | 700 | 0 | 387.89 | 510 | 0 | 0 | No
2030-10-10 21:00 | 2030 Initial | 700 | 0 | 87.89 | 319.04 | 0 | 0 | No
2030-10-10 22:00 | 2030 Initial | 700 | 205 | 210 | 286.68 | 0 | 0 | No
2030-10-10 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 06:00 | 2030 Initial | 589.81 | 205 | 210 | 210 | 0 | 0 | No
2030-10-11 07:00 | 2030 Initial | 700 | 0 | 408.53 | 0 | 0 | 0 | No
2030-10-11 08:00 | 2030 Initial | 700 | 0 | 510 | 233.1 | 0 | 0 | No
2030-10-11 09:00 | 2030 Initial | 700 | 24.28 | 484.32 | 391.02 | 0 | 0 | No
2030-10-11 10:00 | 2030 Initial | 700 | 0 | 184.32 | 91.02 | 0 | 0 | No
2030-10-11 11:00 | 2030 Initial | 700 | 0 | -115.68 | -191.52 | 0 | 0 | No
2030-10-11 12:00 | 2030 Initial | 700 | 0 | -327.35 | 0 | 0 | 0 | No
2030-10-11 13:00 | 2030 Initial | 700 | 0 | -196.99 | 0 | 0 | 0 | No
2030-10-11 14:00 | 2030 Initial | 700 | 0 | -209.02 | 0 | 0 | 0 | No
2030-10-11 15:00 | 2030 Initial | 700 | 0 | 59.53 | 0 | 0 | 0 | No
2030-10-11 16:00 | 2030 Initial | 700 | 0 | 359.53 | 254.58 | 0 | 0 | No
2030-10-11 17:00 | 2030 Initial | 700 | 90.14 | 510 | 510 | 0 | 0 | No
2030-10-11 18:00 | 2030 Initial | 700 | 0 | 246.67 | 210 | 0 | 0 | No
2030-10-11 19:00 | 2030 Initial | 700 | 0 | 264.44 | 0 | 0 | 0 | No
2030-10-11 20:00 | 2030 Initial | 700 | 0 | 510 | 32.59 | 0 | 0 | No
2030-10-11 21:00 | 2030 Initial | 700 | 0 | 510 | 332.59 | 0 | 0 | No
2030-10-11 22:00 | 2030 Initial | 700 | 0 | 347.03 | 209.11 | 0 | 0 | No
2030-10-11 23:00 | 2030 Initial | 700 | 0 | 47.03 | 83.31 | 0 | 0 | No
2030-10-12 | 2030 Initial | 700 | -3.07 | -252.97 | -37.54 | 0 | 0 | No
2030-10-12 01:00 | 2030 Initial | 700 | 0 | -442.47 | 10.35 | 0 | 0 | No
2030-10-12 02:00 | 2030 Initial | 700 | -156.84 | -510 | 71.9 | 0 | 0 | No
2030-10-12 03:00 | 2030 Initial | 700 | -402.66 | -510 | -94.34 | 0 | 0 | No
2030-10-12 04:00 | 2030 Initial | 280 | -526 | -510 | -170.94 | 0 | 0 | No
2030-10-12 05:00 | 2030 Initial | -140 | -526 | -510 | -121.59 | 0 | 0 | No
2030-10-12 06:00 | 2030 Initial | -324.28 | -526 | -510 | -24.59 | 0 | 0 | No
2030-10-12 07:00 | 2030 Initial | -527.11 | -526 | -510 | -316.56 | 0 | 0 | No
2030-10-12 08:00 | 2030 Initial | -584.53 | -526 | -510 | -422.69 | 0 | 0 | No
2030-10-12 09:00 | 2030 Initial | -700 | -526 | -510 | -389.24 | 0 | 0 | No
2030-10-12 10:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 11:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 12:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 13:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 14:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 15:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 16:00 | 2030 Initial | -655.67 | -526 | -510 | -339.93 | 0 | 0 | No
2030-10-12 17:00 | 2030 Initial | -235.67 | -262.37 | -510 | -39.93 | 0 | 0 | No
2030-10-12 18:00 | 2030 Initial | 184.33 | -82.91 | -510 | 154.14 | 0 | 0 | No
2030-10-12 19:00 | 2030 Initial | 604.33 | -32.27 | -497.85 | 454.14 | 0 | 0 | No
2030-10-12 20:00 | 2030 Initial | 700 | 0 | -197.85 | 509.27 | 0 | 0 | No
2030-10-12 21:00 | 2030 Initial | 700 | 205 | 102.15 | 510 | 0 | 0 | No
2030-10-12 22:00 | 2030 Initial | 700 | 505 | 402.15 | 510 | 0 | 0 | No
2030-10-12 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 05:00 | 2030 Initial | 700 | 300 | 479.47 | 510 | 0 | 0 | No
2030-10-13 06:00 | 2030 Initial | 700 | 0 | 179.47 | 210 | 0 | 0 | No
2030-10-13 07:00 | 2030 Initial | 700 | 0 | -120.53 | -32.9 | 0 | 0 | No
2030-10-13 08:00 | 2030 Initial | 700 | 0 | -24.32 | 0 | 0 | 0 | No
2030-10-13 09:00 | 2030 Initial | 567.3 | 205 | 210 | -154.7 | 0 | 0 | No
2030-10-13 10:00 | 2030 Initial | 147.3 | 505 | 510 | 135.96 | 0 | 0 | Yes
2030-10-13 11:00 | 2030 Initial | -272.7 | 505 | 510 | 394.64 | 0 | 0 | Yes
2030-10-13 12:00 | 2030 Initial | -692.7 | 505 | 510 | 335.32 | 0 | 0 | Yes
2030-10-13 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-13 14:00 | 2030 Initial | -377.29 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-13 15:00 | 2030 Initial | 42.71 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 16:00 | 2030 Initial | 462.71 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 17:00 | 2030 Initial | 700 | 205 | 420.33 | 210 | 0 | 0 | No
2030-10-13 18:00 | 2030 Initial | 280 | 0 | 171.48 | 0 | 0 | 0 | No
2030-10-13 19:00 | 2030 Initial | 700 | 300 | 471.48 | 300 | 0 | 0 | No
2030-10-13 20:00 | 2030 Initial | 700 | 505 | 510 | 267.59 | 0 | 0 | Yes
2030-10-13 21:00 | 2030 Initial | 700 | 505 | 510 | 271.27 | 0 | 0 | Yes
2030-10-13 22:00 | 2030 Initial | 700 | 505 | 510 | 435.41 | 0 | 0 | Yes
2030-10-13 23:00 | 2030 Initial | 700 | 505 | 510 | 477.25 | 0 | 0 | Yes
2030-10-14 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-14 02:00 | 2030 Initial | 700 | 505 | 510 | 236.27 | 0 | 0 | Yes
2030-10-14 03:00 | 2030 Initial | 700 | 505 | 510 | 221.61 | 0 | 0 | Yes
2030-10-14 04:00 | 2030 Initial | 700 | 505 | 510 | 190.96 | 0 | 0 | Yes
2030-10-14 05:00 | 2030 Initial | 700 | 505 | 510 | 490.96 | 0 | 0 | Yes
2030-10-14 06:00 | 2030 Initial | 700 | 505 | 510 | 195.4 | 0 | 0 | Yes
2030-10-14 07:00 | 2030 Initial | 700 | 505 | 510 | 226.67 | 0 | 0 | No
2030-10-14 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 16:00 | 2030 Initial | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-10-14 17:00 | 2030 Initial | 700 | 49.93 | 510 | 510 | 0 | 0 | No
2030-10-14 18:00 | 2030 Initial | 700 | 349.93 | 510 | 217.66 | 0 | 0 | No
2030-10-14 19:00 | 2030 Initial | 700 | 398.48 | 510 | 510 | 0 | 0 | No
2030-10-14 20:00 | 2030 Initial | 700 | 398.48 | 510 | 449.52 | 0 | 0 | No
2030-10-14 21:00 | 2030 Initial | 700 | 505 | 510 | 465.44 | 0 | 0 | No
2030-10-14 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 | 2030 Initial | 700 | 505 | 510 | 427.29 | 0 | 0 | No
2030-10-15 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 04:00 | 2030 Initial | 700 | 205 | 428.64 | 210 | 0 | 0 | No
2030-10-15 05:00 | 2030 Initial | 700 | 0 | 249.52 | -90 | 0 | 0 | No
2030-10-15 06:00 | 2030 Initial | 700 | 0 | 510 | 44.94 | 0 | 0 | No
2030-10-15 07:00 | 2030 Initial | 700 | 205 | 510 | 344.17 | 0 | 0 | No
2030-10-15 08:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 09:00 | 2030 Initial | 700 | 443.87 | 510 | 510 | 0 | 0 | No
2030-10-15 10:00 | 2030 Initial | 700 | 143.87 | 510 | 343.3 | 0 | 0 | No
2030-10-15 11:00 | 2030 Initial | 700 | 0 | 468.87 | 43.3 | 0 | 0 | No
2030-10-15 12:00 | 2030 Initial | 700 | 0 | 271.68 | 0 | 0 | 0 | No
2030-10-15 13:00 | 2030 Initial | 700 | 0 | 239.24 | 0 | 0 | 0 | No
2030-10-15 14:00 | 2030 Initial | 700 | 0 | 328.95 | 0 | 0 | 0 | No
2030-10-15 15:00 | 2030 Initial | 700 | 0 | 470.36 | 0 | 0 | 0 | No
2030-10-15 16:00 | 2030 Initial | 700 | 119.83 | 353.72 | 300 | 0 | 0 | No
2030-10-15 17:00 | 2030 Initial | 700 | 0 | 53.72 | 0 | 0 | 0 | No
2030-10-15 18:00 | 2030 Initial | 700 | 20.5 | 210 | 210 | 0 | 0 | No
2030-10-15 19:00 | 2030 Initial | 700 | 320.5 | 510 | 510 | 0 | 0 | No
2030-10-15 20:00 | 2030 Initial | 700 | 505 | 510 | 351.27 | 0 | 0 | No
2030-10-15 21:00 | 2030 Initial | 700 | 205 | 510 | 399.21 | 0 | 0 | No
2030-10-15 22:00 | 2030 Initial | 700 | 0 | 510 | 462.13 | 0 | 0 | No
2030-10-15 23:00 | 2030 Initial | 700 | 0 | 504.07 | 162.13 | 0 | 0 | No
2030-10-16 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-10-16 01:00 | 2030 Initial | 700 | 0 | 448.45 | 0 | 0 | 0 | No
2030-10-16 02:00 | 2030 Initial | 700 | 0 | 459.44 | 0 | 0 | 0 | No
2030-10-16 03:00 | 2030 Initial | 700 | 0 | 159.44 | 0 | 0 | 0 | No
2030-10-16 04:00 | 2030 Initial | 700 | 0 | 78.92 | 0 | 0 | 0 | No
2030-10-16 05:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-16 06:00 | 2030 Initial | 700 | 0 | 183.49 | 0 | 0 | 0 | No
2030-10-16 07:00 | 2030 Initial | 700 | 0 | 243.25 | 0 | 0 | 0 | No
2030-10-16 08:00 | 2030 Initial | 700 | 0 | 510 | 115.44 | 0 | 0 | No
2030-10-16 09:00 | 2030 Initial | 700 | 0 | 510 | 153.35 | 0 | 0 | No
2030-10-16 10:00 | 2030 Initial | 700 | 0 | 210 | 0 | 0 | 0 | No
2030-10-16 11:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-16 12:00 | 2030 Initial | 420 | 0 | 0 | 0 | 0 | 0 | No
2030-10-16 13:00 | 2030 Initial | 0 | 0 | 0 | 0 | 0 | 0 | No
2030-10-16 14:00 | 2030 Initial | 216.45 | 0 | 0 | 0 | 0 | 0 | No
2030-10-16 15:00 | 2030 Initial | 636.45 | 0 | 0 | 0 | 0 | 0 | No
2030-10-16 16:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-16 17:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-16 18:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-16 19:00 | 2030 Initial | 700 | 0 | 168.9 | 0 | 0 | 0 | No
2030-10-16 20:00 | 2030 Initial | 700 | 0 | 468.9 | 163.25 | 0 | 0 | No
2030-10-16 21:00 | 2030 Initial | 700 | 0 | 503.75 | 0 | 0 | 0 | No
2030-10-16 22:00 | 2030 Initial | 700 | 0 | 264.73 | 0 | 0 | 0 | No
2030-10-16 23:00 | 2030 Initial | 700 | -123.48 | -35.27 | -300 | 0 | 0 | No
2030-10-17 | 2030 Initial | 700 | 0 | -16.05 | 0 | 0 | 0 | No
2030-10-17 01:00 | 2030 Initial | 700 | 0 | -316.05 | 0 | 0 | 0 | No
2030-10-17 02:00 | 2030 Initial | 700 | 0 | -443.56 | 0 | 0 | 0 | No
2030-10-17 03:00 | 2030 Initial | 700 | 0 | -143.56 | 0 | 0 | 0 | No
2030-10-17 04:00 | 2030 Initial | 700 | 0 | -143.56 | 0 | 0 | 0 | No
2030-10-17 05:00 | 2030 Initial | 700 | 0 | -222.96 | 0 | 0 | 0 | No
2030-10-17 06:00 | 2030 Initial | 700 | 0 | -300 | 0 | 0 | 0 | No
2030-10-17 07:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-17 08:00 | 2030 Initial | 700 | 0 | 300 | 22.01 | 0 | 0 | No
2030-10-17 09:00 | 2030 Initial | 700 | 0 | 213.99 | 0 | 0 | 0 | No
2030-10-17 10:00 | 2030 Initial | 700 | 0 | -86.01 | 0 | 0 | 0 | No
2030-10-17 11:00 | 2030 Initial | 700 | 0 | -386.01 | 0 | 0 | 0 | No
2030-10-17 12:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 13:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 14:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 15:00 | 2030 Initial | 700 | 0 | -315.35 | 0 | 0 | 0 | No
2030-10-17 16:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 17:00 | 2030 Initial | 700 | 0 | -300.29 | 0 | 0 | 0 | No
2030-10-17 18:00 | 2030 Initial | 700 | 0 | -0.29 | 0 | 0 | 0 | No
2030-10-17 19:00 | 2030 Initial | 700 | 0 | 165.26 | 0 | 0 | 0 | No
2030-10-17 20:00 | 2030 Initial | 700 | 300 | 465.26 | 300 | 0 | 0 | No
2030-10-17 21:00 | 2030 Initial | 700 | 0 | 510 | 285.98 | 0 | 0 | No
2030-10-17 22:00 | 2030 Initial | 700 | 0 | 210 | 116.92 | 0 | 0 | No
2030-10-17 23:00 | 2030 Initial | 700 | 0 | -90 | -40.85 | 0 | 0 | No
2030-10-18 | 2030 Initial | 700 | 0 | 120.61 | 0 | 0 | 0 | No
2030-10-18 01:00 | 2030 Initial | 700 | 0 | 187.82 | 0 | 0 | 0 | No
2030-10-18 02:00 | 2030 Initial | 700 | 0 | 323.82 | 0 | 0 | 0 | No
2030-10-18 03:00 | 2030 Initial | 700 | 0 | 23.82 | 0 | 0 | 0 | No
2030-10-18 04:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-18 05:00 | 2030 Initial | 700 | 0 | 260.42 | 0 | 0 | 0 | No
2030-10-18 06:00 | 2030 Initial | 700 | 0 | 158.78 | 0 | 0 | 0 | No
2030-10-18 07:00 | 2030 Initial | 700 | 0 | -71.23 | 0 | 0 | 0 | No
2030-10-18 08:00 | 2030 Initial | 700 | -300 | -371.23 | -300 | 0 | 0 | No
2030-10-18 09:00 | 2030 Initial | 700 | -300 | -398.44 | -233.72 | 0 | 0 | No
2030-10-18 10:00 | 2030 Initial | 700 | 0 | -98.44 | 66.28 | 0 | 0 | No
2030-10-18 11:00 | 2030 Initial | 700 | 0 | 175.64 | 129.84 | 0 | 0 | No
2030-10-18 12:00 | 2030 Initial | 700 | 0 | 0 | 200.68 | 0 | 0 | No
2030-10-18 13:00 | 2030 Initial | 700 | 0 | 55.73 | 325.02 | 0 | 0 | No
2030-10-18 14:00 | 2030 Initial | 700 | 0 | 55.73 | 59.15 | 0 | 0 | No
2030-10-18 15:00 | 2030 Initial | 700 | 0 | -227.09 | 0 | 0 | 0 | No
2030-10-18 16:00 | 2030 Initial | 700 | 0 | -42.41 | 0 | 0 | 0 | No
2030-10-18 17:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-18 18:00 | 2030 Initial | 700 | 0 | -300 | -295.21 | 0 | 0 | No
2030-10-18 19:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-18 20:00 | 2030 Initial | 700 | 0 | 269.53 | 0 | 0 | 0 | No
2030-10-18 21:00 | 2030 Initial | 700 | 0 | 90 | 38.29 | 0 | 0 | No
2030-10-18 22:00 | 2030 Initial | 700 | 0 | -210 | -162.96 | 0 | 0 | No
2030-10-18 23:00 | 2030 Initial | 692.64 | -300 | -510 | -1.51 | 0 | 0 | No
2030-10-19 | 2030 Initial | 700 | -526 | -510 | 19.23 | 0 | 0 | No
2030-10-19 01:00 | 2030 Initial | 700 | -254.52 | -210 | 116.35 | 0 | 0 | No
2030-10-19 02:00 | 2030 Initial | 700 | 45.48 | 90 | 416.35 | 0 | 0 | No
2030-10-19 03:00 | 2030 Initial | 700 | 345.48 | 390 | 510 | 0 | 0 | No
2030-10-19 04:00 | 2030 Initial | 676.56 | 300 | 300 | 425.46 | 0 | 0 | No
2030-10-19 05:00 | 2030 Initial | 256.56 | 0 | 0 | 125.46 | 0 | 0 | No
2030-10-19 06:00 | 2030 Initial | -163.44 | -300 | -300 | -174.54 | 0 | 0 | No
2030-10-19 07:00 | 2030 Initial | -371.55 | -526 | -510 | -474.54 | 0 | 0 | No
2030-10-19 08:00 | 2030 Initial | -95.02 | -375.33 | -390 | -275.69 | 0 | 0 | No
2030-10-19 09:00 | 2030 Initial | 324.98 | -75.33 | -90 | 24.31 | 0 | 0 | No
2030-10-19 10:00 | 2030 Initial | -95.02 | 224.67 | 210 | 324.31 | 0 | 0 | No
2030-10-19 11:00 | 2030 Initial | -515.02 | 505 | 510 | 510 | 0 | 0 | No
2030-10-19 12:00 | 2030 Initial | -352.78 | 505 | 510 | 510 | 0 | 0 | No
2030-10-19 13:00 | 2030 Initial | 67.22 | 505 | 510 | 510 | 0 | 0 | No
2030-10-19 14:00 | 2030 Initial | -168.74 | 505 | 510 | 510 | 0 | 0 | No
2030-10-19 15:00 | 2030 Initial | -26.65 | 505 | 510 | 510 | 0 | 0 | No
2030-10-19 16:00 | 2030 Initial | 386.11 | 205 | 210 | 210 | 0 | 0 | No
2030-10-19 17:00 | 2030 Initial | 700 | 154.71 | 510 | 281.45 | 0 | 0 | No
2030-10-19 18:00 | 2030 Initial | 700 | 205 | 379.33 | 210 | 0 | 0 | No
2030-10-19 19:00 | 2030 Initial | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-10-19 20:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-10-19 21:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-10-19 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-19 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 03:00 | 2030 Initial | -700 | 505 | 510 | 388.44 | 0 | 0 | Yes
2030-10-20 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 13:00 | 2030 Initial | -700 | 505 | 510 | 345.61 | 0 | 0 | Yes
2030-10-20 14:00 | 2030 Initial | -700 | 505 | 510 | 321.92 | 0 | 0 | Yes
2030-10-20 15:00 | 2030 Initial | -700 | 505 | 510 | 289.85 | 0 | 0 | Yes
2030-10-20 16:00 | 2030 Initial | -700 | 300 | 510 | 139.19 | 0 | 0 | Yes
2030-10-20 17:00 | 2030 Initial | -465.27 | 0 | 210 | -160.81 | 0 | 0 | No
2030-10-20 18:00 | 2030 Initial | -45.27 | 205 | 458.49 | 45.33 | 0 | 0 | No
2030-10-20 19:00 | 2030 Initial | 280 | 505 | 510 | 345.33 | 0 | 0 | No
2030-10-20 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 22:00 | 2030 Initial | 700 | 505 | 510 | 469.8 | 0 | 0 | Yes
2030-10-20 23:00 | 2030 Initial | 700 | 505 | 510 | 394.25 | 0 | 0 | Yes
2030-10-21 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 07:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 08:00 | 2030 Initial | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-10-21 09:00 | 2030 Initial | 700 | 0 | -90 | 510 | 0 | 0 | No
2030-10-21 10:00 | 2030 Initial | 700 | 0 | -390 | 510 | 0 | 0 | No
2030-10-21 11:00 | 2030 Initial | 700 | -226 | -510 | 458.2 | 0 | 0 | No
2030-10-21 12:00 | 2030 Initial | 700 | -526 | -510 | 321.7 | 0 | 0 | No
2030-10-21 13:00 | 2030 Initial | 700 | -526 | -510 | 103.75 | 0 | 0 | No
2030-10-21 14:00 | 2030 Initial | 700 | -526 | -510 | -196.25 | 0 | 0 | No
2030-10-21 15:00 | 2030 Initial | 700 | -526 | -510 | -496.25 | 0 | 0 | No
2030-10-21 16:00 | 2030 Initial | 700 | -298.28 | -510 | -510 | 0 | 0 | No
2030-10-21 17:00 | 2030 Initial | 700 | 0 | -510 | -347.59 | 0 | 0 | No
2030-10-21 18:00 | 2030 Initial | 700 | 0 | -390 | -191.62 | 0 | 0 | No
2030-10-21 19:00 | 2030 Initial | 700 | 0 | -90 | -335.73 | 0 | 0 | No
2030-10-21 20:00 | 2030 Initial | 700 | 205 | 210 | -57.01 | 0 | 0 | No
2030-10-21 21:00 | 2030 Initial | 700 | 505 | 510 | 242.99 | 0 | 0 | Yes
2030-10-21 22:00 | 2030 Initial | 700 | 505 | 510 | 186.19 | 0 | 0 | Yes
2030-10-21 23:00 | 2030 Initial | 700 | 505 | 510 | 40.26 | 0 | 0 | Yes
2030-10-22 | 2030 Initial | 700 | 505 | 510 | 327.83 | 0 | 0 | Yes
2030-10-22 01:00 | 2030 Initial | 700 | 505 | 510 | 27.83 | 0 | 0 | Yes
2030-10-22 02:00 | 2030 Initial | 700 | 505 | 510 | 63.31 | 0 | 0 | Yes
2030-10-22 03:00 | 2030 Initial | 700 | 505 | 510 | 220.54 | 0 | 0 | Yes
2030-10-22 04:00 | 2030 Initial | 700 | 505 | 510 | 503.45 | 0 | 0 | Yes
2030-10-22 05:00 | 2030 Initial | 700 | 505 | 510 | 203.45 | 0 | 0 | Yes
2030-10-22 06:00 | 2030 Initial | 280 | 205 | 210 | -26.21 | 0 | 0 | No
2030-10-22 07:00 | 2030 Initial | 700 | -31.95 | -90 | 84.36 | 0 | 0 | No
2030-10-22 08:00 | 2030 Initial | 700 | 0 | 210 | 178.58 | 0 | 0 | No
2030-10-22 09:00 | 2030 Initial | 700 | 0 | 399.06 | 315.7 | 0 | 0 | No
2030-10-22 10:00 | 2030 Initial | 700 | 0 | 99.06 | 15.7 | 0 | 0 | No
2030-10-22 11:00 | 2030 Initial | 280 | 0 | -10.93 | 72.68 | 0 | 0 | No
2030-10-22 12:00 | 2030 Initial | 276.4 | 0 | -274.69 | 0 | 0 | 0 | No
2030-10-22 13:00 | 2030 Initial | 0 | 0 | -57.52 | 0 | 0 | 0 | No
2030-10-22 14:00 | 2030 Initial | 280 | 0 | -108.03 | 0 | 0 | 0 | No
2030-10-22 15:00 | 2030 Initial | 700 | 0 | -363.6 | -50.36 | 0 | 0 | No
2030-10-22 16:00 | 2030 Initial | 700 | 0 | -63.6 | 0 | 0 | 0 | No
2030-10-22 17:00 | 2030 Initial | 700 | 0 | -363.6 | -91.28 | 0 | 0 | No
2030-10-22 18:00 | 2030 Initial | 489.17 | 0 | -510 | -318.59 | 0 | 0 | No
2030-10-22 19:00 | 2030 Initial | 700 | 0 | -510 | -510 | 0 | 0 | No
2030-10-22 20:00 | 2030 Initial | 700 | -78.73 | -510 | -290.74 | 0 | 0 | No
2030-10-22 21:00 | 2030 Initial | 484.94 | -226 | -510 | -76.88 | 0 | 0 | No
2030-10-22 22:00 | 2030 Initial | 64.94 | -526 | -510 | -153.24 | 0 | 0 | No
2030-10-22 23:00 | 2030 Initial | 182.36 | -526 | -510 | -72.81 | 0 | 0 | No
2030-10-23 | 2030 Initial | 280 | -526 | -510 | -173.86 | 0 | 0 | No
2030-10-23 01:00 | 2030 Initial | 700 | -526 | -510 | -150.05 | 0 | 0 | No
2030-10-23 02:00 | 2030 Initial | 700 | -300 | -492.97 | -50.77 | 0 | 0 | No
2030-10-23 03:00 | 2030 Initial | 700 | 0 | -192.97 | 249.23 | 0 | 0 | No
2030-10-23 04:00 | 2030 Initial | 700 | 300 | 107.03 | 443.41 | 0 | 0 | No
2030-10-23 05:00 | 2030 Initial | 280 | 0 | -192.97 | 143.41 | 0 | 0 | No
2030-10-23 06:00 | 2030 Initial | 700 | 0 | -484.49 | 151.09 | 0 | 0 | No
2030-10-23 07:00 | 2030 Initial | 700 | 0 | -440.59 | 432.07 | 0 | 0 | No
2030-10-23 08:00 | 2030 Initial | 700 | 0 | -140.59 | 369.69 | 0 | 0 | No
2030-10-23 09:00 | 2030 Initial | 700 | 0 | -324.47 | 436.63 | 0 | 0 | No
2030-10-23 10:00 | 2030 Initial | 700 | 0 | -510 | 291.47 | 0 | 0 | No
2030-10-23 11:00 | 2030 Initial | 548.33 | 0 | -510 | 400.82 | 0 | 0 | No
2030-10-23 12:00 | 2030 Initial | 128.33 | -19.79 | -510 | 131.38 | 0 | 0 | No
2030-10-23 13:00 | 2030 Initial | 0 | -97.5 | -510 | -168.62 | 0 | 0 | No
2030-10-23 14:00 | 2030 Initial | 280 | -221.26 | -510 | -84.81 | 0 | 0 | No
2030-10-23 15:00 | 2030 Initial | 700 | 0 | -510 | 129.13 | 0 | 0 | No
2030-10-23 16:00 | 2030 Initial | 700 | 0 | -510 | 388.55 | 0 | 0 | No
2030-10-23 17:00 | 2030 Initial | 700 | 0 | -361.06 | 375.92 | 0 | 0 | No
2030-10-23 18:00 | 2030 Initial | 642.04 | 0 | -234.38 | 510 | 0 | 0 | No
2030-10-23 19:00 | 2030 Initial | 222.04 | -226 | -510 | 450.31 | 0 | 0 | No
2030-10-23 20:00 | 2030 Initial | -197.96 | -526 | -510 | 292.53 | 0 | 0 | No
2030-10-23 21:00 | 2030 Initial | 140 | -526 | -510 | 14.72 | 0 | 0 | No
2030-10-23 22:00 | 2030 Initial | -280 | -226 | -210 | 110.13 | 0 | 0 | No
2030-10-23 23:00 | 2030 Initial | -700 | 74 | 90 | 253.09 | 0 | 0 | Yes
2030-10-24 | 2030 Initial | -700 | 374 | 390 | 303.06 | 0 | 0 | Yes
2030-10-24 01:00 | 2030 Initial | -700 | 505 | 510 | 12.38 | 0 | 0 | Yes
2030-10-24 02:00 | 2030 Initial | -700 | 505 | 510 | 172.23 | 0 | 0 | Yes
2030-10-24 03:00 | 2030 Initial | -700 | 505 | 510 | 198.3 | 0 | 0 | Yes
2030-10-24 04:00 | 2030 Initial | -700 | 505 | 510 | 498.3 | 0 | 0 | Yes
2030-10-24 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 07:00 | 2030 Initial | -540.04 | 505 | 510 | 510 | 0 | 0 | No
2030-10-24 08:00 | 2030 Initial | -120.04 | 505 | 510 | 510 | 0 | 0 | No
2030-10-24 09:00 | 2030 Initial | 137.27 | 505 | 510 | 510 | 0 | 0 | No
2030-10-24 10:00 | 2030 Initial | 236.24 | 505 | 510 | 510 | 0 | 0 | No
2030-10-24 11:00 | 2030 Initial | -86.93 | 505 | 510 | 510 | 0 | 0 | No
2030-10-24 12:00 | 2030 Initial | -482.36 | 505 | 510 | 510 | 0 | 0 | No
2030-10-24 13:00 | 2030 Initial | -438.24 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 14:00 | 2030 Initial | -250.72 | 505 | 510 | 510 | 0 | 0 | No
2030-10-24 15:00 | 2030 Initial | 169.28 | 505 | 510 | 510 | 0 | 0 | No
2030-10-24 16:00 | 2030 Initial | 589.28 | 342.77 | 510 | 510 | 0 | 0 | No
2030-10-24 17:00 | 2030 Initial | 700 | 42.77 | 210 | 493.52 | 0 | 0 | No
2030-10-24 18:00 | 2030 Initial | 700 | -46.74 | -90 | 493.52 | 0 | 0 | No
2030-10-24 19:00 | 2030 Initial | 700 | 0 | -90 | 334.62 | 0 | 0 | No
2030-10-24 20:00 | 2030 Initial | 548.39 | 205 | 210 | 300.52 | 0 | 0 | No
2030-10-24 21:00 | 2030 Initial | 128.39 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 22:00 | 2030 Initial | -291.61 | 505 | 510 | 324.4 | 0 | 0 | Yes
2030-10-24 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-25 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-25 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-25 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-25 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-25 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-25 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-25 07:00 | 2030 Initial | -700 | 495.05 | 510 | 510 | 0 | 0 | No
2030-10-25 08:00 | 2030 Initial | -700 | 195.05 | 210 | 210 | 0 | 0 | No
2030-10-25 09:00 | 2030 Initial | -700 | 491.5 | 510 | 510 | 0 | 0 | No
2030-10-25 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-25 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 15:00 | 2030 Initial | -280 | 300 | 510 | 385.66 | 0 | 0 | No
2030-10-25 16:00 | 2030 Initial | 140 | 0 | 210 | 85.66 | 0 | 0 | No
2030-10-25 17:00 | 2030 Initial | 160.74 | -300 | -90 | -214.34 | 0 | 0 | No
2030-10-25 18:00 | 2030 Initial | 580.74 | -194.78 | -90 | -269.07 | 0 | 0 | No
2030-10-25 19:00 | 2030 Initial | 700 | 0 | 210 | 30.93 | 0 | 0 | No
2030-10-25 20:00 | 2030 Initial | 384.71 | 300 | 510 | 330.93 | 0 | 0 | No
2030-10-25 21:00 | 2030 Initial | -35.29 | 505 | 510 | 510 | 0 | 0 | No
2030-10-25 22:00 | 2030 Initial | -455.29 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-26 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 05:00 | 2030 Initial | -700 | 330.47 | 210 | 210 | 0 | 0 | Yes
2030-10-26 06:00 | 2030 Initial | -700 | 30.47 | -90 | -90 | 0 | 0 | No
2030-10-26 07:00 | 2030 Initial | -280 | -269.53 | -390 | -390 | 0 | 0 | No
2030-10-26 08:00 | 2030 Initial | 0 | 0 | -510 | -486.38 | 0 | 0 | No
2030-10-26 09:00 | 2030 Initial | 140 | 0 | -300 | -246.03 | 0 | 0 | No
2030-10-26 10:00 | 2030 Initial | -280 | 300 | 0 | 53.97 | 0 | 0 | No
2030-10-26 11:00 | 2030 Initial | -700 | 0 | 202.92 | 0 | 0 | 0 | No
2030-10-26 12:00 | 2030 Initial | -700 | 300 | 502.92 | 300 | 0 | 0 | No
2030-10-26 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 14:00 | 2030 Initial | -700 | 505 | 510 | 336.41 | 0 | 0 | No
2030-10-26 15:00 | 2030 Initial | -280 | 505 | 510 | 36.41 | 0 | 0 | No
2030-10-26 16:00 | 2030 Initial | 140 | 205 | 210 | -263.59 | 0 | 0 | No
2030-10-26 17:00 | 2030 Initial | 560 | 0 | -47.34 | 13.22 | 0 | 0 | No
2030-10-26 18:00 | 2030 Initial | 700 | 0 | 252.66 | 313.22 | 0 | 0 | No
2030-10-26 19:00 | 2030 Initial | 700 | 0 | 510 | 502.98 | 0 | 0 | No
2030-10-26 20:00 | 2030 Initial | 700 | 0 | 510 | 446.44 | 0 | 0 | No
2030-10-26 21:00 | 2030 Initial | 700 | 205 | 510 | 264.46 | 0 | 0 | No
2030-10-26 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-26 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 | 2030 Initial | 401.6 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 01:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 02:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 03:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 04:00 | 2030 Initial | 0 | 481.56 | 510 | 510 | 0 | 0 | No
2030-10-27 05:00 | 2030 Initial | 140.26 | 181.56 | 300 | 510 | 0 | 0 | No
2030-10-27 06:00 | 2030 Initial | 280 | 0 | 0 | 276.08 | 0 | 0 | No
2030-10-27 07:00 | 2030 Initial | 700 | 0 | 300 | 331.25 | 0 | 0 | No
2030-10-27 08:00 | 2030 Initial | 700 | 0 | 120.2 | 210 | 0 | 0 | No
2030-10-27 09:00 | 2030 Initial | 700 | 0 | 415.35 | 510 | 0 | 0 | No
2030-10-27 10:00 | 2030 Initial | 280 | 0 | 115.35 | 453.66 | 0 | 0 | No
2030-10-27 11:00 | 2030 Initial | -140 | -199.54 | -184.65 | 153.66 | 0 | 0 | No
2030-10-27 12:00 | 2030 Initial | -560 | 100.46 | 115.35 | 453.66 | 0 | 0 | No
2030-10-27 13:00 | 2030 Initial | -700 | 400.46 | 415.35 | 510 | 0 | 0 | Yes
2030-10-27 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-27 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-27 16:00 | 2030 Initial | -488.13 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 17:00 | 2030 Initial | -68.13 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 18:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 19:00 | 2030 Initial | 188.63 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 20:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 21:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 22:00 | 2030 Initial | -372.01 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 | 2030 Initial | -669.76 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 15:00 | 2030 Initial | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 16:00 | 2030 Initial | -140 | 300 | 510 | 510 | 0 | 0 | Yes
2030-10-28 17:00 | 2030 Initial | 280 | 0 | 248.37 | 210 | 0 | 0 | No
2030-10-28 18:00 | 2030 Initial | 700 | 205 | 340.04 | 210 | 0 | 0 | No
2030-10-28 19:00 | 2030 Initial | 284.96 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 20:00 | 2030 Initial | -1.33 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 21:00 | 2030 Initial | 114.68 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 22:00 | 2030 Initial | 362.76 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 23:00 | 2030 Initial | 431.54 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 | 2030 Initial | 496.29 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 01:00 | 2030 Initial | 205.16 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 02:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 03:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 04:00 | 2030 Initial | -252.61 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 05:00 | 2030 Initial | -347.31 | 505 | 452.91 | 510 | 0 | 0 | No
2030-10-29 06:00 | 2030 Initial | 0 | 205 | 152.91 | 466.08 | 0 | 0 | No
2030-10-29 07:00 | 2030 Initial | -420 | -95 | -147.09 | 218.79 | 0 | 0 | No
2030-10-29 08:00 | 2030 Initial | -89.52 | -395 | -447.09 | 344.27 | 0 | 0 | No
2030-10-29 09:00 | 2030 Initial | 0 | -300 | -300 | 210 | 0 | 0 | No
2030-10-29 10:00 | 2030 Initial | -361.99 | 0 | 0 | 510 | 0 | 0 | No
2030-10-29 11:00 | 2030 Initial | -280 | 205 | 300 | 393.67 | 0 | 0 | No
2030-10-29 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 16:00 | 2030 Initial | -700 | 300 | 210 | 240.41 | 0 | 0 | No
2030-10-29 17:00 | 2030 Initial | -700 | 0 | -90 | -59.59 | 0 | 0 | No
2030-10-29 18:00 | 2030 Initial | -700 | 0 | -39.51 | 0 | 0 | 0 | No
2030-10-29 19:00 | 2030 Initial | -280 | 205 | 260.49 | 246.04 | 0 | 0 | No
2030-10-29 20:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-29 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-29 22:00 | 2030 Initial | -529.12 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-29 23:00 | 2030 Initial | -109.12 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-30 | 2030 Initial | 310.88 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-30 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 05:00 | 2030 Initial | 618.19 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 06:00 | 2030 Initial | 198.19 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 07:00 | 2030 Initial | 543.26 | 205 | 210 | 210 | 0 | 0 | No
2030-10-30 08:00 | 2030 Initial | 700 | 171.17 | 510 | 510 | 0 | 0 | No
2030-10-30 09:00 | 2030 Initial | 700 | 300.32 | 510 | 510 | 0 | 0 | No
2030-10-30 10:00 | 2030 Initial | 700 | 32.56 | 510 | 498.9 | 0 | 0 | No
2030-10-30 11:00 | 2030 Initial | 700 | 0 | 210 | 198.9 | 0 | 0 | No
2030-10-30 12:00 | 2030 Initial | 700 | 0 | 0 | 86.18 | 0 | 0 | No
2030-10-30 13:00 | 2030 Initial | 700 | 0 | 95.15 | 158.54 | 0 | 0 | No
2030-10-30 14:00 | 2030 Initial | 700 | 0 | 165.91 | 0 | 0 | 0 | No
2030-10-30 15:00 | 2030 Initial | 382.72 | 140.03 | 465.91 | 300 | 0 | 0 | No
2030-10-30 16:00 | 2030 Initial | 420 | 440.03 | 408.94 | 510 | 0 | 0 | No
2030-10-30 17:00 | 2030 Initial | 0 | 140.03 | 108.94 | 210 | 0 | 0 | No
2030-10-30 18:00 | 2030 Initial | -420 | -159.97 | -191.06 | -90 | 0 | 0 | No
2030-10-30 19:00 | 2030 Initial | -172.75 | -340.9 | -491.06 | -126.29 | 0 | 0 | No
2030-10-30 20:00 | 2030 Initial | 247.25 | -494.05 | -510 | 173.71 | 0 | 0 | No
2030-10-30 21:00 | 2030 Initial | -128.07 | -526 | -510 | 30.54 | 0 | 0 | No
2030-10-30 22:00 | 2030 Initial | -471.67 | -526 | -510 | -111.1 | 0 | 0 | No
2030-10-30 23:00 | 2030 Initial | -700 | -526 | -510 | -285.11 | 0 | 0 | No
2030-10-31 | 2030 Initial | -382.67 | -526 | 0 | -414.99 | 0 | 0 | No
2030-10-31 01:00 | 2030 Initial | -700 | -226 | 0 | -114.99 | 0 | 0 | Yes
2030-10-31 02:00 | 2030 Initial | -700 | 74 | 0 | 0 | 0 | 0 | Yes
2030-10-31 03:00 | 2030 Initial | -700 | 374 | 0 | 80.09 | 0 | 0 | Yes
2030-10-31 04:00 | 2030 Initial | -700 | 505 | 0 | 204.35 | 0 | 0 | Yes
2030-10-31 05:00 | 2030 Initial | -700 | 505 | 0 | 0 | 0 | 0 | Yes
2030-10-31 06:00 | 2030 Initial | -700 | 505 | 0 | 178.87 | 0 | 0 | Yes
2030-10-31 07:00 | 2030 Initial | -700 | 505 | 0 | 406.04 | 0 | 0 | Yes
2030-10-31 08:00 | 2030 Initial | -700 | 505 | 0 | 447.73 | 0 | 0 | Yes
2030-10-31 09:00 | 2030 Initial | -700 | 505 | 0 | 433.96 | 0 | 0 | Yes
2030-10-31 10:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 11:00 | 2030 Initial | -700 | 505 | 0 | 490.24 | 0 | 0 | Yes
2030-10-31 12:00 | 2030 Initial | -700 | 505 | 0 | 351.56 | 0 | 0 | Yes
2030-10-31 13:00 | 2030 Initial | -700 | 505 | 0 | 314.63 | 0 | 0 | Yes
2030-10-31 14:00 | 2030 Initial | -700 | 505 | 0 | 334.41 | 0 | 0 | Yes
2030-10-31 15:00 | 2030 Initial | -700 | 505 | 0 | 449.23 | 0 | 0 | Yes
2030-10-31 16:00 | 2030 Initial | -283.91 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 17:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 18:00 | 2030 Initial | -385.41 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 19:00 | 2030 Initial | -192.69 | 505 | 0 | 510 | 0 | 0 | No
2030-10-31 20:00 | 2030 Initial | 150.99 | 505 | 0 | 510 | 0 | 0 | No
2030-10-31 21:00 | 2030 Initial | -269.01 | 505 | 0 | 510 | 0 | 0 | No
2030-10-31 22:00 | 2030 Initial | -689.01 | 505 | 0 | 510 | 0 | 0 | No
2030-10-31 23:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 01:00 | 2030 Initial | -700 | 505 | 0 | 453.47 | 0 | 0 | Yes
2030-11-01 02:00 | 2030 Initial | -700 | 505 | 0 | 207.06 | 0 | 0 | Yes
2030-11-01 03:00 | 2030 Initial | -700 | 505 | 0 | 143.33 | 0 | 0 | Yes
2030-11-01 04:00 | 2030 Initial | -700 | 505 | 0 | 443.33 | 0 | 0 | Yes
2030-11-01 05:00 | 2030 Initial | -700 | 505 | 0 | 257.6 | 0 | 0 | Yes
2030-11-01 06:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 07:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 08:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 09:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 10:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 11:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 12:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 13:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 14:00 | 2030 Initial | -657.1 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 15:00 | 2030 Initial | -237.1 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 16:00 | 2030 Initial | 182.9 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 17:00 | 2030 Initial | 602.9 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 18:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 19:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 20:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 21:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 22:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 23:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-02 | 2030 Initial | 700 | 505 | 300 | 510 | 0 | 0 | No
2030-11-02 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 03:00 | 2030 Initial | 455.54 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 04:00 | 2030 Initial | 656.94 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 05:00 | 2030 Initial | 301.51 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 06:00 | 2030 Initial | 301.51 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 07:00 | 2030 Initial | 529.21 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 08:00 | 2030 Initial | 256.73 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 09:00 | 2030 Initial | 477.11 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 10:00 | 2030 Initial | 204.53 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 11:00 | 2030 Initial | 33.61 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 12:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 13:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 14:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 15:00 | 2030 Initial | 268.27 | 205 | 210 | 510 | 0 | 0 | No
2030-11-02 16:00 | 2030 Initial | 688.27 | -95 | -90 | 415.15 | 0 | 0 | No
2030-11-02 17:00 | 2030 Initial | 485.61 | -343.77 | -390 | 379.59 | 0 | 0 | No
2030-11-02 18:00 | 2030 Initial | 700 | -43.77 | -354.42 | 343.59 | 0 | 0 | No
2030-11-02 19:00 | 2030 Initial | 700 | 0 | -54.42 | 224.5 | 0 | 0 | No
2030-11-02 20:00 | 2030 Initial | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-11-02 21:00 | 2030 Initial | 693.84 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 22:00 | 2030 Initial | 544.71 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 23:00 | 2030 Initial | 124.71 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 | 2030 Initial | 544.71 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 02:00 | 2030 Initial | 587.3 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 03:00 | 2030 Initial | 208.28 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 04:00 | 2030 Initial | 22.97 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 05:00 | 2030 Initial | 442.97 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 06:00 | 2030 Initial | 373.58 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 07:00 | 2030 Initial | 700 | 245.77 | 300 | 439.93 | 0 | 0 | No
2030-11-03 08:00 | 2030 Initial | 700 | -54.23 | 0 | 139.93 | 0 | 0 | No
2030-11-03 09:00 | 2030 Initial | 700 | 245.77 | 300 | 439.93 | 0 | 0 | No
2030-11-03 10:00 | 2030 Initial | 700 | 358.39 | 510 | 510 | 0 | 0 | No
2030-11-03 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 12:00 | 2030 Initial | 449.8 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 13:00 | 2030 Initial | 454.13 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 14:00 | 2030 Initial | 577.75 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 15:00 | 2030 Initial | 700 | 300 | 426.43 | 510 | 0 | 0 | No
2030-11-03 16:00 | 2030 Initial | 421.33 | 0 | 126.43 | 493.93 | 0 | 0 | No
2030-11-03 17:00 | 2030 Initial | 700 | 0 | 239.17 | 510 | 0 | 0 | No
2030-11-03 18:00 | 2030 Initial | 700 | 49.5 | 510 | 510 | 0 | 0 | No
2030-11-03 19:00 | 2030 Initial | 700 | 210.72 | 510 | 510 | 0 | 0 | No
2030-11-03 20:00 | 2030 Initial | 700 | 77.11 | 510 | 510 | 0 | 0 | No
2030-11-03 21:00 | 2030 Initial | 700 | 209.15 | 510 | 510 | 0 | 0 | No
2030-11-03 22:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-11-03 23:00 | 2030 Initial | 700 | 0 | 510 | 427.34 | 0 | 0 | No
2030-11-04 | 2030 Initial | 700 | 90.79 | 510 | 510 | 0 | 0 | No
2030-11-04 01:00 | 2030 Initial | 700 | 250.49 | 510 | 510 | 0 | 0 | No
2030-11-04 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 07:00 | 2030 Initial | 443.89 | 205 | 210 | 210 | 0 | 0 | No
2030-11-04 08:00 | 2030 Initial | 700 | 0 | 300 | 121.21 | 0 | 0 | No
2030-11-04 09:00 | 2030 Initial | 700 | 282.38 | 0 | 280.82 | 0 | 0 | No
2030-11-04 10:00 | 2030 Initial | 700 | 260.82 | 0 | 495.62 | 0 | 0 | No
2030-11-04 11:00 | 2030 Initial | 700 | 0 | 0 | 284.43 | 0 | 0 | No
2030-11-04 12:00 | 2030 Initial | 700 | -138.02 | 0 | -15.57 | 0 | 0 | No
2030-11-04 13:00 | 2030 Initial | 700 | -14.01 | 0 | 0 | 0 | 0 | No
2030-11-04 14:00 | 2030 Initial | 700 | 0.25 | 0 | 300 | 0 | 0 | No
2030-11-04 15:00 | 2030 Initial | 700 | 130.75 | 0 | 510 | 0 | 0 | No
2030-11-04 16:00 | 2030 Initial | 700 | 201.01 | 0 | 366.56 | 0 | 0 | No
2030-11-04 17:00 | 2030 Initial | 700 | 501.01 | 0 | 319.13 | 0 | 0 | No
2030-11-04 18:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-04 19:00 | 2030 Initial | 700 | 505 | 0 | 210 | 0 | 0 | No
2030-11-04 20:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-04 21:00 | 2030 Initial | 700 | 505 | 0 | 451.81 | 0 | 0 | No
2030-11-04 22:00 | 2030 Initial | 700 | 374.05 | 0 | 494.02 | 0 | 0 | No
2030-11-04 23:00 | 2030 Initial | 700 | 247.2 | 0 | 271.78 | 0 | 0 | No
2030-11-05 | 2030 Initial | 700 | 205 | 0 | 210 | 0 | 0 | No
2030-11-05 01:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-05 02:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-05 03:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-05 04:00 | 2030 Initial | 700 | 333.7 | 0 | 510 | 0 | 0 | No
2030-11-05 05:00 | 2030 Initial | 444.43 | 33.7 | 0 | 210 | 0 | 0 | No
2030-11-05 06:00 | 2030 Initial | 488.99 | 0 | 0 | 0 | 0 | 0 | No
2030-11-05 07:00 | 2030 Initial | 700 | 0 | 0 | 235.44 | 0 | 0 | No
2030-11-05 08:00 | 2030 Initial | 700 | 297.57 | 0 | 510 | 0 | 0 | No
2030-11-05 09:00 | 2030 Initial | 700 | 447.01 | 0 | 510 | 0 | 0 | No
2030-11-05 10:00 | 2030 Initial | 700 | 318.58 | 0 | 510 | 0 | 0 | No
2030-11-05 11:00 | 2030 Initial | 700 | 18.58 | 0 | 355.96 | 0 | 0 | No
2030-11-05 12:00 | 2030 Initial | 513.77 | 0 | 0 | 321.91 | 0 | 0 | No
2030-11-05 13:00 | 2030 Initial | 93.77 | 0 | 0 | 300 | 0 | 0 | No
2030-11-05 14:00 | 2030 Initial | 423.64 | 0 | 0 | 0 | 0 | 0 | No
2030-11-05 15:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-11-05 16:00 | 2030 Initial | 700 | 60.27 | 0 | -100.08 | 0 | 0 | No
2030-11-05 17:00 | 2030 Initial | 700 | 0 | 0 | -400.08 | 0 | 0 | No
2030-11-05 18:00 | 2030 Initial | 700 | 0 | 0 | -510 | 0 | 0 | No
2030-11-05 19:00 | 2030 Initial | 700 | -6.2 | 0 | -300 | 0 | 0 | No
2030-11-05 20:00 | 2030 Initial | 700 | 112.77 | 0 | 0 | 0 | 0 | No
2030-11-05 21:00 | 2030 Initial | 700 | 353.28 | 0 | 2.25 | 0 | 0 | No
2030-11-05 22:00 | 2030 Initial | 700 | 394.24 | 0 | 0 | 0 | 0 | No
2030-11-05 23:00 | 2030 Initial | 700 | 94.24 | 0 | 286.28 | 0 | 0 | No
2030-11-06 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-11-06 01:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-11-06 02:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-11-06 03:00 | 2030 Initial | 700 | 0 | 0 | 407.96 | 0 | 0 | No
2030-11-06 04:00 | 2030 Initial | 700 | 0 | 0 | 107.96 | 0 | 0 | No
2030-11-06 05:00 | 2030 Initial | 420 | -160.93 | 0 | -192.04 | 0 | 0 | No
2030-11-06 06:00 | 2030 Initial | 0 | -460.93 | 0 | -492.04 | 0 | 0 | No
2030-11-06 07:00 | 2030 Initial | -140 | -526 | 0 | -492.04 | 0 | 0 | No
2030-11-06 08:00 | 2030 Initial | 280 | -526 | 0 | -463.95 | 0 | 0 | No
2030-11-06 09:00 | 2030 Initial | 700 | -526 | -510 | -163.95 | 0 | 0 | No
2030-11-06 10:00 | 2030 Initial | 700 | -414.91 | -510 | -45.71 | 0 | 0 | No
2030-11-06 11:00 | 2030 Initial | 612.58 | -114.91 | -210 | 254.29 | 0 | 0 | No
2030-11-06 12:00 | 2030 Initial | 192.58 | -5.25 | -210 | 11.56 | 0 | 0 | No
2030-11-06 13:00 | 2030 Initial | -227.42 | -305.25 | -510 | -288.44 | 0 | 0 | No
2030-11-06 14:00 | 2030 Initial | -135.19 | -300 | -510 | -368.85 | 0 | 0 | No
2030-11-06 15:00 | 2030 Initial | 180.4 | 0 | -510 | -209.03 | 0 | 0 | No
2030-11-06 16:00 | 2030 Initial | 600.4 | 0 | -510 | -509.03 | 0 | 0 | No
2030-11-06 17:00 | 2030 Initial | 700 | 0 | -510 | -475.57 | 0 | 0 | No
2030-11-06 18:00 | 2030 Initial | 700 | 0 | -286.04 | -214.59 | 0 | 0 | No
2030-11-06 19:00 | 2030 Initial | 700 | 0 | 13.96 | 59.25 | 0 | 0 | No
2030-11-06 20:00 | 2030 Initial | 700 | 300 | 313.96 | 359.25 | 0 | 0 | No
2030-11-06 21:00 | 2030 Initial | 700 | 370.01 | 510 | 510 | 0 | 0 | No
2030-11-06 22:00 | 2030 Initial | 700 | 300 | 317.84 | 300 | 0 | 0 | No
2030-11-06 23:00 | 2030 Initial | 673.53 | 0 | 17.84 | 0 | 0 | 0 | No
2030-11-07 | 2030 Initial | 700 | 0 | 317.84 | 74.13 | 0 | 0 | No
2030-11-07 01:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-11-07 02:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-11-07 03:00 | 2030 Initial | 700 | 0 | 390 | 0 | 0 | 0 | No
2030-11-07 04:00 | 2030 Initial | 700 | 0 | 90 | 136.61 | 0 | 0 | No
2030-11-07 05:00 | 2030 Initial | 420 | 0 | -210 | -131.83 | 0 | 0 | No
2030-11-07 06:00 | 2030 Initial | 0 | -300 | -510 | -431.83 | 0 | 0 | No
2030-11-07 07:00 | 2030 Initial | 216.74 | 0 | -510 | -510 | 0 | 0 | No
2030-11-07 08:00 | 2030 Initial | 636.74 | 0 | -334.31 | -210 | 0 | 0 | No
2030-11-07 09:00 | 2030 Initial | 700 | 0 | -510 | -140.82 | 0 | 0 | No
2030-11-07 10:00 | 2030 Initial | 391.88 | 0 | -510 | -312.62 | 0 | 0 | No
2030-11-07 11:00 | 2030 Initial | 278.23 | 0 | -510 | -381.63 | 0 | 0 | No
2030-11-07 12:00 | 2030 Initial | 0 | -246.5 | -510 | -411.8 | 0 | 0 | No
2030-11-07 13:00 | 2030 Initial | 0 | -436.3 | -510 | -510 | 0 | 0 | No
2030-11-07 14:00 | 2030 Initial | 0 | -314.22 | -510 | -510 | 0 | 0 | No
2030-11-07 15:00 | 2030 Initial | 0 | -159.22 | -510 | -497.58 | 0 | 0 | No
2030-11-07 16:00 | 2030 Initial | 0 | -226 | -510 | -260.39 | 0 | 0 | No
2030-11-07 17:00 | 2030 Initial | -319.1 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 18:00 | 2030 Initial | 100.9 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 19:00 | 2030 Initial | 520.9 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 20:00 | 2030 Initial | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-11-07 21:00 | 2030 Initial | 700 | 0 | -300 | -270.27 | 0 | 0 | No
2030-11-07 22:00 | 2030 Initial | 641.97 | 0 | 0 | 0 | 0 | 0 | No
2030-11-07 23:00 | 2030 Initial | 700 | 0 | -37.51 | 0 | 0 | 0 | No
2030-11-08 | 2030 Initial | 700 | 0 | 105.52 | 0 | 0 | 0 | No
2030-11-08 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-11-08 02:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-11-08 03:00 | 2030 Initial | 560 | 0 | 0 | 0 | 0 | 0 | No
2030-11-08 04:00 | 2030 Initial | 140 | 0 | 0 | 0 | 0 | 0 | No
2030-11-08 05:00 | 2030 Initial | -280 | 0 | 132.44 | 0 | 0 | 0 | No
2030-11-08 06:00 | 2030 Initial | -700 | 0 | 120.08 | 0 | 0 | 0 | No
2030-11-08 07:00 | 2030 Initial | -700 | 0 | -179.92 | 0 | 0 | 0 | No
2030-11-08 08:00 | 2030 Initial | -430.45 | 0 | 0 | 0 | 0 | 0 | No
2030-11-08 09:00 | 2030 Initial | -15.1 | 0 | 0 | 85.29 | 0 | 0 | No
2030-11-08 10:00 | 2030 Initial | -50.95 | 0 | 0 | 213.6 | 0 | 0 | No
2030-11-08 11:00 | 2030 Initial | -236.1 | 0 | 0 | 212.9 | 0 | 0 | No
2030-11-08 12:00 | 2030 Initial | -522.31 | 0 | 0 | 178.55 | 0 | 0 | No
2030-11-08 13:00 | 2030 Initial | -625.39 | 0 | 0 | 169.37 | 0 | 0 | No
2030-11-08 14:00 | 2030 Initial | -205.39 | 0 | -185.94 | 229.36 | 0 | 0 | No
2030-11-08 15:00 | 2030 Initial | 6.51 | 0 | -401.75 | 220.31 | 0 | 0 | No
2030-11-08 16:00 | 2030 Initial | 160.44 | 0 | -510 | 94.79 | 0 | 0 | No
2030-11-08 17:00 | 2030 Initial | 0 | 0 | -510 | 233.98 | 0 | 0 | No
2030-11-08 18:00 | 2030 Initial | 413.36 | 0 | -510 | 393.01 | 0 | 0 | No
2030-11-08 19:00 | 2030 Initial | 223.49 | 0 | -510 | 247.14 | 0 | 0 | No
2030-11-08 20:00 | 2030 Initial | 381.55 | 0 | -510 | 164.88 | 0 | 0 | No
2030-11-08 21:00 | 2030 Initial | 700 | -146.2 | -510 | 419.44 | 0 | 0 | No
2030-11-08 22:00 | 2030 Initial | 700 | -310.51 | -510 | 222.28 | 0 | 0 | No
2030-11-08 23:00 | 2030 Initial | 700 | -502.76 | -510 | 137.03 | 0 | 0 | No
2030-11-09 | 2030 Initial | 700 | -202.76 | -502.28 | 15.72 | 0 | 0 | No
2030-11-09 01:00 | 2030 Initial | 700 | 0 | -510 | 145.75 | 0 | 0 | No
2030-11-09 02:00 | 2030 Initial | 700 | 0 | -510 | 0.49 | 0 | 0 | No
2030-11-09 03:00 | 2030 Initial | 700 | 0 | -510 | 61.75 | 0 | 0 | No
2030-11-09 04:00 | 2030 Initial | 445.6 | 0 | -301.64 | 0 | 0 | 0 | No
2030-11-09 05:00 | 2030 Initial | 25.6 | 0 | -54.99 | 0 | 0 | 0 | No
2030-11-09 06:00 | 2030 Initial | -394.4 | -76.94 | -210 | -163.44 | 0 | 0 | No
2030-11-09 07:00 | 2030 Initial | -700 | -376.94 | -510 | -463.44 | 0 | 0 | No
2030-11-09 08:00 | 2030 Initial | -280 | -161.75 | -510 | -321.56 | 0 | 0 | No
2030-11-09 09:00 | 2030 Initial | 0 | -228.89 | -510 | -230.25 | 0 | 0 | No
2030-11-09 10:00 | 2030 Initial | 0 | -257.34 | -510 | -134.08 | 0 | 0 | No
2030-11-09 11:00 | 2030 Initial | 134.77 | 0 | -210 | 0 | 0 | 0 | No
2030-11-09 12:00 | 2030 Initial | 0 | 0 | -365.64 | 0 | 0 | 0 | No
2030-11-09 13:00 | 2030 Initial | 280 | 0 | -399.66 | 0 | 0 | 0 | No
2030-11-09 14:00 | 2030 Initial | 700 | 0 | -473.12 | -42.81 | 0 | 0 | No
2030-11-09 15:00 | 2030 Initial | 700 | 0 | -173.12 | 0 | 0 | 0 | No
2030-11-09 16:00 | 2030 Initial | 700 | 0 | -165.38 | 0 | 0 | 0 | No
2030-11-09 17:00 | 2030 Initial | 700 | -229.52 | -465.38 | -300 | 0 | 0 | No
2030-11-09 18:00 | 2030 Initial | 700 | 0 | -165.38 | -55.29 | 0 | 0 | No
2030-11-09 19:00 | 2030 Initial | 700 | 300 | 134.62 | 244.71 | 0 | 0 | No
2030-11-09 20:00 | 2030 Initial | 700 | 0 | 434.62 | 310.18 | 0 | 0 | No
2030-11-09 21:00 | 2030 Initial | 700 | 0 | 419.99 | 210 | 0 | 0 | No
2030-11-09 22:00 | 2030 Initial | 700 | 160.32 | 510 | 510 | 0 | 0 | No
2030-11-09 23:00 | 2030 Initial | 700 | 0 | 510 | 372.48 | 0 | 0 | No
2030-11-10 | 2030 Initial | 700 | 0 | 510 | 181.33 | 0 | 0 | No
2030-11-10 01:00 | 2030 Initial | 700 | 0 | 510 | 343.83 | 0 | 0 | No
2030-11-10 02:00 | 2030 Initial | 700 | 0 | 510 | 370.68 | 0 | 0 | No
2030-11-10 03:00 | 2030 Initial | 700 | 0 | 510 | 176.46 | 0 | 0 | No
2030-11-10 04:00 | 2030 Initial | 700 | 0 | 510 | 97.89 | 0 | 0 | No
2030-11-10 05:00 | 2030 Initial | 420 | 0 | 444.14 | 397.89 | 0 | 0 | No
2030-11-10 06:00 | 2030 Initial | 0 | 0 | 144.14 | 179.74 | 0 | 0 | No
2030-11-10 07:00 | 2030 Initial | -420 | 0 | -155.86 | -120.26 | 0 | 0 | No
2030-11-10 08:00 | 2030 Initial | -700 | 0 | -455.86 | -420.26 | 0 | 0 | No
2030-11-10 09:00 | 2030 Initial | -469.54 | -103.98 | -510 | -311.3 | 0 | 0 | No
2030-11-10 10:00 | 2030 Initial | -700 | 0 | -210 | -11.3 | 0 | 0 | No
2030-11-10 11:00 | 2030 Initial | -700 | -226 | -210 | -14.34 | 0 | 0 | No
2030-11-10 12:00 | 2030 Initial | -700 | -526 | -510 | -314.34 | 0 | 0 | No
2030-11-10 13:00 | 2030 Initial | -700 | -446.94 | -510 | -38.19 | 0 | 0 | No
2030-11-10 14:00 | 2030 Initial | -700 | -526 | -510 | -264.85 | 0 | 0 | No
2030-11-10 15:00 | 2030 Initial | -700 | -526 | -510 | -411.43 | 0 | 0 | No
2030-11-10 16:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-10 17:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-10 18:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-10 19:00 | 2030 Initial | -700 | -226 | -510 | -303.1 | 0 | 0 | No
2030-11-10 20:00 | 2030 Initial | -280 | -472.79 | -510 | -37.17 | 0 | 0 | No
2030-11-10 21:00 | 2030 Initial | -433.01 | -526 | -510 | -145.37 | 0 | 0 | No
2030-11-10 22:00 | 2030 Initial | -280 | -375.45 | -510 | -33.2 | 0 | 0 | No
2030-11-10 23:00 | 2030 Initial | -700 | -75.45 | -212.13 | 40.87 | 0 | 0 | No
2030-11-11 | 2030 Initial | -700 | 0 | -81.64 | 0 | 0 | 0 | No
2030-11-11 01:00 | 2030 Initial | -700 | 265.96 | 218.36 | 300 | 0 | 0 | Yes
2030-11-11 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 04:00 | 2030 Initial | -700 | 505 | 510 | 333.2 | 0 | 0 | Yes
2030-11-11 05:00 | 2030 Initial | -700 | 505 | 510 | 178.21 | 0 | 0 | Yes
2030-11-11 06:00 | 2030 Initial | -700 | 505 | 510 | 361.14 | 0 | 0 | Yes
2030-11-11 07:00 | 2030 Initial | -700 | 505 | 510 | 303.47 | 0 | 0 | Yes
2030-11-11 08:00 | 2030 Initial | -700 | 505 | 510 | 505.26 | 0 | 0 | Yes
2030-11-11 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 13:00 | 2030 Initial | -450.3 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 14:00 | 2030 Initial | -30.3 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 15:00 | 2030 Initial | 389.7 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 16:00 | 2030 Initial | -30.3 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 17:00 | 2030 Initial | 187.06 | 264.96 | 510 | 510 | 0 | 0 | No
2030-11-11 18:00 | 2030 Initial | 607.06 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-12 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-12 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-12 03:00 | 2030 Initial | 648.8 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 04:00 | 2030 Initial | 228.8 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-12 05:00 | 2030 Initial | -191.2 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-12 06:00 | 2030 Initial | -611.2 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 07:00 | 2030 Initial | -191.2 | 205 | 210 | 409.83 | 0 | 0 | No
2030-11-12 08:00 | 2030 Initial | -322.76 | 0 | -90 | 495.32 | 0 | 0 | No
2030-11-12 09:00 | 2030 Initial | 0 | -34.98 | -390 | 510 | 0 | 0 | No
2030-11-12 10:00 | 2030 Initial | -280 | -242.92 | -510 | 510 | 0 | 0 | No
2030-11-12 11:00 | 2030 Initial | -700 | -242.92 | -510 | 400.83 | 0 | 0 | No
2030-11-12 12:00 | 2030 Initial | -631.58 | -526 | -510 | 100.83 | 0 | 0 | No
2030-11-12 13:00 | 2030 Initial | -700 | -526 | -510 | 18.42 | 0 | 0 | No
2030-11-12 14:00 | 2030 Initial | -700 | -226 | -510 | -242.25 | 0 | 0 | No
2030-11-12 15:00 | 2030 Initial | -700 | -206.03 | -510 | -34.62 | 0 | 0 | No
2030-11-12 16:00 | 2030 Initial | -700 | 0 | -510 | -37.07 | 0 | 0 | No
2030-11-12 17:00 | 2030 Initial | -700 | -32.69 | -510 | 5.82 | 0 | 0 | No
2030-11-12 18:00 | 2030 Initial | -700 | 0 | -390 | -24.02 | 0 | 0 | No
2030-11-12 19:00 | 2030 Initial | -280 | -95 | -90 | -90 | 0 | 0 | No
2030-11-12 20:00 | 2030 Initial | -198.05 | 205 | 210 | 210 | 0 | 0 | No
2030-11-12 21:00 | 2030 Initial | 221.95 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 22:00 | 2030 Initial | 641.95 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 03:00 | 2030 Initial | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 04:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 05:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 07:00 | 2030 Initial | -700 | 205 | 213.17 | 487.67 | 0 | 0 | No
2030-11-13 08:00 | 2030 Initial | -280 | 0 | -86.83 | 263.85 | 0 | 0 | No
2030-11-13 09:00 | 2030 Initial | 0 | 147.41 | 213.17 | 510 | 0 | 0 | No
2030-11-13 10:00 | 2030 Initial | -183.41 | 0 | 325.28 | 507.18 | 0 | 0 | No
2030-11-13 11:00 | 2030 Initial | -280 | 0 | 116.85 | 343.92 | 0 | 0 | No
2030-11-13 12:00 | 2030 Initial | -700 | 132.1 | 280.07 | 510 | 0 | 0 | No
2030-11-13 13:00 | 2030 Initial | -700 | 0 | -19.93 | 254.8 | 0 | 0 | No
2030-11-13 14:00 | 2030 Initial | -548.53 | 0 | 0 | 510 | 0 | 0 | No
2030-11-13 15:00 | 2030 Initial | -280 | 0 | 233.8 | 393.53 | 0 | 0 | No
2030-11-13 16:00 | 2030 Initial | -700 | 300 | 510 | 510 | 0 | 0 | No
2030-11-13 17:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 18:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 19:00 | 2030 Initial | -280 | 364.24 | 510 | 510 | 0 | 0 | No
2030-11-13 20:00 | 2030 Initial | 140 | 64.24 | 243.69 | 510 | 0 | 0 | No
2030-11-13 21:00 | 2030 Initial | 203.55 | -235.76 | -56.31 | 289.54 | 0 | 0 | No
2030-11-13 22:00 | 2030 Initial | -216.45 | 0 | 194.36 | 303.53 | 0 | 0 | No
2030-11-13 23:00 | 2030 Initial | 140 | 300 | 494.36 | 510 | 0 | 0 | No
2030-11-14 | 2030 Initial | 0 | 331.23 | 510 | 510 | 0 | 0 | No
2030-11-14 01:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 02:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 03:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 04:00 | 2030 Initial | -66.28 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 05:00 | 2030 Initial | -378.28 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 06:00 | 2030 Initial | -700 | 205 | 210 | 219.17 | 0 | 0 | No
2030-11-14 07:00 | 2030 Initial | -420 | -95 | -90 | 147.99 | 0 | 0 | No
2030-11-14 08:00 | 2030 Initial | 0 | -300 | -360.34 | 447.99 | 0 | 0 | No
2030-11-14 09:00 | 2030 Initial | 420 | 0 | -60.34 | 510 | 0 | 0 | No
2030-11-14 10:00 | 2030 Initial | 700 | 0 | 146.07 | 510 | 0 | 0 | No
2030-11-14 11:00 | 2030 Initial | 280 | 300 | 446.07 | 510 | 0 | 0 | No
2030-11-14 12:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 13:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 14:00 | 2030 Initial | 0 | 505 | 412.59 | 510 | 0 | 0 | No
2030-11-14 15:00 | 2030 Initial | 127.97 | 278.39 | 112.59 | 510 | 0 | 0 | No
2030-11-14 16:00 | 2030 Initial | 0 | -21.61 | -187.41 | 210 | 0 | 0 | No
2030-11-14 17:00 | 2030 Initial | 12.03 | 0 | 0 | 0 | 0 | 0 | No
2030-11-14 18:00 | 2030 Initial | 432.03 | 0 | -63.17 | 279.82 | 0 | 0 | No
2030-11-14 19:00 | 2030 Initial | 700 | 205 | 236.83 | 257 | 0 | 0 | No
2030-11-14 20:00 | 2030 Initial | 605.33 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 21:00 | 2030 Initial | 380.88 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 22:00 | 2030 Initial | 48.27 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 23:00 | 2030 Initial | 295.4 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 02:00 | 2030 Initial | 454.29 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 03:00 | 2030 Initial | 454.29 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 05:00 | 2030 Initial | 607.28 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 07:00 | 2030 Initial | 599.63 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 08:00 | 2030 Initial | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-11-15 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 11:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 14:00 | 2030 Initial | 700 | 505 | 452.76 | 510 | 0 | 0 | No
2030-11-15 15:00 | 2030 Initial | 700 | 205 | 152.76 | 436.23 | 0 | 0 | No
2030-11-15 16:00 | 2030 Initial | 700 | -95 | -147.24 | 136.23 | 0 | 0 | No
2030-11-15 17:00 | 2030 Initial | 700 | -393.56 | -447.24 | 412.21 | 0 | 0 | No
2030-11-15 18:00 | 2030 Initial | 700 | -494.05 | -510 | 510 | 0 | 0 | No
2030-11-15 19:00 | 2030 Initial | 700 | -502.57 | -510 | 510 | 0 | 0 | No
2030-11-15 20:00 | 2030 Initial | 700 | -311.05 | -390 | 334.71 | 0 | 0 | No
2030-11-15 21:00 | 2030 Initial | 280 | -11.05 | -90 | 216.23 | 0 | 0 | No
2030-11-15 22:00 | 2030 Initial | -140 | 288.95 | 210 | 510 | 0 | 0 | Yes
2030-11-15 23:00 | 2030 Initial | -560 | 505 | 510 | 461.72 | 0 | 0 | Yes
2030-11-16 | 2030 Initial | -511.88 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-16 01:00 | 2030 Initial | -91.88 | 505 | 510 | 424.21 | 0 | 0 | Yes
2030-11-16 02:00 | 2030 Initial | -90 | 505 | 510 | 207.23 | 0 | 0 | Yes
2030-11-16 03:00 | 2030 Initial | 0 | 505 | 510 | 226.7 | 0 | 0 | Yes
2030-11-16 04:00 | 2030 Initial | 220.15 | 505 | 510 | 199.38 | 0 | 0 | Yes
2030-11-16 05:00 | 2030 Initial | 235.08 | 505 | 510 | 358.26 | 0 | 0 | Yes
2030-11-16 06:00 | 2030 Initial | 255.43 | 505 | 510 | 510 | 0 | 0 | No
2030-11-16 07:00 | 2030 Initial | -164.57 | 505 | 510 | 510 | 0 | 0 | No
2030-11-16 08:00 | 2030 Initial | -584.57 | 505 | 510 | 510 | 0 | 0 | No
2030-11-16 09:00 | 2030 Initial | -577.12 | 205 | 210 | 510 | 0 | 0 | No
2030-11-16 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-16 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-16 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-16 13:00 | 2030 Initial | -700 | 289.43 | 210 | 510 | 0 | 0 | No
2030-11-16 14:00 | 2030 Initial | -700 | -10.57 | -90 | 510 | 0 | 0 | No
2030-11-16 15:00 | 2030 Initial | -326.57 | -310.57 | -390 | 464.85 | 0 | 0 | No
2030-11-16 16:00 | 2030 Initial | -700 | -120.44 | -510 | 510 | 0 | 0 | No
2030-11-16 17:00 | 2030 Initial | -700 | -25.29 | -510 | 510 | 0 | 0 | No
2030-11-16 18:00 | 2030 Initial | -607.32 | -25.29 | -510 | 510 | 0 | 0 | No
2030-11-16 19:00 | 2030 Initial | -187.32 | -325.29 | -510 | 500.11 | 0 | 0 | No
2030-11-16 20:00 | 2030 Initial | -280 | -300 | -510 | 416.8 | 0 | 0 | No
2030-11-16 21:00 | 2030 Initial | -700 | 0 | -213.57 | 510 | 0 | 0 | No
2030-11-16 22:00 | 2030 Initial | -700 | 300 | 86.43 | 510 | 0 | 0 | No
2030-11-16 23:00 | 2030 Initial | -700 | 505 | 386.43 | 510 | 0 | 0 | Yes
2030-11-17 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-17 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-17 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-17 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-17 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-17 15:00 | 2030 Initial | -700 | 300 | 328.35 | 510 | 0 | 0 | No
2030-11-17 16:00 | 2030 Initial | -700 | 0 | 28.35 | 417 | 0 | 0 | No
2030-11-17 17:00 | 2030 Initial | -700 | -285.17 | -271.65 | 509.29 | 0 | 0 | No
2030-11-17 18:00 | 2030 Initial | -700 | -109.51 | -510 | 510 | 0 | 0 | No
2030-11-17 19:00 | 2030 Initial | -280 | -217.24 | -300 | 478.21 | 0 | 0 | No
2030-11-17 20:00 | 2030 Initial | -359.64 | 0 | 0 | 481.71 | 0 | 0 | No
2030-11-17 21:00 | 2030 Initial | -700 | 300 | 300 | 440.12 | 0 | 0 | Yes
2030-11-17 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 23:00 | 2030 Initial | -700 | 505 | 510 | 505.1 | 0 | 0 | Yes
2030-11-18 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 03:00 | 2030 Initial | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-11-18 04:00 | 2030 Initial | -700 | 505 | 510 | 178.6 | 0 | 0 | Yes
2030-11-18 05:00 | 2030 Initial | -700 | 505 | 510 | 478.6 | 0 | 0 | Yes
2030-11-18 06:00 | 2030 Initial | -700 | 505 | 510 | 178.6 | 0 | 0 | Yes
2030-11-18 07:00 | 2030 Initial | -700 | 505 | 510 | 455.11 | 0 | 0 | Yes
2030-11-18 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-18 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-18 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-18 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-18 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-18 15:00 | 2030 Initial | -700 | 300 | 510 | 510 | 0 | 0 | No
2030-11-18 16:00 | 2030 Initial | -700 | 0 | 300 | 423.36 | 0 | 0 | No
2030-11-18 17:00 | 2030 Initial | -455.09 | 0 | 0 | 266.24 | 0 | 0 | No
2030-11-18 18:00 | 2030 Initial | -35.09 | 0 | 0 | 319.87 | 0 | 0 | No
2030-11-18 19:00 | 2030 Initial | -455.09 | 205 | 210 | 486.83 | 0 | 0 | No
2030-11-18 20:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-18 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-18 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-19 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-19 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-19 07:00 | 2030 Initial | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-11-19 08:00 | 2030 Initial | -330.51 | 0 | 510 | 255.71 | 0 | 0 | No
2030-11-19 09:00 | 2030 Initial | 0 | 0 | 406.06 | 210 | 0 | 0 | No
2030-11-19 10:00 | 2030 Initial | 309.45 | 300 | 510 | 510 | 0 | 0 | No
2030-11-19 11:00 | 2030 Initial | 140 | 475.53 | 510 | 510 | 0 | 0 | No
2030-11-19 12:00 | 2030 Initial | -280 | 275.61 | 510 | 510 | 0 | 0 | No
2030-11-19 13:00 | 2030 Initial | -700 | 472.65 | 510 | 510 | 0 | 0 | No
2030-11-19 14:00 | 2030 Initial | -473.9 | 505 | 510 | 510 | 0 | 0 | No
2030-11-19 15:00 | 2030 Initial | -53.9 | 505 | 510 | 510 | 0 | 0 | No
2030-11-19 16:00 | 2030 Initial | 366.1 | 205 | 510 | 210 | 0 | 0 | No
2030-11-19 17:00 | 2030 Initial | 0 | 0 | 510 | 435.82 | 0 | 0 | No
2030-11-19 18:00 | 2030 Initial | 215.26 | 0 | 510 | 135.82 | 0 | 0 | No
2030-11-19 19:00 | 2030 Initial | 635.26 | 0 | 350.77 | 0 | 0 | 0 | No
2030-11-19 20:00 | 2030 Initial | 420 | 0 | 50.77 | 43.51 | 0 | 0 | No
2030-11-19 21:00 | 2030 Initial | 0 | 0 | -249.23 | 0 | 0 | 0 | No
2030-11-19 22:00 | 2030 Initial | -420 | -7.1 | -510 | -46.56 | 0 | 0 | No
2030-11-19 23:00 | 2030 Initial | 0 | -32.02 | -500.66 | -213.44 | 0 | 0 | No
2030-11-20 | 2030 Initial | -382.38 | 0 | -200.66 | 0 | 0 | 0 | No
2030-11-20 01:00 | 2030 Initial | -496.25 | 0 | -500.66 | -138.09 | 0 | 0 | No
2030-11-20 02:00 | 2030 Initial | -467.48 | 0 | -510 | -300 | 0 | 0 | No
2030-11-20 03:00 | 2030 Initial | -700 | 0 | -310.54 | 0 | 0 | 0 | No
2030-11-20 04:00 | 2030 Initial | -700 | 0 | -490.82 | 0 | 0 | 0 | No
2030-11-20 05:00 | 2030 Initial | -700 | 0 | -510 | -300 | 0 | 0 | No
2030-11-20 06:00 | 2030 Initial | -700 | 0 | -510 | -188.09 | 0 | 0 | No
2030-11-20 07:00 | 2030 Initial | -700 | 0 | -210 | -25.85 | 0 | 0 | No
2030-11-20 08:00 | 2030 Initial | -700 | 0 | 90 | 4.03 | 0 | 0 | No
2030-11-20 09:00 | 2030 Initial | -700 | 0 | 37.01 | 0 | 0 | 0 | No
2030-11-20 10:00 | 2030 Initial | -700 | 0 | -156.81 | 0 | 0 | 0 | No
2030-11-20 11:00 | 2030 Initial | -700 | 0 | -179.75 | 72.97 | 0 | 0 | No
2030-11-20 12:00 | 2030 Initial | -700 | 0 | -145.07 | 0 | 0 | 0 | No
2030-11-20 13:00 | 2030 Initial | -700 | 0 | -445.07 | -180.33 | 0 | 0 | No
2030-11-20 14:00 | 2030 Initial | -700 | 0 | -510 | -262.47 | 0 | 0 | No
2030-11-20 15:00 | 2030 Initial | -700 | 0 | -510 | -102.62 | 0 | 0 | No
2030-11-20 16:00 | 2030 Initial | -700 | 0 | -390 | -293.56 | 0 | 0 | No
2030-11-20 17:00 | 2030 Initial | -700 | -216.35 | -90 | 0 | 0 | 0 | No
2030-11-20 18:00 | 2030 Initial | -700 | 40.53 | 210 | 300 | 0 | 0 | No
2030-11-20 19:00 | 2030 Initial | -700 | 271.19 | 510 | 244.07 | 0 | 0 | No
2030-11-20 20:00 | 2030 Initial | -700 | 205 | 436.86 | 210 | 0 | 0 | No
2030-11-20 21:00 | 2030 Initial | -531.91 | 505 | 510 | 510 | 0 | 0 | No
2030-11-20 22:00 | 2030 Initial | -610.33 | 505 | 510 | 510 | 0 | 0 | No
2030-11-20 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 12:00 | 2030 Initial | -676.72 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 15:00 | 2030 Initial | -599.4 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 16:00 | 2030 Initial | -623.05 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 17:00 | 2030 Initial | -203.05 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 18:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 19:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 22:00 | 2030 Initial | 569.6 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 23:00 | 2030 Initial | 280.72 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 03:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 04:00 | 2030 Initial | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 05:00 | 2030 Initial | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 07:00 | 2030 Initial | -700 | 420.69 | 510 | 510 | 0 | 0 | No
2030-11-22 08:00 | 2030 Initial | -643.99 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 09:00 | 2030 Initial | -395.62 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 10:00 | 2030 Initial | -348.48 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 14:00 | 2030 Initial | -698.55 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 15:00 | 2030 Initial | -278.55 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 16:00 | 2030 Initial | 10.09 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 17:00 | 2030 Initial | -409.91 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 18:00 | 2030 Initial | 10.09 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 19:00 | 2030 Initial | 430.09 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 21:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 22:00 | 2030 Initial | 179.91 | 300 | 510 | 413 | 0 | 0 | No
2030-11-22 23:00 | 2030 Initial | 410.76 | 0 | 210 | 113 | 0 | 0 | No
2030-11-23 | 2030 Initial | 59.24 | 0 | 0 | 0 | 0 | 0 | No
2030-11-23 01:00 | 2030 Initial | 179.49 | 0 | -136.42 | 0 | 0 | 0 | No
2030-11-23 02:00 | 2030 Initial | 0 | 0 | -436.42 | -8.94 | 0 | 0 | No
2030-11-23 03:00 | 2030 Initial | -13.1 | -172.92 | -498.12 | 0 | 0 | 0 | No
2030-11-23 04:00 | 2030 Initial | -433.1 | -472.92 | -510 | -67.73 | 0 | 0 | No
2030-11-23 05:00 | 2030 Initial | -700 | -526 | -510 | -346.11 | 0 | 0 | No
2030-11-23 06:00 | 2030 Initial | -700 | -526 | -510 | -240.62 | 0 | 0 | No
2030-11-23 07:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-23 08:00 | 2030 Initial | -700 | -526 | -510 | -314.09 | 0 | 0 | No
2030-11-23 09:00 | 2030 Initial | -700 | -526 | -510 | -14.09 | 0 | 0 | No
2030-11-23 10:00 | 2030 Initial | -700 | -269.95 | -510 | -160.28 | 0 | 0 | No
2030-11-23 11:00 | 2030 Initial | -700 | -208.32 | -210 | -90 | 0 | 0 | No
2030-11-23 12:00 | 2030 Initial | -700 | 91.68 | 90 | 210 | 0 | 0 | No
2030-11-23 13:00 | 2030 Initial | -700 | 391.68 | 390 | 510 | 0 | 0 | No
2030-11-23 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-23 15:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-23 16:00 | 2030 Initial | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-11-23 17:00 | 2030 Initial | -700 | -95 | -90 | -90 | 0 | 0 | No
2030-11-23 18:00 | 2030 Initial | -700 | -300 | -90 | -270.39 | 0 | 0 | No
2030-11-23 19:00 | 2030 Initial | -700 | 0 | 210 | 29.61 | 0 | 0 | No
2030-11-23 20:00 | 2030 Initial | -700 | 300 | 510 | 329.61 | 0 | 0 | No
2030-11-23 21:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-23 22:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-23 23:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 | 2030 Initial | -495.84 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 01:00 | 2030 Initial | -395.58 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 02:00 | 2030 Initial | -5.04 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 03:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 04:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 14:00 | 2030 Initial | -486.64 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 15:00 | 2030 Initial | -556.74 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 16:00 | 2030 Initial | -136.74 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 17:00 | 2030 Initial | 283.26 | 205 | 210 | 510 | 0 | 0 | No
2030-11-24 18:00 | 2030 Initial | 700 | 238.99 | 510 | 510 | 0 | 0 | No
2030-11-24 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 21:00 | 2030 Initial | 700 | 286.52 | 510 | 510 | 0 | 0 | No
2030-11-24 22:00 | 2030 Initial | 700 | 205 | 435.6 | 439.77 | 0 | 0 | No
2030-11-24 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 06:00 | 2030 Initial | 411.44 | 205 | 210 | 210 | 0 | 0 | No
2030-11-25 07:00 | 2030 Initial | 700 | -95 | -18.77 | -90 | 0 | 0 | No
2030-11-25 08:00 | 2030 Initial | 700 | 75.52 | 281.23 | 210 | 0 | 0 | No
2030-11-25 09:00 | 2030 Initial | 700 | 82.89 | 510 | 510 | 0 | 0 | No
2030-11-25 10:00 | 2030 Initial | 700 | 225.68 | 510 | 510 | 0 | 0 | No
2030-11-25 11:00 | 2030 Initial | 700 | 0 | 510 | 359.04 | 0 | 0 | No
2030-11-25 12:00 | 2030 Initial | 700 | 0 | 286.95 | 176.28 | 0 | 0 | No
2030-11-25 13:00 | 2030 Initial | 700 | 0 | 108.9 | 116.31 | 0 | 0 | No
2030-11-25 14:00 | 2030 Initial | 700 | 0 | 146.67 | 0 | 0 | 0 | No
2030-11-25 15:00 | 2030 Initial | 700 | 0 | 446.67 | 0 | 0 | 0 | No
2030-11-25 16:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-11-25 17:00 | 2030 Initial | 700 | 0 | 510 | 170.73 | 0 | 0 | No
2030-11-25 18:00 | 2030 Initial | 700 | 0 | 510 | 470.73 | 0 | 0 | No
2030-11-25 19:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-11-25 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-11-25 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-11-25 22:00 | 2030 Initial | 700 | 291.66 | 510 | 510 | 0 | 0 | No
2030-11-25 23:00 | 2030 Initial | 700 | 0 | 510 | 343.36 | 0 | 0 | No
2030-11-26 | 2030 Initial | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-11-26 01:00 | 2030 Initial | 700 | 382.35 | 510 | 510 | 0 | 0 | No
2030-11-26 02:00 | 2030 Initial | 700 | 489.73 | 510 | 510 | 0 | 0 | No
2030-11-26 03:00 | 2030 Initial | 566.87 | 460.51 | 510 | 510 | 0 | 0 | No
2030-11-26 04:00 | 2030 Initial | 146.87 | 488.65 | 510 | 461.13 | 0 | 0 | No
2030-11-26 05:00 | 2030 Initial | -273.13 | 300 | 300 | 161.13 | 0 | 0 | No
2030-11-26 06:00 | 2030 Initial | 15.43 | 0 | 0 | -138.87 | 0 | 0 | No
2030-11-26 07:00 | 2030 Initial | 325.82 | 0 | -47.6 | -149.92 | 0 | 0 | No
2030-11-26 08:00 | 2030 Initial | 280 | 0 | -347.6 | -449.92 | 0 | 0 | No
2030-11-26 09:00 | 2030 Initial | 700 | -217.23 | -510 | -510 | 0 | 0 | No
2030-11-26 10:00 | 2030 Initial | 415.79 | 0 | -210 | -210 | 0 | 0 | No
2030-11-26 11:00 | 2030 Initial | 311.11 | 0 | -157.86 | 0 | 0 | 0 | No
2030-11-26 12:00 | 2030 Initial | 0 | 0 | -457.86 | -300 | 0 | 0 | No
2030-11-26 13:00 | 2030 Initial | 0 | 0 | -510 | -313.48 | 0 | 0 | No
2030-11-26 14:00 | 2030 Initial | 105.98 | 0 | -510 | -363.4 | 0 | 0 | No
2030-11-26 15:00 | 2030 Initial | 525.98 | -226 | -510 | -240.03 | 0 | 0 | No
2030-11-26 16:00 | 2030 Initial | 697.25 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 17:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 18:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 19:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 20:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 21:00 | 2030 Initial | 700 | -226 | -260.47 | -494.56 | 0 | 0 | No
2030-11-26 22:00 | 2030 Initial | 700 | 74 | 39.53 | -194.56 | 0 | 0 | No
2030-11-26 23:00 | 2030 Initial | 700 | 0 | -97.29 | -37.21 | 0 | 0 | No
2030-11-27 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-11-27 01:00 | 2030 Initial | 700 | 0 | 74.77 | 0 | 0 | 0 | No
2030-11-27 02:00 | 2030 Initial | 700 | 75.77 | 374.77 | 106.98 | 0 | 0 | No
2030-11-27 03:00 | 2030 Initial | 599.05 | 0 | 74.77 | 0 | 0 | 0 | No
2030-11-27 04:00 | 2030 Initial | 179.05 | 0 | 0 | 0 | 0 | 0 | No
2030-11-27 05:00 | 2030 Initial | -240.95 | 0 | 0 | -293.02 | 0 | 0 | No
2030-11-27 06:00 | 2030 Initial | -660.95 | 0 | -210 | -242.14 | 0 | 0 | No
2030-11-27 07:00 | 2030 Initial | -240.95 | -233.05 | -510 | -510 | 0 | 0 | No
2030-11-27 08:00 | 2030 Initial | 179.05 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 09:00 | 2030 Initial | 599.05 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 10:00 | 2030 Initial | 700 | -318.08 | -510 | -510 | 0 | 0 | No
2030-11-27 11:00 | 2030 Initial | 700 | -483.93 | -510 | -510 | 0 | 0 | No
2030-11-27 12:00 | 2030 Initial | 432.57 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 13:00 | 2030 Initial | 448.44 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 14:00 | 2030 Initial | 523.94 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 15:00 | 2030 Initial | 672.15 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 16:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 17:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 18:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 19:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 20:00 | 2030 Initial | 700 | -292.11 | -300 | -300 | 0 | 0 | No
2030-11-27 21:00 | 2030 Initial | 700 | 7.89 | 0 | 0 | 0 | 0 | No
2030-11-27 22:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-11-27 23:00 | 2030 Initial | 700 | 0 | 189.86 | 0 | 0 | 0 | No
2030-11-28 | 2030 Initial | 700 | 0 | 489.86 | 300 | 0 | 0 | No
2030-11-28 01:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-11-28 02:00 | 2030 Initial | 625.53 | 0 | 510 | 510 | 0 | 0 | No
2030-11-28 03:00 | 2030 Initial | 205.53 | 0 | 510 | 510 | 0 | 0 | No
2030-11-28 04:00 | 2030 Initial | -214.47 | 0 | 510 | 481.67 | 0 | 0 | No
2030-11-28 05:00 | 2030 Initial | -634.47 | 150.13 | 510 | 181.67 | 0 | 0 | No
2030-11-28 06:00 | 2030 Initial | -700 | 9.07 | 300 | -118.33 | 0 | 0 | No
2030-11-28 07:00 | 2030 Initial | -280 | 0 | 0 | -418.33 | 0 | 0 | No
2030-11-28 08:00 | 2030 Initial | 0 | 0 | -152.18 | -222.76 | 0 | 0 | No
2030-11-28 09:00 | 2030 Initial | 420 | 0 | -300 | -340.5 | 0 | 0 | No
2030-11-28 10:00 | 2030 Initial | 517.45 | 0 | 0 | -159.91 | 0 | 0 | No
2030-11-28 11:00 | 2030 Initial | 294.09 | 0 | 0 | -48.77 | 0 | 0 | No
2030-11-28 12:00 | 2030 Initial | 0 | 0 | -109.04 | 0 | 0 | 0 | No
2030-11-28 13:00 | 2030 Initial | 0 | 0 | -35.72 | 0 | 0 | 0 | No
2030-11-28 14:00 | 2030 Initial | 224.91 | 0 | 0 | -20.88 | 0 | 0 | No
2030-11-28 15:00 | 2030 Initial | 454.91 | 0 | 0 | 0 | 0 | 0 | No
2030-11-28 16:00 | 2030 Initial | 439.29 | -226 | -210 | -289.87 | 0 | 0 | No
2030-11-28 17:00 | 2030 Initial | 608.22 | -526 | -510 | -510 | 0 | 0 | No
2030-11-28 18:00 | 2030 Initial | 700 | -321.33 | -510 | -510 | 0 | 0 | No
2030-11-28 19:00 | 2030 Initial | 700 | -21.33 | -510 | -276.04 | 0 | 0 | No
2030-11-28 20:00 | 2030 Initial | 700 | 278.67 | 0 | 23.96 | 0 | 0 | No
2030-11-28 21:00 | 2030 Initial | 700 | 473.47 | 0 | 0 | 0 | 0 | No
2030-11-28 22:00 | 2030 Initial | 700 | 221.77 | 0 | 202.89 | 0 | 0 | No
2030-11-28 23:00 | 2030 Initial | 700 | 464.42 | 0 | 502.89 | 0 | 0 | No
2030-11-29 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 01:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 02:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 03:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 04:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 05:00 | 2030 Initial | 465.46 | 505 | 0 | 361.35 | 0 | 0 | No
2030-11-29 06:00 | 2030 Initial | 700 | 205 | 0 | 61.35 | 0 | 0 | No
2030-11-29 07:00 | 2030 Initial | 700 | 16.51 | 0 | -35.05 | 0 | 0 | No
2030-11-29 08:00 | 2030 Initial | 619.4 | 205 | 0 | -335.05 | 0 | 0 | No
2030-11-29 09:00 | 2030 Initial | 700 | 505 | 0 | -35.05 | 0 | 0 | No
2030-11-29 10:00 | 2030 Initial | 700 | 505 | 0 | 111.9 | 0 | 0 | No
2030-11-29 11:00 | 2030 Initial | 700 | 505 | 0 | 1.39 | 0 | 0 | No
2030-11-29 12:00 | 2030 Initial | 700 | 505 | 0 | 1.39 | 0 | 0 | No
2030-11-29 13:00 | 2030 Initial | 700 | 414.38 | 0 | -19.88 | 0 | 0 | No
2030-11-29 14:00 | 2030 Initial | 700 | 300 | 0 | 28.2 | 0 | 0 | No
2030-11-29 15:00 | 2030 Initial | 280 | 0 | 0 | -210 | 0 | 0 | No
2030-11-29 16:00 | 2030 Initial | 700 | -288.87 | 0 | -510 | 0 | 0 | No
2030-11-29 17:00 | 2030 Initial | 700 | -526 | 0 | -510 | 0 | 0 | No
2030-11-29 18:00 | 2030 Initial | 700 | -526 | 0 | -510 | 0 | 0 | No
2030-11-29 19:00 | 2030 Initial | 700 | -286.53 | 0 | -510 | 0 | 0 | No
2030-11-29 20:00 | 2030 Initial | 700 | 13.47 | 0 | -210 | 0 | 0 | No
2030-11-29 21:00 | 2030 Initial | 700 | 170.23 | 0 | -21.77 | 0 | 0 | No
2030-11-29 22:00 | 2030 Initial | 700 | 434.41 | 0 | -125.8 | 0 | 0 | No
2030-11-29 23:00 | 2030 Initial | 700 | 505 | 0 | 174.2 | 0 | 0 | No
2030-11-30 | 2030 Initial | 405.08 | 205 | 0 | 0 | 0 | 0 | No
2030-11-30 01:00 | 2030 Initial | 623.64 | 0 | 0 | 0 | 0 | 0 | No
2030-11-30 02:00 | 2030 Initial | 560 | 0 | 0 | -28.04 | 0 | 0 | No
2030-11-30 03:00 | 2030 Initial | 140 | 0 | 0 | -225.92 | 0 | 0 | No
2030-11-30 04:00 | 2030 Initial | -280 | 0 | 0 | 0 | 0 | 0 | No
2030-11-30 05:00 | 2030 Initial | -700 | 0 | 0 | -140.19 | 0 | 0 | No
2030-11-30 06:00 | 2030 Initial | -700 | 0 | 0 | -307.96 | 0 | 0 | No
2030-11-30 07:00 | 2030 Initial | -700 | 0 | 0 | -382.21 | 0 | 0 | No
2030-11-30 08:00 | 2030 Initial | -700 | 0 | 0 | -419.27 | 0 | 0 | No
2030-11-30 09:00 | 2030 Initial | -700 | 0 | 0 | -183.22 | 0 | 0 | No
2030-11-30 10:00 | 2030 Initial | -700 | 227.28 | 0 | -183.69 | 0 | 0 | No
2030-11-30 11:00 | 2030 Initial | -700 | 505 | 0 | 116.31 | 0 | 0 | No
2030-11-30 12:00 | 2030 Initial | -700 | 505 | 0 | 416.31 | 0 | 0 | No
2030-11-30 13:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 14:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 15:00 | 2030 Initial | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 16:00 | 2030 Initial | -700 | 505 | 0 | 439.92 | 0 | 0 | No
2030-11-30 17:00 | 2030 Initial | -606.66 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 18:00 | 2030 Initial | -186.66 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 19:00 | 2030 Initial | 233.34 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 20:00 | 2030 Initial | 653.34 | 505 | 300 | 510 | 0 | 0 | No
2030-11-30 21:00 | 2030 Initial | 700 | 205 | 339.32 | 210 | 0 | 0 | No
2030-11-30 22:00 | 2030 Initial | 700 | 205 | 510 | 214.4 | 0 | 0 | No
2030-11-30 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 06:00 | 2030 Initial | 700 | 205 | 510 | 210 | 0 | 0 | No
2030-12-01 07:00 | 2030 Initial | 551.21 | 0 | 470.87 | 0 | 0 | 0 | No
2030-12-01 08:00 | 2030 Initial | 131.21 | 0 | 510 | 234.22 | 0 | 0 | No
2030-12-01 09:00 | 2030 Initial | 403.94 | 72.13 | 510 | 510 | 0 | 0 | No
2030-12-01 10:00 | 2030 Initial | 340.66 | 311.63 | 510 | 510 | 0 | 0 | No
2030-12-01 11:00 | 2030 Initial | 160.48 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 12:00 | 2030 Initial | 131.46 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 13:00 | 2030 Initial | 412.06 | 300 | 510 | 510 | 0 | 0 | No
2030-12-01 14:00 | 2030 Initial | 638.72 | 0 | 510 | 369.04 | 0 | 0 | No
2030-12-01 15:00 | 2030 Initial | 218.72 | 0 | 510 | 357.21 | 0 | 0 | No
2030-12-01 16:00 | 2030 Initial | 144.83 | 0 | 300 | 120.66 | 0 | 0 | No
2030-12-01 17:00 | 2030 Initial | 144.83 | 0 | 0 | 0 | 0 | 0 | No
2030-12-01 18:00 | 2030 Initial | 144.83 | 0 | 0 | 0 | 0 | 0 | No
2030-12-01 19:00 | 2030 Initial | 474.64 | 0 | 269.86 | 0 | 0 | 0 | No
2030-12-01 20:00 | 2030 Initial | 700 | 0 | 510 | 262.51 | 0 | 0 | No
2030-12-01 21:00 | 2030 Initial | 700 | 0 | 401.83 | 0 | 0 | 0 | No
2030-12-01 22:00 | 2030 Initial | 700 | 0 | 101.83 | 0 | 0 | 0 | No
2030-12-01 23:00 | 2030 Initial | 700 | 0 | 55.28 | 0 | 0 | 0 | No
2030-12-02 | 2030 Initial | 700 | 0 | 90 | 129.28 | 0 | 0 | No
2030-12-02 01:00 | 2030 Initial | 700 | 0 | -210 | -144.23 | 0 | 0 | No
2030-12-02 02:00 | 2030 Initial | 700 | 0 | -510 | -294.61 | 0 | 0 | No
2030-12-02 03:00 | 2030 Initial | 700 | 0 | -510 | -341.82 | 0 | 0 | No
2030-12-02 04:00 | 2030 Initial | 560 | -120.47 | -510 | -510 | 0 | 0 | No
2030-12-02 05:00 | 2030 Initial | 140 | -334.15 | -410.07 | -510 | 0 | 0 | No
2030-12-02 06:00 | 2030 Initial | -280 | -34.15 | -110.07 | -379.82 | 0 | 0 | No
2030-12-02 07:00 | 2030 Initial | -700 | 0 | 189.93 | -79.82 | 0 | 0 | No
2030-12-02 08:00 | 2030 Initial | -700 | 300 | 489.93 | 210 | 0 | 0 | No
2030-12-02 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-02 10:00 | 2030 Initial | -700 | 505 | 510 | 295.39 | 0 | 0 | No
2030-12-02 11:00 | 2030 Initial | -700 | 402.4 | 510 | 352.21 | 0 | 0 | No
2030-12-02 12:00 | 2030 Initial | -700 | 102.4 | 250.03 | 52.21 | 0 | 0 | No
2030-12-02 13:00 | 2030 Initial | -700 | 0 | 310.24 | 131.89 | 0 | 0 | No
2030-12-02 14:00 | 2030 Initial | -700 | 0 | 510 | 431.89 | 0 | 0 | No
2030-12-02 15:00 | 2030 Initial | -700 | 47.57 | 510 | 444.94 | 0 | 0 | No
2030-12-02 16:00 | 2030 Initial | -700 | 347.57 | 510 | 510 | 0 | 0 | No
2030-12-02 17:00 | 2030 Initial | -700 | 399.27 | 510 | 510 | 0 | 0 | No
2030-12-02 18:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-02 19:00 | 2030 Initial | -470.95 | 505 | 510 | 510 | 0 | 0 | No
2030-12-02 20:00 | 2030 Initial | -50.95 | 505 | 510 | 510 | 0 | 0 | No
2030-12-02 21:00 | 2030 Initial | 369.05 | 205 | 510 | 485.27 | 0 | 0 | No
2030-12-02 22:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-02 23:00 | 2030 Initial | -420 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 01:00 | 2030 Initial | 420 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 04:00 | 2030 Initial | 395.34 | 505 | 510 | 443.05 | 0 | 0 | No
2030-12-03 05:00 | 2030 Initial | -24.66 | 505 | 510 | 143.05 | 0 | 0 | No
2030-12-03 06:00 | 2030 Initial | -444.66 | 370.38 | 510 | 101.39 | 0 | 0 | No
2030-12-03 07:00 | 2030 Initial | -484.37 | 505 | 510 | 288.93 | 0 | 0 | No
2030-12-03 08:00 | 2030 Initial | -64.37 | 287.25 | 510 | 510 | 0 | 0 | No
2030-12-03 09:00 | 2030 Initial | 355.63 | 205 | 449.93 | 210 | 0 | 0 | No
2030-12-03 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 11:00 | 2030 Initial | 673.57 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 16:00 | 2030 Initial | 700 | 205 | 510 | 438.35 | 0 | 0 | No
2030-12-03 17:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-12-03 18:00 | 2030 Initial | 700 | 245.32 | 510 | 510 | 0 | 0 | No
2030-12-03 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 20:00 | 2030 Initial | 700 | 500.75 | 510 | 510 | 0 | 0 | No
2030-12-03 21:00 | 2030 Initial | 700 | 369.44 | 510 | 510 | 0 | 0 | No
2030-12-03 22:00 | 2030 Initial | 700 | 486.91 | 510 | 510 | 0 | 0 | No
2030-12-03 23:00 | 2030 Initial | 700 | 205 | 510 | 210.1 | 0 | 0 | No
2030-12-04 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-04 01:00 | 2030 Initial | 700 | 205 | 493.71 | 210 | 0 | 0 | No
2030-12-04 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-04 03:00 | 2030 Initial | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-12-04 04:00 | 2030 Initial | 140 | 505 | 510 | 482.41 | 0 | 0 | No
2030-12-04 05:00 | 2030 Initial | -280 | 505 | 510 | 182.41 | 0 | 0 | No
2030-12-04 06:00 | 2030 Initial | -700 | 505 | 510 | -117.59 | 0 | 0 | No
2030-12-04 07:00 | 2030 Initial | -700 | 205 | 210 | -417.59 | 0 | 0 | No
2030-12-04 08:00 | 2030 Initial | -700 | 0 | -90 | -433.15 | 0 | 0 | No
2030-12-04 09:00 | 2030 Initial | -700 | 0 | -186.01 | -133.15 | 0 | 0 | No
2030-12-04 10:00 | 2030 Initial | -700 | 0 | -453.48 | -85.63 | 0 | 0 | No
2030-12-04 11:00 | 2030 Initial | -700 | 0 | -313.04 | -85.63 | 0 | 0 | No
2030-12-04 12:00 | 2030 Initial | -700 | 0 | -13.04 | 0 | 0 | 0 | No
2030-12-04 13:00 | 2030 Initial | -700 | 300 | 286.96 | 300 | 0 | 0 | No
2030-12-04 14:00 | 2030 Initial | -700 | 300.88 | 510 | 510 | 0 | 0 | No
2030-12-04 15:00 | 2030 Initial | -700 | 0.88 | 210 | 210 | 0 | 0 | No
2030-12-04 16:00 | 2030 Initial | -700 | -299.12 | -90 | -90 | 0 | 0 | No
2030-12-04 17:00 | 2030 Initial | -700 | 0 | -390 | -371.07 | 0 | 0 | No
2030-12-04 18:00 | 2030 Initial | -700 | 0 | -461.06 | -371.07 | 0 | 0 | No
2030-12-04 19:00 | 2030 Initial | -700 | 0 | -161.06 | -71.07 | 0 | 0 | No
2030-12-04 20:00 | 2030 Initial | -700 | 0 | 138.94 | -30.95 | 0 | 0 | No
2030-12-04 21:00 | 2030 Initial | -700 | 300 | 438.94 | 269.05 | 0 | 0 | Yes
2030-12-04 22:00 | 2030 Initial | -700 | 505 | 510 | 424.29 | 0 | 0 | Yes
2030-12-04 23:00 | 2030 Initial | -700 | 505 | 510 | 275.07 | 0 | 0 | Yes
2030-12-05 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-05 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-05 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-05 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-05 04:00 | 2030 Initial | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-12-05 05:00 | 2030 Initial | -700 | 74 | 90 | 293.99 | 0 | 0 | Yes
2030-12-05 06:00 | 2030 Initial | -700 | -226 | -210 | -6.01 | 0 | 0 | No
2030-12-05 07:00 | 2030 Initial | -700 | -526 | -510 | -50.98 | 0 | 0 | No
2030-12-05 08:00 | 2030 Initial | -700 | -459.5 | -510 | 238.81 | 0 | 0 | No
2030-12-05 09:00 | 2030 Initial | -700 | -175.64 | -510 | -61.19 | 0 | 0 | No
2030-12-05 10:00 | 2030 Initial | -700 | 0 | -299.18 | 0 | 0 | 0 | No
2030-12-05 11:00 | 2030 Initial | -700 | 0 | -387.47 | 52.82 | 0 | 0 | No
2030-12-05 12:00 | 2030 Initial | -700 | 0 | -139.23 | 0 | 0 | 0 | No
2030-12-05 13:00 | 2030 Initial | -280 | 0 | -314.99 | 0 | 0 | 0 | No
2030-12-05 14:00 | 2030 Initial | 0 | 0 | -102.04 | 0 | 0 | 0 | No
2030-12-05 15:00 | 2030 Initial | 381.45 | 0 | -71.82 | 0 | 0 | 0 | No
2030-12-05 16:00 | 2030 Initial | -38.55 | 0 | 183.95 | 0 | 0 | 0 | No
2030-12-05 17:00 | 2030 Initial | 0 | 0 | -116.05 | -54.43 | 0 | 0 | No
2030-12-05 18:00 | 2030 Initial | 280 | 0 | 0 | 0 | 0 | 0 | No
2030-12-05 19:00 | 2030 Initial | 700 | 99.58 | 300 | 300 | 0 | 0 | No
2030-12-05 20:00 | 2030 Initial | 700 | 381.67 | 510 | 443.76 | 0 | 0 | No
2030-12-05 21:00 | 2030 Initial | 700 | 501.53 | 510 | 331.73 | 0 | 0 | No
2030-12-05 22:00 | 2030 Initial | 700 | 310.83 | 510 | 258.96 | 0 | 0 | No
2030-12-05 23:00 | 2030 Initial | 700 | 194.7 | 510 | 510 | 0 | 0 | No
2030-12-06 | 2030 Initial | 700 | 494.7 | 510 | 510 | 0 | 0 | No
2030-12-06 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-06 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-06 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-06 04:00 | 2030 Initial | 700 | 505 | 510 | 477.49 | 0 | 0 | No
2030-12-06 05:00 | 2030 Initial | 544.49 | 505 | 510 | 177.49 | 0 | 0 | No
2030-12-06 06:00 | 2030 Initial | 124.49 | 505 | 510 | -122.51 | 0 | 0 | No
2030-12-06 07:00 | 2030 Initial | 235.92 | 205 | 210 | -422.51 | 0 | 0 | No
2030-12-06 08:00 | 2030 Initial | 655.92 | 0 | -90 | -467.26 | 0 | 0 | No
2030-12-06 09:00 | 2030 Initial | 700 | 0 | -126.29 | -167.26 | 0 | 0 | No
2030-12-06 10:00 | 2030 Initial | 700 | 0 | -166.97 | 0 | 0 | 0 | No
2030-12-06 11:00 | 2030 Initial | 700 | 0 | -438.69 | 0 | 0 | 0 | No
2030-12-06 12:00 | 2030 Initial | 700 | 0 | -510 | -214.03 | 0 | 0 | No
2030-12-06 13:00 | 2030 Initial | 700 | 0 | -510 | -253.73 | 0 | 0 | No
2030-12-06 14:00 | 2030 Initial | 700 | 0 | -510 | -226.53 | 0 | 0 | No
2030-12-06 15:00 | 2030 Initial | 700 | 0 | -510 | -510 | 0 | 0 | No
2030-12-06 16:00 | 2030 Initial | 700 | 0 | -510 | -510 | 0 | 0 | No
2030-12-06 17:00 | 2030 Initial | 700 | 0 | -510 | -410.7 | 0 | 0 | No
2030-12-06 18:00 | 2030 Initial | 700 | 0 | -510 | -110.7 | 0 | 0 | No
2030-12-06 19:00 | 2030 Initial | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-12-06 20:00 | 2030 Initial | 700 | 0 | -510 | -271.06 | 0 | 0 | No
2030-12-06 21:00 | 2030 Initial | 700 | 0 | -489.41 | -405.05 | 0 | 0 | No
2030-12-06 22:00 | 2030 Initial | 700 | 0 | -189.41 | -105.05 | 0 | 0 | No
2030-12-06 23:00 | 2030 Initial | 700 | 257.65 | 110.59 | 194.95 | 0 | 0 | No
2030-12-07 | 2030 Initial | 700 | 0 | 410.59 | 0 | 0 | 0 | No
2030-12-07 01:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-07 02:00 | 2030 Initial | 700 | 170.17 | 510 | 0 | 0 | 0 | No
2030-12-07 03:00 | 2030 Initial | 560 | 345.29 | 510 | 190.89 | 0 | 0 | No
2030-12-07 04:00 | 2030 Initial | 140 | 50.77 | 510 | 24.16 | 0 | 0 | No
2030-12-07 05:00 | 2030 Initial | -280 | 0 | 510 | 0 | 0 | 0 | No
2030-12-07 06:00 | 2030 Initial | -700 | 198.38 | 510 | 0 | 0 | 0 | No
2030-12-07 07:00 | 2030 Initial | -700 | 0 | 210 | -300 | 0 | 0 | No
2030-12-07 08:00 | 2030 Initial | -527.62 | 0 | 0 | -121.11 | 0 | 0 | No
2030-12-07 09:00 | 2030 Initial | -107.62 | 0 | 0 | -115.74 | 0 | 0 | No
2030-12-07 10:00 | 2030 Initial | -107.52 | 205 | 210 | -49.37 | 0 | 0 | No
2030-12-07 11:00 | 2030 Initial | -429.93 | 505 | 510 | 250.63 | 0 | 0 | No
2030-12-07 12:00 | 2030 Initial | -429.93 | 505 | 510 | 160.6 | 0 | 0 | No
2030-12-07 13:00 | 2030 Initial | -251.72 | 505 | 300 | 163.47 | 0 | 0 | No
2030-12-07 14:00 | 2030 Initial | 0 | 505 | 0 | 110.11 | 0 | 0 | No
2030-12-07 15:00 | 2030 Initial | 420 | 505 | 0 | 111.68 | 0 | 0 | No
2030-12-07 16:00 | 2030 Initial | 0 | 505 | 0 | 80.49 | 0 | 0 | No
2030-12-07 17:00 | 2030 Initial | 280 | 505 | 0 | 179.7 | 0 | 0 | No
2030-12-07 18:00 | 2030 Initial | 700 | 505 | 0 | 430.51 | 0 | 0 | No
2030-12-07 19:00 | 2030 Initial | 700 | 455.21 | 0 | 327.46 | 0 | 0 | No
2030-12-07 20:00 | 2030 Initial | 700 | 505 | 0 | 385.56 | 0 | 0 | No
2030-12-07 21:00 | 2030 Initial | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-12-07 22:00 | 2030 Initial | 668.66 | 505 | 0 | 487.4 | 0 | 0 | No
2030-12-07 23:00 | 2030 Initial | 700 | 391.36 | 0 | 360.6 | 0 | 0 | No
2030-12-08 | 2030 Initial | 700 | 219.24 | 0 | 343.4 | 0 | 0 | No
2030-12-08 01:00 | 2030 Initial | 700 | 415.81 | 0 | 107.67 | 0 | 0 | No
2030-12-08 02:00 | 2030 Initial | 700 | 118.3 | 0 | 103.2 | 0 | 0 | No
2030-12-08 03:00 | 2030 Initial | 393.71 | 189.09 | 0 | 0 | 0 | 0 | No
2030-12-08 04:00 | 2030 Initial | 0 | 300 | 0 | -300 | 0 | 0 | No
2030-12-08 05:00 | 2030 Initial | -280 | 0 | 0 | -510 | 0 | 0 | No
2030-12-08 06:00 | 2030 Initial | -700 | -300 | 0 | -510 | 0 | 0 | No
2030-12-08 07:00 | 2030 Initial | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 08:00 | 2030 Initial | -700 | -382.55 | 0 | -510 | 0 | 0 | No
2030-12-08 09:00 | 2030 Initial | -700 | -441.14 | 0 | -510 | 0 | 0 | No
2030-12-08 10:00 | 2030 Initial | -700 | -141.14 | 0 | -510 | 0 | 0 | No
2030-12-08 11:00 | 2030 Initial | -700 | -230.7 | 0 | -510 | 0 | 0 | No
2030-12-08 12:00 | 2030 Initial | -700 | -169.41 | 0 | -510 | 0 | 0 | No
2030-12-08 13:00 | 2030 Initial | -700 | -469.41 | 0 | -510 | 0 | 0 | No
2030-12-08 14:00 | 2030 Initial | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 15:00 | 2030 Initial | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 16:00 | 2030 Initial | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 17:00 | 2030 Initial | -700 | -506.52 | 0 | -510 | 0 | 0 | No
2030-12-08 18:00 | 2030 Initial | -700 | -206.52 | 0 | -323.6 | 0 | 0 | No
2030-12-08 19:00 | 2030 Initial | -420.07 | 0 | 0 | -23.6 | 0 | 0 | No
2030-12-08 20:00 | 2030 Initial | -0.07 | 300 | 0 | 276.4 | 0 | 0 | No
2030-12-08 21:00 | 2030 Initial | 280 | 262.39 | 0 | 326.85 | 0 | 0 | No
2030-12-08 22:00 | 2030 Initial | 700 | 0 | 0 | 26.85 | 0 | 0 | No
2030-12-08 23:00 | 2030 Initial | 282.93 | 1.15 | 0 | -273.15 | 0 | 0 | No
2030-12-09 | 2030 Initial | 700 | 301.15 | 0 | -85.44 | 0 | 0 | No
2030-12-09 01:00 | 2030 Initial | 700 | 147.72 | 0 | -330.58 | 0 | 0 | No
2030-12-09 02:00 | 2030 Initial | 700 | 0 | 0 | -510 | 0 | 0 | No
2030-12-09 03:00 | 2030 Initial | 700 | 0.74 | 0 | -210 | 0 | 0 | No
2030-12-09 04:00 | 2030 Initial | 700 | 0 | 0 | 19.85 | 0 | 0 | No
2030-12-09 05:00 | 2030 Initial | 700 | 0 | 0 | 68.51 | 0 | 0 | No
2030-12-09 06:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-09 07:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-09 08:00 | 2030 Initial | 427.55 | 0 | 0 | 80.74 | 0 | 0 | No
2030-12-09 09:00 | 2030 Initial | 7.55 | -226 | 0 | 243.96 | 0 | 0 | No
2030-12-09 10:00 | 2030 Initial | -412.45 | -526 | 0 | -56.04 | 0 | 0 | No
2030-12-09 11:00 | 2030 Initial | -700 | -526 | 0 | -11.88 | 0 | 0 | No
2030-12-09 12:00 | 2030 Initial | -280 | -260.71 | 0 | 288.12 | 0 | 0 | No
2030-12-09 13:00 | 2030 Initial | 140 | 0 | 0 | 67.55 | 0 | 0 | No
2030-12-09 14:00 | 2030 Initial | 506.09 | 0 | 0 | 0 | 0 | 0 | No
2030-12-09 15:00 | 2030 Initial | 280 | 0 | 0 | 0 | 0 | 0 | No
2030-12-09 16:00 | 2030 Initial | -140 | -300 | -90 | -265.62 | 0 | 0 | No
2030-12-09 17:00 | 2030 Initial | 280 | 0 | 210 | 34.38 | 0 | 0 | No
2030-12-09 18:00 | 2030 Initial | 700 | 300 | 510 | 334.38 | 0 | 0 | No
2030-12-09 19:00 | 2030 Initial | 700 | 0 | 421.45 | 34.38 | 0 | 0 | No
2030-12-09 20:00 | 2030 Initial | 700 | 0 | 510 | 177.41 | 0 | 0 | No
2030-12-09 21:00 | 2030 Initial | 700 | 0 | 363.58 | 0 | 0 | 0 | No
2030-12-09 22:00 | 2030 Initial | 688.55 | 49.23 | 210 | 210 | 0 | 0 | No
2030-12-09 23:00 | 2030 Initial | 700 | 349.23 | 510 | 510 | 0 | 0 | No
2030-12-10 | 2030 Initial | 700 | 293.7 | 510 | 510 | 0 | 0 | No
2030-12-10 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 05:00 | 2030 Initial | 619.78 | 205 | 210 | 210 | 0 | 0 | No
2030-12-10 06:00 | 2030 Initial | 700 | 0 | 374.47 | 210 | 0 | 0 | No
2030-12-10 07:00 | 2030 Initial | 418.77 | 108.29 | 510 | 510 | 0 | 0 | No
2030-12-10 08:00 | 2030 Initial | 569.58 | 408.29 | 510 | 510 | 0 | 0 | No
2030-12-10 09:00 | 2030 Initial | 569.58 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 10:00 | 2030 Initial | 149.58 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 11:00 | 2030 Initial | -215.42 | 232.46 | 300 | 510 | 0 | 0 | No
2030-12-10 12:00 | 2030 Initial | -635.42 | 0 | 0 | 291.55 | 0 | 0 | No
2030-12-10 13:00 | 2030 Initial | -700 | -239.89 | -300 | 85.8 | 0 | 0 | No
2030-12-10 14:00 | 2030 Initial | -700 | -80.2 | -510 | -91.26 | 0 | 0 | No
2030-12-10 15:00 | 2030 Initial | -700 | 0 | -302.11 | 88.03 | 0 | 0 | No
2030-12-10 16:00 | 2030 Initial | -700 | -76.02 | -29.01 | 250.28 | 0 | 0 | No
2030-12-10 17:00 | 2030 Initial | -700 | 91.26 | 270.99 | 510 | 0 | 0 | No
2030-12-10 18:00 | 2030 Initial | -280 | 391.26 | 510 | 510 | 0 | 0 | No
2030-12-10 19:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 20:00 | 2030 Initial | 560 | 209.73 | 510 | 510 | 0 | 0 | No
2030-12-10 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 05:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 06:00 | 2030 Initial | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 07:00 | 2030 Initial | 280 | 205 | 487.59 | 210 | 0 | 0 | No
2030-12-11 08:00 | 2030 Initial | 430.16 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 09:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 10:00 | 2030 Initial | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 11:00 | 2030 Initial | 140 | 489.73 | 510 | 510 | 0 | 0 | No
2030-12-11 12:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 13:00 | 2030 Initial | -700 | 399.38 | 510 | 510 | 0 | 0 | No
2030-12-11 14:00 | 2030 Initial | -700 | 416.41 | 510 | 510 | 0 | 0 | No
2030-12-11 15:00 | 2030 Initial | -280 | 116.41 | 210 | 210 | 0 | 0 | No
2030-12-11 16:00 | 2030 Initial | 0 | 0 | -90 | 362.6 | 0 | 0 | No
2030-12-11 17:00 | 2030 Initial | 420 | 0 | -390 | 363.94 | 0 | 0 | No
2030-12-11 18:00 | 2030 Initial | 452.03 | 0 | -510 | 363.94 | 0 | 0 | No
2030-12-11 19:00 | 2030 Initial | 352.83 | 0 | -403.51 | 316 | 0 | 0 | No
2030-12-11 20:00 | 2030 Initial | 700 | 0 | -103.51 | 133.51 | 0 | 0 | No
2030-12-11 21:00 | 2030 Initial | 700 | 218.78 | 196.49 | 386.11 | 0 | 0 | No
2030-12-11 22:00 | 2030 Initial | 700 | 0 | -103.51 | 86.11 | 0 | 0 | No
2030-12-11 23:00 | 2030 Initial | 700 | 0 | -2.35 | 0 | 0 | 0 | No
2030-12-12 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-12 01:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-12 02:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-12 03:00 | 2030 Initial | 700 | 0 | -216 | 0 | 0 | 0 | No
2030-12-12 04:00 | 2030 Initial | 700 | 0 | -79.46 | 0 | 0 | 0 | No
2030-12-12 05:00 | 2030 Initial | 420 | 0 | -379.46 | 0 | 0 | 0 | No
2030-12-12 06:00 | 2030 Initial | 0 | 0 | -333.09 | -210 | 0 | 0 | No
2030-12-12 07:00 | 2030 Initial | 0 | -107.67 | -510 | -510 | 0 | 0 | No
2030-12-12 08:00 | 2030 Initial | 420 | 0 | -510 | -215.77 | 0 | 0 | No
2030-12-12 09:00 | 2030 Initial | 700 | 0 | -490.07 | 0 | 0 | 0 | No
2030-12-12 10:00 | 2030 Initial | 700 | 0 | -300 | -157.67 | 0 | 0 | No
2030-12-12 11:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-12 12:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-12 13:00 | 2030 Initial | 700 | 0 | 144.37 | 0 | 0 | 0 | No
2030-12-12 14:00 | 2030 Initial | 700 | 0 | 300 | 18.92 | 0 | 0 | No
2030-12-12 15:00 | 2030 Initial | 700 | 62.61 | 0 | 0 | 0 | 0 | No
2030-12-12 16:00 | 2030 Initial | 700 | -237.39 | -300 | -300 | 0 | 0 | No
2030-12-12 17:00 | 2030 Initial | 700 | -526 | -510 | -394.88 | 0 | 0 | No
2030-12-12 18:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 19:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 20:00 | 2030 Initial | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 21:00 | 2030 Initial | 352.7 | -526 | -510 | -369.54 | 0 | 0 | No
2030-12-12 22:00 | 2030 Initial | 150.86 | -526 | -510 | -239.9 | 0 | 0 | No
2030-12-12 23:00 | 2030 Initial | -11.77 | -526 | -510 | -40.64 | 0 | 0 | No
2030-12-13 | 2030 Initial | -431.77 | -526 | -510 | -87.49 | 0 | 0 | No
2030-12-13 01:00 | 2030 Initial | -700 | -526 | -510 | -10.64 | 0 | 0 | No
2030-12-13 02:00 | 2030 Initial | -700 | -526 | -510 | -258.66 | 0 | 0 | No
2030-12-13 03:00 | 2030 Initial | -524.8 | -526 | -510 | -231.65 | 0 | 0 | No
2030-12-13 04:00 | 2030 Initial | -552.08 | -526 | -510 | -510 | 0 | 0 | No
2030-12-13 05:00 | 2030 Initial | -514.05 | -526 | -510 | -510 | 0 | 0 | No
2030-12-13 06:00 | 2030 Initial | -700 | -310.15 | -510 | -510 | 0 | 0 | No
2030-12-13 07:00 | 2030 Initial | -700 | -10.15 | -442 | -235.81 | 0 | 0 | No
2030-12-13 08:00 | 2030 Initial | -700 | 0 | -264.87 | -122.66 | 0 | 0 | No
2030-12-13 09:00 | 2030 Initial | -280 | 0 | -409.8 | -65.14 | 0 | 0 | No
2030-12-13 10:00 | 2030 Initial | 0 | 0 | -110.73 | 0 | 0 | 0 | No
2030-12-13 11:00 | 2030 Initial | -24.18 | 0 | 189.27 | 300 | 0 | 0 | No
2030-12-13 12:00 | 2030 Initial | -444.18 | 0 | 31.24 | 141.45 | 0 | 0 | No
2030-12-13 13:00 | 2030 Initial | -700 | 279.29 | 331.24 | 441.45 | 0 | 0 | No
2030-12-13 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-13 15:00 | 2030 Initial | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-12-13 16:00 | 2030 Initial | -280 | -95 | -90 | 398.04 | 0 | 0 | No
2030-12-13 17:00 | 2030 Initial | 140 | -395 | -390 | 451.96 | 0 | 0 | No
2030-12-13 18:00 | 2030 Initial | 560 | -526 | -510 | 374.53 | 0 | 0 | No
2030-12-13 19:00 | 2030 Initial | 627.71 | -286.07 | -403.65 | 448.9 | 0 | 0 | No
2030-12-13 20:00 | 2030 Initial | 207.71 | -95 | -103.65 | 206.63 | 0 | 0 | No
2030-12-13 21:00 | 2030 Initial | 627.71 | 205 | 196.35 | 210 | 0 | 0 | No
2030-12-13 22:00 | 2030 Initial | 207.71 | 505 | 496.35 | 510 | 0 | 0 | No
2030-12-13 23:00 | 2030 Initial | -212.29 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 01:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 02:00 | 2030 Initial | -190.93 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 03:00 | 2030 Initial | -177.93 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 04:00 | 2030 Initial | -111.48 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 05:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 08:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 09:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 10:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 14:00 | 2030 Initial | -640.13 | 205 | 210 | 420.13 | 0 | 0 | No
2030-12-14 15:00 | 2030 Initial | -220.13 | 0 | 132.94 | 390.2 | 0 | 0 | No
2030-12-14 16:00 | 2030 Initial | 199.87 | 0 | 0 | 360.61 | 0 | 0 | No
2030-12-14 17:00 | 2030 Initial | 371.07 | 0 | 0 | 323.42 | 0 | 0 | No
2030-12-14 18:00 | 2030 Initial | 700 | 0 | 0 | 309.61 | 0 | 0 | No
2030-12-14 19:00 | 2030 Initial | 700 | 0 | 0 | 9.61 | 0 | 0 | No
2030-12-14 20:00 | 2030 Initial | 700 | 0 | 0 | 163.25 | 0 | 0 | No
2030-12-14 21:00 | 2030 Initial | 700 | -131.68 | -90 | 54.19 | 0 | 0 | No
2030-12-14 22:00 | 2030 Initial | 280 | 39.05 | 210 | 210 | 0 | 0 | No
2030-12-14 23:00 | 2030 Initial | 700 | 339.05 | 510 | 510 | 0 | 0 | No
2030-12-15 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 05:00 | 2030 Initial | 489.64 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 06:00 | 2030 Initial | 69.64 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 07:00 | 2030 Initial | -350.36 | 205 | 210 | 210 | 0 | 0 | No
2030-12-15 08:00 | 2030 Initial | -376.86 | -95 | -90 | 337.38 | 0 | 0 | No
2030-12-15 09:00 | 2030 Initial | 43.14 | 0 | -390 | 501.41 | 0 | 0 | No
2030-12-15 10:00 | 2030 Initial | 463.14 | 0 | -510 | 510 | 0 | 0 | No
2030-12-15 11:00 | 2030 Initial | 700 | 0 | -510 | 443.08 | 0 | 0 | No
2030-12-15 12:00 | 2030 Initial | 450.24 | 0 | -316.62 | 435.23 | 0 | 0 | No
2030-12-15 13:00 | 2030 Initial | 30.24 | 0 | -273.2 | 364.2 | 0 | 0 | No
2030-12-15 14:00 | 2030 Initial | 437.47 | -163.33 | -510 | 236.86 | 0 | 0 | No
2030-12-15 15:00 | 2030 Initial | 700 | -137.5 | -510 | 0 | 0 | 0 | No
2030-12-15 16:00 | 2030 Initial | 700 | -47.68 | -510 | 228.91 | 0 | 0 | No
2030-12-15 17:00 | 2030 Initial | 700 | 0 | -510 | 463.02 | 0 | 0 | No
2030-12-15 18:00 | 2030 Initial | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-12-15 19:00 | 2030 Initial | 700 | 0 | -510 | 347.66 | 0 | 0 | No
2030-12-15 20:00 | 2030 Initial | 506.46 | -300 | -349.5 | 510 | 0 | 0 | No
2030-12-15 21:00 | 2030 Initial | 659.66 | 0 | -49.5 | 340.72 | 0 | 0 | No
2030-12-15 22:00 | 2030 Initial | 239.66 | 300 | 250.5 | 510 | 0 | 0 | No
2030-12-15 23:00 | 2030 Initial | -180.34 | 0.25 | 510 | 510 | 0 | 0 | No
2030-12-16 | 2030 Initial | -502.32 | 0 | 510 | 337.59 | 0 | 0 | No
2030-12-16 01:00 | 2030 Initial | -700 | 300 | 510 | 414.29 | 0 | 0 | Yes
2030-12-16 02:00 | 2030 Initial | -700 | 505 | 510 | 246.9 | 0 | 0 | Yes
2030-12-16 03:00 | 2030 Initial | -700 | 505 | 510 | 246.9 | 0 | 0 | Yes
2030-12-16 04:00 | 2030 Initial | -700 | 505 | 510 | 169.05 | 0 | 0 | Yes
2030-12-16 05:00 | 2030 Initial | -700 | 505 | 510 | 120.63 | 0 | 0 | Yes
2030-12-16 06:00 | 2030 Initial | -700 | 505 | 510 | 181.93 | 0 | 0 | Yes
2030-12-16 07:00 | 2030 Initial | -700 | 505 | 510 | 79.61 | 0 | 0 | Yes
2030-12-16 08:00 | 2030 Initial | -700 | 505 | 510 | 274.03 | 0 | 0 | Yes
2030-12-16 09:00 | 2030 Initial | -408.6 | 505 | 510 | 421.7 | 0 | 0 | Yes
2030-12-16 10:00 | 2030 Initial | 11.4 | 505 | 510 | 469.88 | 0 | 0 | Yes
2030-12-16 11:00 | 2030 Initial | 431.4 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 12:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 13:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 14:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 15:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 16:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 17:00 | 2030 Initial | 280 | 285.67 | 510 | 510 | 0 | 0 | No
2030-12-16 18:00 | 2030 Initial | 605.02 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 19:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 20:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 04:00 | 2030 Initial | 478.65 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 05:00 | 2030 Initial | 58.65 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 06:00 | 2030 Initial | -361.35 | 205 | 378.97 | 417.43 | 0 | 0 | No
2030-12-17 07:00 | 2030 Initial | 58.65 | 0 | 263.56 | 121.28 | 0 | 0 | No
2030-12-17 08:00 | 2030 Initial | 20.35 | 0 | 510 | 421.28 | 0 | 0 | No
2030-12-17 09:00 | 2030 Initial | 440.35 | 0 | 305.21 | 510 | 0 | 0 | No
2030-12-17 10:00 | 2030 Initial | 20.35 | 0 | 5.21 | 510 | 0 | 0 | No
2030-12-17 11:00 | 2030 Initial | 0 | 0 | -294.79 | 510 | 0 | 0 | No
2030-12-17 12:00 | 2030 Initial | -280 | 0 | -375.45 | 472.34 | 0 | 0 | No
2030-12-17 13:00 | 2030 Initial | -700 | 0 | -175.37 | 172.34 | 0 | 0 | No
2030-12-17 14:00 | 2030 Initial | -700 | 0 | -185.31 | 201.78 | 0 | 0 | No
2030-12-17 15:00 | 2030 Initial | -700 | 0 | 0 | 400.74 | 0 | 0 | No
2030-12-17 16:00 | 2030 Initial | -700 | 0 | -53.4 | 277.85 | 0 | 0 | No
2030-12-17 17:00 | 2030 Initial | -280 | 0 | 100.84 | 118.28 | 0 | 0 | No
2030-12-17 18:00 | 2030 Initial | 140 | 0 | 359.94 | 0 | 0 | 0 | No
2030-12-17 19:00 | 2030 Initial | 560 | 0 | 359.94 | 0 | 0 | 0 | No
2030-12-17 20:00 | 2030 Initial | 280 | 205 | 210 | 210 | 0 | 0 | No
2030-12-17 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 02:00 | 2030 Initial | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 03:00 | 2030 Initial | -88.31 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 04:00 | 2030 Initial | -508.31 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 06:00 | 2030 Initial | -700 | 505 | 367.99 | 510 | 0 | 0 | No
2030-12-18 07:00 | 2030 Initial | -700 | 205 | 67.99 | 210 | 0 | 0 | No
2030-12-18 08:00 | 2030 Initial | -700 | -95 | -232.01 | -90 | 0 | 0 | No
2030-12-18 09:00 | 2030 Initial | -283.7 | 0 | 0 | 0 | 0 | 0 | No
2030-12-18 10:00 | 2030 Initial | -422.24 | 169.97 | 210 | 210 | 0 | 0 | No
2030-12-18 11:00 | 2030 Initial | -280 | 469.97 | 510 | 510 | 0 | 0 | No
2030-12-18 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 13:00 | 2030 Initial | -375.93 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 14:00 | 2030 Initial | -277.01 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 15:00 | 2030 Initial | -198.52 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 16:00 | 2030 Initial | 221.48 | 205 | 261.16 | 510 | 0 | 0 | No
2030-12-18 17:00 | 2030 Initial | 641.48 | 0 | 393.49 | 510 | 0 | 0 | No
2030-12-18 18:00 | 2030 Initial | 700 | 0 | 93.49 | 510 | 0 | 0 | No
2030-12-18 19:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-12-18 20:00 | 2030 Initial | 700 | 125.03 | 210 | 510 | 0 | 0 | No
2030-12-18 21:00 | 2030 Initial | 700 | 425.03 | 510 | 510 | 0 | 0 | No
2030-12-18 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 23:00 | 2030 Initial | 508.77 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 | 2030 Initial | 88.77 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 01:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 02:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 03:00 | 2030 Initial | -226.35 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 04:00 | 2030 Initial | -119.92 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 05:00 | 2030 Initial | -360.76 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 06:00 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 07:00 | 2030 Initial | 0 | 205 | 435.65 | 210 | 0 | 0 | No
2030-12-19 08:00 | 2030 Initial | 0 | 0 | 142.28 | 287.81 | 0 | 0 | No
2030-12-19 09:00 | 2030 Initial | 0 | 0 | 442.28 | 287.81 | 0 | 0 | No
2030-12-19 10:00 | 2030 Initial | -280 | 205 | 309.19 | 312.99 | 0 | 0 | No
2030-12-19 11:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 12:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 13:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 14:00 | 2030 Initial | -325.99 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 15:00 | 2030 Initial | -145.41 | 400.47 | 510 | 510 | 0 | 0 | No
2030-12-19 16:00 | 2030 Initial | 81.38 | 100.47 | 210 | 395.14 | 0 | 0 | No
2030-12-19 17:00 | 2030 Initial | 501.38 | 0 | 0 | 235.42 | 0 | 0 | No
2030-12-19 18:00 | 2030 Initial | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-12-19 19:00 | 2030 Initial | 700 | 0 | 45.5 | 510 | 0 | 0 | No
2030-12-19 20:00 | 2030 Initial | 700 | 205 | 345.5 | 298.85 | 0 | 0 | No
2030-12-19 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 03:00 | 2030 Initial | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 04:00 | 2030 Initial | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 05:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 08:00 | 2030 Initial | -280 | 205 | 330.15 | 423.85 | 0 | 0 | No
2030-12-20 09:00 | 2030 Initial | 0 | 0 | 320.15 | 510 | 0 | 0 | No
2030-12-20 10:00 | 2030 Initial | 0 | 227.64 | 510 | 510 | 0 | 0 | No
2030-12-20 11:00 | 2030 Initial | -178.76 | 0 | 210 | 316.22 | 0 | 0 | No
2030-12-20 12:00 | 2030 Initial | -259.22 | 0 | 0 | 271.4 | 0 | 0 | No
2030-12-20 13:00 | 2030 Initial | -307.04 | 0 | 0 | 168.69 | 0 | 0 | No
2030-12-20 14:00 | 2030 Initial | -269.04 | 0 | 0 | 335.39 | 0 | 0 | No
2030-12-20 15:00 | 2030 Initial | 0 | 0 | -215.88 | 192.05 | 0 | 0 | No
2030-12-20 16:00 | 2030 Initial | -4.06 | 0 | 0 | 113.38 | 0 | 0 | No
2030-12-20 17:00 | 2030 Initial | 0 | 0 | 276.96 | 26.34 | 0 | 0 | No
2030-12-20 18:00 | 2030 Initial | 420 | 0 | 146.13 | 291.77 | 0 | 0 | No
2030-12-20 19:00 | 2030 Initial | 700 | 0 | 446.13 | 149.83 | 0 | 0 | No
2030-12-20 20:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-20 21:00 | 2030 Initial | 700 | 205 | 510 | 210 | 0 | 0 | No
2030-12-20 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 07:00 | 2030 Initial | 700 | 205 | 210 | 270.6 | 0 | 0 | No
2030-12-21 08:00 | 2030 Initial | 700 | 0 | 26.84 | 240.97 | 0 | 0 | No
2030-12-21 09:00 | 2030 Initial | 700 | 0 | 326.84 | 464.31 | 0 | 0 | No
2030-12-21 10:00 | 2030 Initial | 700 | 0 | 510 | 489.49 | 0 | 0 | No
2030-12-21 11:00 | 2030 Initial | 700 | 0 | 373.52 | 510 | 0 | 0 | No
2030-12-21 12:00 | 2030 Initial | 700 | 0 | 73.52 | 494.66 | 0 | 0 | No
2030-12-21 13:00 | 2030 Initial | 700 | 0 | 291.21 | 510 | 0 | 0 | No
2030-12-21 14:00 | 2030 Initial | 700 | 0 | 436.32 | 289.61 | 0 | 0 | No
2030-12-21 15:00 | 2030 Initial | 700 | 0 | 318.88 | 251.52 | 0 | 0 | No
2030-12-21 16:00 | 2030 Initial | 700 | 0 | 197.27 | 207.35 | 0 | 0 | No
2030-12-21 17:00 | 2030 Initial | 700 | 0 | 497.27 | 493.11 | 0 | 0 | No
2030-12-21 18:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-12-21 19:00 | 2030 Initial | 700 | 225.35 | 510 | 510 | 0 | 0 | No
2030-12-21 20:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-12-21 21:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-12-21 22:00 | 2030 Initial | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-12-21 23:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 01:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 02:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 03:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 04:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 05:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 06:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 07:00 | 2030 Initial | 700 | 205 | 490.07 | 210 | 0 | 0 | No
2030-12-22 08:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-22 09:00 | 2030 Initial | 700 | 0 | 510 | 60.72 | 0 | 0 | No
2030-12-22 10:00 | 2030 Initial | 700 | 0 | 510 | 203.96 | 0 | 0 | No
2030-12-22 11:00 | 2030 Initial | 700 | 0 | 510 | 349.03 | 0 | 0 | No
2030-12-22 12:00 | 2030 Initial | 700 | 0 | 510 | 328.29 | 0 | 0 | No
2030-12-22 13:00 | 2030 Initial | 700 | 0 | 510 | 322.37 | 0 | 0 | No
2030-12-22 14:00 | 2030 Initial | 700 | 0 | 432.31 | 98.19 | 0 | 0 | No
2030-12-22 15:00 | 2030 Initial | 700 | 0 | 219.29 | 0 | 0 | 0 | No
2030-12-22 16:00 | 2030 Initial | 700 | 0 | -80.71 | 0 | 0 | 0 | No
2030-12-22 17:00 | 2030 Initial | 700 | 0 | -32.46 | 0 | 0 | 0 | No
2030-12-22 18:00 | 2030 Initial | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-22 19:00 | 2030 Initial | 700 | 0 | -145.03 | 0 | 0 | 0 | No
2030-12-22 20:00 | 2030 Initial | 700 | 0 | -49.48 | 0 | 0 | 0 | No
2030-12-22 21:00 | 2030 Initial | 700 | 0 | -349.48 | 45.6 | 0 | 0 | No
2030-12-22 22:00 | 2030 Initial | 700 | 0 | -185.98 | 345.6 | 0 | 0 | No
2030-12-22 23:00 | 2030 Initial | 700 | -137.67 | -485.98 | 238.95 | 0 | 0 | No
2030-12-23 | 2030 Initial | 700 | -261.74 | -510 | 181.66 | 0 | 0 | No
2030-12-23 01:00 | 2030 Initial | 700 | -526 | -510 | -15.29 | 0 | 0 | No
2030-12-23 02:00 | 2030 Initial | 700 | -526 | -510 | 56.03 | 0 | 0 | No
2030-12-23 03:00 | 2030 Initial | 700 | -526 | -510 | 104.32 | 0 | 0 | No
2030-12-23 04:00 | 2030 Initial | 700 | -526 | -510 | 16.42 | 0 | 0 | No
2030-12-23 05:00 | 2030 Initial | 700 | -526 | -510 | 236.88 | 0 | 0 | No
2030-12-23 06:00 | 2030 Initial | 700 | -226 | -387.15 | 510 | 0 | 0 | No
2030-12-23 07:00 | 2030 Initial | 700 | -434.36 | -510 | 300.61 | 0 | 0 | No
2030-12-23 08:00 | 2030 Initial | 700 | -526 | -510 | 22.67 | 0 | 0 | No
2030-12-23 09:00 | 2030 Initial | 700 | -526 | -510 | -164.7 | 0 | 0 | No
2030-12-23 10:00 | 2030 Initial | 700 | -526 | -510 | -101.04 | 0 | 0 | No
2030-12-23 11:00 | 2030 Initial | 700 | -226 | -275.83 | 0 | 0 | 0 | No
2030-12-23 12:00 | 2030 Initial | 420 | 0 | -372.6 | 210 | 0 | 0 | No
2030-12-23 13:00 | 2030 Initial | 0 | 300 | -72.6 | 510 | 0 | 0 | No
2030-12-23 14:00 | 2030 Initial | -372.98 | 0 | 219.11 | 210 | 0 | 0 | No
2030-12-23 15:00 | 2030 Initial | -188.72 | 0 | 131.3 | 99.63 | 0 | 0 | No
2030-12-23 16:00 | 2030 Initial | 0 | 0 | -58.77 | 125.4 | 0 | 0 | No
2030-12-23 17:00 | 2030 Initial | 280 | 0 | 0 | 210 | 0 | 0 | No
2030-12-23 18:00 | 2030 Initial | 700 | 0 | 212.05 | 510 | 0 | 0 | No
2030-12-23 19:00 | 2030 Initial | 590.51 | 0 | 500.86 | 244.87 | 0 | 0 | No
2030-12-23 20:00 | 2030 Initial | 230 | 300 | 510 | 510 | 0 | 0 | No
2030-12-23 21:00 | 2030 Initial | 138.24 | 505 | 510 | 510 | 0 | 0 | No
2030-12-23 22:00 | 2030 Initial | 319.44 | 505 | 510 | 510 | 0 | 0 | No
2030-12-23 23:00 | 2030 Initial | -100.56 | 505 | 510 | 510 | 0 | 0 | No
2030-12-24 | 2030 Initial | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-24 01:00 | 2030 Initial | -255.76 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 02:00 | 2030 Initial | -675.76 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 03:00 | 2030 Initial | -561.18 | 505 | 510 | 510 | 0 | 0 | No
2030-12-24 04:00 | 2030 Initial | -694.64 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 05:00 | 2030 Initial | -581.59 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 06:00 | 2030 Initial | -293.32 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 07:00 | 2030 Initial | -111.77 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 08:00 | 2030 Initial | 92.79 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 09:00 | 2030 Initial | 512.79 | 505 | 510 | 369.39 | 0 | 0 | No
2030-12-24 10:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-24 11:00 | 2030 Initial | 280 | 205 | 384.29 | 510 | 0 | 0 | No
2030-12-24 12:00 | 2030 Initial | 0 | 139.73 | 510 | 510 | 0 | 0 | No
2030-12-24 13:00 | 2030 Initial | 0 | 4.13 | 510 | 510 | 0 | 0 | No
2030-12-24 14:00 | 2030 Initial | 0 | 0 | 510 | 363.69 | 0 | 0 | No
2030-12-24 15:00 | 2030 Initial | 420 | 0 | 407.45 | 379.33 | 0 | 0 | No
2030-12-24 16:00 | 2030 Initial | 700 | 0 | 264.38 | 391.9 | 0 | 0 | No
2030-12-24 17:00 | 2030 Initial | 700 | 100.19 | 510 | 510 | 0 | 0 | No
2030-12-24 18:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-12-24 19:00 | 2030 Initial | 700 | 24.58 | 510 | 510 | 0 | 0 | No
2030-12-24 20:00 | 2030 Initial | 700 | 324.58 | 510 | 510 | 0 | 0 | No
2030-12-24 21:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-24 22:00 | 2030 Initial | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-24 23:00 | 2030 Initial | 638.06 | 420.54 | 510 | 510 | 0 | 0 | No
2030-12-25 | 2030 Initial | 700 | 172.16 | 510 | 510 | 0 | 0 | No
2030-12-25 01:00 | 2030 Initial | 700 | 121.08 | 510 | 510 | 0 | 0 | No
2030-12-25 02:00 | 2030 Initial | 316.55 | 421.08 | 510 | 510 | 0 | 0 | No
2030-12-25 03:00 | 2030 Initial | 130.61 | 372.91 | 510 | 510 | 0 | 0 | No
2030-12-25 04:00 | 2030 Initial | 0 | 72.91 | 510 | 510 | 0 | 0 | No
2030-12-25 05:00 | 2030 Initial | -7.37 | 240.17 | 210 | 387.96 | 0 | 0 | No
2030-12-25 06:00 | 2030 Initial | 412.63 | 0 | -90 | 87.96 | 0 | 0 | No
2030-12-25 07:00 | 2030 Initial | 700 | 0 | -342.94 | 11.66 | 0 | 0 | No
2030-12-25 08:00 | 2030 Initial | 700 | 0 | -273.14 | 56.51 | 0 | 0 | No
2030-12-25 09:00 | 2030 Initial | 700 | 0 | -193.31 | 129.38 | 0 | 0 | No
2030-12-25 10:00 | 2030 Initial | 700 | 0 | -229.03 | 46.15 | 0 | 0 | No
2030-12-25 11:00 | 2030 Initial | 700 | 0 | -272.75 | 267.66 | 0 | 0 | No
2030-12-25 12:00 | 2030 Initial | 700 | 0 | -490.25 | 167.18 | 0 | 0 | No
2030-12-25 13:00 | 2030 Initial | 700 | 0 | -510 | 220.94 | 0 | 0 | No
2030-12-25 14:00 | 2030 Initial | 700 | -27.53 | -510 | 342.43 | 0 | 0 | No
2030-12-25 15:00 | 2030 Initial | 700 | 0 | -376.44 | 104.21 | 0 | 0 | No
2030-12-25 16:00 | 2030 Initial | 700 | -132.63 | -510 | 283.09 | 0 | 0 | No
2030-12-25 17:00 | 2030 Initial | 282.5 | -137.22 | -510 | 353.23 | 0 | 0 | No
2030-12-25 18:00 | 2030 Initial | 0 | -144.31 | -510 | 175.57 | 0 | 0 | No
2030-12-25 19:00 | 2030 Initial | 0 | -140.57 | -510 | 134.45 | 0 | 0 | No
2030-12-25 20:00 | 2030 Initial | -73.91 | -9.45 | -226.45 | -165.55 | 0 | 0 | No
2030-12-25 21:00 | 2030 Initial | -493.91 | 0 | 73.55 | -57.66 | 0 | 0 | No
2030-12-25 22:00 | 2030 Initial | -700 | 300 | 373.55 | 1.77 | 0 | 0 | No
2030-12-25 23:00 | 2030 Initial | -700 | 505 | 510 | 301.77 | 0 | 0 | Yes
2030-12-26 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 01:00 | 2030 Initial | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-26 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-26 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 07:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 08:00 | 2030 Initial | -700 | 505 | 510 | 371.62 | 0 | 0 | Yes
2030-12-26 09:00 | 2030 Initial | -700 | 505 | 510 | 334.76 | 0 | 0 | Yes
2030-12-26 10:00 | 2030 Initial | -700 | 505 | 510 | 503.26 | 0 | 0 | Yes
2030-12-26 11:00 | 2030 Initial | -700 | 505 | 510 | 481.9 | 0 | 0 | Yes
2030-12-26 12:00 | 2030 Initial | -700 | 505 | 510 | 475.58 | 0 | 0 | Yes
2030-12-26 13:00 | 2030 Initial | -700 | 505 | 510 | 492.77 | 0 | 0 | Yes
2030-12-26 14:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 15:00 | 2030 Initial | -700 | 505 | 510 | 416.11 | 0 | 0 | Yes
2030-12-26 16:00 | 2030 Initial | -700 | 505 | 510 | 299.93 | 0 | 0 | Yes
2030-12-26 17:00 | 2030 Initial | -700 | 505 | 510 | 262.5 | 0 | 0 | Yes
2030-12-26 18:00 | 2030 Initial | -700 | 505 | 510 | 218.28 | 0 | 0 | Yes
2030-12-26 19:00 | 2030 Initial | -700 | 505 | 510 | 233.09 | 0 | 0 | Yes
2030-12-26 20:00 | 2030 Initial | -700 | 505 | 510 | 299.34 | 0 | 0 | Yes
2030-12-26 21:00 | 2030 Initial | -700 | 505 | 510 | 462.96 | 0 | 0 | Yes
2030-12-26 22:00 | 2030 Initial | -700 | 505 | 510 | 289.86 | 0 | 0 | Yes
2030-12-26 23:00 | 2030 Initial | -700 | 505 | 510 | 318.63 | 0 | 0 | Yes
2030-12-27 | 2030 Initial | -549.15 | 505 | 510 | 510 | 0 | 0 | No
2030-12-27 01:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-27 02:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-27 03:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-27 04:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-27 05:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-27 06:00 | 2030 Initial | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-27 07:00 | 2030 Initial | -509.5 | 300 | 300 | 510 | 0 | 0 | No
2030-12-27 08:00 | 2030 Initial | -95.51 | 0 | 0 | 210 | 0 | 0 | No
2030-12-27 09:00 | 2030 Initial | -353.67 | -300 | -300 | 318.81 | 0 | 0 | No
2030-12-27 10:00 | 2030 Initial | 0 | 0 | -315.84 | 326.4 | 0 | 0 | No
2030-12-27 11:00 | 2030 Initial | 0 | -158.74 | -510 | 115.69 | 0 | 0 | No
2030-12-27 12:00 | 2030 Initial | 0 | -100.78 | -510 | 110.11 | 0 | 0 | No
2030-12-27 13:00 | 2030 Initial | 0 | 0 | -416.66 | 190.09 | 0 | 0 | No
2030-12-27 14:00 | 2030 Initial | 140 | -26.7 | -510 | 209.78 | 0 | 0 | No
2030-12-27 15:00 | 2030 Initial | -280 | -67.42 | -429.12 | 0 | 0 | 0 | No
2030-12-27 16:00 | 2030 Initial | -700 | 0 | -129.12 | 300 | 0 | 0 | No
2030-12-27 17:00 | 2030 Initial | -700 | -137.33 | -370.33 | 0 | 0 | 0 | No
2030-12-27 18:00 | 2030 Initial | -700 | -437.33 | -510 | -112.53 | 0 | 0 | No
2030-12-27 19:00 | 2030 Initial | -280 | -137.33 | -210 | 187.47 | 0 | 0 | No
2030-12-27 20:00 | 2030 Initial | 140 | -166.56 | -510 | 146.75 | 0 | 0 | No
2030-12-27 21:00 | 2030 Initial | 80.14 | -371.7 | -510 | 352.36 | 0 | 0 | No
2030-12-27 22:00 | 2030 Initial | -339.86 | -526 | -510 | 346.44 | 0 | 0 | No
2030-12-27 23:00 | 2030 Initial | -487.41 | -526 | -510 | 273.91 | 0 | 0 | No
2030-12-28 | 2030 Initial | -700 | -526 | -510 | 191.44 | 0 | 0 | No
2030-12-28 01:00 | 2030 Initial | -700 | -526 | -510 | -108.56 | 0 | 0 | No
2030-12-28 02:00 | 2030 Initial | -700 | -526 | -510 | -408.56 | 0 | 0 | No
2030-12-28 03:00 | 2030 Initial | -700 | -526 | -510 | -371.16 | 0 | 0 | No
2030-12-28 04:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 05:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 06:00 | 2030 Initial | -700 | -526 | -510 | -492.23 | 0 | 0 | No
2030-12-28 07:00 | 2030 Initial | -700 | -526 | -510 | -192.23 | 0 | 0 | No
2030-12-28 08:00 | 2030 Initial | -700 | -526 | -510 | 107.77 | 0 | 0 | No
2030-12-28 09:00 | 2030 Initial | -700 | -526 | -510 | 37.31 | 0 | 0 | No
2030-12-28 10:00 | 2030 Initial | -700 | -526 | -510 | 258.5 | 0 | 0 | No
2030-12-28 11:00 | 2030 Initial | -700 | -526 | -510 | 434.82 | 0 | 0 | No
2030-12-28 12:00 | 2030 Initial | -700 | -526 | -510 | 226.51 | 0 | 0 | No
2030-12-28 13:00 | 2030 Initial | -700 | -526 | -510 | -73.49 | 0 | 0 | No
2030-12-28 14:00 | 2030 Initial | -700 | -526 | -510 | -373.49 | 0 | 0 | No
2030-12-28 15:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 16:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 17:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 18:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 19:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 20:00 | 2030 Initial | -700 | -526 | -510 | -445.45 | 0 | 0 | No
2030-12-28 21:00 | 2030 Initial | -700 | -526 | -510 | -145.45 | 0 | 0 | No
2030-12-28 22:00 | 2030 Initial | -700 | -526 | -510 | 154.55 | 0 | 0 | No
2030-12-28 23:00 | 2030 Initial | -700 | -526 | -510 | 84.48 | 0 | 0 | No
2030-12-29 | 2030 Initial | -700 | -526 | -510 | -76.23 | 0 | 0 | No
2030-12-29 01:00 | 2030 Initial | -700 | -526 | -510 | 223.77 | 0 | 0 | No
2030-12-29 02:00 | 2030 Initial | -700 | -526 | -510 | 212.34 | 0 | 0 | No
2030-12-29 03:00 | 2030 Initial | -700 | -526 | -510 | 241.99 | 0 | 0 | No
2030-12-29 04:00 | 2030 Initial | -700 | -526 | -510 | -28.79 | 0 | 0 | No
2030-12-29 05:00 | 2030 Initial | -700 | -526 | -510 | -237.52 | 0 | 0 | No
2030-12-29 06:00 | 2030 Initial | -700 | -526 | -510 | -121.74 | 0 | 0 | No
2030-12-29 07:00 | 2030 Initial | -700 | -526 | -510 | -5.47 | 0 | 0 | No
2030-12-29 08:00 | 2030 Initial | -700 | -526 | -510 | -137.44 | 0 | 0 | No
2030-12-29 09:00 | 2030 Initial | -700 | -526 | -510 | 125.48 | 0 | 0 | No
2030-12-29 10:00 | 2030 Initial | -700 | -526 | -510 | -56.85 | 0 | 0 | No
2030-12-29 11:00 | 2030 Initial | -700 | -526 | -510 | 243.15 | 0 | 0 | No
2030-12-29 12:00 | 2030 Initial | -633.69 | -526 | -510 | 241.29 | 0 | 0 | No
2030-12-29 13:00 | 2030 Initial | -648.62 | -526 | -510 | -58.71 | 0 | 0 | No
2030-12-29 14:00 | 2030 Initial | -245.69 | -526 | -510 | -151.49 | 0 | 0 | No
2030-12-29 15:00 | 2030 Initial | -299.7 | -526 | -510 | -451.49 | 0 | 0 | No
2030-12-29 16:00 | 2030 Initial | -700 | -226 | -350.36 | -151.49 | 0 | 0 | No
2030-12-29 17:00 | 2030 Initial | -625.47 | -91.96 | -300 | -108.08 | 0 | 0 | No
2030-12-29 18:00 | 2030 Initial | -205.47 | 0 | 0 | 191.92 | 0 | 0 | No
2030-12-29 19:00 | 2030 Initial | 214.53 | 0 | 300 | 491.92 | 0 | 0 | No
2030-12-29 20:00 | 2030 Initial | 634.53 | 0 | 386.63 | 191.92 | 0 | 0 | No
2030-12-29 21:00 | 2030 Initial | 700 | 0 | 510 | 41.28 | 0 | 0 | No
2030-12-29 22:00 | 2030 Initial | 700 | 0 | 510 | 226.1 | 0 | 0 | No
2030-12-29 23:00 | 2030 Initial | 700 | 0 | 510 | 201.69 | 0 | 0 | No
2030-12-30 | 2030 Initial | 700 | 0 | 510 | 224.87 | 0 | 0 | No
2030-12-30 01:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-30 02:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-30 03:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-30 04:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-30 05:00 | 2030 Initial | 700 | 0 | 435.63 | 0 | 0 | 0 | No
2030-12-30 06:00 | 2030 Initial | 700 | 0 | 502.36 | 0 | 0 | 0 | No
2030-12-30 07:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-30 08:00 | 2030 Initial | 700 | 0 | 510 | 244.77 | 0 | 0 | No
2030-12-30 09:00 | 2030 Initial | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-12-30 10:00 | 2030 Initial | 700 | 0 | 510 | 462.83 | 0 | 0 | No
2030-12-30 11:00 | 2030 Initial | 700 | 0 | 360.79 | 162.83 | 0 | 0 | No
2030-12-30 12:00 | 2030 Initial | 700 | 0 | 510 | 240.14 | 0 | 0 | No
2030-12-30 13:00 | 2030 Initial | 700 | 0 | 510 | 240.14 | 0 | 0 | No
2030-12-30 14:00 | 2030 Initial | 700 | 0 | 510 | 154.94 | 0 | 0 | No
2030-12-30 15:00 | 2030 Initial | 700 | 0 | 333.5 | 0 | 0 | 0 | No
2030-12-30 16:00 | 2030 Initial | 700 | 0 | 142.02 | 0 | 0 | 0 | No
2030-12-30 17:00 | 2030 Initial | 700 | 0 | 142.02 | 0 | 0 | 0 | No
2030-12-30 18:00 | 2030 Initial | 700 | 0 | 201.49 | 0 | 0 | 0 | No
2030-12-30 19:00 | 2030 Initial | 700 | 0 | 201.49 | 0 | 0 | 0 | No
2030-12-30 20:00 | 2030 Initial | 700 | 0 | 210 | 132.51 | 0 | 0 | No
2030-12-30 21:00 | 2030 Initial | 700 | 0 | 510 | 432.51 | 0 | 0 | No
2030-12-30 22:00 | 2030 Initial | 700 | 19.04 | 510 | 416.74 | 0 | 0 | No
2030-12-30 23:00 | 2030 Initial | 700 | 0 | 510 | 346.47 | 0 | 0 | No
2030-12-31 | 2030 Initial | 700 | 0 | 510 | 468.64 | 0 | 0 | No
2030-12-31 01:00 | 2030 Initial | 700 | 0 | 510 | 168.64 | 0 | 0 | No
2030-12-31 02:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-31 03:00 | 2030 Initial | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-31 04:00 | 2030 Initial | 420 | 0 | 510 | 0 | 0 | 0 | No
2030-12-31 05:00 | 2030 Initial | 0 | 0 | 510 | 0 | 0 | 0 | No
2030-12-31 06:00 | 2030 Initial | -420 | 0 | 390 | 0 | 0 | 0 | No
2030-12-31 07:00 | 2030 Initial | -700 | 289.03 | 90 | 0 | 0 | 0 | No
2030-12-31 08:00 | 2030 Initial | -700 | -10.97 | -210 | -300 | 0 | 0 | No
2030-12-31 09:00 | 2030 Initial | -383.14 | -244.74 | -510 | -510 | 0 | 0 | No
2030-12-31 10:00 | 2030 Initial | -216.69 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 11:00 | 2030 Initial | -96.71 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 12:00 | 2030 Initial | -516.71 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 13:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 14:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 15:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 16:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 17:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 18:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 19:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 20:00 | 2030 Initial | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 21:00 | 2030 Initial | -700 | -226 | -285.74 | -242.24 | 0 | 0 | No
2030-12-31 22:00 | 2030 Initial | -700 | -108.12 | -282.89 | -437.94 | 0 | 0 | No
2030-12-31 23:00 | 2030 Initial | -280 | 0 | 17.11 | -137.94 | 0 | 0 | No
2030-01-01 | 2030 33% ECP | -280 | 0 | 0 | 0 | 0 | 0 | No
2030-01-01 01:00 | 2030 33% ECP | 140 | 300 | 300 | 300 | 0 | 0 | No
2030-01-01 02:00 | 2030 33% ECP | 560 | 37.68 | 300 | 300 | 0 | 0 | No
2030-01-01 03:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-01 04:00 | 2030 33% ECP | 700 | 0 | -128.35 | 0 | 0 | 0 | No
2030-01-01 05:00 | 2030 33% ECP | 700 | 0 | -399.31 | 0 | 0 | 0 | No
2030-01-01 06:00 | 2030 33% ECP | 280 | 0 | -99.31 | 0 | 0 | 0 | No
2030-01-01 07:00 | 2030 33% ECP | 0 | 0 | 0 | 0 | 0 | 0 | No
2030-01-01 08:00 | 2030 33% ECP | 325.22 | 0 | 0 | 0 | 0 | 0 | No
2030-01-01 09:00 | 2030 33% ECP | 140 | 0 | 184.65 | 0 | 0 | 0 | No
2030-01-01 10:00 | 2030 33% ECP | -280 | 199.09 | 0 | 82.97 | 0 | 0 | No
2030-01-01 11:00 | 2030 33% ECP | -700 | 0 | -300 | -217.03 | 0 | 0 | No
2030-01-01 12:00 | 2030 33% ECP | -700 | -100.24 | 0 | -59.78 | 0 | 0 | No
2030-01-01 13:00 | 2030 33% ECP | -700 | 0 | 300 | 240.22 | 0 | 0 | No
2030-01-01 14:00 | 2030 33% ECP | -700 | 285.11 | 170.7 | 300 | 0 | 0 | No
2030-01-01 15:00 | 2030 33% ECP | -700 | 0 | -129.3 | 0 | 0 | 0 | No
2030-01-01 16:00 | 2030 33% ECP | -700 | -24.1 | -429.3 | -20.03 | 0 | 0 | No
2030-01-01 17:00 | 2030 33% ECP | -700 | -289.73 | -510 | -89.35 | 0 | 0 | No
2030-01-01 18:00 | 2030 33% ECP | -700 | -363.29 | -510 | -343.34 | 0 | 0 | No
2030-01-01 19:00 | 2030 33% ECP | -700 | -446.41 | -510 | -254.35 | 0 | 0 | No
2030-01-01 20:00 | 2030 33% ECP | -524.74 | -526 | -510 | 43.71 | 0 | 0 | No
2030-01-01 21:00 | 2030 33% ECP | -700 | -526 | -510 | -10.79 | 0 | 0 | No
2030-01-01 22:00 | 2030 33% ECP | -700 | -526 | -510 | -25.94 | 0 | 0 | No
2030-01-01 23:00 | 2030 33% ECP | -700 | -226 | -210 | 274.06 | 0 | 0 | Yes
2030-01-02 | 2030 33% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-01-02 01:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-02 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 13:00 | 2030 33% ECP | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-01-02 14:00 | 2030 33% ECP | -700 | 485.88 | 90 | 510 | 0 | 0 | Yes
2030-01-02 15:00 | 2030 33% ECP | -700 | 185.88 | -210 | 330.67 | 0 | 0 | Yes
2030-01-02 16:00 | 2030 33% ECP | -700 | -114.12 | -510 | 30.67 | 0 | 0 | No
2030-01-02 17:00 | 2030 33% ECP | -700 | -414.12 | -510 | 177.58 | 0 | 0 | No
2030-01-02 18:00 | 2030 33% ECP | -700 | -395 | -390 | 0 | 0 | 0 | No
2030-01-02 19:00 | 2030 33% ECP | -280 | -95 | -90 | 173.2 | 0 | 0 | No
2030-01-02 20:00 | 2030 33% ECP | 0 | 205 | 210 | 210 | 0 | 0 | No
2030-01-02 21:00 | 2030 33% ECP | -398.52 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 23:00 | 2030 33% ECP | -700 | 505 | 510 | 318.25 | 0 | 0 | Yes
2030-01-03 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 01:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 02:00 | 2030 33% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 03:00 | 2030 33% ECP | 568.26 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 04:00 | 2030 33% ECP | 148.26 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 05:00 | 2030 33% ECP | -271.74 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 06:00 | 2030 33% ECP | -691.74 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 07:00 | 2030 33% ECP | -700 | 205 | 210 | 231.25 | 0 | 0 | No
2030-01-03 08:00 | 2030 33% ECP | -700 | 0 | 440.61 | 210 | 0 | 0 | No
2030-01-03 09:00 | 2030 33% ECP | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-03 10:00 | 2030 33% ECP | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-03 11:00 | 2030 33% ECP | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-03 12:00 | 2030 33% ECP | -534.65 | 0 | 210 | 293.76 | 0 | 0 | No
2030-01-03 13:00 | 2030 33% ECP | -700 | 0 | 463.27 | 144.41 | 0 | 0 | No
2030-01-03 14:00 | 2030 33% ECP | -700 | 0 | 510 | 328.42 | 0 | 0 | No
2030-01-03 15:00 | 2030 33% ECP | -700 | 144.09 | 510 | 510 | 0 | 0 | No
2030-01-03 16:00 | 2030 33% ECP | -700 | 144.09 | 510 | 510 | 0 | 0 | No
2030-01-03 17:00 | 2030 33% ECP | -700 | 444.09 | 510 | 510 | 0 | 0 | No
2030-01-03 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 19:00 | 2030 33% ECP | -700 | 285.4 | 510 | 510 | 0 | 0 | No
2030-01-03 20:00 | 2030 33% ECP | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-03 21:00 | 2030 33% ECP | -700 | 0 | 510 | 460.57 | 0 | 0 | No
2030-01-03 22:00 | 2030 33% ECP | -646.76 | 205 | 510 | 510 | 0 | 0 | No
2030-01-03 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-04 | 2030 33% ECP | -599.65 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 01:00 | 2030 33% ECP | -192.29 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 02:00 | 2030 33% ECP | -612.29 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-04 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 07:00 | 2030 33% ECP | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-04 08:00 | 2030 33% ECP | -700 | 0 | 299.83 | 89.43 | 0 | 0 | No
2030-01-04 09:00 | 2030 33% ECP | -700 | 205 | 510 | 389.43 | 0 | 0 | No
2030-01-04 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 11:00 | 2030 33% ECP | -700 | 486.1 | 510 | 510 | 0 | 0 | No
2030-01-04 12:00 | 2030 33% ECP | -700 | 186.1 | 474.3 | 210 | 0 | 0 | No
2030-01-04 13:00 | 2030 33% ECP | -700 | 189.13 | 510 | 510 | 0 | 0 | No
2030-01-04 14:00 | 2030 33% ECP | -700 | 198.51 | 510 | 510 | 0 | 0 | No
2030-01-04 15:00 | 2030 33% ECP | -700 | 300 | 254.29 | 300 | 0 | 0 | No
2030-01-04 16:00 | 2030 33% ECP | -700 | 0 | -45.71 | 0 | 0 | 0 | No
2030-01-04 17:00 | 2030 33% ECP | -700 | -200.97 | -345.71 | -300 | 0 | 0 | No
2030-01-04 18:00 | 2030 33% ECP | -700 | -488.65 | -510 | -510 | 0 | 0 | No
2030-01-04 19:00 | 2030 33% ECP | -700 | -267.79 | -439.17 | -300 | 0 | 0 | No
2030-01-04 20:00 | 2030 33% ECP | -547.97 | 0 | -139.17 | 0 | 0 | 0 | No
2030-01-04 21:00 | 2030 33% ECP | -700 | 300 | 160.83 | 300 | 0 | 0 | No
2030-01-04 22:00 | 2030 33% ECP | -700 | 0 | 92.21 | 0 | 0 | 0 | No
2030-01-04 23:00 | 2030 33% ECP | -700 | 0 | 14.11 | 0 | 0 | 0 | No
2030-01-05 | 2030 33% ECP | -700 | 0 | -86.75 | 0 | 0 | 0 | No
2030-01-05 01:00 | 2030 33% ECP | -700 | 0 | -13.59 | 12.29 | 0 | 0 | No
2030-01-05 02:00 | 2030 33% ECP | -700 | 205 | 256.59 | 312.29 | 0 | 0 | No
2030-01-05 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-05 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-05 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-05 06:00 | 2030 33% ECP | -700 | 300 | 300 | 428.31 | 0 | 0 | No
2030-01-05 07:00 | 2030 33% ECP | -700 | 0 | 0 | 128.31 | 0 | 0 | No
2030-01-05 08:00 | 2030 33% ECP | -700 | -25.78 | -300 | 194.31 | 0 | 0 | No
2030-01-05 09:00 | 2030 33% ECP | -700 | -31.79 | -510 | -105.69 | 0 | 0 | No
2030-01-05 10:00 | 2030 33% ECP | -700 | 0 | -510 | 194.31 | 0 | 0 | No
2030-01-05 11:00 | 2030 33% ECP | -700 | -29.8 | -510 | 202.11 | 0 | 0 | No
2030-01-05 12:00 | 2030 33% ECP | -700 | -292.44 | -510 | 333.43 | 0 | 0 | No
2030-01-05 13:00 | 2030 33% ECP | -700 | 0 | -510 | 327.01 | 0 | 0 | No
2030-01-05 14:00 | 2030 33% ECP | -700 | 0 | -510 | 294.57 | 0 | 0 | No
2030-01-05 15:00 | 2030 33% ECP | -700 | 0 | -510 | -5.43 | 0 | 0 | No
2030-01-05 16:00 | 2030 33% ECP | -700 | -89.3 | -510 | 264.67 | 0 | 0 | No
2030-01-05 17:00 | 2030 33% ECP | -700 | -13.79 | -510 | 510 | 0 | 0 | No
2030-01-05 18:00 | 2030 33% ECP | -700 | -19.01 | -510 | 510 | 0 | 0 | No
2030-01-05 19:00 | 2030 33% ECP | -700 | -6.66 | -510 | 451.46 | 0 | 0 | No
2030-01-05 20:00 | 2030 33% ECP | -700 | -107.22 | -510 | 373.76 | 0 | 0 | No
2030-01-05 21:00 | 2030 33% ECP | -700 | -294.9 | -510 | 137.33 | 0 | 0 | No
2030-01-05 22:00 | 2030 33% ECP | -700 | -444.3 | -510 | -162.67 | 0 | 0 | No
2030-01-05 23:00 | 2030 33% ECP | -700 | -144.3 | -210 | 137.33 | 0 | 0 | No
2030-01-06 | 2030 33% ECP | -700 | 155.7 | 90 | 437.33 | 0 | 0 | Yes
2030-01-06 01:00 | 2030 33% ECP | -700 | 455.7 | 390 | 510 | 0 | 0 | Yes
2030-01-06 02:00 | 2030 33% ECP | -700 | 505 | 510 | 327.46 | 0 | 0 | Yes
2030-01-06 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 04:00 | 2030 33% ECP | -700 | 505 | 510 | 225.97 | 0 | 0 | Yes
2030-01-06 05:00 | 2030 33% ECP | -700 | 505 | 510 | 197.73 | 0 | 0 | Yes
2030-01-06 06:00 | 2030 33% ECP | -700 | 505 | 510 | 62.13 | 0 | 0 | Yes
2030-01-06 07:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-01-06 08:00 | 2030 33% ECP | -700 | 505 | 510 | 216.14 | 0 | 0 | Yes
2030-01-06 09:00 | 2030 33% ECP | -700 | 505 | 510 | 216.14 | 0 | 0 | Yes
2030-01-06 10:00 | 2030 33% ECP | -700 | 505 | 510 | 385.76 | 0 | 0 | Yes
2030-01-06 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 16:00 | 2030 33% ECP | -700 | 459.8 | 510 | 510 | 0 | 0 | No
2030-01-06 17:00 | 2030 33% ECP | -700 | 170.65 | 510 | 510 | 0 | 0 | No
2030-01-06 18:00 | 2030 33% ECP | -700 | 470.65 | 510 | 510 | 0 | 0 | No
2030-01-06 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-06 20:00 | 2030 33% ECP | -280 | 444.18 | 510 | 510 | 0 | 0 | No
2030-01-06 21:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-01-06 22:00 | 2030 33% ECP | -280 | 205 | 510 | 510 | 0 | 0 | No
2030-01-06 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-07 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 05:00 | 2030 33% ECP | -700 | 505 | 510 | 280.15 | 0 | 0 | Yes
2030-01-07 06:00 | 2030 33% ECP | -700 | 505 | 510 | 455.68 | 0 | 0 | Yes
2030-01-07 07:00 | 2030 33% ECP | -700 | 505 | 510 | 307.01 | 0 | 0 | Yes
2030-01-07 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 17:00 | 2030 33% ECP | -700 | 205 | 398.77 | 210 | 0 | 0 | Yes
2030-01-07 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 20:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-08 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-08 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-08 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 07:00 | 2030 33% ECP | -700 | 205 | 510 | 222.78 | 0 | 0 | No
2030-01-08 08:00 | 2030 33% ECP | -700 | 199.96 | 510 | 306.71 | 0 | 0 | No
2030-01-08 09:00 | 2030 33% ECP | -700 | 499.96 | 510 | 510 | 0 | 0 | No
2030-01-08 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 11:00 | 2030 33% ECP | -700 | 298.37 | 510 | 510 | 0 | 0 | No
2030-01-08 12:00 | 2030 33% ECP | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-08 13:00 | 2030 33% ECP | -700 | 131.56 | 510 | 503.96 | 0 | 0 | No
2030-01-08 14:00 | 2030 33% ECP | -700 | 431.56 | 510 | 472.78 | 0 | 0 | No
2030-01-08 15:00 | 2030 33% ECP | -700 | 505 | 510 | 440.15 | 0 | 0 | No
2030-01-08 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 17:00 | 2030 33% ECP | -700 | 213.83 | 210 | 210 | 0 | 0 | No
2030-01-08 18:00 | 2030 33% ECP | -400.75 | -86.17 | -90 | -90 | 0 | 0 | No
2030-01-08 19:00 | 2030 33% ECP | 19.25 | 0 | -390 | -107.94 | 0 | 0 | No
2030-01-08 20:00 | 2030 33% ECP | 439.25 | 0 | -218.74 | 143.83 | 0 | 0 | No
2030-01-08 21:00 | 2030 33% ECP | 19.25 | -181.02 | -510 | 67.12 | 0 | 0 | No
2030-01-08 22:00 | 2030 33% ECP | 439.25 | 0 | -242.37 | 173.05 | 0 | 0 | No
2030-01-08 23:00 | 2030 33% ECP | 700 | 0 | -290.35 | 37.1 | 0 | 0 | No
2030-01-09 | 2030 33% ECP | 700 | 0 | 9.65 | 0 | 0 | 0 | No
2030-01-09 01:00 | 2030 33% ECP | 700 | 0 | 309.65 | 0 | 0 | 0 | No
2030-01-09 02:00 | 2030 33% ECP | 700 | 205 | 450.99 | 210 | 0 | 0 | No
2030-01-09 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 06:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-09 07:00 | 2030 33% ECP | 280 | 251.36 | 510 | 471.25 | 0 | 0 | No
2030-01-09 08:00 | 2030 33% ECP | 296.86 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 09:00 | 2030 33% ECP | 700 | 248.98 | 510 | 510 | 0 | 0 | No
2030-01-09 10:00 | 2030 33% ECP | 700 | 247.57 | 510 | 510 | 0 | 0 | No
2030-01-09 11:00 | 2030 33% ECP | 700 | 439.4 | 510 | 510 | 0 | 0 | No
2030-01-09 12:00 | 2030 33% ECP | 700 | 139.4 | 510 | 505.64 | 0 | 0 | No
2030-01-09 13:00 | 2030 33% ECP | 297.53 | 439.4 | 510 | 510 | 0 | 0 | No
2030-01-09 14:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 15:00 | 2030 33% ECP | 700 | 205 | 390 | 210 | 0 | 0 | No
2030-01-09 16:00 | 2030 33% ECP | 700 | 0 | 90 | 413.5 | 0 | 0 | No
2030-01-09 17:00 | 2030 33% ECP | 700 | -226 | -210 | 244.97 | 0 | 0 | No
2030-01-09 18:00 | 2030 33% ECP | 700 | -526 | -510 | -55.03 | 0 | 0 | No
2030-01-09 19:00 | 2030 33% ECP | 700 | -526 | -510 | 54.46 | 0 | 0 | No
2030-01-09 20:00 | 2030 33% ECP | 700 | -447.02 | -510 | 292.22 | 0 | 0 | No
2030-01-09 21:00 | 2030 33% ECP | 620.46 | -396.52 | -510 | 295.83 | 0 | 0 | No
2030-01-09 22:00 | 2030 33% ECP | 700 | -96.52 | -300 | 22.13 | 0 | 0 | No
2030-01-09 23:00 | 2030 33% ECP | 700 | 0 | 0 | 16.9 | 0 | 0 | No
2030-01-10 | 2030 33% ECP | 700 | 0 | 300 | 316.9 | 0 | 0 | No
2030-01-10 01:00 | 2030 33% ECP | 700 | 0 | 510 | 58.53 | 0 | 0 | No
2030-01-10 02:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-10 03:00 | 2030 33% ECP | 700 | 0 | 510 | 278.67 | 0 | 0 | No
2030-01-10 04:00 | 2030 33% ECP | 420 | 0 | 510 | 278.67 | 0 | 0 | No
2030-01-10 05:00 | 2030 33% ECP | 0 | 0 | 510 | 341.89 | 0 | 0 | No
2030-01-10 06:00 | 2030 33% ECP | -420 | 0 | 390 | 341.89 | 0 | 0 | No
2030-01-10 07:00 | 2030 33% ECP | -700 | 300 | 90 | 228.14 | 0 | 0 | No
2030-01-10 08:00 | 2030 33% ECP | -700 | 0 | -210 | -71.86 | 0 | 0 | No
2030-01-10 09:00 | 2030 33% ECP | -700 | -300 | -510 | -371.86 | 0 | 0 | No
2030-01-10 10:00 | 2030 33% ECP | -700 | -289.63 | -510 | -71.86 | 0 | 0 | No
2030-01-10 11:00 | 2030 33% ECP | -700 | -398.58 | -510 | -198.56 | 0 | 0 | No
2030-01-10 12:00 | 2030 33% ECP | -700 | -526 | -510 | -102.2 | 0 | 0 | No
2030-01-10 13:00 | 2030 33% ECP | -700 | -526 | -510 | -332.91 | 0 | 0 | No
2030-01-10 14:00 | 2030 33% ECP | -700 | -526 | -510 | -293.1 | 0 | 0 | No
2030-01-10 15:00 | 2030 33% ECP | -700 | -526 | -510 | -288.26 | 0 | 0 | No
2030-01-10 16:00 | 2030 33% ECP | -700 | -526 | -510 | -450.3 | 0 | 0 | No
2030-01-10 17:00 | 2030 33% ECP | -700 | -526 | -510 | -212.21 | 0 | 0 | No
2030-01-10 18:00 | 2030 33% ECP | -700 | -526 | -510 | -161.32 | 0 | 0 | No
2030-01-10 19:00 | 2030 33% ECP | -700 | -526 | -510 | -303.89 | 0 | 0 | No
2030-01-10 20:00 | 2030 33% ECP | -700 | -404.11 | -510 | -338.51 | 0 | 0 | No
2030-01-10 21:00 | 2030 33% ECP | -700 | -104.11 | -210 | -38.51 | 0 | 0 | No
2030-01-10 22:00 | 2030 33% ECP | -700 | 195.89 | 90 | 261.49 | 0 | 0 | Yes
2030-01-10 23:00 | 2030 33% ECP | -700 | 495.89 | 390 | 365.05 | 0 | 0 | Yes
2030-01-11 | 2030 33% ECP | -700 | 505 | 510 | 439.72 | 0 | 0 | Yes
2030-01-11 01:00 | 2030 33% ECP | -700 | 505 | 510 | 264.93 | 0 | 0 | Yes
2030-01-11 02:00 | 2030 33% ECP | -700 | 505 | 510 | 375.92 | 0 | 0 | Yes
2030-01-11 03:00 | 2030 33% ECP | -700 | 505 | 510 | 214.58 | 0 | 0 | Yes
2030-01-11 04:00 | 2030 33% ECP | -700 | 505 | 510 | 275.94 | 0 | 0 | Yes
2030-01-11 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 06:00 | 2030 33% ECP | -700 | 505 | 510 | 217.11 | 0 | 0 | Yes
2030-01-11 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 16:00 | 2030 33% ECP | -700 | 205 | 510 | 295.01 | 0 | 0 | No
2030-01-11 17:00 | 2030 33% ECP | -700 | 235.07 | 510 | 510 | 0 | 0 | No
2030-01-11 18:00 | 2030 33% ECP | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 19:00 | 2030 33% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 20:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 21:00 | 2030 33% ECP | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-01-11 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 05:00 | 2030 33% ECP | 280 | 205 | 210 | 343.86 | 0 | 0 | No
2030-01-12 06:00 | 2030 33% ECP | -140 | -95 | -90 | 43.86 | 0 | 0 | No
2030-01-12 07:00 | 2030 33% ECP | -207.24 | 0 | 0 | 37.59 | 0 | 0 | No
2030-01-12 08:00 | 2030 33% ECP | -420 | 0 | 300 | 263.72 | 0 | 0 | No
2030-01-12 09:00 | 2030 33% ECP | 0 | 0 | 510 | 263.72 | 0 | 0 | No
2030-01-12 10:00 | 2030 33% ECP | 0 | 0 | 510 | 144.9 | 0 | 0 | No
2030-01-12 11:00 | 2030 33% ECP | 0 | 0 | 510 | 444.9 | 0 | 0 | No
2030-01-12 12:00 | 2030 33% ECP | 0 | 0 | 391.81 | 178.3 | 0 | 0 | No
2030-01-12 13:00 | 2030 33% ECP | 0 | 0 | 299.64 | 178.3 | 0 | 0 | No
2030-01-12 14:00 | 2030 33% ECP | -280 | 0 | 510 | 459.79 | 0 | 0 | No
2030-01-12 15:00 | 2030 33% ECP | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-12 16:00 | 2030 33% ECP | -700 | 0 | 510 | 463.37 | 0 | 0 | No
2030-01-12 17:00 | 2030 33% ECP | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-12 18:00 | 2030 33% ECP | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-12 19:00 | 2030 33% ECP | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-12 20:00 | 2030 33% ECP | -700 | 0 | 510 | 259.81 | 0 | 0 | No
2030-01-12 21:00 | 2030 33% ECP | -700 | 0 | 214.39 | 31.35 | 0 | 0 | No
2030-01-12 22:00 | 2030 33% ECP | -700 | 0 | -85.61 | -18.33 | 0 | 0 | No
2030-01-12 23:00 | 2030 33% ECP | -297.67 | 0 | -309.64 | 105.76 | 0 | 0 | No
2030-01-13 | 2030 33% ECP | -700 | 300 | -9.64 | 405.76 | 0 | 0 | No
2030-01-13 01:00 | 2030 33% ECP | -700 | 505 | 290.36 | 510 | 0 | 0 | Yes
2030-01-13 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 06:00 | 2030 33% ECP | -700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-01-13 07:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-01-13 08:00 | 2030 33% ECP | -700 | 505 | 510 | 191.24 | 0 | 0 | Yes
2030-01-13 09:00 | 2030 33% ECP | -700 | 505 | 510 | 491.24 | 0 | 0 | Yes
2030-01-13 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 14:00 | 2030 33% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-01-13 15:00 | 2030 33% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-01-13 16:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-01-13 17:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-13 18:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-13 19:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-01-13 20:00 | 2030 33% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-01-13 21:00 | 2030 33% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-01-13 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 23:00 | 2030 33% ECP | -700 | 505 | 510 | 323.25 | 0 | 0 | Yes
2030-01-14 | 2030 33% ECP | -700 | 505 | 510 | 297.91 | 0 | 0 | Yes
2030-01-14 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 04:00 | 2030 33% ECP | -700 | 505 | 510 | 251.03 | 0 | 0 | Yes
2030-01-14 05:00 | 2030 33% ECP | -700 | 505 | 510 | 384.21 | 0 | 0 | Yes
2030-01-14 06:00 | 2030 33% ECP | -560.91 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 07:00 | 2030 33% ECP | -140.91 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 08:00 | 2030 33% ECP | 279.09 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 09:00 | 2030 33% ECP | 699.09 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 10:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 11:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 12:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 13:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 14:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 15:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 16:00 | 2030 33% ECP | 280 | 205 | 210 | 510 | 0 | 0 | No
2030-01-14 17:00 | 2030 33% ECP | -140 | -95 | -90 | 510 | 0 | 0 | No
2030-01-14 18:00 | 2030 33% ECP | 280 | 205 | 210 | 510 | 0 | 0 | No
2030-01-14 19:00 | 2030 33% ECP | 207.29 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 20:00 | 2030 33% ECP | -212.71 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 21:00 | 2030 33% ECP | -632.71 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 16:00 | 2030 33% ECP | -700 | 205 | 510 | 279.63 | 0 | 0 | No
2030-01-15 17:00 | 2030 33% ECP | -700 | 0 | 510 | 363.79 | 0 | 0 | No
2030-01-15 18:00 | 2030 33% ECP | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-15 19:00 | 2030 33% ECP | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-15 20:00 | 2030 33% ECP | -700 | 205 | 302.89 | 510 | 0 | 0 | No
2030-01-15 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-15 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-15 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 07:00 | 2030 33% ECP | -700 | 300 | 510 | 463.19 | 0 | 0 | Yes
2030-01-16 08:00 | 2030 33% ECP | -700 | 0 | 210 | 163.19 | 0 | 0 | Yes
2030-01-16 09:00 | 2030 33% ECP | -700 | 205 | 221.96 | 210 | 0 | 0 | Yes
2030-01-16 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 15:00 | 2030 33% ECP | -700 | 300 | 510 | 510 | 0 | 0 | Yes
2030-01-16 16:00 | 2030 33% ECP | -566.78 | 0 | 300 | 428.73 | 0 | 0 | No
2030-01-16 17:00 | 2030 33% ECP | -146.78 | 0 | 0 | 324.78 | 0 | 0 | No
2030-01-16 18:00 | 2030 33% ECP | 273.22 | 0 | 0 | 341.25 | 0 | 0 | No
2030-01-16 19:00 | 2030 33% ECP | 693.22 | 0 | 0 | 403.94 | 0 | 0 | No
2030-01-16 20:00 | 2030 33% ECP | 700 | 205 | 210 | 323.52 | 0 | 0 | No
2030-01-16 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-16 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-16 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 04:00 | 2030 33% ECP | 539.61 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 05:00 | 2030 33% ECP | 119.61 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 06:00 | 2030 33% ECP | -300.39 | 205 | 210 | 210 | 0 | 0 | No
2030-01-17 07:00 | 2030 33% ECP | -700 | 0 | -90 | -25.97 | 0 | 0 | No
2030-01-17 08:00 | 2030 33% ECP | -284.09 | 0 | 210 | 165.21 | 0 | 0 | No
2030-01-17 09:00 | 2030 33% ECP | 0 | 0 | 510 | 465.21 | 0 | 0 | No
2030-01-17 10:00 | 2030 33% ECP | 0 | 0 | 510 | 510 | 0 | 0 | No
2030-01-17 11:00 | 2030 33% ECP | -420 | 0 | 444.65 | 395.76 | 0 | 0 | No
2030-01-17 12:00 | 2030 33% ECP | 0 | 0 | 144.65 | 95.76 | 0 | 0 | No
2030-01-17 13:00 | 2030 33% ECP | -63.93 | -187.88 | -44.15 | -83.77 | 0 | 0 | No
2030-01-17 14:00 | 2030 33% ECP | 356.07 | 0 | 255.85 | 216.23 | 0 | 0 | No
2030-01-17 15:00 | 2030 33% ECP | 700 | 0 | 510 | 305.74 | 0 | 0 | No
2030-01-17 16:00 | 2030 33% ECP | 281.13 | 0 | 510 | 478.24 | 0 | 0 | No
2030-01-17 17:00 | 2030 33% ECP | -138.87 | 107.4 | 510 | 178.24 | 0 | 0 | No
2030-01-17 18:00 | 2030 33% ECP | 0 | 344.9 | 510 | 287.8 | 0 | 0 | No
2030-01-17 19:00 | 2030 33% ECP | 420 | 344.9 | 510 | 306.64 | 0 | 0 | No
2030-01-17 20:00 | 2030 33% ECP | 700 | 505 | 510 | 6.64 | 0 | 0 | No
2030-01-17 21:00 | 2030 33% ECP | 700 | 205 | 510 | 306.64 | 0 | 0 | No
2030-01-17 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 04:00 | 2030 33% ECP | 617.15 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 05:00 | 2030 33% ECP | 197.15 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 06:00 | 2030 33% ECP | -222.85 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 07:00 | 2030 33% ECP | -642.85 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 08:00 | 2030 33% ECP | -222.85 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 09:00 | 2030 33% ECP | 89.35 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 10:00 | 2030 33% ECP | -315.06 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 11:00 | 2030 33% ECP | -619.89 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 13:00 | 2030 33% ECP | -653.58 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 14:00 | 2030 33% ECP | -466.11 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 15:00 | 2030 33% ECP | -46.11 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 16:00 | 2030 33% ECP | 307.33 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 17:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 18:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 19:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 20:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 23:00 | 2030 33% ECP | 700 | 205 | 510 | 493.5 | 0 | 0 | No
2030-01-19 | 2030 33% ECP | 700 | 36.32 | 510 | 490.57 | 0 | 0 | No
2030-01-19 01:00 | 2030 33% ECP | 700 | 0 | 510 | 259.68 | 0 | 0 | No
2030-01-19 02:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-19 03:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-19 04:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-19 05:00 | 2030 33% ECP | 420 | 0 | 510 | 0 | 0 | 0 | No
2030-01-19 06:00 | 2030 33% ECP | 0 | 0 | 390 | 0 | 0 | 0 | No
2030-01-19 07:00 | 2030 33% ECP | -280 | 0 | 90 | 94.9 | 0 | 0 | No
2030-01-19 08:00 | 2030 33% ECP | -700 | -122.12 | -210 | -205.1 | 0 | 0 | No
2030-01-19 09:00 | 2030 33% ECP | -575.92 | -422.12 | -510 | -465.78 | 0 | 0 | No
2030-01-19 10:00 | 2030 33% ECP | -155.92 | -122.12 | -210 | -165.78 | 0 | 0 | No
2030-01-19 11:00 | 2030 33% ECP | 0 | -422.12 | -510 | 0 | 0 | 0 | No
2030-01-19 12:00 | 2030 33% ECP | 158.81 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 13:00 | 2030 33% ECP | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 14:00 | 2030 33% ECP | 287.96 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 15:00 | 2030 33% ECP | 145.25 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 16:00 | 2030 33% ECP | 0 | -226 | -332.92 | -133.62 | 0 | 0 | No
2030-01-19 17:00 | 2030 33% ECP | -420 | -526 | -510 | -433.62 | 0 | 0 | No
2030-01-19 18:00 | 2030 33% ECP | 0 | -526 | -510 | -440.19 | 0 | 0 | No
2030-01-19 19:00 | 2030 33% ECP | 420 | -300 | -510 | -140.19 | 0 | 0 | No
2030-01-19 20:00 | 2030 33% ECP | 700 | 0 | -210 | 86.43 | 0 | 0 | No
2030-01-19 21:00 | 2030 33% ECP | 700 | 0 | 90 | 107.32 | 0 | 0 | No
2030-01-19 22:00 | 2030 33% ECP | 538.17 | -300 | -210 | -192.68 | 0 | 0 | No
2030-01-19 23:00 | 2030 33% ECP | 596.99 | -526 | -510 | -370.99 | 0 | 0 | No
2030-01-20 | 2030 33% ECP | 280 | -369.66 | -510 | -82.88 | 0 | 0 | No
2030-01-20 01:00 | 2030 33% ECP | -140 | -163.33 | -210 | 57.2 | 0 | 0 | No
2030-01-20 02:00 | 2030 33% ECP | 280 | 136.67 | 90 | 309.47 | 0 | 0 | No
2030-01-20 03:00 | 2030 33% ECP | 700 | 436.67 | 390 | 510 | 0 | 0 | No
2030-01-20 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-20 05:00 | 2030 33% ECP | 362.05 | 205 | 210 | 510 | 0 | 0 | No
2030-01-20 06:00 | 2030 33% ECP | -57.95 | -95 | -90 | 210 | 0 | 0 | No
2030-01-20 07:00 | 2030 33% ECP | -237.04 | -395 | -390 | -37.52 | 0 | 0 | No
2030-01-20 08:00 | 2030 33% ECP | 182.96 | -322.21 | -510 | 0 | 0 | 0 | No
2030-01-20 09:00 | 2030 33% ECP | 427.35 | -526 | -510 | 6.4 | 0 | 0 | No
2030-01-20 10:00 | 2030 33% ECP | 17.51 | -227.39 | -510 | 306.4 | 0 | 0 | No
2030-01-20 11:00 | 2030 33% ECP | -402.49 | -526 | -510 | 401.01 | 0 | 0 | No
2030-01-20 12:00 | 2030 33% ECP | -700 | -526 | -510 | 456.87 | 0 | 0 | No
2030-01-20 13:00 | 2030 33% ECP | -280 | -408.81 | -510 | 449.98 | 0 | 0 | No
2030-01-20 14:00 | 2030 33% ECP | 140 | -276.39 | -510 | 149.98 | 0 | 0 | No
2030-01-20 15:00 | 2030 33% ECP | 560 | -64.03 | -300 | 333.35 | 0 | 0 | No
2030-01-20 16:00 | 2030 33% ECP | 700 | 0 | 0 | 264 | 0 | 0 | No
2030-01-20 17:00 | 2030 33% ECP | 700 | 0 | 300 | 496.62 | 0 | 0 | No
2030-01-20 18:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-20 19:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-20 20:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-20 21:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-20 22:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-20 23:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-21 | 2030 33% ECP | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-01-21 01:00 | 2030 33% ECP | 700 | 144.33 | 510 | 510 | 0 | 0 | No
2030-01-21 02:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-21 03:00 | 2030 33% ECP | 700 | 300 | 510 | 462.87 | 0 | 0 | No
2030-01-21 04:00 | 2030 33% ECP | 700 | 0 | 510 | 280.66 | 0 | 0 | No
2030-01-21 05:00 | 2030 33% ECP | 700 | 0 | 510 | 431.69 | 0 | 0 | No
2030-01-21 06:00 | 2030 33% ECP | 700 | 41.22 | 510 | 354.16 | 0 | 0 | No
2030-01-21 07:00 | 2030 33% ECP | 700 | 341.22 | 510 | 510 | 0 | 0 | No
2030-01-21 08:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 09:00 | 2030 33% ECP | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-01-21 10:00 | 2030 33% ECP | 700 | 0 | 510 | 302.38 | 0 | 0 | No
2030-01-21 11:00 | 2030 33% ECP | 700 | 0 | 510 | 2.38 | 0 | 0 | No
2030-01-21 12:00 | 2030 33% ECP | 700 | 147.63 | 295.06 | 210 | 0 | 0 | No
2030-01-21 13:00 | 2030 33% ECP | 700 | 447.63 | 510 | 510 | 0 | 0 | No
2030-01-21 14:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 15:00 | 2030 33% ECP | 700 | 205 | 393.66 | 210 | 0 | 0 | No
2030-01-21 16:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-21 17:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-21 18:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-21 19:00 | 2030 33% ECP | 700 | 0 | 510 | 77.81 | 0 | 0 | No
2030-01-21 20:00 | 2030 33% ECP | 700 | 0 | 510 | 377.81 | 0 | 0 | No
2030-01-21 21:00 | 2030 33% ECP | 700 | 205 | 510 | 273.9 | 0 | 0 | No
2030-01-21 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 23:00 | 2030 33% ECP | 700 | 278.04 | 510 | 510 | 0 | 0 | No
2030-01-22 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 05:00 | 2030 33% ECP | 700 | 505 | 510 | 463.7 | 0 | 0 | No
2030-01-22 06:00 | 2030 33% ECP | 700 | 205 | 399.81 | 163.7 | 0 | 0 | No
2030-01-22 07:00 | 2030 33% ECP | 700 | 0 | 99.81 | 0 | 0 | 0 | No
2030-01-22 08:00 | 2030 33% ECP | 700 | 0 | 299.97 | 0 | 0 | 0 | No
2030-01-22 09:00 | 2030 33% ECP | 700 | 254.26 | 510 | 65.92 | 0 | 0 | No
2030-01-22 10:00 | 2030 33% ECP | 700 | 187.42 | 510 | 136.37 | 0 | 0 | No
2030-01-22 11:00 | 2030 33% ECP | 700 | 0 | 510 | 78.13 | 0 | 0 | No
2030-01-22 12:00 | 2030 33% ECP | 700 | 0 | 468.5 | 0 | 0 | 0 | No
2030-01-22 13:00 | 2030 33% ECP | 700 | 0 | 510 | 60.21 | 0 | 0 | No
2030-01-22 14:00 | 2030 33% ECP | 700 | 284.77 | 390 | 88.75 | 0 | 0 | No
2030-01-22 15:00 | 2030 33% ECP | 700 | 0 | 90 | 0 | 0 | 0 | No
2030-01-22 16:00 | 2030 33% ECP | 700 | -226 | -210 | -241.66 | 0 | 0 | No
2030-01-22 17:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-22 18:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-22 19:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-22 20:00 | 2030 33% ECP | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-01-22 21:00 | 2030 33% ECP | 700 | 20.37 | 90 | 90 | 0 | 0 | No
2030-01-22 22:00 | 2030 33% ECP | 700 | 181.46 | 328.95 | 210 | 0 | 0 | No
2030-01-22 23:00 | 2030 33% ECP | 700 | 481.46 | 510 | 510 | 0 | 0 | No
2030-01-23 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 03:00 | 2030 33% ECP | 700 | 505 | 510 | 272.15 | 0 | 0 | No
2030-01-23 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 05:00 | 2030 33% ECP | 700 | 505 | 510 | 377.97 | 0 | 0 | No
2030-01-23 06:00 | 2030 33% ECP | 280 | 348.84 | 510 | 77.97 | 0 | 0 | No
2030-01-23 07:00 | 2030 33% ECP | 23.75 | 48.84 | 210 | -222.03 | 0 | 0 | No
2030-01-23 08:00 | 2030 33% ECP | 443.75 | 0 | 399.29 | 0 | 0 | 0 | No
2030-01-23 09:00 | 2030 33% ECP | 700 | 68.6 | 510 | 0 | 0 | 0 | No
2030-01-23 10:00 | 2030 33% ECP | 700 | 122.3 | 510 | 0 | 0 | 0 | No
2030-01-23 11:00 | 2030 33% ECP | 700 | 0 | 299.57 | 0 | 0 | 0 | No
2030-01-23 12:00 | 2030 33% ECP | 700 | 0 | 14.67 | 0 | 0 | 0 | No
2030-01-23 13:00 | 2030 33% ECP | 700 | 0 | 84.76 | 0 | 0 | 0 | No
2030-01-23 14:00 | 2030 33% ECP | 700 | 0 | 110.49 | 0 | 0 | 0 | No
2030-01-23 15:00 | 2030 33% ECP | 700 | 0 | 410.49 | 0 | 0 | 0 | No
2030-01-23 16:00 | 2030 33% ECP | 700 | 216.3 | 110.49 | -52.27 | 0 | 0 | No
2030-01-23 17:00 | 2030 33% ECP | 280 | -83.7 | -189.51 | -352.27 | 0 | 0 | No
2030-01-23 18:00 | 2030 33% ECP | 700 | -300 | -402.13 | -510 | 0 | 0 | No
2030-01-23 19:00 | 2030 33% ECP | 700 | 0 | -102.13 | -300 | 0 | 0 | No
2030-01-23 20:00 | 2030 33% ECP | 700 | 300 | 197.87 | 0 | 0 | 0 | No
2030-01-23 21:00 | 2030 33% ECP | 700 | 296.12 | 497.87 | 0 | 0 | 0 | No
2030-01-23 22:00 | 2030 33% ECP | 700 | 250.55 | 510 | 3.38 | 0 | 0 | No
2030-01-23 23:00 | 2030 33% ECP | 700 | 429.62 | 510 | 303.38 | 0 | 0 | No
2030-01-24 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 05:00 | 2030 33% ECP | 700 | 505 | 510 | 485 | 0 | 0 | No
2030-01-24 06:00 | 2030 33% ECP | 700 | 505 | 510 | 185 | 0 | 0 | No
2030-01-24 07:00 | 2030 33% ECP | 280 | 285.37 | 510 | -102.43 | 0 | 0 | No
2030-01-24 08:00 | 2030 33% ECP | 0 | 0 | 285.33 | -154.69 | 0 | 0 | No
2030-01-24 09:00 | 2030 33% ECP | 0 | 51.92 | 510 | -50.05 | 0 | 0 | No
2030-01-24 10:00 | 2030 33% ECP | -71.81 | 0 | 210 | -72.12 | 0 | 0 | No
2030-01-24 11:00 | 2030 33% ECP | -58.13 | 0 | 0 | -165.1 | 0 | 0 | No
2030-01-24 12:00 | 2030 33% ECP | 213.87 | 300 | 300 | 0 | 0 | 0 | No
2030-01-24 13:00 | 2030 33% ECP | -206.13 | 0 | 0 | -300 | 0 | 0 | No
2030-01-24 14:00 | 2030 33% ECP | 0 | 0 | -300 | -226.08 | 0 | 0 | No
2030-01-24 15:00 | 2030 33% ECP | 0 | -226 | -210 | -210 | 0 | 0 | No
2030-01-24 16:00 | 2030 33% ECP | 112.57 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 17:00 | 2030 33% ECP | 266.41 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 18:00 | 2030 33% ECP | 686.41 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 19:00 | 2030 33% ECP | 266.41 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 20:00 | 2030 33% ECP | 589.96 | -226 | -217.33 | -415.93 | 0 | 0 | No
2030-01-24 21:00 | 2030 33% ECP | 700 | 74 | 82.67 | -115.93 | 0 | 0 | No
2030-01-24 22:00 | 2030 33% ECP | 662.27 | 0 | -217.33 | -86.66 | 0 | 0 | No
2030-01-24 23:00 | 2030 33% ECP | 242.27 | 0 | 0 | 0 | 0 | 0 | No
2030-01-25 | 2030 33% ECP | 0 | 0 | -210 | 0 | 0 | 0 | No
2030-01-25 01:00 | 2030 33% ECP | 0 | 0 | -510 | 0 | 0 | 0 | No
2030-01-25 02:00 | 2030 33% ECP | 0 | 0 | -510 | 0 | 0 | 0 | No
2030-01-25 03:00 | 2030 33% ECP | -280 | 0 | -210 | 0 | 0 | 0 | No
2030-01-25 04:00 | 2030 33% ECP | -700 | 0 | -125.3 | -75.34 | 0 | 0 | No
2030-01-25 05:00 | 2030 33% ECP | -700 | 0 | -89.42 | -375.34 | 0 | 0 | No
2030-01-25 06:00 | 2030 33% ECP | -700 | 0 | -304.25 | -491.63 | 0 | 0 | No
2030-01-25 07:00 | 2030 33% ECP | -700 | 0 | -4.25 | -238.64 | 0 | 0 | No
2030-01-25 08:00 | 2030 33% ECP | -700 | 0 | 204.46 | 0 | 0 | 0 | No
2030-01-25 09:00 | 2030 33% ECP | -700 | 0 | 380.2 | 0 | 0 | 0 | No
2030-01-25 10:00 | 2030 33% ECP | -700 | 0 | 510 | 184.46 | 0 | 0 | No
2030-01-25 11:00 | 2030 33% ECP | -700 | 0 | 308.05 | 52.79 | 0 | 0 | No
2030-01-25 12:00 | 2030 33% ECP | -700 | 0 | 8.05 | 0 | 0 | 0 | No
2030-01-25 13:00 | 2030 33% ECP | -700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-25 14:00 | 2030 33% ECP | -700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-25 15:00 | 2030 33% ECP | -700 | 0 | 240.7 | 0 | 0 | 0 | No
2030-01-25 16:00 | 2030 33% ECP | -700 | 74 | 14.5 | -27.49 | 0 | 0 | No
2030-01-25 17:00 | 2030 33% ECP | -700 | -226 | -285.5 | -327.49 | 0 | 0 | No
2030-01-25 18:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-25 19:00 | 2030 33% ECP | -700 | -300 | -496.69 | -300 | 0 | 0 | No
2030-01-25 20:00 | 2030 33% ECP | -700 | 0 | -196.69 | 0 | 0 | 0 | No
2030-01-25 21:00 | 2030 33% ECP | -700 | -7.05 | -496.69 | -18.41 | 0 | 0 | No
2030-01-25 22:00 | 2030 33% ECP | -700 | -31.96 | -474.09 | 0 | 0 | 0 | No
2030-01-25 23:00 | 2030 33% ECP | -700 | -331.96 | -510 | -91.51 | 0 | 0 | No
2030-01-26 | 2030 33% ECP | -700 | -31.96 | -210 | 208.49 | 0 | 0 | No
2030-01-26 01:00 | 2030 33% ECP | -700 | 268.04 | 90 | 508.49 | 0 | 0 | Yes
2030-01-26 02:00 | 2030 33% ECP | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-01-26 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-26 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-26 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-26 06:00 | 2030 33% ECP | -700 | 505 | 510 | 412.4 | 0 | 0 | Yes
2030-01-26 07:00 | 2030 33% ECP | -700 | 205 | 210 | 112.4 | 0 | 0 | No
2030-01-26 08:00 | 2030 33% ECP | -700 | 0 | 364.83 | 94.29 | 0 | 0 | No
2030-01-26 09:00 | 2030 33% ECP | -700 | 0 | 510 | 394.29 | 0 | 0 | No
2030-01-26 10:00 | 2030 33% ECP | -700 | 0 | 510 | 124.64 | 0 | 0 | No
2030-01-26 11:00 | 2030 33% ECP | -700 | 0 | 510 | 2.43 | 0 | 0 | No
2030-01-26 12:00 | 2030 33% ECP | -700 | 0 | 433.29 | 20.82 | 0 | 0 | No
2030-01-26 13:00 | 2030 33% ECP | -700 | 31.34 | 510 | 320.82 | 0 | 0 | No
2030-01-26 14:00 | 2030 33% ECP | -700 | 0 | 484.44 | 338.07 | 0 | 0 | No
2030-01-26 15:00 | 2030 33% ECP | -700 | 300 | 184.44 | 384.55 | 0 | 0 | No
2030-01-26 16:00 | 2030 33% ECP | -700 | 0 | -115.56 | 84.55 | 0 | 0 | No
2030-01-26 17:00 | 2030 33% ECP | -700 | -300 | -415.56 | -215.45 | 0 | 0 | No
2030-01-26 18:00 | 2030 33% ECP | -700 | -526 | -510 | -477.36 | 0 | 0 | No
2030-01-26 19:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-26 20:00 | 2030 33% ECP | -700 | -300 | -372.5 | -210 | 0 | 0 | No
2030-01-26 21:00 | 2030 33% ECP | -510.36 | 0 | -72.5 | 90 | 0 | 0 | No
2030-01-26 22:00 | 2030 33% ECP | -455.61 | -300 | -372.5 | 9.1 | 0 | 0 | No
2030-01-26 23:00 | 2030 33% ECP | -635.5 | -526 | -510 | -262.64 | 0 | 0 | No
2030-01-27 | 2030 33% ECP | -700 | -226 | -210 | 37.36 | 0 | 0 | No
2030-01-27 01:00 | 2030 33% ECP | -700 | 74 | 90 | 210 | 0 | 0 | No
2030-01-27 02:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-01-27 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 08:00 | 2030 33% ECP | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-27 09:00 | 2030 33% ECP | -700 | -95 | -90 | -90 | 0 | 0 | No
2030-01-27 10:00 | 2030 33% ECP | -700 | 0 | -255.98 | 0 | 0 | 0 | No
2030-01-27 11:00 | 2030 33% ECP | -700 | -97.14 | -510 | -290.39 | 0 | 0 | No
2030-01-27 12:00 | 2030 33% ECP | -700 | 0 | -367.04 | 9.61 | 0 | 0 | No
2030-01-27 13:00 | 2030 33% ECP | -700 | -250.39 | -67.04 | -144.9 | 0 | 0 | No
2030-01-27 14:00 | 2030 33% ECP | -280 | 0 | 232.96 | 155.1 | 0 | 0 | No
2030-01-27 15:00 | 2030 33% ECP | 93.72 | 0 | 254.38 | 133.84 | 0 | 0 | No
2030-01-27 16:00 | 2030 33% ECP | -280 | 300 | 105.44 | 421.3 | 0 | 0 | No
2030-01-27 17:00 | 2030 33% ECP | -700 | 0 | -194.56 | 121.3 | 0 | 0 | No
2030-01-27 18:00 | 2030 33% ECP | -420 | -272.41 | -90 | 210 | 0 | 0 | No
2030-01-27 19:00 | 2030 33% ECP | 0 | 27.59 | 210 | 510 | 0 | 0 | No
2030-01-27 20:00 | 2030 33% ECP | 420 | 300 | 510 | 510 | 0 | 0 | No
2030-01-27 21:00 | 2030 33% ECP | 700 | 0 | 510 | 476.43 | 0 | 0 | No
2030-01-27 22:00 | 2030 33% ECP | 700 | 0 | 510 | 176.43 | 0 | 0 | No
2030-01-27 23:00 | 2030 33% ECP | 700 | 0 | 210.84 | 187.63 | 0 | 0 | No
2030-01-28 | 2030 33% ECP | 700 | 0 | 24.09 | 109.93 | 0 | 0 | No
2030-01-28 01:00 | 2030 33% ECP | 328.04 | 0 | -240.32 | 0 | 0 | 0 | No
2030-01-28 02:00 | 2030 33% ECP | 62.05 | -95 | -90 | 243.76 | 0 | 0 | No
2030-01-28 03:00 | 2030 33% ECP | 482.05 | 205 | 210 | 210 | 0 | 0 | No
2030-01-28 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-28 05:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-28 06:00 | 2030 33% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-01-28 07:00 | 2030 33% ECP | -560 | 205 | 210 | 210 | 0 | 0 | No
2030-01-28 08:00 | 2030 33% ECP | -700 | -95 | -90 | 468.25 | 0 | 0 | No
2030-01-28 09:00 | 2030 33% ECP | -280 | -395 | -390 | 168.25 | 0 | 0 | No
2030-01-28 10:00 | 2030 33% ECP | 0 | -419.05 | -510 | 404.9 | 0 | 0 | No
2030-01-28 11:00 | 2030 33% ECP | -374.05 | -226 | -210 | 106.99 | 0 | 0 | No
2030-01-28 12:00 | 2030 33% ECP | -700 | -526 | -510 | 110.28 | 0 | 0 | No
2030-01-28 13:00 | 2030 33% ECP | -700 | -526 | -510 | 410.28 | 0 | 0 | No
2030-01-28 14:00 | 2030 33% ECP | -700 | -526 | -510 | 448.44 | 0 | 0 | No
2030-01-28 15:00 | 2030 33% ECP | -396.63 | -501.07 | -510 | 336.23 | 0 | 0 | No
2030-01-28 16:00 | 2030 33% ECP | -280 | -201.07 | -510 | 229.16 | 0 | 0 | No
2030-01-28 17:00 | 2030 33% ECP | -700 | 0 | -510 | 510 | 0 | 0 | No
2030-01-28 18:00 | 2030 33% ECP | -700 | 0 | -510 | 210 | 0 | 0 | No
2030-01-28 19:00 | 2030 33% ECP | -700 | 0 | -390 | 182.94 | 0 | 0 | No
2030-01-28 20:00 | 2030 33% ECP | -700 | 0 | -90 | 482.94 | 0 | 0 | No
2030-01-28 21:00 | 2030 33% ECP | -280 | 205 | 210 | 510 | 0 | 0 | No
2030-01-28 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-28 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 07:00 | 2030 33% ECP | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-29 08:00 | 2030 33% ECP | -700 | 0 | -90 | 288.23 | 0 | 0 | No
2030-01-29 09:00 | 2030 33% ECP | -700 | 0 | -270.82 | 510 | 0 | 0 | No
2030-01-29 10:00 | 2030 33% ECP | -700 | -225.44 | -430.93 | 510 | 0 | 0 | No
2030-01-29 11:00 | 2030 33% ECP | -700 | -525.44 | -510 | 510 | 0 | 0 | No
2030-01-29 12:00 | 2030 33% ECP | -700 | -526 | -510 | 314.61 | 0 | 0 | No
2030-01-29 13:00 | 2030 33% ECP | -700 | -526 | -510 | 14.61 | 0 | 0 | No
2030-01-29 14:00 | 2030 33% ECP | -700 | -484.01 | -510 | -257.89 | 0 | 0 | No
2030-01-29 15:00 | 2030 33% ECP | -700 | -184.01 | -510 | -7.18 | 0 | 0 | No
2030-01-29 16:00 | 2030 33% ECP | -700 | 0 | -510 | 0 | 0 | 0 | No
2030-01-29 17:00 | 2030 33% ECP | -700 | 0 | -210 | 0 | 0 | 0 | No
2030-01-29 18:00 | 2030 33% ECP | -700 | 0 | -20.2 | 210 | 0 | 0 | No
2030-01-29 19:00 | 2030 33% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-01-29 20:00 | 2030 33% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-01-29 21:00 | 2030 33% ECP | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-01-29 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 06:00 | 2030 33% ECP | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-30 07:00 | 2030 33% ECP | -700 | -25.98 | -90 | -89.36 | 0 | 0 | No
2030-01-30 08:00 | 2030 33% ECP | -700 | 0 | -390 | 210 | 0 | 0 | No
2030-01-30 09:00 | 2030 33% ECP | -700 | 0 | -432.71 | 510 | 0 | 0 | No
2030-01-30 10:00 | 2030 33% ECP | -700 | 0 | -390 | 314.77 | 0 | 0 | No
2030-01-30 11:00 | 2030 33% ECP | -700 | -11.01 | -90 | 14.77 | 0 | 0 | No
2030-01-30 12:00 | 2030 33% ECP | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-30 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 16:00 | 2030 33% ECP | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-30 17:00 | 2030 33% ECP | -700 | 0 | 510 | 367.31 | 0 | 0 | No
2030-01-30 18:00 | 2030 33% ECP | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-30 19:00 | 2030 33% ECP | -700 | 185.44 | 510 | 510 | 0 | 0 | No
2030-01-30 20:00 | 2030 33% ECP | -700 | 82.05 | 510 | 510 | 0 | 0 | No
2030-01-30 21:00 | 2030 33% ECP | -280 | 313.87 | 510 | 510 | 0 | 0 | No
2030-01-30 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 06:00 | 2030 33% ECP | -700 | 505 | 426.36 | 510 | 0 | 0 | No
2030-01-31 07:00 | 2030 33% ECP | -700 | 205 | 126.36 | 367.42 | 0 | 0 | No
2030-01-31 08:00 | 2030 33% ECP | -700 | -95 | -173.64 | 67.42 | 0 | 0 | No
2030-01-31 09:00 | 2030 33% ECP | -700 | -324.94 | -390 | 210 | 0 | 0 | No
2030-01-31 10:00 | 2030 33% ECP | -700 | -24.94 | -90 | 510 | 0 | 0 | No
2030-01-31 11:00 | 2030 33% ECP | -700 | 205 | 210 | 311.77 | 0 | 0 | No
2030-01-31 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-31 14:00 | 2030 33% ECP | -700 | 505 | 390.74 | 510 | 0 | 0 | No
2030-01-31 15:00 | 2030 33% ECP | -700 | 205 | 90.74 | 510 | 0 | 0 | No
2030-01-31 16:00 | 2030 33% ECP | -700 | -95 | -209.26 | 210 | 0 | 0 | No
2030-01-31 17:00 | 2030 33% ECP | -700 | -395 | -509.26 | -8.63 | 0 | 0 | No
2030-01-31 18:00 | 2030 33% ECP | -700 | -526 | -510 | -9.32 | 0 | 0 | No
2030-01-31 19:00 | 2030 33% ECP | -700 | -475.66 | -510 | 194.86 | 0 | 0 | No
2030-01-31 20:00 | 2030 33% ECP | -700 | -175.66 | -210 | 494.86 | 0 | 0 | No
2030-01-31 21:00 | 2030 33% ECP | -700 | 124.34 | 90 | 510 | 0 | 0 | Yes
2030-01-31 22:00 | 2030 33% ECP | -700 | 424.34 | 390 | 510 | 0 | 0 | Yes
2030-01-31 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 15:00 | 2030 33% ECP | -528.58 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 16:00 | 2030 33% ECP | -108.58 | 205 | 510 | 303.3 | 0 | 0 | No
2030-02-01 17:00 | 2030 33% ECP | 311.42 | 505 | 510 | 510 | 0 | 0 | No
2030-02-01 18:00 | 2030 33% ECP | 401.38 | 505 | 510 | 510 | 0 | 0 | No
2030-02-01 19:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-01 20:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-01 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-01 22:00 | 2030 33% ECP | 700 | 300 | 319.22 | 510 | 0 | 0 | No
2030-02-01 23:00 | 2030 33% ECP | 568.38 | 0 | 19.22 | 457.93 | 0 | 0 | No
2030-02-02 | 2030 33% ECP | 700 | -242.89 | -280.78 | 157.93 | 0 | 0 | No
2030-02-02 01:00 | 2030 33% ECP | 666.36 | -300 | -344.27 | 123.7 | 0 | 0 | No
2030-02-02 02:00 | 2030 33% ECP | 700 | 0 | -44.27 | 236.83 | 0 | 0 | No
2030-02-02 03:00 | 2030 33% ECP | 700 | -169.9 | -344.27 | -63.17 | 0 | 0 | No
2030-02-02 04:00 | 2030 33% ECP | 392.35 | -469.9 | -510 | -42.56 | 0 | 0 | No
2030-02-02 05:00 | 2030 33% ECP | 36.48 | -526 | -510 | -40.22 | 0 | 0 | No
2030-02-02 06:00 | 2030 33% ECP | -152.46 | -526 | -510 | -163.71 | 0 | 0 | No
2030-02-02 07:00 | 2030 33% ECP | -87.99 | -526 | -510 | 8.62 | 0 | 0 | No
2030-02-02 08:00 | 2030 33% ECP | -280 | -226 | -385.2 | 220.01 | 0 | 0 | No
2030-02-02 09:00 | 2030 33% ECP | -700 | -526 | -510 | 149.26 | 0 | 0 | No
2030-02-02 10:00 | 2030 33% ECP | -700 | -526 | -510 | 215.01 | 0 | 0 | No
2030-02-02 11:00 | 2030 33% ECP | -700 | -526 | -510 | 268.16 | 0 | 0 | No
2030-02-02 12:00 | 2030 33% ECP | -700 | -526 | -510 | 300.12 | 0 | 0 | No
2030-02-02 13:00 | 2030 33% ECP | -700 | -526 | -510 | 253.54 | 0 | 0 | No
2030-02-02 14:00 | 2030 33% ECP | -700 | -526 | -510 | 117.52 | 0 | 0 | No
2030-02-02 15:00 | 2030 33% ECP | -700 | -526 | -510 | 63.58 | 0 | 0 | No
2030-02-02 16:00 | 2030 33% ECP | -700 | -526 | -510 | 55.05 | 0 | 0 | No
2030-02-02 17:00 | 2030 33% ECP | -700 | -526 | -510 | 355.05 | 0 | 0 | No
2030-02-02 18:00 | 2030 33% ECP | -700 | -526 | -510 | 391.48 | 0 | 0 | No
2030-02-02 19:00 | 2030 33% ECP | -700 | -526 | -510 | 91.48 | 0 | 0 | No
2030-02-02 20:00 | 2030 33% ECP | -700 | -510.18 | -510 | 108.38 | 0 | 0 | No
2030-02-02 21:00 | 2030 33% ECP | -700 | -210.18 | -210 | 220.44 | 0 | 0 | No
2030-02-02 22:00 | 2030 33% ECP | -700 | 89.82 | 90 | 510 | 0 | 0 | No
2030-02-02 23:00 | 2030 33% ECP | -700 | 389.82 | 390 | 510 | 0 | 0 | Yes
2030-02-03 | 2030 33% ECP | -700 | 505 | 510 | 239.45 | 0 | 0 | Yes
2030-02-03 01:00 | 2030 33% ECP | -700 | 505 | 510 | 112.55 | 0 | 0 | Yes
2030-02-03 02:00 | 2030 33% ECP | -700 | 505 | 510 | 159.47 | 0 | 0 | Yes
2030-02-03 03:00 | 2030 33% ECP | -700 | 505 | 510 | 193.35 | 0 | 0 | Yes
2030-02-03 04:00 | 2030 33% ECP | -700 | 505 | 510 | 127.16 | 0 | 0 | Yes
2030-02-03 05:00 | 2030 33% ECP | -700 | 505 | 510 | 170.54 | 0 | 0 | Yes
2030-02-03 06:00 | 2030 33% ECP | -700 | 505 | 510 | 255.17 | 0 | 0 | Yes
2030-02-03 07:00 | 2030 33% ECP | -700 | 505 | 510 | 272.15 | 0 | 0 | Yes
2030-02-03 08:00 | 2030 33% ECP | -700 | 505 | 510 | 236.18 | 0 | 0 | Yes
2030-02-03 09:00 | 2030 33% ECP | -700 | 505 | 510 | 487.76 | 0 | 0 | Yes
2030-02-03 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-03 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 12:00 | 2030 33% ECP | -700 | 505 | 510 | 456.42 | 0 | 0 | Yes
2030-02-03 13:00 | 2030 33% ECP | -700 | 505 | 510 | 415.67 | 0 | 0 | Yes
2030-02-03 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 15:00 | 2030 33% ECP | -700 | 505 | 510 | 455.78 | 0 | 0 | Yes
2030-02-03 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-03 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-03 20:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 01:00 | 2030 33% ECP | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-02-04 02:00 | 2030 33% ECP | -700 | 505 | 510 | 346.94 | 0 | 0 | Yes
2030-02-04 03:00 | 2030 33% ECP | -700 | 505 | 510 | 262.97 | 0 | 0 | Yes
2030-02-04 04:00 | 2030 33% ECP | -700 | 505 | 510 | 142.91 | 0 | 0 | Yes
2030-02-04 05:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-02-04 06:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-02-04 07:00 | 2030 33% ECP | -700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-02-04 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 13:00 | 2030 33% ECP | -694.14 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 14:00 | 2030 33% ECP | -274.14 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 15:00 | 2030 33% ECP | 145.86 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 16:00 | 2030 33% ECP | 565.86 | 251.2 | 510 | 510 | 0 | 0 | No
2030-02-04 17:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 18:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 19:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 20:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 22:00 | 2030 33% ECP | 700 | 470.61 | 510 | 510 | 0 | 0 | No
2030-02-04 23:00 | 2030 33% ECP | 700 | 470.61 | 510 | 510 | 0 | 0 | No
2030-02-05 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 05:00 | 2030 33% ECP | 280 | 300 | 510 | 510 | 0 | 0 | No
2030-02-05 06:00 | 2030 33% ECP | -140 | 0 | 210 | 210 | 0 | 0 | No
2030-02-05 07:00 | 2030 33% ECP | -280 | 0 | 0 | 35.66 | 0 | 0 | No
2030-02-05 08:00 | 2030 33% ECP | -700 | 0 | -300 | -54.62 | 0 | 0 | No
2030-02-05 09:00 | 2030 33% ECP | -280 | 0 | 0 | 196.32 | 0 | 0 | No
2030-02-05 10:00 | 2030 33% ECP | -256.16 | -300 | -300 | 0 | 0 | 0 | No
2030-02-05 11:00 | 2030 33% ECP | -673.77 | -300 | -510 | 47.31 | 0 | 0 | No
2030-02-05 12:00 | 2030 33% ECP | -700 | 0 | -330.68 | 28.11 | 0 | 0 | No
2030-02-05 13:00 | 2030 33% ECP | -700 | 0 | -30.68 | 52.85 | 0 | 0 | No
2030-02-05 14:00 | 2030 33% ECP | -700 | 0 | 12.09 | 54.32 | 0 | 0 | No
2030-02-05 15:00 | 2030 33% ECP | -421.54 | 0 | 0 | 84.66 | 0 | 0 | No
2030-02-05 16:00 | 2030 33% ECP | -1.54 | 0 | 0 | 0 | 0 | 0 | No
2030-02-05 17:00 | 2030 33% ECP | -421.54 | 0 | -183.9 | 0 | 0 | 0 | No
2030-02-05 18:00 | 2030 33% ECP | -140 | -300 | -483.9 | -300 | 0 | 0 | No
2030-02-05 19:00 | 2030 33% ECP | 280 | 0 | -183.9 | 0 | 0 | 0 | No
2030-02-05 20:00 | 2030 33% ECP | 700 | 300 | 116.1 | 300 | 0 | 0 | No
2030-02-05 21:00 | 2030 33% ECP | 700 | 0 | 416.1 | 71.74 | 0 | 0 | No
2030-02-05 22:00 | 2030 33% ECP | 280 | 0 | 122.27 | 0 | 0 | 0 | No
2030-02-05 23:00 | 2030 33% ECP | 190.83 | 0 | 422.27 | 286.83 | 0 | 0 | No
2030-02-06 | 2030 33% ECP | 199.28 | 300 | 510 | 510 | 0 | 0 | No
2030-02-06 01:00 | 2030 33% ECP | 619.28 | 505 | 510 | 510 | 0 | 0 | No
2030-02-06 02:00 | 2030 33% ECP | 199.28 | 505 | 510 | 510 | 0 | 0 | No
2030-02-06 03:00 | 2030 33% ECP | -220.72 | 505 | 510 | 510 | 0 | 0 | No
2030-02-06 04:00 | 2030 33% ECP | -640.72 | 300 | 482.22 | 300 | 0 | 0 | No
2030-02-06 05:00 | 2030 33% ECP | -700 | 0 | 182.22 | 0 | 0 | 0 | No
2030-02-06 06:00 | 2030 33% ECP | -700 | -300 | -117.78 | -300 | 0 | 0 | No
2030-02-06 07:00 | 2030 33% ECP | -700 | -172.54 | -210 | -210 | 0 | 0 | No
2030-02-06 08:00 | 2030 33% ECP | -420 | -472.54 | -510 | -510 | 0 | 0 | No
2030-02-06 09:00 | 2030 33% ECP | 0 | -172.54 | -210 | -210 | 0 | 0 | No
2030-02-06 10:00 | 2030 33% ECP | 420 | 0 | -510 | -36.67 | 0 | 0 | No
2030-02-06 11:00 | 2030 33% ECP | 0 | -266.08 | -510 | -147.57 | 0 | 0 | No
2030-02-06 12:00 | 2030 33% ECP | -210.66 | -526 | -510 | -186.91 | 0 | 0 | No
2030-02-06 13:00 | 2030 33% ECP | -410.49 | -526 | -510 | -85.12 | 0 | 0 | No
2030-02-06 14:00 | 2030 33% ECP | 0 | -420.79 | -510 | -182.95 | 0 | 0 | No
2030-02-06 15:00 | 2030 33% ECP | -82.85 | -526 | -510 | -210 | 0 | 0 | No
2030-02-06 16:00 | 2030 33% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 17:00 | 2030 33% ECP | -420 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 18:00 | 2030 33% ECP | -420 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 19:00 | 2030 33% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 20:00 | 2030 33% ECP | -166.17 | -226 | -510 | -302.67 | 0 | 0 | No
2030-02-06 21:00 | 2030 33% ECP | -586.17 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 22:00 | 2030 33% ECP | -700 | -226 | -434.15 | -210 | 0 | 0 | No
2030-02-06 23:00 | 2030 33% ECP | -515.17 | -526 | -510 | -403.59 | 0 | 0 | No
2030-02-07 | 2030 33% ECP | -561.96 | -526 | -510 | -112.15 | 0 | 0 | No
2030-02-07 01:00 | 2030 33% ECP | -700 | -526 | -510 | 119.71 | 0 | 0 | No
2030-02-07 02:00 | 2030 33% ECP | -700 | -526 | -510 | 164.14 | 0 | 0 | No
2030-02-07 03:00 | 2030 33% ECP | -700 | -526 | -510 | -135.86 | 0 | 0 | No
2030-02-07 04:00 | 2030 33% ECP | -700 | -526 | -510 | -50.64 | 0 | 0 | No
2030-02-07 05:00 | 2030 33% ECP | -700 | -526 | -510 | 61.26 | 0 | 0 | No
2030-02-07 06:00 | 2030 33% ECP | -700 | -526 | -510 | 338.77 | 0 | 0 | No
2030-02-07 07:00 | 2030 33% ECP | -700 | -526 | -510 | 38.77 | 0 | 0 | No
2030-02-07 08:00 | 2030 33% ECP | -700 | -526 | -510 | -95.07 | 0 | 0 | No
2030-02-07 09:00 | 2030 33% ECP | -700 | -526 | -510 | -131.25 | 0 | 0 | No
2030-02-07 10:00 | 2030 33% ECP | -700 | -526 | -510 | 161.22 | 0 | 0 | No
2030-02-07 11:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-02-07 12:00 | 2030 33% ECP | -700 | -526 | -510 | -133.14 | 0 | 0 | No
2030-02-07 13:00 | 2030 33% ECP | -700 | -526 | -510 | 166.86 | 0 | 0 | No
2030-02-07 14:00 | 2030 33% ECP | -700 | -226 | -210 | 79.49 | 0 | 0 | No
2030-02-07 15:00 | 2030 33% ECP | -700 | 74 | 90 | 379.49 | 0 | 0 | No
2030-02-07 16:00 | 2030 33% ECP | -700 | -226 | -210 | 79.49 | 0 | 0 | No
2030-02-07 17:00 | 2030 33% ECP | -700 | -526 | -510 | -220.51 | 0 | 0 | No
2030-02-07 18:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-07 19:00 | 2030 33% ECP | -700 | -300 | -385.78 | -385.43 | 0 | 0 | No
2030-02-07 20:00 | 2030 33% ECP | -700 | 0 | -85.78 | -85.43 | 0 | 0 | No
2030-02-07 21:00 | 2030 33% ECP | -700 | 300 | 214.22 | 214.57 | 0 | 0 | No
2030-02-07 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-07 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 09:00 | 2030 33% ECP | -700 | 205 | 381.87 | 210 | 0 | 0 | Yes
2030-02-08 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 17:00 | 2030 33% ECP | -700 | 300 | 298.23 | 408.59 | 0 | 0 | Yes
2030-02-08 18:00 | 2030 33% ECP | -700 | 0 | -1.77 | 108.59 | 0 | 0 | No
2030-02-08 19:00 | 2030 33% ECP | -700 | 174.51 | 210 | 408.59 | 0 | 0 | No
2030-02-08 20:00 | 2030 33% ECP | -700 | 474.51 | 510 | 510 | 0 | 0 | No
2030-02-08 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-08 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-08 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-09 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 06:00 | 2030 33% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-02-09 07:00 | 2030 33% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-02-09 08:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-02-09 09:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-09 10:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-09 11:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-09 12:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-09 13:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 14:00 | 2030 33% ECP | -700 | -226 | -510 | -452.18 | 0 | 0 | No
2030-02-09 15:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-02-09 16:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-09 17:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-09 18:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-09 19:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-02-09 20:00 | 2030 33% ECP | -700 | 74 | 90 | 90 | 0 | 0 | No
2030-02-09 21:00 | 2030 33% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-02-09 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 | 2030 33% ECP | -700 | 505 | 510 | 446.31 | 0 | 0 | Yes
2030-02-10 01:00 | 2030 33% ECP | -700 | 505 | 510 | 225.07 | 0 | 0 | Yes
2030-02-10 02:00 | 2030 33% ECP | -700 | 505 | 510 | 232.33 | 0 | 0 | Yes
2030-02-10 03:00 | 2030 33% ECP | -700 | 505 | 510 | 385.52 | 0 | 0 | Yes
2030-02-10 04:00 | 2030 33% ECP | -700 | 505 | 510 | 368.81 | 0 | 0 | Yes
2030-02-10 05:00 | 2030 33% ECP | -700 | 505 | 510 | 98.22 | 0 | 0 | Yes
2030-02-10 06:00 | 2030 33% ECP | -700 | 505 | 510 | 64.87 | 0 | 0 | Yes
2030-02-10 07:00 | 2030 33% ECP | -700 | 505 | 510 | 246.57 | 0 | 0 | Yes
2030-02-10 08:00 | 2030 33% ECP | -700 | 505 | 510 | 393.75 | 0 | 0 | Yes
2030-02-10 09:00 | 2030 33% ECP | -700 | 505 | 510 | 200.21 | 0 | 0 | Yes
2030-02-10 10:00 | 2030 33% ECP | -700 | 505 | 510 | 361.04 | 0 | 0 | Yes
2030-02-10 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 12:00 | 2030 33% ECP | -700 | 505 | 510 | 301.9 | 0 | 0 | Yes
2030-02-10 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 15:00 | 2030 33% ECP | -700 | 505 | 510 | 263.82 | 0 | 0 | Yes
2030-02-10 16:00 | 2030 33% ECP | -700 | 505 | 510 | 458.49 | 0 | 0 | Yes
2030-02-10 17:00 | 2030 33% ECP | -700 | 505 | 510 | 346.4 | 0 | 0 | Yes
2030-02-10 18:00 | 2030 33% ECP | -700 | 505 | 510 | 466.83 | 0 | 0 | Yes
2030-02-10 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 20:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 22:00 | 2030 33% ECP | -700 | 505 | 510 | 461.51 | 0 | 0 | Yes
2030-02-10 23:00 | 2030 33% ECP | -700 | 505 | 510 | 314.1 | 0 | 0 | Yes
2030-02-11 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 01:00 | 2030 33% ECP | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-02-11 02:00 | 2030 33% ECP | -700 | 505 | 510 | 263.02 | 0 | 0 | Yes
2030-02-11 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 04:00 | 2030 33% ECP | -700 | 505 | 510 | 339.1 | 0 | 0 | Yes
2030-02-11 05:00 | 2030 33% ECP | -700 | 505 | 510 | 149.12 | 0 | 0 | Yes
2030-02-11 06:00 | 2030 33% ECP | -700 | 505 | 510 | 449.12 | 0 | 0 | Yes
2030-02-11 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-11 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-11 20:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-11 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-11 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 01:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 02:00 | 2030 33% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 03:00 | 2030 33% ECP | 662.43 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 04:00 | 2030 33% ECP | 242.43 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 05:00 | 2030 33% ECP | -177.57 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 06:00 | 2030 33% ECP | -597.57 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 08:00 | 2030 33% ECP | -297.94 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 09:00 | 2030 33% ECP | -587.46 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 13:00 | 2030 33% ECP | -476.5 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 14:00 | 2030 33% ECP | -56.5 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 15:00 | 2030 33% ECP | -39.28 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 16:00 | 2030 33% ECP | -280 | 205 | 210 | 510 | 0 | 0 | No
2030-02-12 17:00 | 2030 33% ECP | -700 | -95 | -90 | 510 | 0 | 0 | No
2030-02-12 18:00 | 2030 33% ECP | -700 | -395 | -390 | 510 | 0 | 0 | No
2030-02-12 19:00 | 2030 33% ECP | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-02-12 20:00 | 2030 33% ECP | -354.04 | -526 | -510 | 510 | 0 | 0 | No
2030-02-12 21:00 | 2030 33% ECP | -700 | -300 | -357.23 | 426.04 | 0 | 0 | No
2030-02-12 22:00 | 2030 33% ECP | -280 | 0 | -57.23 | 126.04 | 0 | 0 | No
2030-02-12 23:00 | 2030 33% ECP | -700 | 300 | 242.77 | 426.04 | 0 | 0 | Yes
2030-02-13 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 01:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 02:00 | 2030 33% ECP | 560 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 04:00 | 2030 33% ECP | 700 | 505 | 510 | 333.53 | 0 | 0 | Yes
2030-02-13 05:00 | 2030 33% ECP | 700 | 505 | 510 | 362.7 | 0 | 0 | Yes
2030-02-13 06:00 | 2030 33% ECP | 700 | 505 | 510 | 243.09 | 0 | 0 | Yes
2030-02-13 07:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 08:00 | 2030 33% ECP | 700 | 205 | 210 | 277.27 | 0 | 0 | No
2030-02-13 09:00 | 2030 33% ECP | 700 | -95 | -90 | 37.97 | 0 | 0 | No
2030-02-13 10:00 | 2030 33% ECP | 280 | -395 | -390 | 337.97 | 0 | 0 | No
2030-02-13 11:00 | 2030 33% ECP | 235.53 | -526 | -510 | 300.24 | 0 | 0 | No
2030-02-13 12:00 | 2030 33% ECP | 280 | -526 | -510 | 0.24 | 0 | 0 | No
2030-02-13 13:00 | 2030 33% ECP | -140 | -526 | -510 | -237.12 | 0 | 0 | No
2030-02-13 14:00 | 2030 33% ECP | 280 | -526 | -510 | 62.88 | 0 | 0 | No
2030-02-13 15:00 | 2030 33% ECP | 700 | -226 | -390.7 | 324.74 | 0 | 0 | No
2030-02-13 16:00 | 2030 33% ECP | 700 | -33.88 | -90.7 | 510 | 0 | 0 | No
2030-02-13 17:00 | 2030 33% ECP | 700 | 0 | 209.3 | 510 | 0 | 0 | No
2030-02-13 18:00 | 2030 33% ECP | 700 | -33.26 | -90 | 510 | 0 | 0 | No
2030-02-13 19:00 | 2030 33% ECP | 700 | 48.57 | 210 | 510 | 0 | 0 | No
2030-02-13 20:00 | 2030 33% ECP | 700 | 348.57 | 510 | 510 | 0 | 0 | No
2030-02-13 21:00 | 2030 33% ECP | 700 | 48.57 | 210 | 510 | 0 | 0 | No
2030-02-13 22:00 | 2030 33% ECP | 560 | -225.57 | -90 | 400 | 0 | 0 | No
2030-02-13 23:00 | 2030 33% ECP | 140 | -395.3 | -390 | 100 | 0 | 0 | No
2030-02-14 | 2030 33% ECP | -280 | -471.5 | -510 | -192.58 | 0 | 0 | No
2030-02-14 01:00 | 2030 33% ECP | -700 | -526 | -510 | -10.86 | 0 | 0 | No
2030-02-14 02:00 | 2030 33% ECP | -700 | -526 | -510 | 60.83 | 0 | 0 | No
2030-02-14 03:00 | 2030 33% ECP | -700 | -526 | -510 | -162.76 | 0 | 0 | No
2030-02-14 04:00 | 2030 33% ECP | -700 | -526 | -510 | -122.62 | 0 | 0 | No
2030-02-14 05:00 | 2030 33% ECP | -700 | -526 | -510 | -362.78 | 0 | 0 | No
2030-02-14 06:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-14 07:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-14 08:00 | 2030 33% ECP | -700 | -526 | -510 | -405.12 | 0 | 0 | No
2030-02-14 09:00 | 2030 33% ECP | -700 | -226 | -210 | -105.12 | 0 | 0 | No
2030-02-14 10:00 | 2030 33% ECP | -700 | 74 | 90 | 194.88 | 0 | 0 | Yes
2030-02-14 11:00 | 2030 33% ECP | -700 | 374 | 390 | 494.88 | 0 | 0 | Yes
2030-02-14 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 16:00 | 2030 33% ECP | -700 | 363.53 | 510 | 510 | 0 | 0 | No
2030-02-14 17:00 | 2030 33% ECP | -700 | 63.53 | 210 | 210 | 0 | 0 | No
2030-02-14 18:00 | 2030 33% ECP | -700 | 0 | 510 | 406.79 | 0 | 0 | No
2030-02-14 19:00 | 2030 33% ECP | -280 | 0 | 255.54 | 480.67 | 0 | 0 | No
2030-02-14 20:00 | 2030 33% ECP | 140 | 0 | 255.54 | 480.67 | 0 | 0 | No
2030-02-14 21:00 | 2030 33% ECP | 0 | 0 | 199.65 | 481.33 | 0 | 0 | No
2030-02-14 22:00 | 2030 33% ECP | -420 | 205 | 402.25 | 307.81 | 0 | 0 | No
2030-02-14 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-15 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-15 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 12:00 | 2030 33% ECP | -700 | 505 | 382.89 | 510 | 0 | 0 | Yes
2030-02-15 13:00 | 2030 33% ECP | -700 | 205 | 82.89 | 247.25 | 0 | 0 | Yes
2030-02-15 14:00 | 2030 33% ECP | -700 | -95 | -217.11 | -52.75 | 0 | 0 | No
2030-02-15 15:00 | 2030 33% ECP | -700 | 46.18 | -210 | 175.5 | 0 | 0 | No
2030-02-15 16:00 | 2030 33% ECP | -285.95 | -253.82 | -510 | -124.5 | 0 | 0 | No
2030-02-15 17:00 | 2030 33% ECP | -647.9 | -526 | -510 | 175.5 | 0 | 0 | No
2030-02-15 18:00 | 2030 33% ECP | -518.81 | -526 | -510 | 145.46 | 0 | 0 | No
2030-02-15 19:00 | 2030 33% ECP | -98.81 | -526 | -510 | 445.46 | 0 | 0 | No
2030-02-15 20:00 | 2030 33% ECP | 140 | -233.33 | -510 | 221.2 | 0 | 0 | No
2030-02-15 21:00 | 2030 33% ECP | -280 | 66.67 | -210 | 510 | 0 | 0 | No
2030-02-15 22:00 | 2030 33% ECP | -700 | 366.67 | 90 | 510 | 0 | 0 | Yes
2030-02-15 23:00 | 2030 33% ECP | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-02-16 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 01:00 | 2030 33% ECP | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-02-16 02:00 | 2030 33% ECP | -700 | 505 | 510 | 458.83 | 0 | 0 | Yes
2030-02-16 03:00 | 2030 33% ECP | -700 | 505 | 510 | 342.29 | 0 | 0 | Yes
2030-02-16 04:00 | 2030 33% ECP | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-02-16 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 11:00 | 2030 33% ECP | -700 | 505 | 510 | 489.43 | 0 | 0 | Yes
2030-02-16 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 15:00 | 2030 33% ECP | -700 | 505 | 429.98 | 390 | 0 | 0 | Yes
2030-02-16 16:00 | 2030 33% ECP | -700 | 205 | 129.98 | 90 | 0 | 0 | Yes
2030-02-16 17:00 | 2030 33% ECP | -700 | -95 | -170.02 | -210 | 0 | 0 | Yes
2030-02-16 18:00 | 2030 33% ECP | -700 | -395 | -470.02 | -510 | 0 | 0 | No
2030-02-16 19:00 | 2030 33% ECP | -700 | -95 | -170.02 | -210 | 0 | 0 | No
2030-02-16 20:00 | 2030 33% ECP | -700 | 205 | 129.98 | 90 | 0 | 0 | Yes
2030-02-16 21:00 | 2030 33% ECP | -700 | 505 | 429.98 | 390 | 0 | 0 | Yes
2030-02-16 22:00 | 2030 33% ECP | -700 | 505 | 510 | 323.13 | 0 | 0 | Yes
2030-02-16 23:00 | 2030 33% ECP | -700 | 505 | 510 | 236.92 | 0 | 0 | Yes
2030-02-17 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 01:00 | 2030 33% ECP | -700 | 505 | 510 | 284.96 | 0 | 0 | Yes
2030-02-17 02:00 | 2030 33% ECP | -700 | 505 | 510 | 358.87 | 0 | 0 | Yes
2030-02-17 03:00 | 2030 33% ECP | -700 | 505 | 510 | 106.87 | 0 | 0 | Yes
2030-02-17 04:00 | 2030 33% ECP | -700 | 505 | 510 | 254.24 | 0 | 0 | Yes
2030-02-17 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 12:00 | 2030 33% ECP | -700 | 505 | 510 | 500.47 | 0 | 0 | Yes
2030-02-17 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-17 20:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-17 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-17 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-17 23:00 | 2030 33% ECP | -700 | 505 | 510 | 359.96 | 0 | 0 | Yes
2030-02-18 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 18:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 19:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 20:00 | 2030 33% ECP | 420 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 22:00 | 2030 33% ECP | 675.81 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 23:00 | 2030 33% ECP | 255.81 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 | 2030 33% ECP | 675.81 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 04:00 | 2030 33% ECP | 622.41 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 05:00 | 2030 33% ECP | 202.41 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 06:00 | 2030 33% ECP | -217.59 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 07:00 | 2030 33% ECP | -637.59 | 205 | 210 | 510 | 0 | 0 | No
2030-02-19 08:00 | 2030 33% ECP | -700 | -95 | -90 | 366.44 | 0 | 0 | No
2030-02-19 09:00 | 2030 33% ECP | -700 | -300 | -300 | 428.75 | 0 | 0 | No
2030-02-19 10:00 | 2030 33% ECP | -700 | 0 | 0 | 441.78 | 0 | 0 | No
2030-02-19 11:00 | 2030 33% ECP | -549.07 | 300 | 300 | 510 | 0 | 0 | No
2030-02-19 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 15:00 | 2030 33% ECP | -287.82 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 16:00 | 2030 33% ECP | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-02-19 17:00 | 2030 33% ECP | -700 | -95 | -90 | 210 | 0 | 0 | No
2030-02-19 18:00 | 2030 33% ECP | -700 | -395 | -390 | 97.6 | 0 | 0 | No
2030-02-19 19:00 | 2030 33% ECP | -366.11 | -95 | -90 | 397.6 | 0 | 0 | No
2030-02-19 20:00 | 2030 33% ECP | 53.89 | 205 | 210 | 510 | 0 | 0 | No
2030-02-19 21:00 | 2030 33% ECP | 473.89 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 22:00 | 2030 33% ECP | 64.37 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 23:00 | 2030 33% ECP | -25.45 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 | 2030 33% ECP | -445.45 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 01:00 | 2030 33% ECP | -533.45 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 02:00 | 2030 33% ECP | -113.45 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 03:00 | 2030 33% ECP | 58.69 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 04:00 | 2030 33% ECP | -361.31 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 08:00 | 2030 33% ECP | -700 | 205 | 510 | 298.04 | 0 | 0 | No
2030-02-20 09:00 | 2030 33% ECP | -280 | 443.96 | 510 | 510 | 0 | 0 | No
2030-02-20 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 16:00 | 2030 33% ECP | -700 | 300 | 255.41 | 510 | 0 | 0 | Yes
2030-02-20 17:00 | 2030 33% ECP | -700 | 0 | -44.59 | 345.49 | 0 | 0 | No
2030-02-20 18:00 | 2030 33% ECP | -700 | -300 | -344.59 | 45.49 | 0 | 0 | No
2030-02-20 19:00 | 2030 33% ECP | -700 | -95 | -90 | 37.5 | 0 | 0 | No
2030-02-20 20:00 | 2030 33% ECP | -700 | 205 | 210 | 337.5 | 0 | 0 | No
2030-02-20 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 15:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-21 16:00 | 2030 33% ECP | -700 | 74 | 90 | 245.41 | 0 | 0 | Yes
2030-02-21 17:00 | 2030 33% ECP | -700 | -226 | -210 | -54.59 | 0 | 0 | No
2030-02-21 18:00 | 2030 33% ECP | -700 | -526 | -510 | -354.59 | 0 | 0 | No
2030-02-21 19:00 | 2030 33% ECP | -700 | -526 | -510 | -453.5 | 0 | 0 | No
2030-02-21 20:00 | 2030 33% ECP | -700 | -226 | -210 | -153.5 | 0 | 0 | No
2030-02-21 21:00 | 2030 33% ECP | -700 | 74 | 90 | 146.5 | 0 | 0 | No
2030-02-21 22:00 | 2030 33% ECP | -700 | 374 | 390 | 446.5 | 0 | 0 | Yes
2030-02-21 23:00 | 2030 33% ECP | -700 | 505 | 510 | 370.59 | 0 | 0 | Yes
2030-02-22 | 2030 33% ECP | -700 | 505 | 510 | 493.54 | 0 | 0 | Yes
2030-02-22 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 02:00 | 2030 33% ECP | -700 | 505 | 510 | 314.35 | 0 | 0 | Yes
2030-02-22 03:00 | 2030 33% ECP | -700 | 505 | 510 | 501.65 | 0 | 0 | Yes
2030-02-22 04:00 | 2030 33% ECP | -700 | 505 | 510 | 394.56 | 0 | 0 | Yes
2030-02-22 05:00 | 2030 33% ECP | -700 | 505 | 510 | 135.49 | 0 | 0 | Yes
2030-02-22 06:00 | 2030 33% ECP | -700 | 505 | 510 | 114.61 | 0 | 0 | Yes
2030-02-22 07:00 | 2030 33% ECP | -700 | 505 | 510 | 333.1 | 0 | 0 | Yes
2030-02-22 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 16:00 | 2030 33% ECP | -700 | 505 | 210 | 458.31 | 0 | 0 | Yes
2030-02-22 17:00 | 2030 33% ECP | -700 | 300 | -90 | 158.31 | 0 | 0 | No
2030-02-22 18:00 | 2030 33% ECP | -350.71 | 0 | -390 | -141.69 | 0 | 0 | No
2030-02-22 19:00 | 2030 33% ECP | 0 | -95 | -90 | 112.44 | 0 | 0 | No
2030-02-22 20:00 | 2030 33% ECP | 0 | 205 | 210 | 412.44 | 0 | 0 | No
2030-02-22 21:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-02-22 22:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-22 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 05:00 | 2030 33% ECP | 351.18 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 06:00 | 2030 33% ECP | -68.82 | 205 | 210 | 412.12 | 0 | 0 | No
2030-02-23 07:00 | 2030 33% ECP | -488.82 | -95 | -90 | 334.7 | 0 | 0 | No
2030-02-23 08:00 | 2030 33% ECP | -444.52 | -395 | -390 | 34.7 | 0 | 0 | No
2030-02-23 09:00 | 2030 33% ECP | -24.52 | -95 | -90 | -107.95 | 0 | 0 | No
2030-02-23 10:00 | 2030 33% ECP | 395.48 | 205 | 210 | 192.05 | 0 | 0 | No
2030-02-23 11:00 | 2030 33% ECP | 0 | 505 | 510 | 117.75 | 0 | 0 | Yes
2030-02-23 12:00 | 2030 33% ECP | -420 | 505 | 510 | 417.75 | 0 | 0 | Yes
2030-02-23 13:00 | 2030 33% ECP | -114.65 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 14:00 | 2030 33% ECP | 14.09 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-23 15:00 | 2030 33% ECP | 434.09 | 505 | 510 | 359.33 | 0 | 0 | No
2030-02-23 16:00 | 2030 33% ECP | 700 | 205 | 210 | 59.33 | 0 | 0 | No
2030-02-23 17:00 | 2030 33% ECP | 700 | 0 | 510 | 359.33 | 0 | 0 | No
2030-02-23 18:00 | 2030 33% ECP | 642 | 0 | 510 | 510 | 0 | 0 | No
2030-02-23 19:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-02-23 20:00 | 2030 33% ECP | 621.03 | 48.77 | 510 | 510 | 0 | 0 | No
2030-02-23 21:00 | 2030 33% ECP | 201.03 | 0 | 210 | 510 | 0 | 0 | No
2030-02-23 22:00 | 2030 33% ECP | -218.97 | -95.2 | -90 | 510 | 0 | 0 | No
2030-02-23 23:00 | 2030 33% ECP | -324.81 | -395.2 | -390 | 510 | 0 | 0 | No
2030-02-24 | 2030 33% ECP | -533.27 | -526 | -510 | 498.57 | 0 | 0 | No
2030-02-24 01:00 | 2030 33% ECP | -700 | -526 | -510 | 198.57 | 0 | 0 | No
2030-02-24 02:00 | 2030 33% ECP | -700 | -526 | -510 | -101.43 | 0 | 0 | No
2030-02-24 03:00 | 2030 33% ECP | -700 | -526 | -510 | -401.43 | 0 | 0 | No
2030-02-24 04:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-24 05:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-24 06:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-02-24 07:00 | 2030 33% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-02-24 08:00 | 2030 33% ECP | -700 | 300 | 98.77 | 390 | 0 | 0 | Yes
2030-02-24 09:00 | 2030 33% ECP | -700 | 0 | -201.23 | 399.08 | 0 | 0 | Yes
2030-02-24 10:00 | 2030 33% ECP | -700 | -300 | -501.23 | 510 | 0 | 0 | No
2030-02-24 11:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-02-24 12:00 | 2030 33% ECP | -700 | -526 | -510 | 440.33 | 0 | 0 | No
2030-02-24 13:00 | 2030 33% ECP | -700 | -526 | -510 | 489.02 | 0 | 0 | No
2030-02-24 14:00 | 2030 33% ECP | -700 | -526 | -510 | 189.02 | 0 | 0 | No
2030-02-24 15:00 | 2030 33% ECP | -700 | -526 | -510 | -110.98 | 0 | 0 | No
2030-02-24 16:00 | 2030 33% ECP | -700 | -228.76 | -510 | -410.98 | 0 | 0 | No
2030-02-24 17:00 | 2030 33% ECP | -627.2 | -179.95 | -510 | -510 | 0 | 0 | No
2030-02-24 18:00 | 2030 33% ECP | -207.2 | -300 | -510 | -210 | 0 | 0 | No
2030-02-24 19:00 | 2030 33% ECP | 212.8 | 0 | -210 | 4.2 | 0 | 0 | No
2030-02-24 20:00 | 2030 33% ECP | 632.8 | 0 | 0 | 4.2 | 0 | 0 | No
2030-02-24 21:00 | 2030 33% ECP | 212.8 | 205 | 210 | 210 | 0 | 0 | No
2030-02-24 22:00 | 2030 33% ECP | 349.41 | 505 | 510 | 510 | 0 | 0 | No
2030-02-24 23:00 | 2030 33% ECP | 225.48 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 | 2030 33% ECP | 645.48 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 04:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 05:00 | 2030 33% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 06:00 | 2030 33% ECP | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 07:00 | 2030 33% ECP | -420 | 222.05 | 210 | 510 | 0 | 0 | No
2030-02-25 08:00 | 2030 33% ECP | 0 | -34.66 | -90 | 246.81 | 0 | 0 | No
2030-02-25 09:00 | 2030 33% ECP | 140 | -52.16 | -390 | 510 | 0 | 0 | No
2030-02-25 10:00 | 2030 33% ECP | -280 | -261.89 | -510 | 246.46 | 0 | 0 | No
2030-02-25 11:00 | 2030 33% ECP | -700 | -526 | -510 | 369.86 | 0 | 0 | No
2030-02-25 12:00 | 2030 33% ECP | -700 | -526 | -510 | 358.45 | 0 | 0 | No
2030-02-25 13:00 | 2030 33% ECP | -700 | -526 | -510 | 207.75 | 0 | 0 | No
2030-02-25 14:00 | 2030 33% ECP | -316.34 | -526 | -510 | 23.92 | 0 | 0 | No
2030-02-25 15:00 | 2030 33% ECP | 103.66 | -526 | -510 | 323.92 | 0 | 0 | No
2030-02-25 16:00 | 2030 33% ECP | -316.34 | -526 | -510 | 469.39 | 0 | 0 | No
2030-02-25 17:00 | 2030 33% ECP | 103.66 | -300 | -510 | 169.39 | 0 | 0 | No
2030-02-25 18:00 | 2030 33% ECP | 523.66 | 0 | -510 | 405.31 | 0 | 0 | No
2030-02-25 19:00 | 2030 33% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-02-25 20:00 | 2030 33% ECP | 700 | -128.22 | -510 | 510 | 0 | 0 | No
2030-02-25 21:00 | 2030 33% ECP | 420 | -428.22 | -510 | 510 | 0 | 0 | No
2030-02-25 22:00 | 2030 33% ECP | 0 | -489.06 | -510 | 510 | 0 | 0 | No
2030-02-25 23:00 | 2030 33% ECP | 94.31 | -189.06 | -210 | 433.52 | 0 | 0 | No
2030-02-26 | 2030 33% ECP | 514.31 | 110.94 | 90 | 510 | 0 | 0 | No
2030-02-26 01:00 | 2030 33% ECP | 700 | 410.94 | 390 | 510 | 0 | 0 | No
2030-02-26 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-26 03:00 | 2030 33% ECP | 295.42 | 505 | 445.19 | 510 | 0 | 0 | No
2030-02-26 04:00 | 2030 33% ECP | -124.58 | 238.5 | 145.19 | 230.67 | 0 | 0 | No
2030-02-26 05:00 | 2030 33% ECP | -544.58 | -61.5 | -154.81 | -69.33 | 0 | 0 | No
2030-02-26 06:00 | 2030 33% ECP | -700 | -319.54 | -454.81 | -369.33 | 0 | 0 | No
2030-02-26 07:00 | 2030 33% ECP | -700 | -19.54 | -210 | -71.6 | 0 | 0 | No
2030-02-26 08:00 | 2030 33% ECP | -461.1 | 280.46 | 90 | 228.4 | 0 | 0 | No
2030-02-26 09:00 | 2030 33% ECP | -41.1 | -19.54 | -210 | 224.62 | 0 | 0 | No
2030-02-26 10:00 | 2030 33% ECP | -352.18 | -319.54 | -510 | 61.6 | 0 | 0 | No
2030-02-26 11:00 | 2030 33% ECP | -700 | -526 | -510 | 13.35 | 0 | 0 | No
2030-02-26 12:00 | 2030 33% ECP | -559.6 | -526 | -510 | -173.58 | 0 | 0 | No
2030-02-26 13:00 | 2030 33% ECP | -700 | -526 | -510 | -207.04 | 0 | 0 | No
2030-02-26 14:00 | 2030 33% ECP | -289.6 | -395 | -390 | -182.13 | 0 | 0 | No
2030-02-26 15:00 | 2030 33% ECP | 8.96 | -95 | -90 | -90 | 0 | 0 | No
2030-02-26 16:00 | 2030 33% ECP | 58.93 | 205 | 210 | 210 | 0 | 0 | No
2030-02-26 17:00 | 2030 33% ECP | -217.36 | 505 | 510 | 510 | 0 | 0 | No
2030-02-26 18:00 | 2030 33% ECP | 34.23 | 205 | 210 | 210 | 0 | 0 | No
2030-02-26 19:00 | 2030 33% ECP | 57.04 | 0 | -90 | -90 | 0 | 0 | No
2030-02-26 20:00 | 2030 33% ECP | 57.04 | 205 | 210 | 210 | 0 | 0 | No
2030-02-26 21:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-26 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-26 23:00 | 2030 33% ECP | 700 | 462.83 | 510 | 510 | 0 | 0 | No
2030-02-27 | 2030 33% ECP | 700 | 460.87 | 510 | 495.16 | 0 | 0 | No
2030-02-27 01:00 | 2030 33% ECP | 700 | 160.87 | 510 | 405.18 | 0 | 0 | No
2030-02-27 02:00 | 2030 33% ECP | 700 | 0 | 341.46 | 105.18 | 0 | 0 | No
2030-02-27 03:00 | 2030 33% ECP | 700 | 0 | 247.11 | 0 | 0 | 0 | No
2030-02-27 04:00 | 2030 33% ECP | 700 | -18.94 | -52.89 | -300 | 0 | 0 | No
2030-02-27 05:00 | 2030 33% ECP | 420 | 0 | -348.88 | -133.62 | 0 | 0 | No
2030-02-27 06:00 | 2030 33% ECP | 0 | 0 | -48.88 | 0 | 0 | 0 | No
2030-02-27 07:00 | 2030 33% ECP | 283.1 | 0 | 0 | 164.7 | 0 | 0 | No
2030-02-27 08:00 | 2030 33% ECP | 560 | 74 | 90 | 464.7 | 0 | 0 | No
2030-02-27 09:00 | 2030 33% ECP | 140 | -226 | -210 | 175.87 | 0 | 0 | No
2030-02-27 10:00 | 2030 33% ECP | -280 | -526 | -510 | -69.88 | 0 | 0 | No
2030-02-27 11:00 | 2030 33% ECP | -700 | -479.93 | -390 | -38.04 | 0 | 0 | No
2030-02-27 12:00 | 2030 33% ECP | -700 | -179.93 | -90 | -90 | 0 | 0 | No
2030-02-27 13:00 | 2030 33% ECP | -700 | 120.07 | 210 | 210 | 0 | 0 | No
2030-02-27 14:00 | 2030 33% ECP | -700 | 420.07 | 510 | 510 | 0 | 0 | No
2030-02-27 15:00 | 2030 33% ECP | -700 | 120.07 | 210 | 210 | 0 | 0 | No
2030-02-27 16:00 | 2030 33% ECP | -280 | 41.03 | 371.8 | 158.47 | 0 | 0 | No
2030-02-27 17:00 | 2030 33% ECP | 140 | 341.03 | 510 | 458.47 | 0 | 0 | No
2030-02-27 18:00 | 2030 33% ECP | -280 | 41.03 | 210 | 158.47 | 0 | 0 | No
2030-02-27 19:00 | 2030 33% ECP | -700 | 0 | -90 | -21.54 | 0 | 0 | No
2030-02-27 20:00 | 2030 33% ECP | -280 | 300 | 210 | 278.46 | 0 | 0 | No
2030-02-27 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-27 22:00 | 2030 33% ECP | -280 | 300 | 300 | 479.73 | 0 | 0 | No
2030-02-27 23:00 | 2030 33% ECP | -70.53 | 0 | 0 | 179.73 | 0 | 0 | No
2030-02-28 | 2030 33% ECP | 0 | -211.34 | -300 | -72.59 | 0 | 0 | No
2030-02-28 01:00 | 2030 33% ECP | 0 | -137.21 | -347.28 | 227.41 | 0 | 0 | No
2030-02-28 02:00 | 2030 33% ECP | -420 | -437.21 | -510 | 181.09 | 0 | 0 | No
2030-02-28 03:00 | 2030 33% ECP | -280 | -256 | -510 | 111.94 | 0 | 0 | No
2030-02-28 04:00 | 2030 33% ECP | -700 | -149.91 | -510 | 155.82 | 0 | 0 | No
2030-02-28 05:00 | 2030 33% ECP | -700 | -447.24 | -510 | 71.53 | 0 | 0 | No
2030-02-28 06:00 | 2030 33% ECP | -700 | -526 | -510 | -228.47 | 0 | 0 | No
2030-02-28 07:00 | 2030 33% ECP | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-02-28 08:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-28 09:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-28 10:00 | 2030 33% ECP | -394.16 | -526 | -510 | -390 | 0 | 0 | No
2030-02-28 11:00 | 2030 33% ECP | -560 | -300 | -385.82 | -90 | 0 | 0 | No
2030-02-28 12:00 | 2030 33% ECP | -140 | 0 | -85.82 | 210 | 0 | 0 | No
2030-02-28 13:00 | 2030 33% ECP | 280 | 216.92 | 214.18 | 510 | 0 | 0 | No
2030-02-28 14:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-28 15:00 | 2030 33% ECP | 700 | 300 | 313.18 | 510 | 0 | 0 | No
2030-02-28 16:00 | 2030 33% ECP | 280 | 0 | 13.18 | 210 | 0 | 0 | No
2030-02-28 17:00 | 2030 33% ECP | -140 | -300 | -286.82 | 89.59 | 0 | 0 | No
2030-02-28 18:00 | 2030 33% ECP | -11.33 | -526 | -510 | 298.67 | 0 | 0 | No
2030-02-28 19:00 | 2030 33% ECP | -280 | -526 | -510 | 325.64 | 0 | 0 | No
2030-02-28 20:00 | 2030 33% ECP | 140 | -526 | -510 | 434.89 | 0 | 0 | No
2030-02-28 21:00 | 2030 33% ECP | 560 | -300 | -510 | 134.89 | 0 | 0 | No
2030-02-28 22:00 | 2030 33% ECP | 140 | 0 | -210 | 114.09 | 0 | 0 | No
2030-02-28 23:00 | 2030 33% ECP | -280 | 300 | 90 | 414.09 | 0 | 0 | No
2030-03-01 | 2030 33% ECP | -700 | 505 | 390 | 448.95 | 0 | 0 | Yes
2030-03-01 01:00 | 2030 33% ECP | -700 | 505 | 510 | 304.21 | 0 | 0 | Yes
2030-03-01 02:00 | 2030 33% ECP | -700 | 505 | 510 | 58.87 | 0 | 0 | Yes
2030-03-01 03:00 | 2030 33% ECP | -700 | 505 | 510 | 34.41 | 0 | 0 | Yes
2030-03-01 04:00 | 2030 33% ECP | -700 | 505 | 510 | 282.24 | 0 | 0 | Yes
2030-03-01 05:00 | 2030 33% ECP | -700 | 505 | 510 | 185.25 | 0 | 0 | Yes
2030-03-01 06:00 | 2030 33% ECP | -700 | 505 | 510 | 68.27 | 0 | 0 | Yes
2030-03-01 07:00 | 2030 33% ECP | -700 | 505 | 510 | 368.27 | 0 | 0 | Yes
2030-03-01 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 16:00 | 2030 33% ECP | -685.31 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 17:00 | 2030 33% ECP | -265.31 | 505 | 510 | 510 | 0 | 0 | No
2030-03-01 18:00 | 2030 33% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-03-01 19:00 | 2030 33% ECP | 280 | 429.55 | 510 | 510 | 0 | 0 | No
2030-03-01 20:00 | 2030 33% ECP | 700 | 129.55 | 510 | 510 | 0 | 0 | No
2030-03-01 21:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-01 22:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-01 23:00 | 2030 33% ECP | 700 | 205 | 433.66 | 510 | 0 | 0 | No
2030-03-02 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-02 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-02 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-02 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-02 04:00 | 2030 33% ECP | 280 | 205 | 210 | 232.29 | 0 | 0 | No
2030-03-02 05:00 | 2030 33% ECP | 0 | -95 | -90 | 227.75 | 0 | 0 | No
2030-03-02 06:00 | 2030 33% ECP | -420 | -100.32 | -390 | -34.98 | 0 | 0 | No
2030-03-02 07:00 | 2030 33% ECP | -700 | -378.75 | -510 | -190.28 | 0 | 0 | No
2030-03-02 08:00 | 2030 33% ECP | -700 | -526 | -510 | -37.23 | 0 | 0 | No
2030-03-02 09:00 | 2030 33% ECP | -696.61 | -526 | -510 | 262.77 | 0 | 0 | No
2030-03-02 10:00 | 2030 33% ECP | -700 | -526 | -510 | 84.95 | 0 | 0 | No
2030-03-02 11:00 | 2030 33% ECP | -700 | -526 | -510 | -215.05 | 0 | 0 | No
2030-03-02 12:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-02 13:00 | 2030 33% ECP | -700 | -526 | -510 | -226.11 | 0 | 0 | No
2030-03-02 14:00 | 2030 33% ECP | -700 | -526 | -510 | -39.52 | 0 | 0 | No
2030-03-02 15:00 | 2030 33% ECP | -700 | -526 | -510 | -214.77 | 0 | 0 | No
2030-03-02 16:00 | 2030 33% ECP | -700 | -526 | -510 | -40.02 | 0 | 0 | No
2030-03-02 17:00 | 2030 33% ECP | -280 | -526 | -510 | 194.25 | 0 | 0 | No
2030-03-02 18:00 | 2030 33% ECP | -700 | -526 | -510 | -20.39 | 0 | 0 | No
2030-03-02 19:00 | 2030 33% ECP | -280 | -526 | -510 | 279.61 | 0 | 0 | No
2030-03-02 20:00 | 2030 33% ECP | 140 | -354.98 | -510 | 343.92 | 0 | 0 | No
2030-03-02 21:00 | 2030 33% ECP | 560 | -368.93 | -510 | 439.46 | 0 | 0 | No
2030-03-02 22:00 | 2030 33% ECP | 542.61 | -526 | -510 | 405.95 | 0 | 0 | No
2030-03-02 23:00 | 2030 33% ECP | 122.61 | -398.85 | -510 | 217.81 | 0 | 0 | No
2030-03-03 | 2030 33% ECP | -297.39 | -98.85 | -300 | 114.98 | 0 | 0 | No
2030-03-03 01:00 | 2030 33% ECP | 103.12 | 0 | 0 | 414.98 | 0 | 0 | No
2030-03-03 02:00 | 2030 33% ECP | 127.72 | 1.32 | 157.91 | 510 | 0 | 0 | No
2030-03-03 03:00 | 2030 33% ECP | -292.28 | 0 | -142.09 | 210 | 0 | 0 | No
2030-03-03 04:00 | 2030 33% ECP | 0 | 0 | -442.09 | -17.45 | 0 | 0 | No
2030-03-03 05:00 | 2030 33% ECP | -267.2 | -300 | -510 | -317.45 | 0 | 0 | No
2030-03-03 06:00 | 2030 33% ECP | -294.99 | -526 | -510 | -298.21 | 0 | 0 | No
2030-03-03 07:00 | 2030 33% ECP | -265.43 | -226 | -469.25 | -108.92 | 0 | 0 | No
2030-03-03 08:00 | 2030 33% ECP | -105.88 | -226 | -510 | -408.92 | 0 | 0 | No
2030-03-03 09:00 | 2030 33% ECP | -479.71 | -526 | -510 | -108.92 | 0 | 0 | No
2030-03-03 10:00 | 2030 33% ECP | -700 | -526 | -510 | -408.92 | 0 | 0 | No
2030-03-03 11:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-03 12:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-03 13:00 | 2030 33% ECP | -700 | -526 | -510 | -405.59 | 0 | 0 | No
2030-03-03 14:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-03 15:00 | 2030 33% ECP | -280 | -335.2 | -510 | -334.56 | 0 | 0 | No
2030-03-03 16:00 | 2030 33% ECP | 140 | -35.2 | -281.36 | -60.42 | 0 | 0 | No
2030-03-03 17:00 | 2030 33% ECP | 560 | 257.17 | 0 | 0 | 0 | 0 | No
2030-03-03 18:00 | 2030 33% ECP | 140 | -42.83 | -300 | -300 | 0 | 0 | No
2030-03-03 19:00 | 2030 33% ECP | 280 | -12.87 | -90 | -90 | 0 | 0 | No
2030-03-03 20:00 | 2030 33% ECP | 700 | 287.13 | 210 | 210 | 0 | 0 | No
2030-03-03 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-03 22:00 | 2030 33% ECP | 700 | 307.66 | 510 | 510 | 0 | 0 | No
2030-03-03 23:00 | 2030 33% ECP | 700 | 7.66 | 510 | 350.93 | 0 | 0 | No
2030-03-04 | 2030 33% ECP | 700 | 263.54 | 510 | 510 | 0 | 0 | No
2030-03-04 01:00 | 2030 33% ECP | 700 | 418.47 | 510 | 510 | 0 | 0 | No
2030-03-04 02:00 | 2030 33% ECP | 700 | 418.47 | 510 | 510 | 0 | 0 | No
2030-03-04 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-04 04:00 | 2030 33% ECP | 700 | 445.02 | 510 | 510 | 0 | 0 | No
2030-03-04 05:00 | 2030 33% ECP | 700 | 445.02 | 510 | 510 | 0 | 0 | No
2030-03-04 06:00 | 2030 33% ECP | 700 | 445.02 | 510 | 510 | 0 | 0 | No
2030-03-04 07:00 | 2030 33% ECP | 700 | 445.02 | 510 | 510 | 0 | 0 | No
2030-03-04 08:00 | 2030 33% ECP | 700 | 274.93 | 510 | 510 | 0 | 0 | No
2030-03-04 09:00 | 2030 33% ECP | 700 | 0 | 390 | 259.74 | 0 | 0 | No
2030-03-04 10:00 | 2030 33% ECP | 700 | 0 | 90 | 218.48 | 0 | 0 | No
2030-03-04 11:00 | 2030 33% ECP | 700 | -212.32 | -210 | -81.52 | 0 | 0 | No
2030-03-04 12:00 | 2030 33% ECP | 700 | -512.32 | -510 | -334.35 | 0 | 0 | No
2030-03-04 13:00 | 2030 33% ECP | 700 | -431.24 | -510 | -303 | 0 | 0 | No
2030-03-04 14:00 | 2030 33% ECP | 700 | -279.51 | -510 | -308.94 | 0 | 0 | No
2030-03-04 15:00 | 2030 33% ECP | 700 | 0 | -300 | -274 | 0 | 0 | No
2030-03-04 16:00 | 2030 33% ECP | 700 | 13.81 | 0 | 0 | 0 | 0 | No
2030-03-04 17:00 | 2030 33% ECP | 700 | -286.19 | -300 | -300 | 0 | 0 | No
2030-03-04 18:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-04 19:00 | 2030 33% ECP | 700 | -300 | -480.18 | -510 | 0 | 0 | No
2030-03-04 20:00 | 2030 33% ECP | 700 | 0 | -180.18 | -210 | 0 | 0 | No
2030-03-04 21:00 | 2030 33% ECP | 700 | 300 | 119.82 | 90 | 0 | 0 | No
2030-03-04 22:00 | 2030 33% ECP | 700 | 488.22 | 419.82 | 0 | 0 | 0 | No
2030-03-04 23:00 | 2030 33% ECP | 700 | 294.07 | 510 | 0 | 0 | 0 | No
2030-03-05 | 2030 33% ECP | 700 | 505 | 510 | 0 | 0 | 0 | No
2030-03-05 01:00 | 2030 33% ECP | 700 | 205 | 306.93 | 14.28 | 0 | 0 | No
2030-03-05 02:00 | 2030 33% ECP | 700 | 505 | 510 | 314.28 | 0 | 0 | No
2030-03-05 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-05 04:00 | 2030 33% ECP | 700 | 505 | 510 | 348.74 | 0 | 0 | No
2030-03-05 05:00 | 2030 33% ECP | 280 | 299.3 | 350.93 | 48.74 | 0 | 0 | No
2030-03-05 06:00 | 2030 33% ECP | 700 | 0 | 50.93 | -49.71 | 0 | 0 | No
2030-03-05 07:00 | 2030 33% ECP | 700 | 0 | 0 | -15.29 | 0 | 0 | No
2030-03-05 08:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-03-05 09:00 | 2030 33% ECP | 700 | 0 | -97.98 | 0 | 0 | 0 | No
2030-03-05 10:00 | 2030 33% ECP | 345.72 | 0 | 0 | 0 | 0 | 0 | No
2030-03-05 11:00 | 2030 33% ECP | 700 | 0 | 300 | 300 | 0 | 0 | No
2030-03-05 12:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-05 13:00 | 2030 33% ECP | 700 | 144.2 | 510 | 510 | 0 | 0 | No
2030-03-05 14:00 | 2030 33% ECP | 700 | 444.2 | 510 | 510 | 0 | 0 | No
2030-03-05 15:00 | 2030 33% ECP | 700 | 505 | 390 | 390 | 0 | 0 | No
2030-03-05 16:00 | 2030 33% ECP | 700 | 242.09 | 90 | 90 | 0 | 0 | No
2030-03-05 17:00 | 2030 33% ECP | 700 | -57.91 | -210 | -210 | 0 | 0 | No
2030-03-05 18:00 | 2030 33% ECP | 700 | -357.91 | -510 | -510 | 0 | 0 | No
2030-03-05 19:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-05 20:00 | 2030 33% ECP | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-03-05 21:00 | 2030 33% ECP | 700 | 74 | 90 | 71.1 | 0 | 0 | No
2030-03-05 22:00 | 2030 33% ECP | 700 | 0 | -210 | -120.37 | 0 | 0 | No
2030-03-05 23:00 | 2030 33% ECP | 700 | 29.4 | 90 | 179.63 | 0 | 0 | No
2030-03-06 | 2030 33% ECP | 700 | 0 | -7.38 | 52.77 | 0 | 0 | No
2030-03-06 01:00 | 2030 33% ECP | 700 | 0 | -272.72 | 60.71 | 0 | 0 | No
2030-03-06 02:00 | 2030 33% ECP | 560 | -11.14 | -510 | 60.71 | 0 | 0 | No
2030-03-06 03:00 | 2030 33% ECP | 140 | 0 | -360.86 | 0 | 0 | 0 | No
2030-03-06 04:00 | 2030 33% ECP | -280 | 0 | -341.98 | 0 | 0 | 0 | No
2030-03-06 05:00 | 2030 33% ECP | -700 | -226 | -210 | -186.31 | 0 | 0 | No
2030-03-06 06:00 | 2030 33% ECP | -700 | -526 | -510 | -486.31 | 0 | 0 | No
2030-03-06 07:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 08:00 | 2030 33% ECP | -700 | -526 | -510 | -337.71 | 0 | 0 | No
2030-03-06 09:00 | 2030 33% ECP | -700 | -526 | -510 | -502.82 | 0 | 0 | No
2030-03-06 10:00 | 2030 33% ECP | -700 | -526 | -510 | -202.82 | 0 | 0 | No
2030-03-06 11:00 | 2030 33% ECP | -700 | -526 | -510 | -202.4 | 0 | 0 | No
2030-03-06 12:00 | 2030 33% ECP | -700 | -526 | -510 | -228.72 | 0 | 0 | No
2030-03-06 13:00 | 2030 33% ECP | -700 | -526 | -510 | -232.09 | 0 | 0 | No
2030-03-06 14:00 | 2030 33% ECP | -700 | -526 | -510 | 67.91 | 0 | 0 | No
2030-03-06 15:00 | 2030 33% ECP | -342.78 | -526 | -510 | -74.95 | 0 | 0 | No
2030-03-06 16:00 | 2030 33% ECP | 77.22 | -526 | -510 | -374.95 | 0 | 0 | No
2030-03-06 17:00 | 2030 33% ECP | 497.22 | -226 | -210 | -150.01 | 0 | 0 | No
2030-03-06 18:00 | 2030 33% ECP | 280 | -526 | -510 | -450.01 | 0 | 0 | No
2030-03-06 19:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 20:00 | 2030 33% ECP | 700 | -300 | -510 | -510 | 0 | 0 | No
2030-03-06 21:00 | 2030 33% ECP | 700 | 0 | -210 | -210 | 0 | 0 | No
2030-03-06 22:00 | 2030 33% ECP | 700 | 0 | -508.41 | -197.12 | 0 | 0 | No
2030-03-06 23:00 | 2030 33% ECP | 700 | 0 | -208.41 | 0 | 0 | 0 | No
2030-03-07 | 2030 33% ECP | 316.64 | -300 | -508.41 | -275.21 | 0 | 0 | No
2030-03-07 01:00 | 2030 33% ECP | 154.99 | -271.21 | -510 | -266.12 | 0 | 0 | No
2030-03-07 02:00 | 2030 33% ECP | -265.01 | -526 | -510 | -166.32 | 0 | 0 | No
2030-03-07 03:00 | 2030 33% ECP | -685.01 | -526 | -510 | -25.81 | 0 | 0 | No
2030-03-07 04:00 | 2030 33% ECP | -700 | -526 | -510 | -164.87 | 0 | 0 | No
2030-03-07 05:00 | 2030 33% ECP | -700 | -526 | -510 | 135.13 | 0 | 0 | No
2030-03-07 06:00 | 2030 33% ECP | -700 | -526 | -510 | 16.6 | 0 | 0 | No
2030-03-07 07:00 | 2030 33% ECP | -700 | -526 | -510 | -12.83 | 0 | 0 | No
2030-03-07 08:00 | 2030 33% ECP | -700 | -526 | -510 | 6.39 | 0 | 0 | No
2030-03-07 09:00 | 2030 33% ECP | -700 | -526 | -510 | -9.64 | 0 | 0 | No
2030-03-07 10:00 | 2030 33% ECP | -700 | -526 | -510 | -309.64 | 0 | 0 | No
2030-03-07 11:00 | 2030 33% ECP | -700 | -226 | -210 | -9.64 | 0 | 0 | Yes
2030-03-07 12:00 | 2030 33% ECP | -700 | 74 | 90 | 290.36 | 0 | 0 | Yes
2030-03-07 13:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-07 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-07 15:00 | 2030 33% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-03-07 16:00 | 2030 33% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-03-07 17:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-03-07 18:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-07 19:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-07 20:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-07 21:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-03-07 22:00 | 2030 33% ECP | -700 | 74 | 90 | 90 | 0 | 0 | No
2030-03-07 23:00 | 2030 33% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-03-08 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-08 07:00 | 2030 33% ECP | -563.27 | 205 | 300 | 375.43 | 0 | 0 | No
2030-03-08 08:00 | 2030 33% ECP | -563.27 | 0 | 0 | 170.04 | 0 | 0 | No
2030-03-08 09:00 | 2030 33% ECP | -700 | 0 | 0 | 210 | 0 | 0 | No
2030-03-08 10:00 | 2030 33% ECP | -700 | 13.87 | 300 | 510 | 0 | 0 | Yes
2030-03-08 11:00 | 2030 33% ECP | -700 | 221.81 | 510 | 510 | 0 | 0 | Yes
2030-03-08 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-08 13:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-08 14:00 | 2030 33% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-08 15:00 | 2030 33% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-03-08 16:00 | 2030 33% ECP | -696.46 | -526 | -510 | 219.31 | 0 | 0 | No
2030-03-08 17:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-08 18:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-08 19:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-08 20:00 | 2030 33% ECP | -700 | -526 | -510 | 507.66 | 0 | 0 | No
2030-03-08 21:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-08 22:00 | 2030 33% ECP | -280 | -226 | -489.28 | 457.5 | 0 | 0 | No
2030-03-08 23:00 | 2030 33% ECP | -700 | 74 | -189.28 | 510 | 0 | 0 | No
2030-03-09 | 2030 33% ECP | -280 | 374 | 110.72 | 510 | 0 | 0 | No
2030-03-09 01:00 | 2030 33% ECP | 140 | 505 | 410.72 | 510 | 0 | 0 | No
2030-03-09 02:00 | 2030 33% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-03-09 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-09 04:00 | 2030 33% ECP | 316.37 | 505 | 510 | 510 | 0 | 0 | No
2030-03-09 05:00 | 2030 33% ECP | -103.63 | 205 | 210 | 210 | 0 | 0 | No
2030-03-09 06:00 | 2030 33% ECP | 0 | -95 | -90 | -90 | 0 | 0 | No
2030-03-09 07:00 | 2030 33% ECP | 36.72 | -395 | -390 | 41.03 | 0 | 0 | No
2030-03-09 08:00 | 2030 33% ECP | 420 | -526 | -510 | 297.42 | 0 | 0 | No
2030-03-09 09:00 | 2030 33% ECP | 0 | -526 | -510 | 297.42 | 0 | 0 | No
2030-03-09 10:00 | 2030 33% ECP | -280 | -526 | -510 | 90 | 0 | 0 | No
2030-03-09 11:00 | 2030 33% ECP | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-03-09 12:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-09 13:00 | 2030 33% ECP | -700 | -526 | -510 | -294.81 | 0 | 0 | No
2030-03-09 14:00 | 2030 33% ECP | -280 | -226 | -278.43 | 0 | 0 | 0 | No
2030-03-09 15:00 | 2030 33% ECP | 0 | 0 | 21.57 | 300 | 0 | 0 | No
2030-03-09 16:00 | 2030 33% ECP | -280 | -226 | -210 | 510 | 0 | 0 | No
2030-03-09 17:00 | 2030 33% ECP | -700 | -526 | -510 | 368.04 | 0 | 0 | No
2030-03-09 18:00 | 2030 33% ECP | -700 | -526 | -510 | 68.04 | 0 | 0 | No
2030-03-09 19:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-03-09 20:00 | 2030 33% ECP | -389.98 | -226 | -210 | 280.53 | 0 | 0 | No
2030-03-09 21:00 | 2030 33% ECP | -700 | 74 | 90 | 496.67 | 0 | 0 | Yes
2030-03-09 22:00 | 2030 33% ECP | -700 | 374 | 390 | 310.98 | 0 | 0 | Yes
2030-03-09 23:00 | 2030 33% ECP | -700 | 505 | 510 | 393.06 | 0 | 0 | Yes
2030-03-10 | 2030 33% ECP | -700 | 505 | 510 | 481.02 | 0 | 0 | Yes
2030-03-10 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 02:00 | 2030 33% ECP | -700 | 505 | 510 | 402.96 | 0 | 0 | Yes
2030-03-10 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 04:00 | 2030 33% ECP | -700 | 505 | 510 | 317.83 | 0 | 0 | Yes
2030-03-10 05:00 | 2030 33% ECP | -700 | 505 | 510 | 255.21 | 0 | 0 | Yes
2030-03-10 06:00 | 2030 33% ECP | -700 | 505 | 510 | 455.02 | 0 | 0 | Yes
2030-03-10 07:00 | 2030 33% ECP | -700 | 505 | 510 | 258.41 | 0 | 0 | Yes
2030-03-10 08:00 | 2030 33% ECP | -700 | 505 | 510 | 365.42 | 0 | 0 | Yes
2030-03-10 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 10:00 | 2030 33% ECP | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-03-10 11:00 | 2030 33% ECP | -700 | 505 | 510 | 129.43 | 0 | 0 | Yes
2030-03-10 12:00 | 2030 33% ECP | -700 | 505 | 510 | 199.79 | 0 | 0 | Yes
2030-03-10 13:00 | 2030 33% ECP | -700 | 505 | 510 | 499.79 | 0 | 0 | Yes
2030-03-10 14:00 | 2030 33% ECP | -700 | 505 | 510 | 199.79 | 0 | 0 | Yes
2030-03-10 15:00 | 2030 33% ECP | -700 | 505 | 510 | 458.16 | 0 | 0 | Yes
2030-03-10 16:00 | 2030 33% ECP | -412.23 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 17:00 | 2030 33% ECP | 7.77 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 18:00 | 2030 33% ECP | 427.77 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 19:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 20:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 22:00 | 2030 33% ECP | 401.25 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 23:00 | 2030 33% ECP | -18.75 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 | 2030 33% ECP | -438.75 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 16:00 | 2030 33% ECP | -700 | 505 | 333.21 | 510 | 0 | 0 | Yes
2030-03-11 17:00 | 2030 33% ECP | -492.61 | 300 | 33.21 | 510 | 0 | 0 | No
2030-03-11 18:00 | 2030 33% ECP | -72.61 | 0 | -266.79 | 210 | 0 | 0 | No
2030-03-11 19:00 | 2030 33% ECP | -492.61 | -282.32 | -90 | 510 | 0 | 0 | No
2030-03-11 20:00 | 2030 33% ECP | -420.72 | 17.68 | 210 | 506.66 | 0 | 0 | No
2030-03-11 21:00 | 2030 33% ECP | -700 | 317.68 | 510 | 510 | 0 | 0 | No
2030-03-11 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 15:00 | 2030 33% ECP | -700 | 505 | 390 | 390 | 0 | 0 | Yes
2030-03-12 16:00 | 2030 33% ECP | -700 | 239.19 | 90 | 90 | 0 | 0 | Yes
2030-03-12 17:00 | 2030 33% ECP | -700 | -60.81 | -210 | -210 | 0 | 0 | No
2030-03-12 18:00 | 2030 33% ECP | -700 | -360.81 | -510 | -510 | 0 | 0 | No
2030-03-12 19:00 | 2030 33% ECP | -700 | -395 | -390 | -390 | 0 | 0 | No
2030-03-12 20:00 | 2030 33% ECP | -280 | -95 | -90 | -90 | 0 | 0 | No
2030-03-12 21:00 | 2030 33% ECP | 140 | 205 | 210 | 210 | 0 | 0 | No
2030-03-12 22:00 | 2030 33% ECP | -74.55 | 505 | 510 | 510 | 0 | 0 | No
2030-03-12 23:00 | 2030 33% ECP | -224.98 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 | 2030 33% ECP | 195.02 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 01:00 | 2030 33% ECP | 615.02 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 04:00 | 2030 33% ECP | 420 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 05:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 06:00 | 2030 33% ECP | -154.4 | 205 | 210 | 210 | 0 | 0 | No
2030-03-13 07:00 | 2030 33% ECP | 0 | 0 | 510 | 295.08 | 0 | 0 | No
2030-03-13 08:00 | 2030 33% ECP | -240.05 | 0 | 300 | 466.68 | 0 | 0 | No
2030-03-13 09:00 | 2030 33% ECP | 179.95 | 0 | 0 | 510 | 0 | 0 | No
2030-03-13 10:00 | 2030 33% ECP | 0 | -226 | -210 | 290.82 | 0 | 0 | No
2030-03-13 11:00 | 2030 33% ECP | -420 | -526 | -510 | -9.18 | 0 | 0 | No
2030-03-13 12:00 | 2030 33% ECP | -700 | -526 | -510 | -305.98 | 0 | 0 | No
2030-03-13 13:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 14:00 | 2030 33% ECP | -587.98 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 15:00 | 2030 33% ECP | -167.98 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 16:00 | 2030 33% ECP | 142.34 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 17:00 | 2030 33% ECP | -277.66 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 18:00 | 2030 33% ECP | -604.74 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 19:00 | 2030 33% ECP | -184.74 | -300 | -510 | -510 | 0 | 0 | No
2030-03-13 20:00 | 2030 33% ECP | 235.26 | 0 | -210 | -210 | 0 | 0 | No
2030-03-13 21:00 | 2030 33% ECP | 655.26 | 300 | 90 | 90 | 0 | 0 | No
2030-03-13 22:00 | 2030 33% ECP | 700 | 0 | 390 | 68.43 | 0 | 0 | No
2030-03-13 23:00 | 2030 33% ECP | 700 | 0 | 140.68 | -196.75 | 0 | 0 | No
2030-03-14 | 2030 33% ECP | 700 | 0 | 20.53 | -119.53 | 0 | 0 | No
2030-03-14 01:00 | 2030 33% ECP | 306.35 | 205 | 210 | 180.47 | 0 | 0 | No
2030-03-14 02:00 | 2030 33% ECP | 700 | 505 | 510 | 480.47 | 0 | 0 | No
2030-03-14 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-14 04:00 | 2030 33% ECP | 696.77 | 505 | 510 | 510 | 0 | 0 | No
2030-03-14 05:00 | 2030 33% ECP | 276.77 | 300.24 | 510 | 510 | 0 | 0 | No
2030-03-14 06:00 | 2030 33% ECP | 329.44 | 0.24 | 210 | 210 | 0 | 0 | No
2030-03-14 07:00 | 2030 33% ECP | -90.56 | 0 | -31.98 | 12.16 | 0 | 0 | No
2030-03-14 08:00 | 2030 33% ECP | -280 | -226 | -210 | 288.91 | 0 | 0 | No
2030-03-14 09:00 | 2030 33% ECP | -700 | -526 | -510 | 491.69 | 0 | 0 | No
2030-03-14 10:00 | 2030 33% ECP | -700 | -526 | -510 | 191.69 | 0 | 0 | No
2030-03-14 11:00 | 2030 33% ECP | -700 | -234.46 | -510 | 353.82 | 0 | 0 | No
2030-03-14 12:00 | 2030 33% ECP | -700 | 65.54 | -210 | 510 | 0 | 0 | No
2030-03-14 13:00 | 2030 33% ECP | -700 | 365.54 | 90 | 510 | 0 | 0 | No
2030-03-14 14:00 | 2030 33% ECP | -700 | 505 | 390 | 510 | 0 | 0 | No
2030-03-14 15:00 | 2030 33% ECP | -700 | 228.29 | 90 | 300 | 0 | 0 | No
2030-03-14 16:00 | 2030 33% ECP | -700 | -71.71 | -210 | 0 | 0 | 0 | No
2030-03-14 17:00 | 2030 33% ECP | -700 | -371.71 | -510 | -300 | 0 | 0 | No
2030-03-14 18:00 | 2030 33% ECP | -700 | -395 | -390 | 0 | 0 | 0 | No
2030-03-14 19:00 | 2030 33% ECP | -700 | -95 | -90 | 149.27 | 0 | 0 | No
2030-03-14 20:00 | 2030 33% ECP | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-03-14 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-14 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-14 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 13:00 | 2030 33% ECP | -700 | 374 | 390 | 454.49 | 0 | 0 | Yes
2030-03-15 14:00 | 2030 33% ECP | -700 | 74 | 90 | 154.49 | 0 | 0 | Yes
2030-03-15 15:00 | 2030 33% ECP | -700 | -226 | -210 | -145.51 | 0 | 0 | Yes
2030-03-15 16:00 | 2030 33% ECP | -700 | -526 | -510 | -445.51 | 0 | 0 | No
2030-03-15 17:00 | 2030 33% ECP | -685.77 | -226 | -210 | -145.51 | 0 | 0 | No
2030-03-15 18:00 | 2030 33% ECP | -700 | 74 | 90 | 154.49 | 0 | 0 | No
2030-03-15 19:00 | 2030 33% ECP | -655.95 | 0 | 210 | 143.85 | 0 | 0 | No
2030-03-15 20:00 | 2030 33% ECP | -235.95 | 300 | 510 | 443.85 | 0 | 0 | No
2030-03-15 21:00 | 2030 33% ECP | 184.05 | 505 | 510 | 510 | 0 | 0 | No
2030-03-15 22:00 | 2030 33% ECP | 604.05 | 505 | 510 | 510 | 0 | 0 | No
2030-03-15 23:00 | 2030 33% ECP | 700 | 354.42 | 510 | 510 | 0 | 0 | No
2030-03-16 | 2030 33% ECP | 700 | 318.01 | 510 | 510 | 0 | 0 | No
2030-03-16 01:00 | 2030 33% ECP | 700 | 488.74 | 510 | 510 | 0 | 0 | No
2030-03-16 02:00 | 2030 33% ECP | 700 | 188.74 | 486.72 | 510 | 0 | 0 | No
2030-03-16 03:00 | 2030 33% ECP | 280 | 165.12 | 186.72 | 510 | 0 | 0 | No
2030-03-16 04:00 | 2030 33% ECP | -140 | 0 | -113.28 | 233.66 | 0 | 0 | No
2030-03-16 05:00 | 2030 33% ECP | -560 | -300 | -413.28 | -66.34 | 0 | 0 | No
2030-03-16 06:00 | 2030 33% ECP | -700 | -526 | -510 | -366.34 | 0 | 0 | No
2030-03-16 07:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-16 08:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-16 09:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 10:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 11:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 12:00 | 2030 33% ECP | -700 | -526 | -510 | -278.82 | 0 | 0 | Yes
2030-03-16 13:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 14:00 | 2030 33% ECP | -700 | -526 | -510 | -379.4 | 0 | 0 | Yes
2030-03-16 15:00 | 2030 33% ECP | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-03-16 16:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 17:00 | 2030 33% ECP | -700 | -526 | -510 | -426.21 | 0 | 0 | No
2030-03-16 18:00 | 2030 33% ECP | -700 | -395 | -390 | -218.23 | 0 | 0 | No
2030-03-16 19:00 | 2030 33% ECP | -700 | -95 | -90 | -46.67 | 0 | 0 | No
2030-03-16 20:00 | 2030 33% ECP | -700 | 205 | 210 | 253.33 | 0 | 0 | No
2030-03-16 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-16 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-16 23:00 | 2030 33% ECP | -693.27 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 18:00 | 2030 33% ECP | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-03-17 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 20:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 21:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 22:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 23:00 | 2030 33% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 06:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 07:00 | 2030 33% ECP | 544.95 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 08:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 09:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 10:00 | 2030 33% ECP | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-03-18 11:00 | 2030 33% ECP | 558.68 | -95 | -90 | 313.34 | 0 | 0 | No
2030-03-18 12:00 | 2030 33% ECP | 700 | -354.51 | -390 | 86.51 | 0 | 0 | No
2030-03-18 13:00 | 2030 33% ECP | 700 | -116.15 | -510 | 155.32 | 0 | 0 | No
2030-03-18 14:00 | 2030 33% ECP | 700 | 0 | -221.97 | 78.14 | 0 | 0 | No
2030-03-18 15:00 | 2030 33% ECP | 700 | 0 | -90 | -64.76 | 0 | 0 | No
2030-03-18 16:00 | 2030 33% ECP | 700 | 0 | 210 | 169.92 | 0 | 0 | No
2030-03-18 17:00 | 2030 33% ECP | 700 | 300 | 510 | 469.92 | 0 | 0 | No
2030-03-18 18:00 | 2030 33% ECP | 700 | 346.99 | 510 | 510 | 0 | 0 | No
2030-03-18 19:00 | 2030 33% ECP | 700 | 346.99 | 510 | 510 | 0 | 0 | No
2030-03-18 20:00 | 2030 33% ECP | 700 | 346.99 | 510 | 510 | 0 | 0 | No
2030-03-18 21:00 | 2030 33% ECP | 700 | 165.11 | 510 | 510 | 0 | 0 | No
2030-03-18 22:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-18 23:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-19 | 2030 33% ECP | 700 | 74.34 | 510 | 510 | 0 | 0 | No
2030-03-19 01:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-19 02:00 | 2030 33% ECP | 700 | 243.84 | 510 | 510 | 0 | 0 | No
2030-03-19 03:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-19 04:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-19 05:00 | 2030 33% ECP | 445.71 | 0 | 390 | 510 | 0 | 0 | No
2030-03-19 06:00 | 2030 33% ECP | 25.71 | 56.46 | 90 | 210 | 0 | 0 | No
2030-03-19 07:00 | 2030 33% ECP | -394.29 | -243.54 | -210 | -90 | 0 | 0 | No
2030-03-19 08:00 | 2030 33% ECP | -656.34 | -526 | -510 | -193.39 | 0 | 0 | No
2030-03-19 09:00 | 2030 33% ECP | -236.34 | -526 | -510 | -126.32 | 0 | 0 | No
2030-03-19 10:00 | 2030 33% ECP | 0 | -526 | -510 | -378.81 | 0 | 0 | No
2030-03-19 11:00 | 2030 33% ECP | -397.13 | -526 | -510 | -401.17 | 0 | 0 | No
2030-03-19 12:00 | 2030 33% ECP | 0 | -526 | -510 | -367.26 | 0 | 0 | No
2030-03-19 13:00 | 2030 33% ECP | -2.97 | -526 | -510 | -510 | 0 | 0 | No
2030-03-19 14:00 | 2030 33% ECP | 0 | -526 | -510 | -488.93 | 0 | 0 | No
2030-03-19 15:00 | 2030 33% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-03-19 16:00 | 2030 33% ECP | 243.23 | -526 | -510 | -510 | 0 | 0 | No
2030-03-19 17:00 | 2030 33% ECP | 0 | -526 | -510 | -406.42 | 0 | 0 | No
2030-03-19 18:00 | 2030 33% ECP | 0 | -382.07 | -510 | -106.42 | 0 | 0 | No
2030-03-19 19:00 | 2030 33% ECP | 280 | -526 | -510 | -132.34 | 0 | 0 | No
2030-03-19 20:00 | 2030 33% ECP | 700 | -402.73 | -510 | -74.12 | 0 | 0 | No
2030-03-19 21:00 | 2030 33% ECP | 700 | -102.73 | -300 | -13.58 | 0 | 0 | No
2030-03-19 22:00 | 2030 33% ECP | 700 | 0 | 0 | 84.85 | 0 | 0 | No
2030-03-19 23:00 | 2030 33% ECP | 700 | 0 | -158.73 | 0 | 0 | 0 | No
2030-03-20 | 2030 33% ECP | 700 | 0 | -458.73 | 0 | 0 | 0 | No
2030-03-20 01:00 | 2030 33% ECP | 700 | 0 | -510 | -134.01 | 0 | 0 | No
2030-03-20 02:00 | 2030 33% ECP | 700 | 0 | -510 | -74.84 | 0 | 0 | No
2030-03-20 03:00 | 2030 33% ECP | 700 | 0 | -510 | 6.28 | 0 | 0 | No
2030-03-20 04:00 | 2030 33% ECP | 700 | -99.82 | -510 | 11.33 | 0 | 0 | No
2030-03-20 05:00 | 2030 33% ECP | 522.02 | -136.15 | -510 | -11.81 | 0 | 0 | No
2030-03-20 06:00 | 2030 33% ECP | 102.02 | 0 | -510 | 21.59 | 0 | 0 | No
2030-03-20 07:00 | 2030 33% ECP | 140 | 0 | -400.89 | 130.38 | 0 | 0 | No
2030-03-20 08:00 | 2030 33% ECP | -280 | -226 | -402.42 | 218.95 | 0 | 0 | No
2030-03-20 09:00 | 2030 33% ECP | -700 | -526 | -510 | 145.13 | 0 | 0 | No
2030-03-20 10:00 | 2030 33% ECP | -700 | -526 | -510 | 307.93 | 0 | 0 | No
2030-03-20 11:00 | 2030 33% ECP | -280 | -526 | -510 | 189.75 | 0 | 0 | No
2030-03-20 12:00 | 2030 33% ECP | -634.21 | -526 | -510 | 235.99 | 0 | 0 | No
2030-03-20 13:00 | 2030 33% ECP | -700 | -526 | -510 | 159.31 | 0 | 0 | No
2030-03-20 14:00 | 2030 33% ECP | -280 | -526 | -510 | 164.81 | 0 | 0 | No
2030-03-20 15:00 | 2030 33% ECP | 140 | -526 | -510 | 227.27 | 0 | 0 | No
2030-03-20 16:00 | 2030 33% ECP | 560 | -526 | -510 | 278.84 | 0 | 0 | No
2030-03-20 17:00 | 2030 33% ECP | 667.04 | -526 | -510 | 335.24 | 0 | 0 | No
2030-03-20 18:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-20 19:00 | 2030 33% ECP | 700 | -296.3 | -510 | 510 | 0 | 0 | No
2030-03-20 20:00 | 2030 33% ECP | 700 | 0 | -510 | 331.26 | 0 | 0 | No
2030-03-20 21:00 | 2030 33% ECP | 700 | -300 | -510 | 229.77 | 0 | 0 | No
2030-03-20 22:00 | 2030 33% ECP | 700 | 0 | -211.38 | 134.6 | 0 | 0 | No
2030-03-20 23:00 | 2030 33% ECP | 280 | 300 | 88.62 | 434.6 | 0 | 0 | No
2030-03-21 | 2030 33% ECP | 0 | 0 | 388.62 | 321.52 | 0 | 0 | No
2030-03-21 01:00 | 2030 33% ECP | 0 | 0 | 196.96 | 21.52 | 0 | 0 | No
2030-03-21 02:00 | 2030 33% ECP | -115.1 | 205 | 496.96 | 296.51 | 0 | 0 | No
2030-03-21 03:00 | 2030 33% ECP | -355.76 | 505 | 510 | 510 | 0 | 0 | No
2030-03-21 04:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-21 05:00 | 2030 33% ECP | -280 | 300 | 210 | 230.22 | 0 | 0 | No
2030-03-21 06:00 | 2030 33% ECP | -700 | 0 | -90 | -69.78 | 0 | 0 | No
2030-03-21 07:00 | 2030 33% ECP | -700 | -300 | -390 | -369.78 | 0 | 0 | No
2030-03-21 08:00 | 2030 33% ECP | -280 | -242.15 | -300 | -510 | 0 | 0 | No
2030-03-21 09:00 | 2030 33% ECP | 0 | 57.85 | 0 | -210 | 0 | 0 | No
2030-03-21 10:00 | 2030 33% ECP | -420 | 357.85 | 300 | -40.29 | 0 | 0 | No
2030-03-21 11:00 | 2030 33% ECP | -631 | 505 | 510 | 259.71 | 0 | 0 | Yes
2030-03-21 12:00 | 2030 33% ECP | -211 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 13:00 | 2030 33% ECP | -428.26 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 14:00 | 2030 33% ECP | -8.26 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 15:00 | 2030 33% ECP | 280 | 505 | 510 | 257.59 | 0 | 0 | No
2030-03-21 16:00 | 2030 33% ECP | 700 | 205 | 210 | -42.41 | 0 | 0 | No
2030-03-21 17:00 | 2030 33% ECP | 700 | 0 | 510 | 130.09 | 0 | 0 | No
2030-03-21 18:00 | 2030 33% ECP | 700 | 0 | 510 | 323.34 | 0 | 0 | No
2030-03-21 19:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-21 20:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-21 21:00 | 2030 33% ECP | 700 | 232.01 | 510 | 510 | 0 | 0 | No
2030-03-21 22:00 | 2030 33% ECP | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-03-21 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 05:00 | 2030 33% ECP | 280 | 205 | 210 | 265.01 | 0 | 0 | No
2030-03-22 06:00 | 2030 33% ECP | 198.13 | -95 | -90 | 424.27 | 0 | 0 | No
2030-03-22 07:00 | 2030 33% ECP | 618.13 | -395 | -390 | 459.47 | 0 | 0 | No
2030-03-22 08:00 | 2030 33% ECP | 570.3 | -526 | -510 | 461.56 | 0 | 0 | No
2030-03-22 09:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-22 10:00 | 2030 33% ECP | 280 | -526 | -510 | 362.07 | 0 | 0 | No
2030-03-22 11:00 | 2030 33% ECP | -140 | -526 | -510 | 252.09 | 0 | 0 | No
2030-03-22 12:00 | 2030 33% ECP | -451.88 | -526 | -510 | 77.18 | 0 | 0 | No
2030-03-22 13:00 | 2030 33% ECP | -31.88 | -526 | -510 | 0 | 0 | 0 | No
2030-03-22 14:00 | 2030 33% ECP | -13.87 | -526 | -510 | -55.98 | 0 | 0 | No
2030-03-22 15:00 | 2030 33% ECP | 280 | -526 | -510 | -216.48 | 0 | 0 | No
2030-03-22 16:00 | 2030 33% ECP | 700 | -526 | -510 | -49.85 | 0 | 0 | No
2030-03-22 17:00 | 2030 33% ECP | 700 | -226 | -510 | 0 | 0 | 0 | No
2030-03-22 18:00 | 2030 33% ECP | 700 | 0 | -280.73 | 242.16 | 0 | 0 | No
2030-03-22 19:00 | 2030 33% ECP | 700 | 0 | 0 | 442.1 | 0 | 0 | No
2030-03-22 20:00 | 2030 33% ECP | 700 | 0 | -90 | 402.97 | 0 | 0 | No
2030-03-22 21:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-03-22 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 05:00 | 2030 33% ECP | 345.79 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 06:00 | 2030 33% ECP | -74.21 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 07:00 | 2030 33% ECP | -494.21 | 205 | 210 | 210 | 0 | 0 | No
2030-03-23 08:00 | 2030 33% ECP | -700 | 0 | 0 | 0 | 0 | 0 | No
2030-03-23 09:00 | 2030 33% ECP | -678.47 | 0 | 210 | 175.1 | 0 | 0 | No
2030-03-23 10:00 | 2030 33% ECP | -700 | 300 | 510 | 475.1 | 0 | 0 | Yes
2030-03-23 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-23 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-23 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-23 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-23 15:00 | 2030 33% ECP | -700 | 300 | 220.9 | 471.2 | 0 | 0 | No
2030-03-23 16:00 | 2030 33% ECP | -700 | 0 | -79.1 | 171.2 | 0 | 0 | No
2030-03-23 17:00 | 2030 33% ECP | -280 | -226 | -379.1 | 0 | 0 | 0 | No
2030-03-23 18:00 | 2030 33% ECP | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-03-23 19:00 | 2030 33% ECP | 0 | -304.46 | -510 | -50.14 | 0 | 0 | No
2030-03-23 20:00 | 2030 33% ECP | 0 | -4.46 | -210 | 184.09 | 0 | 0 | No
2030-03-23 21:00 | 2030 33% ECP | 0 | 295.54 | 90 | 484.09 | 0 | 0 | No
2030-03-23 22:00 | 2030 33% ECP | -280 | 501.33 | 390 | 510 | 0 | 0 | No
2030-03-23 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 16:00 | 2030 33% ECP | -700 | 505 | 510 | 417.27 | 0 | 0 | Yes
2030-03-24 17:00 | 2030 33% ECP | -700 | 300 | 311.68 | 269.59 | 0 | 0 | Yes
2030-03-24 18:00 | 2030 33% ECP | -700 | 0 | 11.68 | -14.14 | 0 | 0 | No
2030-03-24 19:00 | 2030 33% ECP | -700 | -95 | -288.32 | -300 | 0 | 0 | No
2030-03-24 20:00 | 2030 33% ECP | -700 | 205 | 11.68 | 0 | 0 | 0 | No
2030-03-24 21:00 | 2030 33% ECP | -700 | 505 | 311.68 | 300 | 0 | 0 | No
2030-03-24 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-24 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 01:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 02:00 | 2030 33% ECP | 305.99 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 03:00 | 2030 33% ECP | 205.06 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 04:00 | 2030 33% ECP | 625.06 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 05:00 | 2030 33% ECP | 625.06 | 300 | 260.8 | 510 | 0 | 0 | No
2030-03-25 06:00 | 2030 33% ECP | 280 | 0 | -39.2 | 210 | 0 | 0 | No
2030-03-25 07:00 | 2030 33% ECP | -140 | -300 | -339.2 | -62.36 | 0 | 0 | No
2030-03-25 08:00 | 2030 33% ECP | 280 | -526 | -510 | -41.85 | 0 | 0 | No
2030-03-25 09:00 | 2030 33% ECP | 700 | -526 | -510 | 227.4 | 0 | 0 | No
2030-03-25 10:00 | 2030 33% ECP | 700 | -526 | -510 | 135.61 | 0 | 0 | No
2030-03-25 11:00 | 2030 33% ECP | 700 | -526 | -510 | -148.77 | 0 | 0 | No
2030-03-25 12:00 | 2030 33% ECP | 700 | -526 | -510 | -192.38 | 0 | 0 | No
2030-03-25 13:00 | 2030 33% ECP | 700 | -526 | -510 | -101.99 | 0 | 0 | No
2030-03-25 14:00 | 2030 33% ECP | 700 | -526 | -510 | 6.11 | 0 | 0 | No
2030-03-25 15:00 | 2030 33% ECP | 700 | -526 | -510 | 64.86 | 0 | 0 | No
2030-03-25 16:00 | 2030 33% ECP | 700 | -526 | -510 | 149.86 | 0 | 0 | No
2030-03-25 17:00 | 2030 33% ECP | 700 | -390.32 | -510 | -150.14 | 0 | 0 | No
2030-03-25 18:00 | 2030 33% ECP | 700 | -90.32 | -390 | -353.02 | 0 | 0 | No
2030-03-25 19:00 | 2030 33% ECP | 700 | -90.32 | -90 | -90 | 0 | 0 | No
2030-03-25 20:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-03-25 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 22:00 | 2030 33% ECP | 700 | 250.39 | 510 | 510 | 0 | 0 | No
2030-03-25 23:00 | 2030 33% ECP | 700 | 0 | 510 | 431.43 | 0 | 0 | No
2030-03-26 | 2030 33% ECP | 700 | 0 | 510 | 203.58 | 0 | 0 | No
2030-03-26 01:00 | 2030 33% ECP | 700 | 0 | 499.02 | 0 | 0 | 0 | No
2030-03-26 02:00 | 2030 33% ECP | 700 | 0 | 499.02 | 0 | 0 | 0 | No
2030-03-26 03:00 | 2030 33% ECP | 700 | 0 | 206.39 | 0 | 0 | 0 | No
2030-03-26 04:00 | 2030 33% ECP | 700 | 0 | 139.31 | 0 | 0 | 0 | No
2030-03-26 05:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-03-26 06:00 | 2030 33% ECP | 700 | 0 | -136.32 | 0 | 0 | 0 | No
2030-03-26 07:00 | 2030 33% ECP | 700 | -226 | -436.32 | -269.72 | 0 | 0 | No
2030-03-26 08:00 | 2030 33% ECP | 700 | -526 | -510 | -313.72 | 0 | 0 | No
2030-03-26 09:00 | 2030 33% ECP | 280 | -526 | -510 | -13.72 | 0 | 0 | No
2030-03-26 10:00 | 2030 33% ECP | -25.12 | -526 | -510 | 0 | 0 | 0 | No
2030-03-26 11:00 | 2030 33% ECP | 394.88 | -526 | -510 | 0 | 0 | 0 | No
2030-03-26 12:00 | 2030 33% ECP | 266.75 | -526 | -510 | 0 | 0 | 0 | No
2030-03-26 13:00 | 2030 33% ECP | -153.25 | -526 | -510 | 3.24 | 0 | 0 | No
2030-03-26 14:00 | 2030 33% ECP | -31.66 | -526 | -510 | 0 | 0 | 0 | No
2030-03-26 15:00 | 2030 33% ECP | 388.34 | -526 | -510 | 0 | 0 | 0 | No
2030-03-26 16:00 | 2030 33% ECP | 700 | -526 | -510 | 66.86 | 0 | 0 | No
2030-03-26 17:00 | 2030 33% ECP | 700 | -526 | -510 | -233.14 | 0 | 0 | No
2030-03-26 18:00 | 2030 33% ECP | 700 | -512.48 | -510 | -82.9 | 0 | 0 | No
2030-03-26 19:00 | 2030 33% ECP | 700 | -281.88 | -510 | -125.62 | 0 | 0 | No
2030-03-26 20:00 | 2030 33% ECP | 700 | -162.39 | -510 | -93 | 0 | 0 | No
2030-03-26 21:00 | 2030 33% ECP | 700 | 0 | -300 | 0 | 0 | 0 | No
2030-03-26 22:00 | 2030 33% ECP | 700 | 40.94 | 0 | 300 | 0 | 0 | No
2030-03-26 23:00 | 2030 33% ECP | 700 | 0 | 171.32 | 0 | 0 | 0 | No
2030-03-27 | 2030 33% ECP | 700 | 0 | -76.86 | 0 | 0 | 0 | No
2030-03-27 01:00 | 2030 33% ECP | 700 | 0 | -376.86 | -100.21 | 0 | 0 | No
2030-03-27 02:00 | 2030 33% ECP | 700 | 0 | -510 | -51.45 | 0 | 0 | No
2030-03-27 03:00 | 2030 33% ECP | 700 | 0 | -510 | -95.7 | 0 | 0 | No
2030-03-27 04:00 | 2030 33% ECP | 700 | 0 | -510 | -260.54 | 0 | 0 | No
2030-03-27 05:00 | 2030 33% ECP | 420 | 0 | -510 | -118.86 | 0 | 0 | No
2030-03-27 06:00 | 2030 33% ECP | 0 | 0 | -510 | -11.66 | 0 | 0 | No
2030-03-27 07:00 | 2030 33% ECP | 0 | 0 | -510 | -51.76 | 0 | 0 | No
2030-03-27 08:00 | 2030 33% ECP | -61.56 | -226 | -284.52 | 0 | 0 | 0 | No
2030-03-27 09:00 | 2030 33% ECP | -481.56 | -526 | -510 | -7.75 | 0 | 0 | No
2030-03-27 10:00 | 2030 33% ECP | -700 | -526 | -510 | -48.58 | 0 | 0 | No
2030-03-27 11:00 | 2030 33% ECP | -700 | -526 | -510 | -73.95 | 0 | 0 | No
2030-03-27 12:00 | 2030 33% ECP | -700 | -526 | -510 | -207.51 | 0 | 0 | No
2030-03-27 13:00 | 2030 33% ECP | -700 | -526 | -510 | -187.39 | 0 | 0 | No
2030-03-27 14:00 | 2030 33% ECP | -700 | -526 | -510 | -221.79 | 0 | 0 | No
2030-03-27 15:00 | 2030 33% ECP | -591.07 | -526 | -510 | -146.08 | 0 | 0 | No
2030-03-27 16:00 | 2030 33% ECP | -171.07 | -526 | -510 | -35.02 | 0 | 0 | No
2030-03-27 17:00 | 2030 33% ECP | 248.93 | -414.38 | -510 | 62.85 | 0 | 0 | No
2030-03-27 18:00 | 2030 33% ECP | 0 | -114.38 | -510 | -26.11 | 0 | 0 | No
2030-03-27 19:00 | 2030 33% ECP | 0 | -224.95 | -510 | -129.16 | 0 | 0 | No
2030-03-27 20:00 | 2030 33% ECP | 420 | 0 | -510 | -210.71 | 0 | 0 | No
2030-03-27 21:00 | 2030 33% ECP | 700 | -95 | -390 | -510 | 0 | 0 | No
2030-03-27 22:00 | 2030 33% ECP | 589.66 | -95 | -90 | -510 | 0 | 0 | No
2030-03-27 23:00 | 2030 33% ECP | 479.03 | 205 | 210 | -331.22 | 0 | 0 | No
2030-03-28 | 2030 33% ECP | 700 | 505 | 510 | -31.22 | 0 | 0 | No
2030-03-28 01:00 | 2030 33% ECP | 700 | 505 | 510 | 268.78 | 0 | 0 | No
2030-03-28 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 03:00 | 2030 33% ECP | 517.8 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 04:00 | 2030 33% ECP | 97.8 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 05:00 | 2030 33% ECP | -322.2 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 07:00 | 2030 33% ECP | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-03-28 08:00 | 2030 33% ECP | -700 | -95 | -90 | 262.34 | 0 | 0 | No
2030-03-28 09:00 | 2030 33% ECP | -700 | 205 | 210 | 510 | 0 | 0 | Yes
2030-03-28 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 15:00 | 2030 33% ECP | -700 | 405.69 | 390 | 510 | 0 | 0 | Yes
2030-03-28 16:00 | 2030 33% ECP | -700 | 105.69 | 90 | 510 | 0 | 0 | Yes
2030-03-28 17:00 | 2030 33% ECP | -420 | -194.31 | -210 | 510 | 0 | 0 | Yes
2030-03-28 18:00 | 2030 33% ECP | 0 | -494.31 | -510 | 210 | 0 | 0 | No
2030-03-28 19:00 | 2030 33% ECP | 420 | -194.31 | -210 | 23.5 | 0 | 0 | No
2030-03-28 20:00 | 2030 33% ECP | 700 | 105.69 | 90 | 210 | 0 | 0 | No
2030-03-28 21:00 | 2030 33% ECP | 700 | 405.69 | 390 | 510 | 0 | 0 | No
2030-03-28 22:00 | 2030 33% ECP | 403.76 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 23:00 | 2030 33% ECP | -16.24 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 01:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 02:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 03:00 | 2030 33% ECP | 46.63 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 04:00 | 2030 33% ECP | 23.23 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 05:00 | 2030 33% ECP | 443.23 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 06:00 | 2030 33% ECP | 443.23 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 07:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 08:00 | 2030 33% ECP | -280 | 381.17 | 510 | 510 | 0 | 0 | No
2030-03-29 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 14:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-29 15:00 | 2030 33% ECP | -634.66 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-29 16:00 | 2030 33% ECP | -214.66 | -226 | -210 | 510 | 0 | 0 | Yes
2030-03-29 17:00 | 2030 33% ECP | 205.34 | -526 | -510 | 210 | 0 | 0 | No
2030-03-29 18:00 | 2030 33% ECP | 625.34 | -226 | -210 | 510 | 0 | 0 | No
2030-03-29 19:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-03-29 20:00 | 2030 33% ECP | 700 | 0 | 300 | 346.6 | 0 | 0 | No
2030-03-29 21:00 | 2030 33% ECP | 700 | 0 | 510 | 162.56 | 0 | 0 | No
2030-03-29 22:00 | 2030 33% ECP | 700 | 205 | 422.51 | 462.56 | 0 | 0 | No
2030-03-29 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 05:00 | 2030 33% ECP | 700 | 505 | 510 | 367.92 | 0 | 0 | No
2030-03-30 06:00 | 2030 33% ECP | 700 | 505 | 510 | 67.92 | 0 | 0 | No
2030-03-30 07:00 | 2030 33% ECP | 280 | 489.41 | 510 | -232.08 | 0 | 0 | No
2030-03-30 08:00 | 2030 33% ECP | -140 | 189.41 | 210 | -510 | 0 | 0 | No
2030-03-30 09:00 | 2030 33% ECP | -560 | -110.59 | -90 | -244.68 | 0 | 0 | No
2030-03-30 10:00 | 2030 33% ECP | -700 | -226 | -325.96 | 55.32 | 0 | 0 | No
2030-03-30 11:00 | 2030 33% ECP | -700 | -526 | -510 | -185.91 | 0 | 0 | No
2030-03-30 12:00 | 2030 33% ECP | -700 | -526 | -510 | -485.91 | 0 | 0 | No
2030-03-30 13:00 | 2030 33% ECP | -700 | -526 | -510 | -429.46 | 0 | 0 | No
2030-03-30 14:00 | 2030 33% ECP | -700 | -526 | -510 | -129.46 | 0 | 0 | No
2030-03-30 15:00 | 2030 33% ECP | -560 | -526 | -510 | 170.54 | 0 | 0 | No
2030-03-30 16:00 | 2030 33% ECP | -140 | -451.78 | -510 | 110.46 | 0 | 0 | No
2030-03-30 17:00 | 2030 33% ECP | 280 | -526 | -510 | 152.15 | 0 | 0 | No
2030-03-30 18:00 | 2030 33% ECP | 700 | -226 | -300 | 452.15 | 0 | 0 | No
2030-03-30 19:00 | 2030 33% ECP | 700 | 0 | 0 | 392.08 | 0 | 0 | No
2030-03-30 20:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-03-30 21:00 | 2030 33% ECP | 700 | 205 | 210 | 327.6 | 0 | 0 | No
2030-03-30 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-31 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-03-31 01:00 | 2030 33% ECP | 700 | 0 | -90 | 0 | 0 | 0 | No
2030-03-31 02:00 | 2030 33% ECP | 700 | 0 | -390 | 0 | 0 | 0 | No
2030-03-31 03:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-03-31 04:00 | 2030 33% ECP | 700 | 0 | -471.4 | 96.17 | 0 | 0 | No
2030-03-31 05:00 | 2030 33% ECP | 700 | 0 | -510 | 55.6 | 0 | 0 | No
2030-03-31 06:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-03-31 07:00 | 2030 33% ECP | 700 | 0 | -508.05 | 0 | 0 | 0 | No
2030-03-31 08:00 | 2030 33% ECP | 700 | -226 | -510 | 63.13 | 0 | 0 | No
2030-03-31 09:00 | 2030 33% ECP | 700 | -526 | -510 | 63.13 | 0 | 0 | No
2030-03-31 10:00 | 2030 33% ECP | 700 | -526 | -510 | 181.43 | 0 | 0 | No
2030-03-31 11:00 | 2030 33% ECP | 700 | -526 | -510 | 341.13 | 0 | 0 | No
2030-03-31 12:00 | 2030 33% ECP | 700 | -526 | -510 | 291.46 | 0 | 0 | No
2030-03-31 13:00 | 2030 33% ECP | 700 | -526 | -510 | 263.67 | 0 | 0 | No
2030-03-31 14:00 | 2030 33% ECP | 700 | -526 | -510 | 221.1 | 0 | 0 | No
2030-03-31 15:00 | 2030 33% ECP | 700 | -526 | -510 | 21.09 | 0 | 0 | No
2030-03-31 16:00 | 2030 33% ECP | 700 | -526 | -510 | 100.52 | 0 | 0 | No
2030-03-31 17:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-03-31 18:00 | 2030 33% ECP | 700 | -226 | -210 | 300 | 0 | 0 | No
2030-03-31 19:00 | 2030 33% ECP | 700 | 0 | 0 | 300 | 0 | 0 | No
2030-03-31 20:00 | 2030 33% ECP | 700 | 0 | 47.39 | 390.45 | 0 | 0 | No
2030-03-31 21:00 | 2030 33% ECP | 700 | 0 | 347.39 | 246.92 | 0 | 0 | No
2030-03-31 22:00 | 2030 33% ECP | 700 | 0 | 105.76 | 246.92 | 0 | 0 | No
2030-03-31 23:00 | 2030 33% ECP | 700 | 0 | 405.76 | 377.71 | 0 | 0 | No
2030-04-01 | 2030 33% ECP | 700 | 0 | 105.76 | 304.62 | 0 | 0 | No
2030-04-01 01:00 | 2030 33% ECP | 700 | 0 | 70.62 | 211.24 | 0 | 0 | No
2030-04-01 02:00 | 2030 33% ECP | 700 | 0 | 220.1 | 255.33 | 0 | 0 | No
2030-04-01 03:00 | 2030 33% ECP | 700 | 0 | 0 | 285.13 | 0 | 0 | No
2030-04-01 04:00 | 2030 33% ECP | 700 | 0 | 0 | 247 | 0 | 0 | No
2030-04-01 05:00 | 2030 33% ECP | 700 | 0 | 0 | 105.07 | 0 | 0 | No
2030-04-01 06:00 | 2030 33% ECP | 700 | 0 | 116.7 | 226.29 | 0 | 0 | No
2030-04-01 07:00 | 2030 33% ECP | 700 | 3.34 | 416.7 | 461.59 | 0 | 0 | No
2030-04-01 08:00 | 2030 33% ECP | 700 | 303.34 | 510 | 510 | 0 | 0 | No
2030-04-01 09:00 | 2030 33% ECP | 671.66 | 3.34 | 210 | 475.17 | 0 | 0 | No
2030-04-01 10:00 | 2030 33% ECP | 251.66 | 0 | 0 | 322.21 | 0 | 0 | No
2030-04-01 11:00 | 2030 33% ECP | 0 | 0 | 0 | 293.63 | 0 | 0 | No
2030-04-01 12:00 | 2030 33% ECP | -106.51 | 0 | 0 | 31.49 | 0 | 0 | No
2030-04-01 13:00 | 2030 33% ECP | -106.51 | 0 | 0 | 210 | 0 | 0 | No
2030-04-01 14:00 | 2030 33% ECP | 0 | 134.59 | 300 | 510 | 0 | 0 | No
2030-04-01 15:00 | 2030 33% ECP | 280 | 157.1 | 0 | 510 | 0 | 0 | No
2030-04-01 16:00 | 2030 33% ECP | 700 | -142.9 | -300 | 210 | 0 | 0 | No
2030-04-01 17:00 | 2030 33% ECP | 700 | 0 | -510 | 457.94 | 0 | 0 | No
2030-04-01 18:00 | 2030 33% ECP | 700 | 0 | -300 | 345.06 | 0 | 0 | No
2030-04-01 19:00 | 2030 33% ECP | 700 | 0 | 0 | 205.02 | 0 | 0 | No
2030-04-01 20:00 | 2030 33% ECP | 700 | 0 | -224.56 | 0 | 0 | 0 | No
2030-04-01 21:00 | 2030 33% ECP | 700 | 0 | -90 | 121.84 | 0 | 0 | No
2030-04-01 22:00 | 2030 33% ECP | 700 | 205 | 210 | 408.9 | 0 | 0 | No
2030-04-01 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 01:00 | 2030 33% ECP | 302.86 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 02:00 | 2030 33% ECP | 290.97 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 03:00 | 2030 33% ECP | 352.9 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 04:00 | 2030 33% ECP | -31.04 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 05:00 | 2030 33% ECP | -382.58 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 07:00 | 2030 33% ECP | -348.2 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 17:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 18:00 | 2030 33% ECP | -432.73 | 205 | 210 | 210 | 0 | 0 | No
2030-04-02 19:00 | 2030 33% ECP | -12.73 | 0 | -90 | 510 | 0 | 0 | No
2030-04-02 20:00 | 2030 33% ECP | 407.27 | -23.83 | -390 | 210 | 0 | 0 | No
2030-04-02 21:00 | 2030 33% ECP | 700 | -23.83 | -510 | 510 | 0 | 0 | No
2030-04-02 22:00 | 2030 33% ECP | 700 | 0 | -300 | 407.67 | 0 | 0 | No
2030-04-02 23:00 | 2030 33% ECP | 700 | 222.95 | 0 | 510 | 0 | 0 | No
2030-04-03 | 2030 33% ECP | 544.27 | 0 | 0 | 210 | 0 | 0 | No
2030-04-03 01:00 | 2030 33% ECP | 523.53 | 0 | 0 | 89.39 | 0 | 0 | No
2030-04-03 02:00 | 2030 33% ECP | 111.23 | 0 | 0 | 314.55 | 0 | 0 | No
2030-04-03 03:00 | 2030 33% ECP | 373.12 | 0 | -133.13 | 49.92 | 0 | 0 | No
2030-04-03 04:00 | 2030 33% ECP | 420 | -68.65 | -433.13 | 0 | 0 | 0 | No
2030-04-03 05:00 | 2030 33% ECP | 0 | 0 | -133.13 | 67.35 | 0 | 0 | No
2030-04-03 06:00 | 2030 33% ECP | -420 | 0 | 166.87 | 275.38 | 0 | 0 | No
2030-04-03 07:00 | 2030 33% ECP | -420 | 0 | 90 | 418.3 | 0 | 0 | No
2030-04-03 08:00 | 2030 33% ECP | 0 | -211.75 | -210 | 510 | 0 | 0 | No
2030-04-03 09:00 | 2030 33% ECP | -420 | -511.75 | -510 | 329.98 | 0 | 0 | No
2030-04-03 10:00 | 2030 33% ECP | -700 | -526 | -510 | 305.06 | 0 | 0 | No
2030-04-03 11:00 | 2030 33% ECP | -700 | -526 | -510 | 283.45 | 0 | 0 | No
2030-04-03 12:00 | 2030 33% ECP | -700 | -526 | -510 | 107.48 | 0 | 0 | No
2030-04-03 13:00 | 2030 33% ECP | -700 | -526 | -510 | 120.24 | 0 | 0 | No
2030-04-03 14:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-03 15:00 | 2030 33% ECP | -698.51 | -526 | -510 | 0 | 0 | 0 | No
2030-04-03 16:00 | 2030 33% ECP | -278.51 | -226 | -504.58 | 166.58 | 0 | 0 | No
2030-04-03 17:00 | 2030 33% ECP | 141.49 | -9.17 | -210 | 239.04 | 0 | 0 | No
2030-04-03 18:00 | 2030 33% ECP | 0 | -309.17 | -510 | -60.96 | 0 | 0 | No
2030-04-03 19:00 | 2030 33% ECP | 0 | -300 | -283.22 | -246.02 | 0 | 0 | No
2030-04-03 20:00 | 2030 33% ECP | 280 | 0 | 16.78 | 53.98 | 0 | 0 | No
2030-04-03 21:00 | 2030 33% ECP | 700 | 300 | 316.78 | 353.98 | 0 | 0 | No
2030-04-03 22:00 | 2030 33% ECP | 700 | 0 | 293.49 | 479.25 | 0 | 0 | No
2030-04-03 23:00 | 2030 33% ECP | 700 | 0 | -6.51 | 193.7 | 0 | 0 | No
2030-04-04 | 2030 33% ECP | 700 | 0 | -292.24 | 19.71 | 0 | 0 | No
2030-04-04 01:00 | 2030 33% ECP | 700 | 0 | -510 | 107.22 | 0 | 0 | No
2030-04-04 02:00 | 2030 33% ECP | 700 | 0 | -510 | 86.41 | 0 | 0 | No
2030-04-04 03:00 | 2030 33% ECP | 700 | 0 | -510 | 70.15 | 0 | 0 | No
2030-04-04 04:00 | 2030 33% ECP | 404.86 | 0 | -510 | 0 | 0 | 0 | No
2030-04-04 05:00 | 2030 33% ECP | -15.14 | 0 | -510 | 46.05 | 0 | 0 | No
2030-04-04 06:00 | 2030 33% ECP | -435.14 | 0 | -510 | 169.39 | 0 | 0 | No
2030-04-04 07:00 | 2030 33% ECP | -15.14 | -226 | -316.98 | 350.72 | 0 | 0 | No
2030-04-04 08:00 | 2030 33% ECP | -350.78 | -526 | -510 | 468.01 | 0 | 0 | No
2030-04-04 09:00 | 2030 33% ECP | -700 | -526 | -510 | 232.68 | 0 | 0 | No
2030-04-04 10:00 | 2030 33% ECP | -700 | -526 | -510 | -67.32 | 0 | 0 | Yes
2030-04-04 11:00 | 2030 33% ECP | -700 | -526 | -510 | 210 | 0 | 0 | Yes
2030-04-04 12:00 | 2030 33% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-04-04 13:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-04 14:00 | 2030 33% ECP | -700 | -226 | -225.46 | 510 | 0 | 0 | Yes
2030-04-04 15:00 | 2030 33% ECP | -700 | -526 | -510 | 360.87 | 0 | 0 | Yes
2030-04-04 16:00 | 2030 33% ECP | -700 | -526 | -510 | 234.09 | 0 | 0 | Yes
2030-04-04 17:00 | 2030 33% ECP | -700 | -526 | -510 | 395.79 | 0 | 0 | No
2030-04-04 18:00 | 2030 33% ECP | -700 | -526 | -510 | 96.57 | 0 | 0 | No
2030-04-04 19:00 | 2030 33% ECP | -460.76 | -454.03 | -510 | 96.57 | 0 | 0 | No
2030-04-04 20:00 | 2030 33% ECP | -40.76 | -154.03 | -210 | 396.57 | 0 | 0 | No
2030-04-04 21:00 | 2030 33% ECP | -280 | 145.97 | 90 | 510 | 0 | 0 | No
2030-04-04 22:00 | 2030 33% ECP | -700 | 445.97 | 390 | 510 | 0 | 0 | Yes
2030-04-04 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 03:00 | 2030 33% ECP | -700 | 505 | 510 | 485.67 | 0 | 0 | Yes
2030-04-05 04:00 | 2030 33% ECP | -700 | 505 | 510 | 185.67 | 0 | 0 | Yes
2030-04-05 05:00 | 2030 33% ECP | -700 | 505 | 510 | 170.53 | 0 | 0 | Yes
2030-04-05 06:00 | 2030 33% ECP | -700 | 505 | 510 | 243.51 | 0 | 0 | Yes
2030-04-05 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 12:00 | 2030 33% ECP | -700 | 505 | 510 | 483.6 | 0 | 0 | Yes
2030-04-05 13:00 | 2030 33% ECP | -700 | 505 | 510 | 263.75 | 0 | 0 | Yes
2030-04-05 14:00 | 2030 33% ECP | -700 | 505 | 510 | 216.05 | 0 | 0 | Yes
2030-04-05 15:00 | 2030 33% ECP | -700 | 505 | 510 | 220.16 | 0 | 0 | Yes
2030-04-05 16:00 | 2030 33% ECP | -700 | 505 | 510 | 313.38 | 0 | 0 | Yes
2030-04-05 17:00 | 2030 33% ECP | -700 | 505 | 510 | 365.25 | 0 | 0 | Yes
2030-04-05 18:00 | 2030 33% ECP | -700 | 505 | 510 | 336.08 | 0 | 0 | Yes
2030-04-05 19:00 | 2030 33% ECP | -700 | 505 | 510 | 304.4 | 0 | 0 | Yes
2030-04-05 20:00 | 2030 33% ECP | -700 | 505 | 510 | 310.88 | 0 | 0 | Yes
2030-04-05 21:00 | 2030 33% ECP | -700 | 505 | 510 | 299.13 | 0 | 0 | Yes
2030-04-05 22:00 | 2030 33% ECP | -700 | 505 | 510 | 228.76 | 0 | 0 | Yes
2030-04-05 23:00 | 2030 33% ECP | -700 | 505 | 510 | 157.88 | 0 | 0 | Yes
2030-04-06 | 2030 33% ECP | -700 | 505 | 510 | 457.88 | 0 | 0 | Yes
2030-04-06 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 13:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-04-06 14:00 | 2030 33% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-04-06 15:00 | 2030 33% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-04-06 16:00 | 2030 33% ECP | -280 | -526 | -510 | 227.59 | 0 | 0 | No
2030-04-06 17:00 | 2030 33% ECP | -183.16 | -526 | -510 | 352.48 | 0 | 0 | No
2030-04-06 18:00 | 2030 33% ECP | 236.84 | -226 | -210 | 510 | 0 | 0 | No
2030-04-06 19:00 | 2030 33% ECP | 323.9 | 0 | 0 | 446.56 | 0 | 0 | No
2030-04-06 20:00 | 2030 33% ECP | 700 | 0 | 0 | 384.61 | 0 | 0 | No
2030-04-06 21:00 | 2030 33% ECP | 700 | 0 | 0 | 384.61 | 0 | 0 | No
2030-04-06 22:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-04-06 23:00 | 2030 33% ECP | 700 | 0 | 0 | 482.22 | 0 | 0 | No
2030-04-07 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-04-07 01:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-04-07 02:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-04-07 03:00 | 2030 33% ECP | 700 | 0 | -258.49 | 445.79 | 0 | 0 | No
2030-04-07 04:00 | 2030 33% ECP | 700 | 0 | -409.65 | 348.62 | 0 | 0 | No
2030-04-07 05:00 | 2030 33% ECP | 560 | 0 | -109.65 | 403.52 | 0 | 0 | No
2030-04-07 06:00 | 2030 33% ECP | 140 | 0 | -166.07 | 318.21 | 0 | 0 | No
2030-04-07 07:00 | 2030 33% ECP | -280 | -226 | -466.07 | 474.99 | 0 | 0 | No
2030-04-07 08:00 | 2030 33% ECP | -700 | -526 | -510 | 425.27 | 0 | 0 | No
2030-04-07 09:00 | 2030 33% ECP | -700 | -526 | -510 | 219.29 | 0 | 0 | Yes
2030-04-07 10:00 | 2030 33% ECP | -700 | -526 | -510 | -80.71 | 0 | 0 | Yes
2030-04-07 11:00 | 2030 33% ECP | -700 | -526 | -510 | -218.62 | 0 | 0 | Yes
2030-04-07 12:00 | 2030 33% ECP | -700 | -226 | -210 | 81.38 | 0 | 0 | Yes
2030-04-07 13:00 | 2030 33% ECP | -700 | -526 | -510 | 176.66 | 0 | 0 | Yes
2030-04-07 14:00 | 2030 33% ECP | -700 | -526 | -510 | 8.55 | 0 | 0 | Yes
2030-04-07 15:00 | 2030 33% ECP | -700 | -291.94 | -510 | 230.83 | 0 | 0 | Yes
2030-04-07 16:00 | 2030 33% ECP | -388.78 | -526 | -510 | -69.17 | 0 | 0 | No
2030-04-07 17:00 | 2030 33% ECP | -497.25 | -526 | -510 | 230.83 | 0 | 0 | No
2030-04-07 18:00 | 2030 33% ECP | -77.25 | -226 | -510 | 510 | 0 | 0 | No
2030-04-07 19:00 | 2030 33% ECP | 342.75 | 0 | -510 | 510 | 0 | 0 | No
2030-04-07 20:00 | 2030 33% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-04-07 21:00 | 2030 33% ECP | 700 | 0 | -510 | 483.97 | 0 | 0 | No
2030-04-07 22:00 | 2030 33% ECP | 700 | 0 | -510 | 369 | 0 | 0 | No
2030-04-07 23:00 | 2030 33% ECP | 700 | -173.08 | -510 | 295.65 | 0 | 0 | No
2030-04-08 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-08 01:00 | 2030 33% ECP | 700 | 0 | -510 | -113.32 | 0 | 0 | No
2030-04-08 02:00 | 2030 33% ECP | 700 | 0 | -510 | -219.89 | 0 | 0 | No
2030-04-08 03:00 | 2030 33% ECP | 700 | 0 | -510 | -219.89 | 0 | 0 | No
2030-04-08 04:00 | 2030 33% ECP | 700 | 0 | -510 | -356.52 | 0 | 0 | No
2030-04-08 05:00 | 2030 33% ECP | 700 | 0 | -510 | -91.05 | 0 | 0 | No
2030-04-08 06:00 | 2030 33% ECP | 700 | 0 | -510 | -200.51 | 0 | 0 | No
2030-04-08 07:00 | 2030 33% ECP | 700 | 0 | -510 | -142.91 | 0 | 0 | No
2030-04-08 08:00 | 2030 33% ECP | 302.9 | -300 | -510 | 68.28 | 0 | 0 | No
2030-04-08 09:00 | 2030 33% ECP | 700 | -526 | -510 | 107.64 | 0 | 0 | No
2030-04-08 10:00 | 2030 33% ECP | 700 | -526 | -510 | 81.52 | 0 | 0 | No
2030-04-08 11:00 | 2030 33% ECP | 301.12 | -526 | -510 | 59.14 | 0 | 0 | No
2030-04-08 12:00 | 2030 33% ECP | 700 | -526 | -510 | 40.02 | 0 | 0 | No
2030-04-08 13:00 | 2030 33% ECP | 700 | -526 | -510 | 30.5 | 0 | 0 | No
2030-04-08 14:00 | 2030 33% ECP | 700 | -526 | -510 | 18.18 | 0 | 0 | No
2030-04-08 15:00 | 2030 33% ECP | 700 | -526 | -510 | 5.91 | 0 | 0 | No
2030-04-08 16:00 | 2030 33% ECP | 700 | -526 | -510 | 181.84 | 0 | 0 | No
2030-04-08 17:00 | 2030 33% ECP | 700 | -226 | -387.12 | 280.65 | 0 | 0 | No
2030-04-08 18:00 | 2030 33% ECP | 700 | 0 | -510 | -19.35 | 0 | 0 | No
2030-04-08 19:00 | 2030 33% ECP | 300.34 | 0 | -510 | -319.35 | 0 | 0 | No
2030-04-08 20:00 | 2030 33% ECP | 700 | 0 | -300 | -219.17 | 0 | 0 | No
2030-04-08 21:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-08 22:00 | 2030 33% ECP | 700 | 164.01 | 300 | 300 | 0 | 0 | No
2030-04-08 23:00 | 2030 33% ECP | 700 | 0 | 240.77 | 0 | 0 | 0 | No
2030-04-09 | 2030 33% ECP | 700 | 0 | 510 | 300 | 0 | 0 | No
2030-04-09 01:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-04-09 02:00 | 2030 33% ECP | 700 | 0 | 510 | 22.96 | 0 | 0 | No
2030-04-09 03:00 | 2030 33% ECP | 700 | 0 | 390 | 22.96 | 0 | 0 | No
2030-04-09 04:00 | 2030 33% ECP | 676.46 | 0 | 90 | 71.85 | 0 | 0 | No
2030-04-09 05:00 | 2030 33% ECP | 256.46 | 0 | -210 | -210 | 0 | 0 | No
2030-04-09 06:00 | 2030 33% ECP | -163.54 | -300 | -510 | -510 | 0 | 0 | No
2030-04-09 07:00 | 2030 33% ECP | -583.54 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 08:00 | 2030 33% ECP | -281.89 | -526 | -510 | -407.15 | 0 | 0 | No
2030-04-09 09:00 | 2030 33% ECP | -700 | -526 | -510 | -376.24 | 0 | 0 | No
2030-04-09 10:00 | 2030 33% ECP | -700 | -526 | -510 | -396.02 | 0 | 0 | No
2030-04-09 11:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 12:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 13:00 | 2030 33% ECP | -700 | -526 | -510 | -501.39 | 0 | 0 | No
2030-04-09 14:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 15:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 16:00 | 2030 33% ECP | -506.61 | -526 | -510 | -434.14 | 0 | 0 | No
2030-04-09 17:00 | 2030 33% ECP | -128.53 | -226 | -210 | -210 | 0 | 0 | No
2030-04-09 18:00 | 2030 33% ECP | -548.53 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 19:00 | 2030 33% ECP | -128.53 | -300 | -510 | -510 | 0 | 0 | No
2030-04-09 20:00 | 2030 33% ECP | 291.47 | 0 | -210 | -210 | 0 | 0 | No
2030-04-09 21:00 | 2030 33% ECP | 700 | 0 | 90 | 90 | 0 | 0 | No
2030-04-09 22:00 | 2030 33% ECP | 700 | 0 | -23.39 | 0 | 0 | 0 | No
2030-04-09 23:00 | 2030 33% ECP | 700 | 0 | -197.23 | 0 | 0 | 0 | No
2030-04-10 | 2030 33% ECP | 700 | 0 | 102.77 | 0 | 0 | 0 | No
2030-04-10 01:00 | 2030 33% ECP | 700 | 0 | 102.77 | 0 | 0 | 0 | No
2030-04-10 02:00 | 2030 33% ECP | 700 | 0 | 45.71 | 0 | 0 | 0 | No
2030-04-10 03:00 | 2030 33% ECP | 700 | 0 | 223.14 | 0 | 0 | 0 | No
2030-04-10 04:00 | 2030 33% ECP | 700 | 0 | 223.14 | 0 | 0 | 0 | No
2030-04-10 05:00 | 2030 33% ECP | 420 | 0 | 223.14 | 0 | 0 | 0 | No
2030-04-10 06:00 | 2030 33% ECP | 0 | 0 | -76.86 | 73.99 | 0 | 0 | No
2030-04-10 07:00 | 2030 33% ECP | -62.26 | -300 | -376.86 | -226.01 | 0 | 0 | No
2030-04-10 08:00 | 2030 33% ECP | 357.74 | 0 | -210 | 73.99 | 0 | 0 | No
2030-04-10 09:00 | 2030 33% ECP | 700 | -300 | -510 | 78.7 | 0 | 0 | No
2030-04-10 10:00 | 2030 33% ECP | 655.26 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 11:00 | 2030 33% ECP | 235.26 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 12:00 | 2030 33% ECP | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 13:00 | 2030 33% ECP | 135.35 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 14:00 | 2030 33% ECP | 546.14 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 15:00 | 2030 33% ECP | 700 | -300 | -510 | 0 | 0 | 0 | No
2030-04-10 16:00 | 2030 33% ECP | 700 | 0 | -461.66 | 39.11 | 0 | 0 | No
2030-04-10 17:00 | 2030 33% ECP | 700 | 0 | -510 | -260.89 | 0 | 0 | No
2030-04-10 18:00 | 2030 33% ECP | 280 | 0 | -390 | -390 | 0 | 0 | No
2030-04-10 19:00 | 2030 33% ECP | 461.11 | 0 | -90 | -90 | 0 | 0 | No
2030-04-10 20:00 | 2030 33% ECP | 280 | 175.81 | 210 | 210 | 0 | 0 | No
2030-04-10 21:00 | 2030 33% ECP | 700 | 475.81 | 510 | 510 | 0 | 0 | No
2030-04-10 22:00 | 2030 33% ECP | 700 | 175.81 | 510 | 326.58 | 0 | 0 | No
2030-04-10 23:00 | 2030 33% ECP | 700 | 0 | 245.95 | 26.58 | 0 | 0 | No
2030-04-11 | 2030 33% ECP | 700 | 0 | 5.27 | 0 | 0 | 0 | No
2030-04-11 01:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 02:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 03:00 | 2030 33% ECP | 700 | 0 | 157.57 | 0 | 0 | 0 | No
2030-04-11 04:00 | 2030 33% ECP | 280 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 05:00 | 2030 33% ECP | -140 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 06:00 | 2030 33% ECP | -560 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 07:00 | 2030 33% ECP | -700 | 0 | 90 | 245.07 | 0 | 0 | No
2030-04-11 08:00 | 2030 33% ECP | -280 | -226 | -210 | -8.55 | 0 | 0 | No
2030-04-11 09:00 | 2030 33% ECP | -700 | -526 | -510 | -173.43 | 0 | 0 | No
2030-04-11 10:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-11 11:00 | 2030 33% ECP | -700 | -526 | -510 | -125.72 | 0 | 0 | No
2030-04-11 12:00 | 2030 33% ECP | -700 | -526 | -510 | -104.79 | 0 | 0 | No
2030-04-11 13:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-11 14:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-11 15:00 | 2030 33% ECP | -700 | -526 | -510 | -102.6 | 0 | 0 | No
2030-04-11 16:00 | 2030 33% ECP | -700 | -526 | -510 | -92.17 | 0 | 0 | No
2030-04-11 17:00 | 2030 33% ECP | -280 | -256.8 | -510 | -188.77 | 0 | 0 | No
2030-04-11 18:00 | 2030 33% ECP | -560 | -526 | -510 | -488.77 | 0 | 0 | No
2030-04-11 19:00 | 2030 33% ECP | -140 | -300 | -329.73 | -300 | 0 | 0 | No
2030-04-11 20:00 | 2030 33% ECP | 280 | 0 | -29.73 | 0 | 0 | 0 | No
2030-04-11 21:00 | 2030 33% ECP | 700 | 300 | 270.27 | 300 | 0 | 0 | No
2030-04-11 22:00 | 2030 33% ECP | 700 | 0 | 510 | 225.89 | 0 | 0 | No
2030-04-11 23:00 | 2030 33% ECP | 700 | 0 | 370.74 | 0 | 0 | 0 | No
2030-04-12 | 2030 33% ECP | 700 | 300 | 510 | 300 | 0 | 0 | No
2030-04-12 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-12 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-12 03:00 | 2030 33% ECP | 700 | 505 | 390 | 510 | 0 | 0 | No
2030-04-12 04:00 | 2030 33% ECP | 700 | 205 | 90 | 228.51 | 0 | 0 | No
2030-04-12 05:00 | 2030 33% ECP | 280 | -95 | -210 | -71.49 | 0 | 0 | No
2030-04-12 06:00 | 2030 33% ECP | 0 | -395 | -510 | -371.49 | 0 | 0 | No
2030-04-12 07:00 | 2030 33% ECP | 0 | -526 | -510 | -466.91 | 0 | 0 | No
2030-04-12 08:00 | 2030 33% ECP | 280 | -526 | -510 | -510 | 0 | 0 | No
2030-04-12 09:00 | 2030 33% ECP | 700 | -526 | -510 | -455.99 | 0 | 0 | No
2030-04-12 10:00 | 2030 33% ECP | 374.47 | -513.89 | -510 | -155.99 | 0 | 0 | No
2030-04-12 11:00 | 2030 33% ECP | -45.53 | -526 | -510 | 144.01 | 0 | 0 | No
2030-04-12 12:00 | 2030 33% ECP | -374.31 | -526 | -510 | -155.99 | 0 | 0 | No
2030-04-12 13:00 | 2030 33% ECP | -700 | -526 | -510 | -155.23 | 0 | 0 | No
2030-04-12 14:00 | 2030 33% ECP | -611.23 | -526 | -510 | -337.62 | 0 | 0 | No
2030-04-12 15:00 | 2030 33% ECP | -700 | -526 | -510 | -199.88 | 0 | 0 | No
2030-04-12 16:00 | 2030 33% ECP | -700 | -526 | -510 | -59.26 | 0 | 0 | No
2030-04-12 17:00 | 2030 33% ECP | -700 | -526 | -510 | 84.98 | 0 | 0 | No
2030-04-12 18:00 | 2030 33% ECP | -694.32 | -526 | -510 | -16.06 | 0 | 0 | No
2030-04-12 19:00 | 2030 33% ECP | -550.18 | -328.31 | -510 | 76.31 | 0 | 0 | No
2030-04-12 20:00 | 2030 33% ECP | -491.76 | -28.31 | -210 | 71.78 | 0 | 0 | No
2030-04-12 21:00 | 2030 33% ECP | -700 | 271.69 | 90 | -138.17 | 0 | 0 | No
2030-04-12 22:00 | 2030 33% ECP | -700 | 505 | 390 | 62.43 | 0 | 0 | Yes
2030-04-12 23:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-04-13 | 2030 33% ECP | -280 | 505 | 510 | 300 | 0 | 0 | Yes
2030-04-13 01:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-13 02:00 | 2030 33% ECP | -250.42 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-13 03:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-13 04:00 | 2030 33% ECP | 0 | 479.07 | 390 | 492.06 | 0 | 0 | Yes
2030-04-13 05:00 | 2030 33% ECP | -280 | 179.07 | 90 | 192.06 | 0 | 0 | No
2030-04-13 06:00 | 2030 33% ECP | -700 | -120.93 | -210 | -107.94 | 0 | 0 | No
2030-04-13 07:00 | 2030 33% ECP | -700 | -420.93 | -510 | -407.94 | 0 | 0 | No
2030-04-13 08:00 | 2030 33% ECP | -280 | -526 | -510 | -107.94 | 0 | 0 | No
2030-04-13 09:00 | 2030 33% ECP | -700 | -526 | -510 | 192.06 | 0 | 0 | Yes
2030-04-13 10:00 | 2030 33% ECP | -700 | -526 | -510 | 492.06 | 0 | 0 | Yes
2030-04-13 11:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 12:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 13:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 14:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 15:00 | 2030 33% ECP | -560 | -526 | -510 | 324.04 | 0 | 0 | Yes
2030-04-13 16:00 | 2030 33% ECP | -140 | -526 | -510 | 426.03 | 0 | 0 | No
2030-04-13 17:00 | 2030 33% ECP | 280 | -526 | -510 | 510 | 0 | 0 | No
2030-04-13 18:00 | 2030 33% ECP | 700 | -226 | -426.13 | 510 | 0 | 0 | No
2030-04-13 19:00 | 2030 33% ECP | 700 | 0 | -300 | 510 | 0 | 0 | No
2030-04-13 20:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-04-13 21:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-04-13 22:00 | 2030 33% ECP | 700 | 0 | -260.54 | 510 | 0 | 0 | No
2030-04-13 23:00 | 2030 33% ECP | 700 | 0 | -260.54 | 450.92 | 0 | 0 | No
2030-04-14 | 2030 33% ECP | 700 | 0 | -510 | 150.92 | 0 | 0 | No
2030-04-14 01:00 | 2030 33% ECP | 700 | 0 | -252.81 | 169.69 | 0 | 0 | No
2030-04-14 02:00 | 2030 33% ECP | 700 | 0 | -252.81 | 181.32 | 0 | 0 | No
2030-04-14 03:00 | 2030 33% ECP | 700 | 0 | -210 | 91.24 | 0 | 0 | No
2030-04-14 04:00 | 2030 33% ECP | 700 | 0 | -510 | 86.36 | 0 | 0 | No
2030-04-14 05:00 | 2030 33% ECP | 700 | 0 | -210 | 90.87 | 0 | 0 | No
2030-04-14 06:00 | 2030 33% ECP | 700 | 0 | -398.91 | 166 | 0 | 0 | No
2030-04-14 07:00 | 2030 33% ECP | 560 | -226 | -510 | 196.15 | 0 | 0 | No
2030-04-14 08:00 | 2030 33% ECP | 140 | -526 | -510 | 140.05 | 0 | 0 | No
2030-04-14 09:00 | 2030 33% ECP | -280 | -526 | -510 | 82.21 | 0 | 0 | Yes
2030-04-14 10:00 | 2030 33% ECP | -700 | -526 | -510 | 99.34 | 0 | 0 | Yes
2030-04-14 11:00 | 2030 33% ECP | -700 | -526 | -510 | 62.86 | 0 | 0 | Yes
2030-04-14 12:00 | 2030 33% ECP | -700 | -526 | -510 | 115.22 | 0 | 0 | Yes
2030-04-14 13:00 | 2030 33% ECP | -700 | -526 | -510 | 57 | 0 | 0 | Yes
2030-04-14 14:00 | 2030 33% ECP | -700 | -526 | -510 | 90.32 | 0 | 0 | No
2030-04-14 15:00 | 2030 33% ECP | -280 | -526 | -510 | 94.72 | 0 | 0 | Yes
2030-04-14 16:00 | 2030 33% ECP | 140 | -526 | -510 | 187.3 | 0 | 0 | No
2030-04-14 17:00 | 2030 33% ECP | 560 | -526 | -510 | 270.08 | 0 | 0 | No
2030-04-14 18:00 | 2030 33% ECP | 700 | -226 | -210 | 331.96 | 0 | 0 | No
2030-04-14 19:00 | 2030 33% ECP | 700 | 0 | 0 | 397.42 | 0 | 0 | No
2030-04-14 20:00 | 2030 33% ECP | 700 | 0 | 0 | 367.2 | 0 | 0 | No
2030-04-14 21:00 | 2030 33% ECP | 700 | 0 | 296.54 | 359.7 | 0 | 0 | No
2030-04-14 22:00 | 2030 33% ECP | 700 | 0 | 510 | 252.41 | 0 | 0 | No
2030-04-14 23:00 | 2030 33% ECP | 700 | 0 | 210 | 147.65 | 0 | 0 | No
2030-04-15 | 2030 33% ECP | 700 | 0 | 210 | 88.91 | 0 | 0 | No
2030-04-15 01:00 | 2030 33% ECP | 700 | 0 | 278.61 | 83.85 | 0 | 0 | No
2030-04-15 02:00 | 2030 33% ECP | 700 | 0 | 67.31 | 89.69 | 0 | 0 | No
2030-04-15 03:00 | 2030 33% ECP | 700 | 0 | 367.31 | 79.94 | 0 | 0 | No
2030-04-15 04:00 | 2030 33% ECP | 700 | 0 | 232.53 | 53.62 | 0 | 0 | No
2030-04-15 05:00 | 2030 33% ECP | 700 | 0 | 376.39 | 70.04 | 0 | 0 | No
2030-04-15 06:00 | 2030 33% ECP | 700 | 0 | 76.39 | 154.6 | 0 | 0 | No
2030-04-15 07:00 | 2030 33% ECP | 700 | -226 | -210 | 249.36 | 0 | 0 | No
2030-04-15 08:00 | 2030 33% ECP | 700 | -526 | -510 | 272.29 | 0 | 0 | No
2030-04-15 09:00 | 2030 33% ECP | 280 | -526 | -510 | 242.45 | 0 | 0 | No
2030-04-15 10:00 | 2030 33% ECP | -140 | -526 | -510 | 207.98 | 0 | 0 | No
2030-04-15 11:00 | 2030 33% ECP | -560 | -526 | -510 | 203.13 | 0 | 0 | No
2030-04-15 12:00 | 2030 33% ECP | -700 | -526 | -510 | 207.77 | 0 | 0 | No
2030-04-15 13:00 | 2030 33% ECP | -621.27 | -526 | -510 | 175.3 | 0 | 0 | No
2030-04-15 14:00 | 2030 33% ECP | -201.27 | -526 | -510 | 151.87 | 0 | 0 | No
2030-04-15 15:00 | 2030 33% ECP | 218.73 | -526 | -510 | 178.35 | 0 | 0 | No
2030-04-15 16:00 | 2030 33% ECP | 638.73 | -526 | -510 | 279.41 | 0 | 0 | No
2030-04-15 17:00 | 2030 33% ECP | 700 | -526 | -510 | 426.04 | 0 | 0 | No
2030-04-15 18:00 | 2030 33% ECP | 700 | -226 | -210 | 402.94 | 0 | 0 | No
2030-04-15 19:00 | 2030 33% ECP | 700 | 0 | 0 | 351.76 | 0 | 0 | No
2030-04-15 20:00 | 2030 33% ECP | 700 | 0 | 0 | 310.4 | 0 | 0 | No
2030-04-15 21:00 | 2030 33% ECP | 700 | 0 | 0 | 374.15 | 0 | 0 | No
2030-04-15 22:00 | 2030 33% ECP | 700 | 0 | 0 | 266.82 | 0 | 0 | No
2030-04-15 23:00 | 2030 33% ECP | 700 | 0 | 0 | 41.37 | 0 | 0 | No
2030-04-16 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-16 01:00 | 2030 33% ECP | 700 | 0 | -287.65 | 0 | 0 | 0 | No
2030-04-16 02:00 | 2030 33% ECP | 700 | 0 | -29.97 | 0 | 0 | 0 | No
2030-04-16 03:00 | 2030 33% ECP | 700 | 0 | -329.97 | 0 | 0 | 0 | No
2030-04-16 04:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-16 05:00 | 2030 33% ECP | 575.86 | 0 | -449.58 | 0 | 0 | 0 | No
2030-04-16 06:00 | 2030 33% ECP | 155.86 | 0 | -391.2 | 0 | 0 | 0 | No
2030-04-16 07:00 | 2030 33% ECP | -264.14 | -226 | -268.14 | 141.79 | 0 | 0 | No
2030-04-16 08:00 | 2030 33% ECP | -684.14 | -526 | -510 | 226.34 | 0 | 0 | No
2030-04-16 09:00 | 2030 33% ECP | -700 | -526 | -510 | 187.14 | 0 | 0 | No
2030-04-16 10:00 | 2030 33% ECP | -700 | -526 | -510 | 97.7 | 0 | 0 | No
2030-04-16 11:00 | 2030 33% ECP | -700 | -526 | -510 | -40.79 | 0 | 0 | No
2030-04-16 12:00 | 2030 33% ECP | -700 | -526 | -510 | -253.41 | 0 | 0 | No
2030-04-16 13:00 | 2030 33% ECP | -700 | -526 | -510 | -371.53 | 0 | 0 | No
2030-04-16 14:00 | 2030 33% ECP | -700 | -526 | -510 | -371.89 | 0 | 0 | No
2030-04-16 15:00 | 2030 33% ECP | -700 | -526 | -510 | -358.18 | 0 | 0 | No
2030-04-16 16:00 | 2030 33% ECP | -700 | -526 | -510 | -58.18 | 0 | 0 | No
2030-04-16 17:00 | 2030 33% ECP | -280 | -226 | -510 | 240.57 | 0 | 0 | No
2030-04-16 18:00 | 2030 33% ECP | 0 | 0 | -345.02 | 308.78 | 0 | 0 | No
2030-04-16 19:00 | 2030 33% ECP | -259 | -300 | -510 | 178.75 | 0 | 0 | No
2030-04-16 20:00 | 2030 33% ECP | 161 | 0 | -460.55 | 0 | 0 | 0 | No
2030-04-16 21:00 | 2030 33% ECP | 581 | 0 | -405.18 | 0 | 0 | 0 | No
2030-04-16 22:00 | 2030 33% ECP | 700 | 0 | -105.18 | -61.14 | 0 | 0 | No
2030-04-16 23:00 | 2030 33% ECP | 700 | 0 | -405.18 | -310.66 | 0 | 0 | No
2030-04-17 | 2030 33% ECP | 700 | 0 | -360.55 | -10.66 | 0 | 0 | No
2030-04-17 01:00 | 2030 33% ECP | 700 | 0 | -510 | -22.57 | 0 | 0 | No
2030-04-17 02:00 | 2030 33% ECP | 700 | 0 | -367.73 | 0 | 0 | 0 | No
2030-04-17 03:00 | 2030 33% ECP | 700 | 0 | -463.91 | 0 | 0 | 0 | No
2030-04-17 04:00 | 2030 33% ECP | 700 | 0 | -510 | -100.35 | 0 | 0 | No
2030-04-17 05:00 | 2030 33% ECP | 700 | 0 | -510 | -207.76 | 0 | 0 | No
2030-04-17 06:00 | 2030 33% ECP | 280 | 0 | -487.65 | 0 | 0 | 0 | No
2030-04-17 07:00 | 2030 33% ECP | 60.14 | -226 | -510 | -50.16 | 0 | 0 | No
2030-04-17 08:00 | 2030 33% ECP | -359.86 | -526 | -510 | -350.16 | 0 | 0 | No
2030-04-17 09:00 | 2030 33% ECP | -700 | -526 | -510 | -171.31 | 0 | 0 | No
2030-04-17 10:00 | 2030 33% ECP | -700 | -526 | -510 | 83.72 | 0 | 0 | No
2030-04-17 11:00 | 2030 33% ECP | -280 | -526 | -510 | -216.28 | 0 | 0 | No
2030-04-17 12:00 | 2030 33% ECP | -700 | -526 | -510 | -260.89 | 0 | 0 | No
2030-04-17 13:00 | 2030 33% ECP | -700 | -526 | -510 | -375.01 | 0 | 0 | No
2030-04-17 14:00 | 2030 33% ECP | -700 | -526 | -510 | -229.83 | 0 | 0 | No
2030-04-17 15:00 | 2030 33% ECP | -700 | -526 | -510 | 29.45 | 0 | 0 | No
2030-04-17 16:00 | 2030 33% ECP | -700 | -526 | -510 | 83.08 | 0 | 0 | No
2030-04-17 17:00 | 2030 33% ECP | -280 | -519.12 | -510 | 311.35 | 0 | 0 | No
2030-04-17 18:00 | 2030 33% ECP | 140 | -338.91 | -510 | 92.03 | 0 | 0 | Yes
2030-04-17 19:00 | 2030 33% ECP | 0 | -38.91 | -510 | 392.03 | 0 | 0 | No
2030-04-17 20:00 | 2030 33% ECP | 159.27 | 0 | -510 | 467.63 | 0 | 0 | No
2030-04-17 21:00 | 2030 33% ECP | 579.27 | -2.84 | -510 | 167.63 | 0 | 0 | No
2030-04-17 22:00 | 2030 33% ECP | 700 | -156.98 | -510 | -132.37 | 0 | 0 | No
2030-04-17 23:00 | 2030 33% ECP | 700 | -456.98 | -510 | -227.64 | 0 | 0 | No
2030-04-18 | 2030 33% ECP | 700 | -156.98 | -510 | -510 | 0 | 0 | No
2030-04-18 01:00 | 2030 33% ECP | 700 | -32.2 | -510 | -363.63 | 0 | 0 | No
2030-04-18 02:00 | 2030 33% ECP | 700 | 0 | -510 | -63.63 | 0 | 0 | No
2030-04-18 03:00 | 2030 33% ECP | 700 | -175.37 | -510 | -63.63 | 0 | 0 | No
2030-04-18 04:00 | 2030 33% ECP | 420 | -158.39 | -510 | -76.05 | 0 | 0 | No
2030-04-18 05:00 | 2030 33% ECP | 0 | -36.9 | -510 | -336.34 | 0 | 0 | No
2030-04-18 06:00 | 2030 33% ECP | 0 | -36.9 | -510 | -254.37 | 0 | 0 | No
2030-04-18 07:00 | 2030 33% ECP | 0 | 0 | -510 | -57.15 | 0 | 0 | No
2030-04-18 08:00 | 2030 33% ECP | -280 | -300 | -510 | 0 | 0 | 0 | No
2030-04-18 09:00 | 2030 33% ECP | -700 | -526 | -510 | -9.22 | 0 | 0 | No
2030-04-18 10:00 | 2030 33% ECP | -700 | -526 | -510 | -128.89 | 0 | 0 | No
2030-04-18 11:00 | 2030 33% ECP | -700 | -526 | -510 | -81.58 | 0 | 0 | No
2030-04-18 12:00 | 2030 33% ECP | -700 | -526 | -510 | -221.86 | 0 | 0 | No
2030-04-18 13:00 | 2030 33% ECP | -700 | -526 | -510 | -374.45 | 0 | 0 | No
2030-04-18 14:00 | 2030 33% ECP | -700 | -526 | -510 | -74.45 | 0 | 0 | No
2030-04-18 15:00 | 2030 33% ECP | -385.76 | -526 | -510 | 19.82 | 0 | 0 | No
2030-04-18 16:00 | 2030 33% ECP | 34.24 | -503.92 | -510 | -128.16 | 0 | 0 | No
2030-04-18 17:00 | 2030 33% ECP | 454.24 | -237.22 | -510 | -128.16 | 0 | 0 | No
2030-04-18 18:00 | 2030 33% ECP | 34.24 | 0 | -510 | -428.16 | 0 | 0 | No
2030-04-18 19:00 | 2030 33% ECP | 34.3 | -201.83 | -510 | -510 | 0 | 0 | No
2030-04-18 20:00 | 2030 33% ECP | 454.3 | -501.83 | -510 | -336.96 | 0 | 0 | No
2030-04-18 21:00 | 2030 33% ECP | 700 | -300 | -461.04 | -300 | 0 | 0 | No
2030-04-18 22:00 | 2030 33% ECP | 700 | 0 | -161.04 | 0 | 0 | 0 | No
2030-04-18 23:00 | 2030 33% ECP | 700 | 0 | -461.04 | -33.6 | 0 | 0 | No
2030-04-19 | 2030 33% ECP | 675.72 | -300 | -510 | -333.6 | 0 | 0 | No
2030-04-19 01:00 | 2030 33% ECP | 700 | -163.97 | -510 | -505.77 | 0 | 0 | No
2030-04-19 02:00 | 2030 33% ECP | 700 | -381.74 | -510 | -510 | 0 | 0 | No
2030-04-19 03:00 | 2030 33% ECP | 700 | -81.74 | -510 | -307.33 | 0 | 0 | No
2030-04-19 04:00 | 2030 33% ECP | 700 | -381.74 | -510 | -510 | 0 | 0 | No
2030-04-19 05:00 | 2030 33% ECP | 643.42 | -431.08 | -510 | -274.9 | 0 | 0 | No
2030-04-19 06:00 | 2030 33% ECP | 223.42 | -222.86 | -510 | -162.33 | 0 | 0 | Yes
2030-04-19 07:00 | 2030 33% ECP | 0 | -299.89 | -510 | -460.03 | 0 | 0 | No
2030-04-19 08:00 | 2030 33% ECP | -401.57 | -526 | -510 | -160.03 | 0 | 0 | No
2030-04-19 09:00 | 2030 33% ECP | -700 | -526 | -510 | -326.74 | 0 | 0 | No
2030-04-19 10:00 | 2030 33% ECP | -700 | -526 | -510 | -489.9 | 0 | 0 | No
2030-04-19 11:00 | 2030 33% ECP | -700 | -526 | -510 | -419.61 | 0 | 0 | No
2030-04-19 12:00 | 2030 33% ECP | -700 | -526 | -510 | -190.23 | 0 | 0 | No
2030-04-19 13:00 | 2030 33% ECP | -700 | -526 | -510 | -490.23 | 0 | 0 | No
2030-04-19 14:00 | 2030 33% ECP | -700 | -526 | -510 | -353.65 | 0 | 0 | No
2030-04-19 15:00 | 2030 33% ECP | -700 | -526 | -510 | -105.77 | 0 | 0 | No
2030-04-19 16:00 | 2030 33% ECP | -700 | -526 | -510 | -53.72 | 0 | 0 | No
2030-04-19 17:00 | 2030 33% ECP | -384.86 | -526 | -510 | 82.31 | 0 | 0 | No
2030-04-19 18:00 | 2030 33% ECP | 35.14 | -445.87 | -510 | 233.96 | 0 | 0 | No
2030-04-19 19:00 | 2030 33% ECP | 455.14 | -302.17 | -510 | 177.15 | 0 | 0 | No
2030-04-19 20:00 | 2030 33% ECP | 700 | -302.17 | -510 | -114.05 | 0 | 0 | No
2030-04-19 21:00 | 2030 33% ECP | 700 | -2.17 | -210 | -0.33 | 0 | 0 | No
2030-04-19 22:00 | 2030 33% ECP | 700 | 179.49 | 90 | 144.94 | 0 | 0 | No
2030-04-19 23:00 | 2030 33% ECP | 700 | 479.49 | 390 | 444.94 | 0 | 0 | No
2030-04-20 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 05:00 | 2030 33% ECP | 280 | 205 | 210 | 210 | 0 | 0 | No
2030-04-20 06:00 | 2030 33% ECP | -140 | -95 | -90 | -90 | 0 | 0 | No
2030-04-20 07:00 | 2030 33% ECP | -560 | -395 | -390 | -390 | 0 | 0 | No
2030-04-20 08:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-20 09:00 | 2030 33% ECP | -700 | -526 | -510 | -323.53 | 0 | 0 | Yes
2030-04-20 10:00 | 2030 33% ECP | -700 | -226 | -210 | -23.53 | 0 | 0 | Yes
2030-04-20 11:00 | 2030 33% ECP | -700 | 74 | 90 | 276.47 | 0 | 0 | Yes
2030-04-20 12:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-04-20 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-20 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-20 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-20 16:00 | 2030 33% ECP | -700 | 223.53 | 210 | 510 | 0 | 0 | Yes
2030-04-20 17:00 | 2030 33% ECP | -700 | -76.47 | -90 | 510 | 0 | 0 | No
2030-04-20 18:00 | 2030 33% ECP | -700 | -376.47 | -390 | 297.66 | 0 | 0 | No
2030-04-20 19:00 | 2030 33% ECP | -468.25 | -95 | -90 | 47.91 | 0 | 0 | No
2030-04-20 20:00 | 2030 33% ECP | -48.25 | 205 | 210 | 210 | 0 | 0 | No
2030-04-20 21:00 | 2030 33% ECP | 371.75 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-21 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 02:00 | 2030 33% ECP | 700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-04-21 03:00 | 2030 33% ECP | 700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-04-21 04:00 | 2030 33% ECP | 691.53 | 505 | 510 | 300 | 0 | 0 | Yes
2030-04-21 05:00 | 2030 33% ECP | 271.53 | 505 | 510 | 365.12 | 0 | 0 | Yes
2030-04-21 06:00 | 2030 33% ECP | -148.47 | 505 | 510 | 65.12 | 0 | 0 | Yes
2030-04-21 07:00 | 2030 33% ECP | -568.47 | 505 | 510 | 65.12 | 0 | 0 | Yes
2030-04-21 08:00 | 2030 33% ECP | -700 | 505 | 510 | 365.12 | 0 | 0 | Yes
2030-04-21 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 16:00 | 2030 33% ECP | -639.54 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 17:00 | 2030 33% ECP | -219.54 | 505 | 510 | 510 | 0 | 0 | No
2030-04-21 18:00 | 2030 33% ECP | 200.46 | 362.89 | 510 | 510 | 0 | 0 | No
2030-04-21 19:00 | 2030 33% ECP | -55.13 | 62.89 | 210 | 210 | 0 | 0 | No
2030-04-21 20:00 | 2030 33% ECP | 364.87 | 205 | 510 | 456.96 | 0 | 0 | No
2030-04-21 21:00 | 2030 33% ECP | 700 | 505 | 510 | 388.39 | 0 | 0 | Yes
2030-04-21 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 23:00 | 2030 33% ECP | 700 | 505 | 510 | 274.7 | 0 | 0 | Yes
2030-04-22 | 2030 33% ECP | 700 | 505 | 510 | 276.69 | 0 | 0 | Yes
2030-04-22 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-22 02:00 | 2030 33% ECP | 700 | 505 | 510 | 300.33 | 0 | 0 | Yes
2030-04-22 03:00 | 2030 33% ECP | 700 | 505 | 510 | 0.33 | 0 | 0 | Yes
2030-04-22 04:00 | 2030 33% ECP | 700 | 505 | 510 | 222.3 | 0 | 0 | Yes
2030-04-22 05:00 | 2030 33% ECP | 700 | 505 | 510 | -5.97 | 0 | 0 | No
2030-04-22 06:00 | 2030 33% ECP | 658.76 | 505 | 510 | -5.97 | 0 | 0 | No
2030-04-22 07:00 | 2030 33% ECP | 238.76 | 286.39 | 210 | -5.97 | 0 | 0 | No
2030-04-22 08:00 | 2030 33% ECP | -181.24 | -13.61 | -90 | -305.97 | 0 | 0 | No
2030-04-22 09:00 | 2030 33% ECP | -601.24 | -313.61 | -390 | -301.12 | 0 | 0 | Yes
2030-04-22 10:00 | 2030 33% ECP | -700 | -13.61 | -318.35 | -1.12 | 0 | 0 | Yes
2030-04-22 11:00 | 2030 33% ECP | -700 | 0 | -41.2 | 0 | 0 | 0 | Yes
2030-04-22 12:00 | 2030 33% ECP | -700 | 300 | 258.8 | 300 | 0 | 0 | Yes
2030-04-22 13:00 | 2030 33% ECP | -700 | 0 | 390 | 320.19 | 0 | 0 | Yes
2030-04-22 14:00 | 2030 33% ECP | -700 | 252.13 | 90 | 510 | 0 | 0 | Yes
2030-04-22 15:00 | 2030 33% ECP | -280 | -47.87 | -210 | 510 | 0 | 0 | No
2030-04-22 16:00 | 2030 33% ECP | 140 | -347.87 | -510 | 276.44 | 0 | 0 | No
2030-04-22 17:00 | 2030 33% ECP | 280 | -432.82 | -510 | 0 | 0 | 0 | No
2030-04-22 18:00 | 2030 33% ECP | 700 | -132.82 | -510 | 0 | 0 | 0 | No
2030-04-22 19:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-22 20:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-22 21:00 | 2030 33% ECP | 700 | 0 | -510 | 300 | 0 | 0 | No
2030-04-22 22:00 | 2030 33% ECP | 700 | 0 | -460.77 | 300 | 0 | 0 | No
2030-04-22 23:00 | 2030 33% ECP | 700 | 0 | -460.77 | 0 | 0 | 0 | No
2030-04-23 | 2030 33% ECP | 700 | 0 | -460.77 | 0 | 0 | 0 | No
2030-04-23 01:00 | 2030 33% ECP | 700 | 0 | -446.58 | 0 | 0 | 0 | No
2030-04-23 02:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-23 03:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-23 04:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-23 05:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-23 06:00 | 2030 33% ECP | 280 | 0 | -510 | 0 | 0 | 0 | No
2030-04-23 07:00 | 2030 33% ECP | 0 | 0 | -510 | 0 | 0 | 0 | No
2030-04-23 08:00 | 2030 33% ECP | -280 | -226 | -510 | -127.89 | 0 | 0 | No
2030-04-23 09:00 | 2030 33% ECP | -700 | -526 | -510 | -127.89 | 0 | 0 | No
2030-04-23 10:00 | 2030 33% ECP | -700 | -526 | -510 | -224.73 | 0 | 0 | No
2030-04-23 11:00 | 2030 33% ECP | -700 | -526 | -510 | -126.88 | 0 | 0 | No
2030-04-23 12:00 | 2030 33% ECP | -700 | -526 | -510 | -214.15 | 0 | 0 | No
2030-04-23 13:00 | 2030 33% ECP | -700 | -526 | -510 | -174.13 | 0 | 0 | No
2030-04-23 14:00 | 2030 33% ECP | -700 | -526 | -510 | -184.45 | 0 | 0 | No
2030-04-23 15:00 | 2030 33% ECP | -294.88 | -526 | -510 | -141.62 | 0 | 0 | No
2030-04-23 16:00 | 2030 33% ECP | 125.12 | -526 | -510 | 0 | 0 | 0 | No
2030-04-23 17:00 | 2030 33% ECP | 545.12 | -465.34 | -510 | -300 | 0 | 0 | No
2030-04-23 18:00 | 2030 33% ECP | 700 | -165.34 | -510 | -355.97 | 0 | 0 | No
2030-04-23 19:00 | 2030 33% ECP | 385.25 | 0 | -510 | -443.55 | 0 | 0 | No
2030-04-23 20:00 | 2030 33% ECP | 0 | 0 | -510 | -310.33 | 0 | 0 | No
2030-04-23 21:00 | 2030 33% ECP | 385.69 | 0 | -300 | -298.46 | 0 | 0 | No
2030-04-23 22:00 | 2030 33% ECP | 700 | 0 | 0 | 1.54 | 0 | 0 | No
2030-04-23 23:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-24 | 2030 33% ECP | 700 | 0 | 300 | 300 | 0 | 0 | No
2030-04-24 01:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-04-24 02:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-04-24 03:00 | 2030 33% ECP | 700 | 0 | 390 | 510 | 0 | 0 | No
2030-04-24 04:00 | 2030 33% ECP | 451.79 | 0 | 90 | 210 | 0 | 0 | No
2030-04-24 05:00 | 2030 33% ECP | 31.79 | -226 | -210 | -90 | 0 | 0 | No
2030-04-24 06:00 | 2030 33% ECP | -388.21 | -526 | -510 | -13.3 | 0 | 0 | No
2030-04-24 07:00 | 2030 33% ECP | -700 | -526 | -510 | -313.3 | 0 | 0 | No
2030-04-24 08:00 | 2030 33% ECP | -700 | -526 | -510 | -54.02 | 0 | 0 | No
2030-04-24 09:00 | 2030 33% ECP | -700 | -526 | -510 | -187.36 | 0 | 0 | No
2030-04-24 10:00 | 2030 33% ECP | -700 | -526 | -510 | 112.64 | 0 | 0 | No
2030-04-24 11:00 | 2030 33% ECP | -700 | -526 | -510 | 412.64 | 0 | 0 | No
2030-04-24 12:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-24 13:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-24 14:00 | 2030 33% ECP | -700 | -526 | -510 | 300 | 0 | 0 | No
2030-04-24 15:00 | 2030 33% ECP | -280 | -526 | -510 | 0 | 0 | 0 | No
2030-04-24 16:00 | 2030 33% ECP | 140 | -526 | -510 | 105.54 | 0 | 0 | No
2030-04-24 17:00 | 2030 33% ECP | 560 | -525.86 | -510 | 243.26 | 0 | 0 | No
2030-04-24 18:00 | 2030 33% ECP | 700 | -226 | -316.17 | -56.74 | 0 | 0 | No
2030-04-24 19:00 | 2030 33% ECP | 700 | -526 | -510 | -356.74 | 0 | 0 | No
2030-04-24 20:00 | 2030 33% ECP | 700 | -226 | -210 | -56.74 | 0 | 0 | No
2030-04-24 21:00 | 2030 33% ECP | 700 | 0 | 0 | 229.88 | 0 | 0 | No
2030-04-24 22:00 | 2030 33% ECP | 700 | 0 | 42.74 | 141.64 | 0 | 0 | No
2030-04-24 23:00 | 2030 33% ECP | 700 | 96.96 | 342.74 | 441.64 | 0 | 0 | No
2030-04-25 | 2030 33% ECP | 700 | 396.96 | 510 | 510 | 0 | 0 | No
2030-04-25 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-25 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-25 03:00 | 2030 33% ECP | 700 | 505 | 393.23 | 510 | 0 | 0 | No
2030-04-25 04:00 | 2030 33% ECP | 700 | 300 | 93.23 | 300 | 0 | 0 | No
2030-04-25 05:00 | 2030 33% ECP | 280 | 0 | -206.77 | 0 | 0 | 0 | No
2030-04-25 06:00 | 2030 33% ECP | 0 | -300 | -506.77 | -255.51 | 0 | 0 | No
2030-04-25 07:00 | 2030 33% ECP | -150.55 | -526 | -510 | 0 | 0 | 0 | No
2030-04-25 08:00 | 2030 33% ECP | -570.55 | -526 | -510 | -246.51 | 0 | 0 | No
2030-04-25 09:00 | 2030 33% ECP | -700 | -526 | -510 | -159.33 | 0 | 0 | No
2030-04-25 10:00 | 2030 33% ECP | -700 | -526 | -510 | 123.99 | 0 | 0 | No
2030-04-25 11:00 | 2030 33% ECP | -700 | -526 | -510 | 423.99 | 0 | 0 | No
2030-04-25 12:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-25 13:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-25 14:00 | 2030 33% ECP | -700 | -526 | -510 | 232.99 | 0 | 0 | No
2030-04-25 15:00 | 2030 33% ECP | -351.31 | -526 | -510 | 396.09 | 0 | 0 | No
2030-04-25 16:00 | 2030 33% ECP | 68.69 | -526 | -510 | 96.09 | 0 | 0 | No
2030-04-25 17:00 | 2030 33% ECP | 488.69 | -504.49 | -510 | 205.67 | 0 | 0 | No
2030-04-25 18:00 | 2030 33% ECP | 700 | -226 | -210 | 45.34 | 0 | 0 | No
2030-04-25 19:00 | 2030 33% ECP | 700 | -526 | -510 | -254.66 | 0 | 0 | No
2030-04-25 20:00 | 2030 33% ECP | 700 | -462.37 | -510 | -168.85 | 0 | 0 | No
2030-04-25 21:00 | 2030 33% ECP | 700 | -162.37 | -210 | 131.15 | 0 | 0 | No
2030-04-25 22:00 | 2030 33% ECP | 700 | 0 | 90 | 428.69 | 0 | 0 | No
2030-04-25 23:00 | 2030 33% ECP | 700 | 0 | 301 | 128.69 | 0 | 0 | No
2030-04-26 | 2030 33% ECP | 700 | 300 | 510 | 428.69 | 0 | 0 | No
2030-04-26 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-26 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-26 03:00 | 2030 33% ECP | 700 | 374 | 390 | 390 | 0 | 0 | No
2030-04-26 04:00 | 2030 33% ECP | 700 | 74 | 90 | 90 | 0 | 0 | No
2030-04-26 05:00 | 2030 33% ECP | 280 | -226 | -210 | -210 | 0 | 0 | No
2030-04-26 06:00 | 2030 33% ECP | -140 | -526 | -510 | -510 | 0 | 0 | No
2030-04-26 07:00 | 2030 33% ECP | -267.05 | -526 | -510 | -510 | 0 | 0 | No
2030-04-26 08:00 | 2030 33% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-04-26 09:00 | 2030 33% ECP | 420 | -325.2 | -510 | -276.39 | 0 | 0 | No
2030-04-26 10:00 | 2030 33% ECP | 700 | -526 | -510 | -471.09 | 0 | 0 | No
2030-04-26 11:00 | 2030 33% ECP | 700 | -378.31 | -510 | -171.09 | 0 | 0 | No
2030-04-26 12:00 | 2030 33% ECP | 700 | -78.31 | -510 | -446.27 | 0 | 0 | No
2030-04-26 13:00 | 2030 33% ECP | 700 | 0 | -510 | -404.74 | 0 | 0 | No
2030-04-26 14:00 | 2030 33% ECP | 700 | -297.81 | -510 | -104.74 | 0 | 0 | No
2030-04-26 15:00 | 2030 33% ECP | 700 | 0 | -510 | -300 | 0 | 0 | No
2030-04-26 16:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-26 17:00 | 2030 33% ECP | 700 | 0 | -210 | -67.77 | 0 | 0 | No
2030-04-26 18:00 | 2030 33% ECP | 660.17 | -300 | -510 | -367.77 | 0 | 0 | No
2030-04-26 19:00 | 2030 33% ECP | 240.17 | -394.76 | -510 | -510 | 0 | 0 | Yes
2030-04-26 20:00 | 2030 33% ECP | 0 | -94.76 | -510 | -510 | 0 | 0 | No
2030-04-26 21:00 | 2030 33% ECP | 280 | -27.31 | -300 | -300 | 0 | 0 | No
2030-04-26 22:00 | 2030 33% ECP | 700 | 272.69 | 0 | 0 | 0 | 0 | No
2030-04-26 23:00 | 2030 33% ECP | 700 | 0 | -26.3 | 0 | 0 | 0 | No
2030-04-27 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 01:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 02:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 03:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 04:00 | 2030 33% ECP | 560 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 05:00 | 2030 33% ECP | 140 | -76.1 | -210 | -210 | 0 | 0 | No
2030-04-27 06:00 | 2030 33% ECP | -280 | -376.1 | -510 | -510 | 0 | 0 | No
2030-04-27 07:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-27 08:00 | 2030 33% ECP | -337.34 | -526 | -510 | -334.66 | 0 | 0 | No
2030-04-27 09:00 | 2030 33% ECP | -700 | -526 | -510 | -34.66 | 0 | 0 | No
2030-04-27 10:00 | 2030 33% ECP | -700 | -526 | -510 | -34.66 | 0 | 0 | No
2030-04-27 11:00 | 2030 33% ECP | -700 | -526 | -510 | -34.66 | 0 | 0 | No
2030-04-27 12:00 | 2030 33% ECP | -700 | -526 | -510 | -334.66 | 0 | 0 | No
2030-04-27 13:00 | 2030 33% ECP | -700 | -526 | -510 | -404.02 | 0 | 0 | No
2030-04-27 14:00 | 2030 33% ECP | -700 | -526 | -510 | -387.36 | 0 | 0 | No
2030-04-27 15:00 | 2030 33% ECP | -700 | -526 | -510 | -376.56 | 0 | 0 | No
2030-04-27 16:00 | 2030 33% ECP | -460.31 | -526 | -510 | -237.82 | 0 | 0 | No
2030-04-27 17:00 | 2030 33% ECP | -40.31 | -226 | -263.87 | -210 | 0 | 0 | No
2030-04-27 18:00 | 2030 33% ECP | 379.69 | -526 | -510 | -510 | 0 | 0 | No
2030-04-27 19:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-27 20:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-27 21:00 | 2030 33% ECP | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-04-27 22:00 | 2030 33% ECP | 700 | 0 | 90 | 29.31 | 0 | 0 | No
2030-04-27 23:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-28 | 2030 33% ECP | 700 | 0 | -174.86 | 0 | 0 | 0 | No
2030-04-28 01:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-28 02:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-28 03:00 | 2030 33% ECP | 700 | 0 | -179.87 | 0 | 0 | 0 | No
2030-04-28 04:00 | 2030 33% ECP | 700 | 0 | -149.56 | 0 | 0 | 0 | No
2030-04-28 05:00 | 2030 33% ECP | 700 | 0 | -39.89 | 0 | 0 | 0 | No
2030-04-28 06:00 | 2030 33% ECP | 700 | 0 | -230.88 | 0 | 0 | 0 | No
2030-04-28 07:00 | 2030 33% ECP | 700 | -248.86 | -510 | -111.1 | 0 | 0 | No
2030-04-28 08:00 | 2030 33% ECP | 700 | -526 | -510 | -157.71 | 0 | 0 | No
2030-04-28 09:00 | 2030 33% ECP | 280 | -526 | -510 | -218.43 | 0 | 0 | No
2030-04-28 10:00 | 2030 33% ECP | 0 | -526 | -510 | -272.87 | 0 | 0 | No
2030-04-28 11:00 | 2030 33% ECP | 0 | -526 | -510 | -226.25 | 0 | 0 | No
2030-04-28 12:00 | 2030 33% ECP | 0 | -526 | -510 | -241.25 | 0 | 0 | No
2030-04-28 13:00 | 2030 33% ECP | 0 | -526 | -510 | -207.73 | 0 | 0 | No
2030-04-28 14:00 | 2030 33% ECP | 273.73 | -526 | -510 | -302.37 | 0 | 0 | No
2030-04-28 15:00 | 2030 33% ECP | 280 | -526 | -510 | -153.43 | 0 | 0 | No
2030-04-28 16:00 | 2030 33% ECP | 700 | -526 | -510 | -139.23 | 0 | 0 | No
2030-04-28 17:00 | 2030 33% ECP | 700 | -526 | -510 | -8.88 | 0 | 0 | No
2030-04-28 18:00 | 2030 33% ECP | 700 | -286.72 | -510 | 35.28 | 0 | 0 | No
2030-04-28 19:00 | 2030 33% ECP | 700 | -526 | -510 | 62.37 | 0 | 0 | No
2030-04-28 20:00 | 2030 33% ECP | 700 | -226 | -510 | 151.73 | 0 | 0 | No
2030-04-28 21:00 | 2030 33% ECP | 700 | 0 | -510 | 136.7 | 0 | 0 | No
2030-04-28 22:00 | 2030 33% ECP | 700 | -226 | -510 | 60.43 | 0 | 0 | No
2030-04-28 23:00 | 2030 33% ECP | 700 | -526 | -510 | 84.6 | 0 | 0 | No
2030-04-29 | 2030 33% ECP | 700 | -397.3 | -510 | -101.23 | 0 | 0 | No
2030-04-29 01:00 | 2030 33% ECP | 700 | -526 | -510 | -144.22 | 0 | 0 | No
2030-04-29 02:00 | 2030 33% ECP | 700 | -526 | -510 | -121.39 | 0 | 0 | No
2030-04-29 03:00 | 2030 33% ECP | 700 | -526 | -510 | 49.37 | 0 | 0 | No
2030-04-29 04:00 | 2030 33% ECP | 700 | -526 | -510 | -187.91 | 0 | 0 | No
2030-04-29 05:00 | 2030 33% ECP | 700 | -526 | -510 | -107.2 | 0 | 0 | No
2030-04-29 06:00 | 2030 33% ECP | 700 | -526 | -510 | -64.96 | 0 | 0 | No
2030-04-29 07:00 | 2030 33% ECP | 700 | -526 | -510 | 10.31 | 0 | 0 | No
2030-04-29 08:00 | 2030 33% ECP | 700 | -526 | -510 | -157.83 | 0 | 0 | No
2030-04-29 09:00 | 2030 33% ECP | 700 | -526 | -510 | -61.51 | 0 | 0 | No
2030-04-29 10:00 | 2030 33% ECP | 700 | -526 | -510 | -361.51 | 0 | 0 | No
2030-04-29 11:00 | 2030 33% ECP | 700 | -526 | -510 | -114.05 | 0 | 0 | No
2030-04-29 12:00 | 2030 33% ECP | 700 | -226 | -210 | 185.95 | 0 | 0 | No
2030-04-29 13:00 | 2030 33% ECP | 362.24 | 74 | 90 | 485.95 | 0 | 0 | No
2030-04-29 14:00 | 2030 33% ECP | 280 | 374 | 390 | 510 | 0 | 0 | No
2030-04-29 15:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-29 16:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-29 17:00 | 2030 33% ECP | 700 | 222.5 | 510 | 510 | 0 | 0 | No
2030-04-29 18:00 | 2030 33% ECP | 700 | 454.38 | 510 | 510 | 0 | 0 | No
2030-04-29 19:00 | 2030 33% ECP | 700 | 154.38 | 210 | 510 | 0 | 0 | Yes
2030-04-29 20:00 | 2030 33% ECP | 700 | -145.62 | -90 | 510 | 0 | 0 | No
2030-04-29 21:00 | 2030 33% ECP | 700 | 154.38 | 210 | 510 | 0 | 0 | No
2030-04-29 22:00 | 2030 33% ECP | 700 | 454.38 | 510 | 510 | 0 | 0 | No
2030-04-29 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 06:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-04-30 07:00 | 2030 33% ECP | 700 | -95 | -90 | -90 | 0 | 0 | No
2030-04-30 08:00 | 2030 33% ECP | 700 | 50.88 | 210 | 210 | 0 | 0 | No
2030-04-30 09:00 | 2030 33% ECP | 700 | 350.88 | 510 | 510 | 0 | 0 | No
2030-04-30 10:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 11:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 12:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 13:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 14:00 | 2030 33% ECP | 700 | 300 | 264.98 | 510 | 0 | 0 | No
2030-04-30 15:00 | 2030 33% ECP | 700 | 0 | -35.02 | 493.09 | 0 | 0 | No
2030-04-30 16:00 | 2030 33% ECP | 700 | -300 | -335.02 | 193.09 | 0 | 0 | No
2030-04-30 17:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-30 18:00 | 2030 33% ECP | 700 | -226 | -495.14 | 0 | 0 | 0 | No
2030-04-30 19:00 | 2030 33% ECP | 700 | 0 | -495.14 | 300 | 0 | 0 | No
2030-04-30 20:00 | 2030 33% ECP | 700 | 0 | -195.14 | 510 | 0 | 0 | No
2030-04-30 21:00 | 2030 33% ECP | 700 | 0 | 0 | 477.41 | 0 | 0 | No
2030-04-30 22:00 | 2030 33% ECP | 700 | 0 | -182.21 | 375.36 | 0 | 0 | No
2030-04-30 23:00 | 2030 33% ECP | 700 | 0 | 117.79 | 510 | 0 | 0 | No
2030-05-01 | 2030 33% ECP | 700 | 300 | 417.79 | 510 | 0 | 0 | No
2030-05-01 01:00 | 2030 33% ECP | 700 | 398.36 | 510 | 510 | 0 | 0 | No
2030-05-01 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-01 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-01 04:00 | 2030 33% ECP | 700 | 382.36 | 390 | 510 | 0 | 0 | No
2030-05-01 05:00 | 2030 33% ECP | 700 | 82.36 | 90 | 510 | 0 | 0 | No
2030-05-01 06:00 | 2030 33% ECP | 700 | -217.64 | -210 | 510 | 0 | 0 | No
2030-05-01 07:00 | 2030 33% ECP | 594.94 | -517.64 | -510 | 510 | 0 | 0 | No
2030-05-01 08:00 | 2030 33% ECP | 174.94 | -526 | -510 | 510 | 0 | 0 | No
2030-05-01 09:00 | 2030 33% ECP | -245.06 | -526 | -510 | 510 | 0 | 0 | No
2030-05-01 10:00 | 2030 33% ECP | -665.06 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 11:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 12:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 13:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 14:00 | 2030 33% ECP | -700 | -526 | -510 | 475.94 | 0 | 0 | Yes
2030-05-01 15:00 | 2030 33% ECP | -615.03 | -526 | -510 | 175.94 | 0 | 0 | Yes
2030-05-01 16:00 | 2030 33% ECP | -195.03 | -526 | -510 | -124.06 | 0 | 0 | No
2030-05-01 17:00 | 2030 33% ECP | 224.97 | -526 | -510 | -128.68 | 0 | 0 | No
2030-05-01 18:00 | 2030 33% ECP | 644.97 | -526 | -510 | 171.32 | 0 | 0 | No
2030-05-01 19:00 | 2030 33% ECP | 700 | -526 | -510 | 471.32 | 0 | 0 | No
2030-05-01 20:00 | 2030 33% ECP | 700 | -226 | -510 | 510 | 0 | 0 | No
2030-05-01 21:00 | 2030 33% ECP | 700 | -226 | -510 | 510 | 0 | 0 | No
2030-05-01 22:00 | 2030 33% ECP | 700 | -151.22 | -510 | 510 | 0 | 0 | No
2030-05-01 23:00 | 2030 33% ECP | 700 | -29.4 | -510 | 360.77 | 0 | 0 | No
2030-05-02 | 2030 33% ECP | 700 | -43.45 | -210 | 274.19 | 0 | 0 | No
2030-05-02 01:00 | 2030 33% ECP | 700 | 0 | 90 | 210 | 0 | 0 | No
2030-05-02 02:00 | 2030 33% ECP | 700 | 300 | 390 | 510 | 0 | 0 | No
2030-05-02 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-02 04:00 | 2030 33% ECP | 700 | 421.39 | 495.64 | 510 | 0 | 0 | No
2030-05-02 05:00 | 2030 33% ECP | 700 | 121.39 | 195.64 | 267.96 | 0 | 0 | No
2030-05-02 06:00 | 2030 33% ECP | 605.51 | 0 | -104.36 | -32.04 | 0 | 0 | No
2030-05-02 07:00 | 2030 33% ECP | 185.51 | -226 | -404.36 | -79.1 | 0 | 0 | No
2030-05-02 08:00 | 2030 33% ECP | -234.49 | -526 | -510 | -262.97 | 0 | 0 | No
2030-05-02 09:00 | 2030 33% ECP | 185.51 | -526 | -510 | -88.99 | 0 | 0 | No
2030-05-02 10:00 | 2030 33% ECP | -234.49 | -526 | -510 | 211.01 | 0 | 0 | No
2030-05-02 11:00 | 2030 33% ECP | -654.49 | -526 | -510 | 286.75 | 0 | 0 | No
2030-05-02 12:00 | 2030 33% ECP | -700 | -526 | -510 | 227.77 | 0 | 0 | No
2030-05-02 13:00 | 2030 33% ECP | -700 | -526 | -510 | 185.42 | 0 | 0 | No
2030-05-02 14:00 | 2030 33% ECP | -700 | -526 | -510 | 219.23 | 0 | 0 | No
2030-05-02 15:00 | 2030 33% ECP | -700 | -526 | -510 | 338.37 | 0 | 0 | No
2030-05-02 16:00 | 2030 33% ECP | -280 | -517.31 | -510 | 38.37 | 0 | 0 | No
2030-05-02 17:00 | 2030 33% ECP | 140 | -217.31 | -288.45 | 145.83 | 0 | 0 | No
2030-05-02 18:00 | 2030 33% ECP | 560 | -226 | -431.03 | 0 | 0 | 0 | No
2030-05-02 19:00 | 2030 33% ECP | 700 | -526 | -510 | -300 | 0 | 0 | No
2030-05-02 20:00 | 2030 33% ECP | 700 | -526 | -510 | -198.99 | 0 | 0 | No
2030-05-02 21:00 | 2030 33% ECP | 700 | -226 | -210 | 101.01 | 0 | 0 | No
2030-05-02 22:00 | 2030 33% ECP | 700 | 0 | 90 | 146.04 | 0 | 0 | No
2030-05-02 23:00 | 2030 33% ECP | 700 | 0 | 169.85 | 11.54 | 0 | 0 | No
2030-05-03 | 2030 33% ECP | 700 | 0 | 323.49 | 59.22 | 0 | 0 | No
2030-05-03 01:00 | 2030 33% ECP | 700 | 0 | 32.39 | 59.22 | 0 | 0 | No
2030-05-03 02:00 | 2030 33% ECP | 700 | 0 | -67.05 | 3.07 | 0 | 0 | No
2030-05-03 03:00 | 2030 33% ECP | 700 | 0 | -34.38 | 3.07 | 0 | 0 | No
2030-05-03 04:00 | 2030 33% ECP | 700 | 0 | -334.38 | 3.07 | 0 | 0 | No
2030-05-03 05:00 | 2030 33% ECP | 700 | 0 | -378.04 | 0 | 0 | 0 | No
2030-05-03 06:00 | 2030 33% ECP | 416.49 | 0 | -317.69 | 0 | 0 | 0 | No
2030-05-03 07:00 | 2030 33% ECP | -3.51 | -226 | -210 | 129.34 | 0 | 0 | No
2030-05-03 08:00 | 2030 33% ECP | -423.51 | -526 | -510 | 97.96 | 0 | 0 | No
2030-05-03 09:00 | 2030 33% ECP | -700 | -526 | -510 | 76.04 | 0 | 0 | No
2030-05-03 10:00 | 2030 33% ECP | -700 | -526 | -510 | 11.84 | 0 | 0 | No
2030-05-03 11:00 | 2030 33% ECP | -700 | -526 | -510 | 93.07 | 0 | 0 | No
2030-05-03 12:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-03 13:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-03 14:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-03 15:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-03 16:00 | 2030 33% ECP | -362.33 | -526 | -510 | 7.24 | 0 | 0 | No
2030-05-03 17:00 | 2030 33% ECP | 57.67 | -526 | -510 | -125.93 | 0 | 0 | No
2030-05-03 18:00 | 2030 33% ECP | 477.67 | -526 | -510 | -425.93 | 0 | 0 | No
2030-05-03 19:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-05-03 20:00 | 2030 33% ECP | 700 | -526 | -510 | -330.95 | 0 | 0 | No
2030-05-03 21:00 | 2030 33% ECP | 700 | -226 | -210 | -30.95 | 0 | 0 | No
2030-05-03 22:00 | 2030 33% ECP | 700 | 0 | 90 | 268.31 | 0 | 0 | No
2030-05-03 23:00 | 2030 33% ECP | 700 | 0 | -1.58 | 0 | 0 | 0 | No
2030-05-04 | 2030 33% ECP | 700 | -35.14 | -301.58 | -300 | 0 | 0 | No
2030-05-04 01:00 | 2030 33% ECP | 700 | 0 | -510 | -291.39 | 0 | 0 | No
2030-05-04 02:00 | 2030 33% ECP | 700 | 0 | -510 | -220.75 | 0 | 0 | No
2030-05-04 03:00 | 2030 33% ECP | 700 | -229.64 | -510 | -247.64 | 0 | 0 | No
2030-05-04 04:00 | 2030 33% ECP | 623.88 | -520.48 | -510 | -234.11 | 0 | 0 | No
2030-05-04 05:00 | 2030 33% ECP | 203.88 | -520.48 | -510 | -286.61 | 0 | 0 | No
2030-05-04 06:00 | 2030 33% ECP | -216.12 | -520.48 | -510 | -312.29 | 0 | 0 | No
2030-05-04 07:00 | 2030 33% ECP | -636.12 | -526 | -510 | -259.7 | 0 | 0 | No
2030-05-04 08:00 | 2030 33% ECP | -700 | -526 | -510 | 40.12 | 0 | 0 | No
2030-05-04 09:00 | 2030 33% ECP | -700 | -526 | -510 | -75.5 | 0 | 0 | Yes
2030-05-04 10:00 | 2030 33% ECP | -700 | -526 | -510 | -214.04 | 0 | 0 | Yes
2030-05-04 11:00 | 2030 33% ECP | -700 | -526 | -510 | -194.42 | 0 | 0 | Yes
2030-05-04 12:00 | 2030 33% ECP | -700 | -526 | -510 | 18.43 | 0 | 0 | Yes
2030-05-04 13:00 | 2030 33% ECP | -700 | -526 | -510 | -34.85 | 0 | 0 | Yes
2030-05-04 14:00 | 2030 33% ECP | -700 | -526 | -510 | -275.08 | 0 | 0 | Yes
2030-05-04 15:00 | 2030 33% ECP | -700 | -526 | -510 | -300.08 | 0 | 0 | Yes
2030-05-04 16:00 | 2030 33% ECP | -700 | -526 | -510 | -260.7 | 0 | 0 | Yes
2030-05-04 17:00 | 2030 33% ECP | -408.83 | -526 | -510 | -309.52 | 0 | 0 | Yes
2030-05-04 18:00 | 2030 33% ECP | 11.17 | -526 | -510 | -246.84 | 0 | 0 | No
2030-05-04 19:00 | 2030 33% ECP | 431.17 | -526 | -510 | -220.64 | 0 | 0 | No
2030-05-04 20:00 | 2030 33% ECP | 700 | -526 | -510 | -196.3 | 0 | 0 | No
2030-05-04 21:00 | 2030 33% ECP | 700 | -526 | -510 | -172.62 | 0 | 0 | No
2030-05-04 22:00 | 2030 33% ECP | 700 | -526 | -510 | -409.38 | 0 | 0 | No
2030-05-04 23:00 | 2030 33% ECP | 700 | -226 | -210 | -109.38 | 0 | 0 | No
2030-05-05 | 2030 33% ECP | 280 | 0 | -373.63 | 106.48 | 0 | 0 | No
2030-05-05 01:00 | 2030 33% ECP | -86.61 | 0 | -163.84 | 285.5 | 0 | 0 | No
2030-05-05 02:00 | 2030 33% ECP | -506.61 | 0 | 0 | 83.55 | 0 | 0 | No
2030-05-05 03:00 | 2030 33% ECP | -698.86 | 0 | 0 | 0 | 0 | 0 | No
2030-05-05 04:00 | 2030 33% ECP | -700 | 0 | 0 | 37.65 | 0 | 0 | No
2030-05-05 05:00 | 2030 33% ECP | -672.94 | -14.53 | -300 | -73.72 | 0 | 0 | No
2030-05-05 06:00 | 2030 33% ECP | -700 | -314.53 | -510 | -213.83 | 0 | 0 | No
2030-05-05 07:00 | 2030 33% ECP | -700 | -526 | -510 | -319.68 | 0 | 0 | Yes
2030-05-05 08:00 | 2030 33% ECP | -700 | -526 | -510 | -383.97 | 0 | 0 | Yes
2030-05-05 09:00 | 2030 33% ECP | -700 | -526 | -510 | -83.97 | 0 | 0 | Yes
2030-05-05 10:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-05 11:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-05 12:00 | 2030 33% ECP | -700 | -526 | -510 | -103.9 | 0 | 0 | Yes
2030-05-05 13:00 | 2030 33% ECP | -700 | -526 | -510 | -287.17 | 0 | 0 | Yes
2030-05-05 14:00 | 2030 33% ECP | -700 | -526 | -510 | -340.74 | 0 | 0 | Yes
2030-05-05 15:00 | 2030 33% ECP | -700 | -526 | -510 | -341.73 | 0 | 0 | Yes
2030-05-05 16:00 | 2030 33% ECP | -700 | -526 | -510 | -115.51 | 0 | 0 | Yes
2030-05-05 17:00 | 2030 33% ECP | -700 | -526 | -510 | 18.26 | 0 | 0 | Yes
2030-05-05 18:00 | 2030 33% ECP | -700 | -526 | -510 | 72.59 | 0 | 0 | No
2030-05-05 19:00 | 2030 33% ECP | -651.44 | -526 | -510 | 354.44 | 0 | 0 | No
2030-05-05 20:00 | 2030 33% ECP | -257.16 | -526 | -510 | 326.99 | 0 | 0 | No
2030-05-05 21:00 | 2030 33% ECP | -450.04 | -526 | -510 | 209.58 | 0 | 0 | No
2030-05-05 22:00 | 2030 33% ECP | -585.68 | -526 | -510 | 2.52 | 0 | 0 | No
2030-05-05 23:00 | 2030 33% ECP | -683.04 | -526 | -510 | 203.35 | 0 | 0 | No
2030-05-06 | 2030 33% ECP | -436.5 | -526 | -510 | 173.39 | 0 | 0 | No
2030-05-06 01:00 | 2030 33% ECP | -31.71 | -526 | -510 | 10.4 | 0 | 0 | No
2030-05-06 02:00 | 2030 33% ECP | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-05-06 03:00 | 2030 33% ECP | 280 | -526 | -510 | 64.8 | 0 | 0 | No
2030-05-06 04:00 | 2030 33% ECP | 700 | -526 | -510 | -14.72 | 0 | 0 | No
2030-05-06 05:00 | 2030 33% ECP | 700 | -526 | -510 | -84.84 | 0 | 0 | No
2030-05-06 06:00 | 2030 33% ECP | 560 | -526 | -510 | 62.5 | 0 | 0 | No
2030-05-06 07:00 | 2030 33% ECP | 140 | -526 | -510 | 57.07 | 0 | 0 | No
2030-05-06 08:00 | 2030 33% ECP | -280 | -526 | -510 | 160.37 | 0 | 0 | Yes
2030-05-06 09:00 | 2030 33% ECP | -700 | -526 | -510 | 122.1 | 0 | 0 | Yes
2030-05-06 10:00 | 2030 33% ECP | -700 | -526 | -510 | 10.91 | 0 | 0 | Yes
2030-05-06 11:00 | 2030 33% ECP | -700 | -526 | -510 | -65.22 | 0 | 0 | Yes
2030-05-06 12:00 | 2030 33% ECP | -700 | -526 | -510 | -43.31 | 0 | 0 | Yes
2030-05-06 13:00 | 2030 33% ECP | -700 | -526 | -510 | -28.11 | 0 | 0 | Yes
2030-05-06 14:00 | 2030 33% ECP | -700 | -526 | -510 | -27.19 | 0 | 0 | Yes
2030-05-06 15:00 | 2030 33% ECP | -700 | -526 | -510 | -56.92 | 0 | 0 | Yes
2030-05-06 16:00 | 2030 33% ECP | -641.57 | -526 | -510 | 229.5 | 0 | 0 | Yes
2030-05-06 17:00 | 2030 33% ECP | -221.57 | -526 | -510 | 394.81 | 0 | 0 | No
2030-05-06 18:00 | 2030 33% ECP | 198.43 | -526 | -510 | 468.79 | 0 | 0 | No
2030-05-06 19:00 | 2030 33% ECP | -89.51 | -526 | -510 | 510 | 0 | 0 | No
2030-05-06 20:00 | 2030 33% ECP | -89.51 | -526 | -510 | 299.63 | 0 | 0 | No
2030-05-06 21:00 | 2030 33% ECP | 0 | -526 | -510 | 366.7 | 0 | 0 | No
2030-05-06 22:00 | 2030 33% ECP | 280 | -526 | -510 | 332.45 | 0 | 0 | No
2030-05-06 23:00 | 2030 33% ECP | 700 | -526 | -510 | 249.11 | 0 | 0 | No
2030-05-07 | 2030 33% ECP | 291.54 | -526 | -510 | 228.74 | 0 | 0 | No
2030-05-07 01:00 | 2030 33% ECP | 700 | -526 | -510 | 234.25 | 0 | 0 | No
2030-05-07 02:00 | 2030 33% ECP | 326.69 | -526 | -510 | 175.51 | 0 | 0 | No
2030-05-07 03:00 | 2030 33% ECP | 444.17 | -526 | -510 | 162.38 | 0 | 0 | No
2030-05-07 04:00 | 2030 33% ECP | 24.17 | -526 | -510 | 173.69 | 0 | 0 | No
2030-05-07 05:00 | 2030 33% ECP | 214.42 | -526 | -510 | 182.17 | 0 | 0 | No
2030-05-07 06:00 | 2030 33% ECP | 0 | -526 | -510 | 208.09 | 0 | 0 | No
2030-05-07 07:00 | 2030 33% ECP | 280 | -526 | -510 | 334.52 | 0 | 0 | No
2030-05-07 08:00 | 2030 33% ECP | 700 | -526 | -510 | 407.03 | 0 | 0 | No
2030-05-07 09:00 | 2030 33% ECP | 498.85 | -526 | -510 | 311.95 | 0 | 0 | No
2030-05-07 10:00 | 2030 33% ECP | 400.15 | -526 | -510 | 292.16 | 0 | 0 | No
2030-05-07 11:00 | 2030 33% ECP | 0 | -526 | -510 | 234.29 | 0 | 0 | No
2030-05-07 12:00 | 2030 33% ECP | 179.03 | -526 | -510 | 105.28 | 0 | 0 | No
2030-05-07 13:00 | 2030 33% ECP | 162.23 | -526 | -510 | 65.74 | 0 | 0 | No
2030-05-07 14:00 | 2030 33% ECP | 204.53 | -526 | -510 | -3.91 | 0 | 0 | No
2030-05-07 15:00 | 2030 33% ECP | 624.53 | -526 | -510 | -30.8 | 0 | 0 | No
2030-05-07 16:00 | 2030 33% ECP | 700 | -526 | -510 | 190.3 | 0 | 0 | No
2030-05-07 17:00 | 2030 33% ECP | 700 | -526 | -510 | 359.12 | 0 | 0 | No
2030-05-07 18:00 | 2030 33% ECP | 700 | -226 | -225.39 | 322.65 | 0 | 0 | No
2030-05-07 19:00 | 2030 33% ECP | 700 | 0 | -225.39 | 402.7 | 0 | 0 | No
2030-05-07 20:00 | 2030 33% ECP | 700 | -45.26 | -510 | 382.43 | 0 | 0 | No
2030-05-07 21:00 | 2030 33% ECP | 700 | 0 | -215.11 | 488.3 | 0 | 0 | No
2030-05-07 22:00 | 2030 33% ECP | 700 | 0 | 0 | 499.8 | 0 | 0 | No
2030-05-07 23:00 | 2030 33% ECP | 700 | 0 | 0 | 291.9 | 0 | 0 | No
2030-05-08 | 2030 33% ECP | 700 | 0 | 57.89 | 0 | 0 | 0 | No
2030-05-08 01:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-08 02:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-08 03:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-08 04:00 | 2030 33% ECP | 700 | 0 | 104.91 | 0 | 0 | 0 | No
2030-05-08 05:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-08 06:00 | 2030 33% ECP | 700 | 0 | -53.61 | 13.06 | 0 | 0 | No
2030-05-08 07:00 | 2030 33% ECP | 700 | -300 | -353.61 | 32.02 | 0 | 0 | No
2030-05-08 08:00 | 2030 33% ECP | 700 | -526 | -510 | 88.55 | 0 | 0 | No
2030-05-08 09:00 | 2030 33% ECP | 280 | -526 | -510 | 82.62 | 0 | 0 | No
2030-05-08 10:00 | 2030 33% ECP | 0 | -526 | -510 | 14.73 | 0 | 0 | No
2030-05-08 11:00 | 2030 33% ECP | 0 | -526 | -510 | 6.5 | 0 | 0 | No
2030-05-08 12:00 | 2030 33% ECP | -238.42 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 13:00 | 2030 33% ECP | 0 | -526 | -510 | 107.72 | 0 | 0 | No
2030-05-08 14:00 | 2030 33% ECP | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 15:00 | 2030 33% ECP | 280 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 16:00 | 2030 33% ECP | 700 | -526 | -510 | 75.54 | 0 | 0 | No
2030-05-08 17:00 | 2030 33% ECP | 700 | -526 | -510 | -95.09 | 0 | 0 | No
2030-05-08 18:00 | 2030 33% ECP | 700 | -526 | -510 | -334.72 | 0 | 0 | No
2030-05-08 19:00 | 2030 33% ECP | 700 | -526 | -510 | -34.72 | 0 | 0 | No
2030-05-08 20:00 | 2030 33% ECP | 700 | -526 | -510 | -73.65 | 0 | 0 | No
2030-05-08 21:00 | 2030 33% ECP | 700 | -300 | -396.52 | -73.65 | 0 | 0 | No
2030-05-08 22:00 | 2030 33% ECP | 700 | 0 | -96.52 | 211.3 | 0 | 0 | No
2030-05-08 23:00 | 2030 33% ECP | 700 | 0 | 203.48 | 51.3 | 0 | 0 | No
2030-05-09 | 2030 33% ECP | 700 | 0 | -20.89 | 0 | 0 | 0 | No
2030-05-09 01:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-09 02:00 | 2030 33% ECP | 700 | 0 | -220.39 | 0 | 0 | 0 | No
2030-05-09 03:00 | 2030 33% ECP | 700 | 0 | -287.73 | 0 | 0 | 0 | No
2030-05-09 04:00 | 2030 33% ECP | 700 | 0 | -223.37 | 0 | 0 | 0 | No
2030-05-09 05:00 | 2030 33% ECP | 585.66 | 0 | -414.55 | 0 | 0 | 0 | No
2030-05-09 06:00 | 2030 33% ECP | 165.66 | -226 | -174.82 | 0 | 0 | 0 | No
2030-05-09 07:00 | 2030 33% ECP | -254.34 | -526 | 0 | -186.89 | 0 | 0 | No
2030-05-09 08:00 | 2030 33% ECP | -674.34 | -526 | 0 | 104.48 | 0 | 0 | No
2030-05-09 09:00 | 2030 33% ECP | -700 | -526 | 0 | 87.38 | 0 | 0 | No
2030-05-09 10:00 | 2030 33% ECP | -280 | -526 | 0 | 52.09 | 0 | 0 | No
2030-05-09 11:00 | 2030 33% ECP | 0 | -526 | 0 | 69.33 | 0 | 0 | No
2030-05-09 12:00 | 2030 33% ECP | -52.55 | -526 | 0 | 80.43 | 0 | 0 | No
2030-05-09 13:00 | 2030 33% ECP | -52.55 | -526 | 0 | 50.64 | 0 | 0 | No
2030-05-09 14:00 | 2030 33% ECP | -71.77 | -526 | 0 | 38.79 | 0 | 0 | No
2030-05-09 15:00 | 2030 33% ECP | 0 | -526 | 0 | 92.74 | 0 | 0 | No
2030-05-09 16:00 | 2030 33% ECP | 44.41 | -526 | 0 | 204.95 | 0 | 0 | No
2030-05-09 17:00 | 2030 33% ECP | 63.91 | -526 | 0 | 161.95 | 0 | 0 | No
2030-05-09 18:00 | 2030 33% ECP | 483.91 | -471.52 | 0 | -74.79 | 0 | 0 | No
2030-05-09 19:00 | 2030 33% ECP | 700 | -471.52 | 0 | 10.05 | 0 | 0 | No
2030-05-09 20:00 | 2030 33% ECP | 700 | -171.52 | 0 | 126.91 | 0 | 0 | No
2030-05-09 21:00 | 2030 33% ECP | 700 | -207.93 | 0 | 33.23 | 0 | 0 | No
2030-05-09 22:00 | 2030 33% ECP | 700 | -507.93 | 0 | -111.21 | 0 | 0 | No
2030-05-09 23:00 | 2030 33% ECP | 700 | -526 | 0 | 188.36 | 0 | 0 | No
2030-05-10 | 2030 33% ECP | 280 | -526 | 0 | 90.69 | 0 | 0 | No
2030-05-10 01:00 | 2030 33% ECP | -140 | -252.97 | 0 | -6.37 | 0 | 0 | No
2030-05-10 02:00 | 2030 33% ECP | 280 | 47.03 | 0 | 210 | 0 | 0 | No
2030-05-10 03:00 | 2030 33% ECP | 700 | 347.03 | 0 | 510 | 0 | 0 | No
2030-05-10 04:00 | 2030 33% ECP | 518.26 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 05:00 | 2030 33% ECP | 114.83 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 06:00 | 2030 33% ECP | -286.4 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 07:00 | 2030 33% ECP | -597.12 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 08:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 09:00 | 2030 33% ECP | -700 | 505 | 0 | 449.93 | 0 | 0 | Yes
2030-05-10 10:00 | 2030 33% ECP | -700 | 505 | 0 | 149.93 | 0 | 0 | Yes
2030-05-10 11:00 | 2030 33% ECP | -700 | 505 | 0 | 338.56 | 0 | 0 | Yes
2030-05-10 12:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 13:00 | 2030 33% ECP | -700 | 505 | 0 | 363.6 | 0 | 0 | Yes
2030-05-10 14:00 | 2030 33% ECP | -700 | 505 | 0 | 211.8 | 0 | 0 | Yes
2030-05-10 15:00 | 2030 33% ECP | -700 | 505 | 0 | 444.36 | 0 | 0 | Yes
2030-05-10 16:00 | 2030 33% ECP | -700 | 505 | 0 | 502.23 | 0 | 0 | Yes
2030-05-10 17:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 18:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 19:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 20:00 | 2030 33% ECP | -280 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 21:00 | 2030 33% ECP | 0 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 22:00 | 2030 33% ECP | 0 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 23:00 | 2030 33% ECP | 0 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 | 2030 33% ECP | 0 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 01:00 | 2030 33% ECP | 420 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 02:00 | 2030 33% ECP | 670.94 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 03:00 | 2030 33% ECP | 670.94 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 04:00 | 2030 33% ECP | 545.51 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 05:00 | 2030 33% ECP | 125.51 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 06:00 | 2030 33% ECP | -280 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 07:00 | 2030 33% ECP | -700 | 505 | 300 | 510 | 0 | 0 | Yes
2030-05-11 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 14:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-05-11 15:00 | 2030 33% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-05-11 16:00 | 2030 33% ECP | -607.27 | -226 | -210 | 327.67 | 0 | 0 | Yes
2030-05-11 17:00 | 2030 33% ECP | -187.27 | -526 | -510 | 27.67 | 0 | 0 | No
2030-05-11 18:00 | 2030 33% ECP | 232.73 | -526 | -510 | 0 | 0 | 0 | No
2030-05-11 19:00 | 2030 33% ECP | 652.73 | -226 | -510 | 0 | 0 | 0 | No
2030-05-11 20:00 | 2030 33% ECP | 700 | 0 | -510 | 82.8 | 0 | 0 | No
2030-05-11 21:00 | 2030 33% ECP | 700 | 0 | -390 | 382.8 | 0 | 0 | No
2030-05-11 22:00 | 2030 33% ECP | 700 | 0 | -90 | 137.65 | 0 | 0 | No
2030-05-11 23:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-05-12 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 06:00 | 2030 33% ECP | 560 | 300 | 300 | 510 | 0 | 0 | No
2030-05-12 07:00 | 2030 33% ECP | 140 | 0 | 0 | 510 | 0 | 0 | No
2030-05-12 08:00 | 2030 33% ECP | -280 | -300 | -300 | 224.84 | 0 | 0 | Yes
2030-05-12 09:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-12 10:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-12 11:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-12 12:00 | 2030 33% ECP | -700 | -526 | -510 | -262.38 | 0 | 0 | Yes
2030-05-12 13:00 | 2030 33% ECP | -700 | -526 | -510 | -468.71 | 0 | 0 | Yes
2030-05-12 14:00 | 2030 33% ECP | -700 | -526 | -510 | -168.71 | 0 | 0 | No
2030-05-12 15:00 | 2030 33% ECP | -280 | -526 | -510 | -455.89 | 0 | 0 | No
2030-05-12 16:00 | 2030 33% ECP | 140 | -526 | -510 | -380.63 | 0 | 0 | No
2030-05-12 17:00 | 2030 33% ECP | 560 | -526 | -510 | -474.7 | 0 | 0 | No
2030-05-12 18:00 | 2030 33% ECP | 700 | -226 | -510 | -174.7 | 0 | 0 | No
2030-05-12 19:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-05-12 20:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-05-12 21:00 | 2030 33% ECP | 700 | 0 | -421.29 | -143.25 | 0 | 0 | No
2030-05-12 22:00 | 2030 33% ECP | 700 | 0 | -121.29 | 0 | 0 | 0 | No
2030-05-12 23:00 | 2030 33% ECP | 700 | 115.08 | 178.71 | 210 | 0 | 0 | No
2030-05-13 | 2030 33% ECP | 700 | 415.08 | 478.71 | 510 | 0 | 0 | No
2030-05-13 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 06:00 | 2030 33% ECP | 560 | 374 | 476.87 | 510 | 0 | 0 | No
2030-05-13 07:00 | 2030 33% ECP | 140 | 74 | 176.87 | 510 | 0 | 0 | No
2030-05-13 08:00 | 2030 33% ECP | -280 | -226 | -123.13 | 510 | 0 | 0 | No
2030-05-13 09:00 | 2030 33% ECP | -700 | -526 | -423.13 | 510 | 0 | 0 | Yes
2030-05-13 10:00 | 2030 33% ECP | -700 | -431.34 | -510 | 510 | 0 | 0 | Yes
2030-05-13 11:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 12:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 13:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 14:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 15:00 | 2030 33% ECP | -700 | -322.41 | -510 | 510 | 0 | 0 | Yes
2030-05-13 16:00 | 2030 33% ECP | -280 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 17:00 | 2030 33% ECP | 140 | -526 | -510 | 510 | 0 | 0 | No
2030-05-13 18:00 | 2030 33% ECP | 560 | -526 | -510 | 469.05 | 0 | 0 | No
2030-05-13 19:00 | 2030 33% ECP | 700 | -226 | -510 | 383.68 | 0 | 0 | No
2030-05-13 20:00 | 2030 33% ECP | 700 | 0 | -510 | 462.26 | 0 | 0 | No
2030-05-13 21:00 | 2030 33% ECP | 700 | 0 | -277.13 | 483.88 | 0 | 0 | No
2030-05-13 22:00 | 2030 33% ECP | 700 | 0 | -510 | 483.88 | 0 | 0 | No
2030-05-13 23:00 | 2030 33% ECP | 700 | 0 | -406.29 | 391.93 | 0 | 0 | No
2030-05-14 | 2030 33% ECP | 700 | 0 | -510 | 91.93 | 0 | 0 | No
2030-05-14 01:00 | 2030 33% ECP | 700 | 0 | -510 | 115.47 | 0 | 0 | No
2030-05-14 02:00 | 2030 33% ECP | 700 | 0 | -471.9 | 93.9 | 0 | 0 | No
2030-05-14 03:00 | 2030 33% ECP | 700 | 0 | -171.9 | 102.78 | 0 | 0 | No
2030-05-14 04:00 | 2030 33% ECP | 700 | 0 | -171.9 | 100.07 | 0 | 0 | No
2030-05-14 05:00 | 2030 33% ECP | 700 | 0 | -471.9 | 98.81 | 0 | 0 | No
2030-05-14 06:00 | 2030 33% ECP | 700 | -226 | -510 | 144.47 | 0 | 0 | No
2030-05-14 07:00 | 2030 33% ECP | 700 | -526 | -510 | 387.45 | 0 | 0 | No
2030-05-14 08:00 | 2030 33% ECP | 280 | -526 | -510 | 306.1 | 0 | 0 | No
2030-05-14 09:00 | 2030 33% ECP | -7.94 | -526 | -510 | 312.87 | 0 | 0 | No
2030-05-14 10:00 | 2030 33% ECP | -427.94 | -526 | -510 | 251.58 | 0 | 0 | No
2030-05-14 11:00 | 2030 33% ECP | -572.23 | -526 | -510 | 64.09 | 0 | 0 | No
2030-05-14 12:00 | 2030 33% ECP | -700 | -526 | -510 | -62.7 | 0 | 0 | No
2030-05-14 13:00 | 2030 33% ECP | -700 | -526 | -510 | -130.59 | 0 | 0 | No
2030-05-14 14:00 | 2030 33% ECP | -560 | -526 | -510 | 68.87 | 0 | 0 | No
2030-05-14 15:00 | 2030 33% ECP | -140 | -526 | -510 | -53.32 | 0 | 0 | No
2030-05-14 16:00 | 2030 33% ECP | 280 | -526 | -510 | -219.72 | 0 | 0 | No
2030-05-14 17:00 | 2030 33% ECP | 700 | -526 | -510 | 68.38 | 0 | 0 | No
2030-05-14 18:00 | 2030 33% ECP | 700 | -526 | -510 | 92.17 | 0 | 0 | No
2030-05-14 19:00 | 2030 33% ECP | 700 | -226 | -210 | 0 | 0 | 0 | No
2030-05-14 20:00 | 2030 33% ECP | 700 | 0 | 0 | 130.51 | 0 | 0 | No
2030-05-14 21:00 | 2030 33% ECP | 700 | 0 | 0 | 257.59 | 0 | 0 | No
2030-05-14 22:00 | 2030 33% ECP | 700 | 0 | 0 | 280.58 | 0 | 0 | No
2030-05-14 23:00 | 2030 33% ECP | 700 | 0 | 0 | 149.54 | 0 | 0 | No
2030-05-15 | 2030 33% ECP | 700 | 0 | 0 | 81.54 | 0 | 0 | No
2030-05-15 01:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-15 02:00 | 2030 33% ECP | 700 | 0 | 0 | 125.13 | 0 | 0 | No
2030-05-15 03:00 | 2030 33% ECP | 700 | 0 | 164.64 | 113.79 | 0 | 0 | No
2030-05-15 04:00 | 2030 33% ECP | 700 | 0 | 10.66 | 81.1 | 0 | 0 | No
2030-05-15 05:00 | 2030 33% ECP | 700 | 0 | 90 | 87.92 | 0 | 0 | No
2030-05-15 06:00 | 2030 33% ECP | 700 | -226 | -210 | 0 | 0 | 0 | No
2030-05-15 07:00 | 2030 33% ECP | 700 | -526 | -510 | 141.49 | 0 | 0 | No
2030-05-15 08:00 | 2030 33% ECP | 568.13 | -526 | -510 | 173.4 | 0 | 0 | No
2030-05-15 09:00 | 2030 33% ECP | 148.13 | -526 | -510 | -60.14 | 0 | 0 | No
2030-05-15 10:00 | 2030 33% ECP | -169.88 | -526 | -510 | -139.13 | 0 | 0 | No
2030-05-15 11:00 | 2030 33% ECP | -158.48 | -526 | -510 | -215.91 | 0 | 0 | No
2030-05-15 12:00 | 2030 33% ECP | -420 | -526 | -510 | -302.67 | 0 | 0 | No
2030-05-15 13:00 | 2030 33% ECP | 0 | -526 | -510 | -208.06 | 0 | 0 | No
2030-05-15 14:00 | 2030 33% ECP | 76.47 | -526 | -510 | -291.2 | 0 | 0 | No
2030-05-15 15:00 | 2030 33% ECP | 496.47 | -526 | -510 | -80.64 | 0 | 0 | No
2030-05-15 16:00 | 2030 33% ECP | 700 | -526 | -510 | 55.16 | 0 | 0 | No
2030-05-15 17:00 | 2030 33% ECP | 700 | -474.63 | -510 | 174.56 | 0 | 0 | No
2030-05-15 18:00 | 2030 33% ECP | 700 | -174.63 | -210 | 360.68 | 0 | 0 | No
2030-05-15 19:00 | 2030 33% ECP | 700 | 0 | 90 | 412.51 | 0 | 0 | No
2030-05-15 20:00 | 2030 33% ECP | 700 | 0 | 286.77 | 404.36 | 0 | 0 | No
2030-05-15 21:00 | 2030 33% ECP | 700 | 0 | 337.82 | 418.21 | 0 | 0 | No
2030-05-15 22:00 | 2030 33% ECP | 700 | 0 | 37.82 | 259.13 | 0 | 0 | No
2030-05-15 23:00 | 2030 33% ECP | 700 | 0 | 337.82 | 115.32 | 0 | 0 | No
2030-05-16 | 2030 33% ECP | 700 | 0 | 148.24 | 29.05 | 0 | 0 | No
2030-05-16 01:00 | 2030 33% ECP | 700 | 0 | 210 | 13.45 | 0 | 0 | No
2030-05-16 02:00 | 2030 33% ECP | 700 | 0 | 510 | 238.06 | 0 | 0 | No
2030-05-16 03:00 | 2030 33% ECP | 700 | 0 | 510 | 339.04 | 0 | 0 | No
2030-05-16 04:00 | 2030 33% ECP | 700 | 0 | 421.64 | 75.78 | 0 | 0 | No
2030-05-16 05:00 | 2030 33% ECP | 700 | 0 | 121.64 | 0 | 0 | 0 | No
2030-05-16 06:00 | 2030 33% ECP | 700 | 0 | -178.36 | 0 | 0 | 0 | No
2030-05-16 07:00 | 2030 33% ECP | 700 | -229.67 | -478.36 | 138.98 | 0 | 0 | No
2030-05-16 08:00 | 2030 33% ECP | 700 | -526 | -510 | 290.64 | 0 | 0 | No
2030-05-16 09:00 | 2030 33% ECP | 700 | -526 | -510 | 240.84 | 0 | 0 | No
2030-05-16 10:00 | 2030 33% ECP | 700 | -305.92 | -510 | 510 | 0 | 0 | No
2030-05-16 11:00 | 2030 33% ECP | 700 | -525.73 | -510 | 510 | 0 | 0 | No
2030-05-16 12:00 | 2030 33% ECP | 700 | -526 | -510 | 340.62 | 0 | 0 | No
2030-05-16 13:00 | 2030 33% ECP | 700 | -526 | -510 | 128.36 | 0 | 0 | No
2030-05-16 14:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-16 15:00 | 2030 33% ECP | 700 | -526 | -510 | 196.94 | 0 | 0 | No
2030-05-16 16:00 | 2030 33% ECP | 700 | -226 | -409.25 | 395.8 | 0 | 0 | No
2030-05-16 17:00 | 2030 33% ECP | 700 | 0 | -145.87 | 408.31 | 0 | 0 | No
2030-05-16 18:00 | 2030 33% ECP | 700 | 0 | 0 | 444.63 | 0 | 0 | No
2030-05-16 19:00 | 2030 33% ECP | 700 | 0 | 0 | 407.01 | 0 | 0 | No
2030-05-16 20:00 | 2030 33% ECP | 700 | 0 | 0 | 385.62 | 0 | 0 | No
2030-05-16 21:00 | 2030 33% ECP | 700 | 0 | 0 | 388.66 | 0 | 0 | No
2030-05-16 22:00 | 2030 33% ECP | 700 | 0 | 0 | 340.05 | 0 | 0 | No
2030-05-16 23:00 | 2030 33% ECP | 700 | 0 | 0 | 219.54 | 0 | 0 | No
2030-05-17 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-17 01:00 | 2030 33% ECP | 700 | 0 | -251.32 | 150.68 | 0 | 0 | No
2030-05-17 02:00 | 2030 33% ECP | 700 | -103.81 | -510 | 0 | 0 | 0 | No
2030-05-17 03:00 | 2030 33% ECP | 700 | -190.85 | -510 | 130.43 | 0 | 0 | No
2030-05-17 04:00 | 2030 33% ECP | 700 | -442.43 | -510 | 118.28 | 0 | 0 | No
2030-05-17 05:00 | 2030 33% ECP | 329.62 | -526 | -510 | 0 | 0 | 0 | No
2030-05-17 06:00 | 2030 33% ECP | 439.77 | -526 | -510 | 180.62 | 0 | 0 | No
2030-05-17 07:00 | 2030 33% ECP | 581.13 | -526 | -510 | 297.41 | 0 | 0 | No
2030-05-17 08:00 | 2030 33% ECP | 700 | -526 | -510 | 439.71 | 0 | 0 | No
2030-05-17 09:00 | 2030 33% ECP | 700 | -526 | -510 | 471.06 | 0 | 0 | No
2030-05-17 10:00 | 2030 33% ECP | 351.29 | -226 | -210 | 510 | 0 | 0 | No
2030-05-17 11:00 | 2030 33% ECP | 247.94 | 0 | 0 | 510 | 0 | 0 | No
2030-05-17 12:00 | 2030 33% ECP | 0 | 300 | 300 | 510 | 0 | 0 | No
2030-05-17 13:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-05-17 14:00 | 2030 33% ECP | 0 | 505 | 477.8 | 510 | 0 | 0 | No
2030-05-17 15:00 | 2030 33% ECP | 280 | 205 | 177.8 | 510 | 0 | 0 | No
2030-05-17 16:00 | 2030 33% ECP | 700 | -95 | -122.2 | 366.41 | 0 | 0 | No
2030-05-17 17:00 | 2030 33% ECP | 700 | -395 | -422.2 | 366.41 | 0 | 0 | No
2030-05-17 18:00 | 2030 33% ECP | 280 | -526 | -510 | 114.05 | 0 | 0 | No
2030-05-17 19:00 | 2030 33% ECP | -140 | -526 | -510 | 100.07 | 0 | 0 | No
2030-05-17 20:00 | 2030 33% ECP | -445.18 | -526 | -510 | 283.27 | 0 | 0 | No
2030-05-17 21:00 | 2030 33% ECP | -25.18 | -526 | -510 | 418.44 | 0 | 0 | No
2030-05-17 22:00 | 2030 33% ECP | -25.18 | -395 | -493.59 | 427.85 | 0 | 0 | No
2030-05-17 23:00 | 2030 33% ECP | -140 | -95 | -193.59 | 278.7 | 0 | 0 | No
2030-05-18 | 2030 33% ECP | 280 | 138.88 | 106.41 | 444.92 | 0 | 0 | No
2030-05-18 01:00 | 2030 33% ECP | 700 | 438.88 | 406.41 | 510 | 0 | 0 | No
2030-05-18 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 05:00 | 2030 33% ECP | 434.66 | 213.13 | 210 | 510 | 0 | 0 | No
2030-05-18 06:00 | 2030 33% ECP | 14.66 | -86.87 | -90 | 218.28 | 0 | 0 | No
2030-05-18 07:00 | 2030 33% ECP | 410.57 | 205 | 210 | 510 | 0 | 0 | No
2030-05-18 08:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 09:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 10:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 11:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 12:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 13:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 14:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 15:00 | 2030 33% ECP | 700 | 505 | 488.88 | 510 | 0 | 0 | No
2030-05-18 16:00 | 2030 33% ECP | 700 | 205 | 188.88 | 280.5 | 0 | 0 | No
2030-05-18 17:00 | 2030 33% ECP | 700 | -95 | -111.12 | 510 | 0 | 0 | No
2030-05-18 18:00 | 2030 33% ECP | 700 | -395 | -411.12 | 510 | 0 | 0 | No
2030-05-18 19:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-18 20:00 | 2030 33% ECP | 700 | -501.17 | -510 | 510 | 0 | 0 | No
2030-05-18 21:00 | 2030 33% ECP | 700 | -501.17 | -510 | 479.81 | 0 | 0 | No
2030-05-18 22:00 | 2030 33% ECP | 700 | -526 | -510 | 179.81 | 0 | 0 | No
2030-05-18 23:00 | 2030 33% ECP | 700 | -526 | -510 | 90.57 | 0 | 0 | No
2030-05-19 | 2030 33% ECP | 700 | -228.01 | -259.63 | 90.57 | 0 | 0 | No
2030-05-19 01:00 | 2030 33% ECP | 700 | 0 | 40.37 | 341.58 | 0 | 0 | No
2030-05-19 02:00 | 2030 33% ECP | 700 | 300 | 340.37 | 510 | 0 | 0 | No
2030-05-19 03:00 | 2030 33% ECP | 700 | 86.41 | 300 | 510 | 0 | 0 | No
2030-05-19 04:00 | 2030 33% ECP | 700 | 0 | 0 | 273.2 | 0 | 0 | No
2030-05-19 05:00 | 2030 33% ECP | 700 | -233.17 | -300 | -6.83 | 0 | 0 | No
2030-05-19 06:00 | 2030 33% ECP | 700 | -54.39 | -510 | 64.68 | 0 | 0 | No
2030-05-19 07:00 | 2030 33% ECP | 700 | -354.39 | -510 | 75.89 | 0 | 0 | No
2030-05-19 08:00 | 2030 33% ECP | 700 | -526 | -510 | 75.89 | 0 | 0 | No
2030-05-19 09:00 | 2030 33% ECP | 593.68 | -526 | -510 | 0 | 0 | 0 | No
2030-05-19 10:00 | 2030 33% ECP | 173.68 | -526 | -510 | -47.95 | 0 | 0 | No
2030-05-19 11:00 | 2030 33% ECP | -95.33 | -526 | -510 | 9.68 | 0 | 0 | No
2030-05-19 12:00 | 2030 33% ECP | -237.19 | -526 | -510 | 39.31 | 0 | 0 | No
2030-05-19 13:00 | 2030 33% ECP | 0 | -526 | -510 | 284.89 | 0 | 0 | No
2030-05-19 14:00 | 2030 33% ECP | -181.31 | -526 | -510 | 335.44 | 0 | 0 | No
2030-05-19 15:00 | 2030 33% ECP | 238.69 | -526 | -510 | 290.71 | 0 | 0 | No
2030-05-19 16:00 | 2030 33% ECP | 658.69 | -526 | -510 | 290.71 | 0 | 0 | No
2030-05-19 17:00 | 2030 33% ECP | 700 | -526 | -510 | 430.49 | 0 | 0 | No
2030-05-19 18:00 | 2030 33% ECP | 700 | -526 | -510 | 434.43 | 0 | 0 | No
2030-05-19 19:00 | 2030 33% ECP | 700 | -226 | -510 | 249.77 | 0 | 0 | No
2030-05-19 20:00 | 2030 33% ECP | 700 | 0 | -510 | 88.57 | 0 | 0 | No
2030-05-19 21:00 | 2030 33% ECP | 700 | 0 | -510 | 88.57 | 0 | 0 | No
2030-05-19 22:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-05-19 23:00 | 2030 33% ECP | 700 | 0 | -510 | -115.68 | 0 | 0 | No
2030-05-20 | 2030 33% ECP | 700 | 0 | -510 | -25.42 | 0 | 0 | No
2030-05-20 01:00 | 2030 33% ECP | 700 | -96.02 | -510 | -14.67 | 0 | 0 | No
2030-05-20 02:00 | 2030 33% ECP | 700 | -396.02 | -510 | 13.33 | 0 | 0 | No
2030-05-20 03:00 | 2030 33% ECP | 700 | -526 | -510 | -0.81 | 0 | 0 | No
2030-05-20 04:00 | 2030 33% ECP | 700 | -526 | -510 | -143.23 | 0 | 0 | No
2030-05-20 05:00 | 2030 33% ECP | 700 | -526 | -510 | -48.59 | 0 | 0 | No
2030-05-20 06:00 | 2030 33% ECP | 420 | -526 | -510 | 40.52 | 0 | 0 | No
2030-05-20 07:00 | 2030 33% ECP | 0 | -526 | -510 | 128.07 | 0 | 0 | No
2030-05-20 08:00 | 2030 33% ECP | -420 | -526 | -510 | 10.58 | 0 | 0 | Yes
2030-05-20 09:00 | 2030 33% ECP | -700 | -526 | -510 | -81.61 | 0 | 0 | Yes
2030-05-20 10:00 | 2030 33% ECP | -700 | -526 | -510 | 158.42 | 0 | 0 | Yes
2030-05-20 11:00 | 2030 33% ECP | -700 | -526 | -510 | -62.67 | 0 | 0 | Yes
2030-05-20 12:00 | 2030 33% ECP | -700 | -526 | -510 | 237.33 | 0 | 0 | Yes
2030-05-20 13:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-20 14:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-20 15:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-20 16:00 | 2030 33% ECP | -700 | -526 | -510 | 439.87 | 0 | 0 | Yes
2030-05-20 17:00 | 2030 33% ECP | -365.59 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-20 18:00 | 2030 33% ECP | 54.41 | -226 | -472.43 | 510 | 0 | 0 | No
2030-05-20 19:00 | 2030 33% ECP | -142.32 | -395 | -390 | 510 | 0 | 0 | No
2030-05-20 20:00 | 2030 33% ECP | -40.52 | -95 | -90 | 510 | 0 | 0 | No
2030-05-20 21:00 | 2030 33% ECP | 280 | 205 | 210 | 510 | 0 | 0 | No
2030-05-20 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-20 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-21 | 2030 33% ECP | 700 | 317.98 | 510 | 510 | 0 | 0 | No
2030-05-21 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-21 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-21 03:00 | 2030 33% ECP | 700 | 328.13 | 510 | 510 | 0 | 0 | No
2030-05-21 04:00 | 2030 33% ECP | 700 | 28.13 | 210 | 319.25 | 0 | 0 | No
2030-05-21 05:00 | 2030 33% ECP | 700 | 0 | -90 | 214.66 | 0 | 0 | No
2030-05-21 06:00 | 2030 33% ECP | 700 | 0 | -390 | 300.73 | 0 | 0 | No
2030-05-21 07:00 | 2030 33% ECP | 561.62 | -234.48 | -510 | 348.13 | 0 | 0 | No
2030-05-21 08:00 | 2030 33% ECP | 141.62 | -526 | -510 | 354.82 | 0 | 0 | No
2030-05-21 09:00 | 2030 33% ECP | -278.38 | -526 | -510 | 436.86 | 0 | 0 | No
2030-05-21 10:00 | 2030 33% ECP | -698.38 | -526 | -510 | 455.1 | 0 | 0 | Yes
2030-05-21 11:00 | 2030 33% ECP | -700 | -526 | -510 | 465.7 | 0 | 0 | Yes
2030-05-21 12:00 | 2030 33% ECP | -700 | -526 | -510 | 477.03 | 0 | 0 | Yes
2030-05-21 13:00 | 2030 33% ECP | -700 | -526 | -510 | 350.87 | 0 | 0 | Yes
2030-05-21 14:00 | 2030 33% ECP | -700 | -526 | -510 | 62.22 | 0 | 0 | Yes
2030-05-21 15:00 | 2030 33% ECP | -700 | -526 | -510 | -237.78 | 0 | 0 | Yes
2030-05-21 16:00 | 2030 33% ECP | -700 | -526 | -510 | -95.47 | 0 | 0 | Yes
2030-05-21 17:00 | 2030 33% ECP | -700 | -526 | -510 | 7.42 | 0 | 0 | No
2030-05-21 18:00 | 2030 33% ECP | -595.95 | -526 | -510 | -292.58 | 0 | 0 | No
2030-05-21 19:00 | 2030 33% ECP | -595.95 | -526 | -510 | 7.42 | 0 | 0 | No
2030-05-21 20:00 | 2030 33% ECP | -700 | -526 | -510 | 217.22 | 0 | 0 | No
2030-05-21 21:00 | 2030 33% ECP | -700 | -526 | -510 | -82.78 | 0 | 0 | No
2030-05-21 22:00 | 2030 33% ECP | -700 | -226 | -210 | -156.73 | 0 | 0 | No
2030-05-21 23:00 | 2030 33% ECP | -700 | 74 | 90 | 143.27 | 0 | 0 | Yes
2030-05-22 | 2030 33% ECP | -700 | 374 | 390 | 347.41 | 0 | 0 | Yes
2030-05-22 01:00 | 2030 33% ECP | -700 | 505 | 510 | 47.41 | 0 | 0 | Yes
2030-05-22 02:00 | 2030 33% ECP | -700 | 505 | 510 | 6.25 | 0 | 0 | Yes
2030-05-22 03:00 | 2030 33% ECP | -700 | 505 | 510 | 156.59 | 0 | 0 | Yes
2030-05-22 04:00 | 2030 33% ECP | -700 | 505 | 510 | 334.76 | 0 | 0 | Yes
2030-05-22 05:00 | 2030 33% ECP | -700 | 505 | 510 | 209.12 | 0 | 0 | Yes
2030-05-22 06:00 | 2030 33% ECP | -700 | 505 | 510 | 124.06 | 0 | 0 | Yes
2030-05-22 07:00 | 2030 33% ECP | -700 | 505 | 510 | 226.15 | 0 | 0 | Yes
2030-05-22 08:00 | 2030 33% ECP | -700 | 505 | 510 | 308.24 | 0 | 0 | Yes
2030-05-22 09:00 | 2030 33% ECP | -700 | 505 | 510 | 288.52 | 0 | 0 | Yes
2030-05-22 10:00 | 2030 33% ECP | -700 | 505 | 510 | 207.73 | 0 | 0 | Yes
2030-05-22 11:00 | 2030 33% ECP | -700 | 505 | 510 | 164.85 | 0 | 0 | Yes
2030-05-22 12:00 | 2030 33% ECP | -700 | 505 | 510 | 146.94 | 0 | 0 | Yes
2030-05-22 13:00 | 2030 33% ECP | -700 | 505 | 510 | 114.71 | 0 | 0 | Yes
2030-05-22 14:00 | 2030 33% ECP | -700 | 505 | 510 | 102.01 | 0 | 0 | Yes
2030-05-22 15:00 | 2030 33% ECP | -700 | 505 | 510 | 112.27 | 0 | 0 | Yes
2030-05-22 16:00 | 2030 33% ECP | -700 | 505 | 510 | 221.95 | 0 | 0 | Yes
2030-05-22 17:00 | 2030 33% ECP | -700 | 505 | 510 | 303.07 | 0 | 0 | Yes
2030-05-22 18:00 | 2030 33% ECP | -700 | 505 | 510 | 331.54 | 0 | 0 | Yes
2030-05-22 19:00 | 2030 33% ECP | -700 | 505 | 510 | 324.83 | 0 | 0 | Yes
2030-05-22 20:00 | 2030 33% ECP | -700 | 505 | 510 | 293.18 | 0 | 0 | Yes
2030-05-22 21:00 | 2030 33% ECP | -700 | 505 | 510 | 505.1 | 0 | 0 | Yes
2030-05-22 22:00 | 2030 33% ECP | -700 | 505 | 510 | 456.95 | 0 | 0 | Yes
2030-05-22 23:00 | 2030 33% ECP | -700 | 505 | 510 | 246.33 | 0 | 0 | Yes
2030-05-23 | 2030 33% ECP | -700 | 505 | 510 | 443.01 | 0 | 0 | Yes
2030-05-23 01:00 | 2030 33% ECP | -700 | 505 | 510 | 268.55 | 0 | 0 | Yes
2030-05-23 02:00 | 2030 33% ECP | -700 | 505 | 510 | 30.27 | 0 | 0 | Yes
2030-05-23 03:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-05-23 04:00 | 2030 33% ECP | -700 | 505 | 510 | 30.24 | 0 | 0 | Yes
2030-05-23 05:00 | 2030 33% ECP | -700 | 505 | 510 | -103.5 | 0 | 0 | Yes
2030-05-23 06:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-05-23 07:00 | 2030 33% ECP | -700 | 505 | 510 | 139.82 | 0 | 0 | Yes
2030-05-23 08:00 | 2030 33% ECP | -700 | 505 | 510 | 264.98 | 0 | 0 | Yes
2030-05-23 09:00 | 2030 33% ECP | -700 | 505 | 510 | 304.71 | 0 | 0 | Yes
2030-05-23 10:00 | 2030 33% ECP | -700 | 505 | 510 | 281.55 | 0 | 0 | Yes
2030-05-23 11:00 | 2030 33% ECP | -700 | 505 | 510 | 289.41 | 0 | 0 | Yes
2030-05-23 12:00 | 2030 33% ECP | -700 | 505 | 510 | 295.98 | 0 | 0 | Yes
2030-05-23 13:00 | 2030 33% ECP | -700 | 505 | 510 | 252.77 | 0 | 0 | Yes
2030-05-23 14:00 | 2030 33% ECP | -700 | 505 | 510 | 204.25 | 0 | 0 | Yes
2030-05-23 15:00 | 2030 33% ECP | -700 | 505 | 510 | 274.77 | 0 | 0 | Yes
2030-05-23 16:00 | 2030 33% ECP | -700 | 505 | 510 | 429.33 | 0 | 0 | Yes
2030-05-23 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-23 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-23 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-23 20:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-23 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-23 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-23 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 14:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-05-24 15:00 | 2030 33% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-05-24 16:00 | 2030 33% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-05-24 17:00 | 2030 33% ECP | -280 | -526 | -510 | 484.48 | 0 | 0 | No
2030-05-24 18:00 | 2030 33% ECP | -215.24 | -526 | -510 | 510 | 0 | 0 | No
2030-05-24 19:00 | 2030 33% ECP | 204.76 | -300 | -510 | 510 | 0 | 0 | No
2030-05-24 20:00 | 2030 33% ECP | 624.76 | 0 | -510 | 510 | 0 | 0 | No
2030-05-24 21:00 | 2030 33% ECP | 700 | -48.01 | -510 | 510 | 0 | 0 | No
2030-05-24 22:00 | 2030 33% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-05-24 23:00 | 2030 33% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-05-25 | 2030 33% ECP | 381.69 | -300 | -510 | 377.94 | 0 | 0 | No
2030-05-25 01:00 | 2030 33% ECP | 700 | -526 | -510 | 399.86 | 0 | 0 | No
2030-05-25 02:00 | 2030 33% ECP | 582.24 | -526 | 0 | 242.3 | 0 | 0 | No
2030-05-25 03:00 | 2030 33% ECP | 620.08 | -526 | 0 | 327.49 | 0 | 0 | No
2030-05-25 04:00 | 2030 33% ECP | 351.23 | -526 | 0 | 341.19 | 0 | 0 | No
2030-05-25 05:00 | 2030 33% ECP | -68.77 | -526 | 0 | 173.12 | 0 | 0 | No
2030-05-25 06:00 | 2030 33% ECP | -488.77 | -526 | 0 | 345.16 | 0 | 0 | No
2030-05-25 07:00 | 2030 33% ECP | -700 | -526 | 0 | 268.26 | 0 | 0 | Yes
2030-05-25 08:00 | 2030 33% ECP | -700 | -526 | 0 | -31.74 | 0 | 0 | Yes
2030-05-25 09:00 | 2030 33% ECP | -700 | -526 | 0 | 0 | 0 | 0 | Yes
2030-05-25 10:00 | 2030 33% ECP | -700 | -526 | 0 | -131.96 | 0 | 0 | Yes
2030-05-25 11:00 | 2030 33% ECP | -700 | -526 | 0 | -360.86 | 0 | 0 | Yes
2030-05-25 12:00 | 2030 33% ECP | -700 | -526 | 0 | -109.04 | 0 | 0 | Yes
2030-05-25 13:00 | 2030 33% ECP | -700 | -526 | 0 | -150.18 | 0 | 0 | Yes
2030-05-25 14:00 | 2030 33% ECP | -700 | -526 | 0 | -51.44 | 0 | 0 | Yes
2030-05-25 15:00 | 2030 33% ECP | -564.79 | -526 | 0 | 167.39 | 0 | 0 | Yes
2030-05-25 16:00 | 2030 33% ECP | -144.79 | -526 | 0 | 310.24 | 0 | 0 | No
2030-05-25 17:00 | 2030 33% ECP | 275.21 | -526 | 0 | 300 | 0 | 0 | No
2030-05-25 18:00 | 2030 33% ECP | 695.21 | -526 | 0 | 0 | 0 | 0 | No
2030-05-25 19:00 | 2030 33% ECP | 700 | -526 | 0 | 300 | 0 | 0 | No
2030-05-25 20:00 | 2030 33% ECP | 700 | -526 | 0 | 287.81 | 0 | 0 | No
2030-05-25 21:00 | 2030 33% ECP | 700 | -392.01 | 0 | -12.19 | 0 | 0 | No
2030-05-25 22:00 | 2030 33% ECP | 700 | -216.46 | 0 | 287.81 | 0 | 0 | No
2030-05-25 23:00 | 2030 33% ECP | 700 | -377.56 | 0 | 350.13 | 0 | 0 | No
2030-05-26 | 2030 33% ECP | 700 | -377.56 | 0 | 50.13 | 0 | 0 | No
2030-05-26 01:00 | 2030 33% ECP | 700 | -526 | 0 | -45.6 | 0 | 0 | No
2030-05-26 02:00 | 2030 33% ECP | 700 | -274.17 | 0 | -68.86 | 0 | 0 | No
2030-05-26 03:00 | 2030 33% ECP | 700 | -526 | 0 | -87.93 | 0 | 0 | No
2030-05-26 04:00 | 2030 33% ECP | 700 | -526 | 0 | -191.33 | 0 | 0 | No
2030-05-26 05:00 | 2030 33% ECP | 700 | -526 | 0 | -70.33 | 0 | 0 | Yes
2030-05-26 06:00 | 2030 33% ECP | 560 | -526 | 0 | 0 | 0 | 0 | No
2030-05-26 07:00 | 2030 33% ECP | 140 | -526 | 0 | 0 | 0 | 0 | No
2030-05-26 08:00 | 2030 33% ECP | -280 | -526 | 0 | 25.73 | 0 | 0 | No
2030-05-26 09:00 | 2030 33% ECP | -700 | -526 | 0 | 0 | 0 | 0 | Yes
2030-05-26 10:00 | 2030 33% ECP | -700 | -526 | 0 | -146.48 | 0 | 0 | Yes
2030-05-26 11:00 | 2030 33% ECP | -700 | -526 | 0 | -85.34 | 0 | 0 | Yes
2030-05-26 12:00 | 2030 33% ECP | -700 | -526 | 0 | -64.69 | 0 | 0 | No
2030-05-26 13:00 | 2030 33% ECP | -700 | -526 | 0 | -82.74 | 0 | 0 | Yes
2030-05-26 14:00 | 2030 33% ECP | -560 | -526 | 0 | -125.1 | 0 | 0 | No
2030-05-26 15:00 | 2030 33% ECP | -140 | -526 | 0 | 91.87 | 0 | 0 | No
2030-05-26 16:00 | 2030 33% ECP | 280 | -526 | 0 | 163.66 | 0 | 0 | No
2030-05-26 17:00 | 2030 33% ECP | 700 | -526 | 0 | 291.36 | 0 | 0 | No
2030-05-26 18:00 | 2030 33% ECP | 700 | -526 | 0 | 246.81 | 0 | 0 | No
2030-05-26 19:00 | 2030 33% ECP | 700 | -226 | 0 | 132.03 | 0 | 0 | No
2030-05-26 20:00 | 2030 33% ECP | 700 | 0 | 0 | 132.03 | 0 | 0 | No
2030-05-26 21:00 | 2030 33% ECP | 700 | 0 | 0 | 167.74 | 0 | 0 | No
2030-05-26 22:00 | 2030 33% ECP | 700 | 0 | 0 | 201.18 | 0 | 0 | No
2030-05-26 23:00 | 2030 33% ECP | 700 | 0 | 0 | 52.1 | 0 | 0 | No
2030-05-27 | 2030 33% ECP | 700 | 0 | 0 | 60.56 | 0 | 0 | No
2030-05-27 01:00 | 2030 33% ECP | 700 | 0 | 0 | 50.43 | 0 | 0 | No
2030-05-27 02:00 | 2030 33% ECP | 700 | 0 | -510 | 48.41 | 0 | 0 | No
2030-05-27 03:00 | 2030 33% ECP | 700 | 0 | -510 | 33.22 | 0 | 0 | No
2030-05-27 04:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-05-27 05:00 | 2030 33% ECP | 700 | -14.73 | -510 | -4.36 | 0 | 0 | No
2030-05-27 06:00 | 2030 33% ECP | 700 | -103.82 | -510 | 44.04 | 0 | 0 | No
2030-05-27 07:00 | 2030 33% ECP | 700 | -403.82 | -510 | 121.48 | 0 | 0 | No
2030-05-27 08:00 | 2030 33% ECP | 700 | -526 | -510 | 158.32 | 0 | 0 | No
2030-05-27 09:00 | 2030 33% ECP | 700 | -526 | -510 | 136.35 | 0 | 0 | No
2030-05-27 10:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-27 11:00 | 2030 33% ECP | 700 | -526 | -510 | -6.4 | 0 | 0 | No
2030-05-27 12:00 | 2030 33% ECP | 321.51 | -526 | -510 | -104.04 | 0 | 0 | No
2030-05-27 13:00 | 2030 33% ECP | 191.38 | -526 | -510 | -150.23 | 0 | 0 | No
2030-05-27 14:00 | 2030 33% ECP | 101.25 | -526 | -510 | -138.25 | 0 | 0 | No
2030-05-27 15:00 | 2030 33% ECP | 521.25 | -526 | -510 | -126.37 | 0 | 0 | No
2030-05-27 16:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-27 17:00 | 2030 33% ECP | 700 | -526 | -510 | 130.39 | 0 | 0 | No
2030-05-27 18:00 | 2030 33% ECP | 700 | -269.84 | -510 | 119.62 | 0 | 0 | No
2030-05-27 19:00 | 2030 33% ECP | 700 | 0 | -510 | 86.69 | 0 | 0 | No
2030-05-27 20:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-05-27 21:00 | 2030 33% ECP | 700 | 0 | -510 | 201.36 | 0 | 0 | No
2030-05-27 22:00 | 2030 33% ECP | 700 | 0 | -510 | 177.45 | 0 | 0 | No
2030-05-27 23:00 | 2030 33% ECP | 700 | 0 | -510 | 101.47 | 0 | 0 | No
2030-05-28 | 2030 33% ECP | 700 | -188.69 | -510 | 108.19 | 0 | 0 | No
2030-05-28 01:00 | 2030 33% ECP | 700 | -122.05 | -510 | 125.21 | 0 | 0 | No
2030-05-28 02:00 | 2030 33% ECP | 700 | -422.05 | -510 | 125.93 | 0 | 0 | No
2030-05-28 03:00 | 2030 33% ECP | 700 | -526 | -510 | 110.43 | 0 | 0 | No
2030-05-28 04:00 | 2030 33% ECP | 700 | -526 | -510 | 84.75 | 0 | 0 | No
2030-05-28 05:00 | 2030 33% ECP | 700 | -526 | -510 | 59.83 | 0 | 0 | No
2030-05-28 06:00 | 2030 33% ECP | 560 | -526 | -510 | 119.19 | 0 | 0 | No
2030-05-28 07:00 | 2030 33% ECP | 140 | -526 | -510 | 171.14 | 0 | 0 | No
2030-05-28 08:00 | 2030 33% ECP | -280 | -526 | -510 | 255.38 | 0 | 0 | Yes
2030-05-28 09:00 | 2030 33% ECP | -700 | -526 | -510 | 194.46 | 0 | 0 | Yes
2030-05-28 10:00 | 2030 33% ECP | -700 | -526 | -510 | 147.69 | 0 | 0 | Yes
2030-05-28 11:00 | 2030 33% ECP | -700 | -526 | -510 | 130.79 | 0 | 0 | Yes
2030-05-28 12:00 | 2030 33% ECP | -700 | -526 | -510 | 67.47 | 0 | 0 | Yes
2030-05-28 13:00 | 2030 33% ECP | -700 | -526 | -510 | -30.48 | 0 | 0 | Yes
2030-05-28 14:00 | 2030 33% ECP | -700 | -526 | -510 | -73.21 | 0 | 0 | Yes
2030-05-28 15:00 | 2030 33% ECP | -700 | -526 | -510 | 31.28 | 0 | 0 | Yes
2030-05-28 16:00 | 2030 33% ECP | -574.98 | -526 | -510 | 64.74 | 0 | 0 | Yes
2030-05-28 17:00 | 2030 33% ECP | -154.98 | -526 | -510 | 176.48 | 0 | 0 | No
2030-05-28 18:00 | 2030 33% ECP | 265.02 | -526 | -510 | 166.98 | 0 | 0 | No
2030-05-28 19:00 | 2030 33% ECP | 685.02 | -526 | -510 | 160.03 | 0 | 0 | No
2030-05-28 20:00 | 2030 33% ECP | 700 | -526 | -510 | 196.13 | 0 | 0 | No
2030-05-28 21:00 | 2030 33% ECP | 700 | -526 | -510 | 232.43 | 0 | 0 | No
2030-05-28 22:00 | 2030 33% ECP | 700 | -526 | -510 | 170.26 | 0 | 0 | No
2030-05-28 23:00 | 2030 33% ECP | 700 | -526 | -510 | 56.53 | 0 | 0 | No
2030-05-29 | 2030 33% ECP | 700 | -526 | -510 | -51.65 | 0 | 0 | No
2030-05-29 01:00 | 2030 33% ECP | 700 | -526 | -510 | 17.86 | 0 | 0 | No
2030-05-29 02:00 | 2030 33% ECP | 700 | -526 | -510 | -37.19 | 0 | 0 | No
2030-05-29 03:00 | 2030 33% ECP | 700 | -526 | -510 | 3.85 | 0 | 0 | No
2030-05-29 04:00 | 2030 33% ECP | 700 | -526 | -510 | -76.14 | 0 | 0 | No
2030-05-29 05:00 | 2030 33% ECP | 512.67 | -526 | -510 | 83.82 | 0 | 0 | No
2030-05-29 06:00 | 2030 33% ECP | 92.67 | -526 | -510 | 41.05 | 0 | 0 | No
2030-05-29 07:00 | 2030 33% ECP | -327.33 | -526 | -510 | -25.62 | 0 | 0 | Yes
2030-05-29 08:00 | 2030 33% ECP | -700 | -526 | -510 | -125.72 | 0 | 0 | Yes
2030-05-29 09:00 | 2030 33% ECP | -700 | -526 | -510 | -349.48 | 0 | 0 | Yes
2030-05-29 10:00 | 2030 33% ECP | -700 | -526 | -510 | -487.89 | 0 | 0 | Yes
2030-05-29 11:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 12:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 13:00 | 2030 33% ECP | -700 | -526 | -510 | -404.46 | 0 | 0 | Yes
2030-05-29 14:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 15:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 16:00 | 2030 33% ECP | -700 | -526 | -510 | -304.8 | 0 | 0 | Yes
2030-05-29 17:00 | 2030 33% ECP | -280 | -526 | -510 | -111.93 | 0 | 0 | Yes
2030-05-29 18:00 | 2030 33% ECP | 140 | -526 | -510 | 0 | 0 | 0 | No
2030-05-29 19:00 | 2030 33% ECP | 560 | -526 | -510 | 299.18 | 0 | 0 | No
2030-05-29 20:00 | 2030 33% ECP | 700 | -526 | -510 | 344.28 | 0 | 0 | No
2030-05-29 21:00 | 2030 33% ECP | 583.1 | -526 | -510 | 333.77 | 0 | 0 | No
2030-05-29 22:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-29 23:00 | 2030 33% ECP | 700 | -526 | -510 | 459.7 | 0 | 0 | No
2030-05-30 | 2030 33% ECP | 700 | -526 | -510 | 334.03 | 0 | 0 | No
2030-05-30 01:00 | 2030 33% ECP | 700 | -526 | -510 | 361.4 | 0 | 0 | No
2030-05-30 02:00 | 2030 33% ECP | 700 | -526 | -510 | 327.07 | 0 | 0 | No
2030-05-30 03:00 | 2030 33% ECP | 700 | -226 | -250.23 | 510 | 0 | 0 | No
2030-05-30 04:00 | 2030 33% ECP | 700 | -526 | -510 | 478.9 | 0 | 0 | No
2030-05-30 05:00 | 2030 33% ECP | 560 | -526 | -510 | 178.9 | 0 | 0 | No
2030-05-30 06:00 | 2030 33% ECP | 140 | -526 | -510 | 253.91 | 0 | 0 | No
2030-05-30 07:00 | 2030 33% ECP | -280 | -526 | -510 | 258.73 | 0 | 0 | No
2030-05-30 08:00 | 2030 33% ECP | -700 | -526 | -510 | 356.26 | 0 | 0 | Yes
2030-05-30 09:00 | 2030 33% ECP | -700 | -526 | -510 | 142.01 | 0 | 0 | Yes
2030-05-30 10:00 | 2030 33% ECP | -700 | -526 | -510 | 268.82 | 0 | 0 | Yes
2030-05-30 11:00 | 2030 33% ECP | -700 | -226 | -474.11 | 510 | 0 | 0 | Yes
2030-05-30 12:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-30 13:00 | 2030 33% ECP | -700 | -526 | -510 | 452.17 | 0 | 0 | Yes
2030-05-30 14:00 | 2030 33% ECP | -700 | -526 | -510 | 152.17 | 0 | 0 | Yes
2030-05-30 15:00 | 2030 33% ECP | -700 | -526 | -510 | 129.61 | 0 | 0 | Yes
2030-05-30 16:00 | 2030 33% ECP | -332.17 | -526 | -510 | 129.61 | 0 | 0 | Yes
2030-05-30 17:00 | 2030 33% ECP | 87.83 | -526 | -510 | 0 | 0 | 0 | No
2030-05-30 18:00 | 2030 33% ECP | 507.83 | -526 | -510 | 3.66 | 0 | 0 | No
2030-05-30 19:00 | 2030 33% ECP | 537.24 | -491.94 | -510 | 303.66 | 0 | 0 | No
2030-05-30 20:00 | 2030 33% ECP | 365.24 | -191.94 | -210 | 510 | 0 | 0 | Yes
2030-05-30 21:00 | 2030 33% ECP | 280 | 108.06 | 90 | 318.24 | 0 | 0 | No
2030-05-30 22:00 | 2030 33% ECP | 700 | 408.06 | 390 | 510 | 0 | 0 | No
2030-05-30 23:00 | 2030 33% ECP | 700 | 505 | 510 | 290.77 | 0 | 0 | No
2030-05-31 | 2030 33% ECP | 700 | 505 | 510 | 125.62 | 0 | 0 | No
2030-05-31 01:00 | 2030 33% ECP | 700 | 505 | 510 | 125.62 | 0 | 0 | No
2030-05-31 02:00 | 2030 33% ECP | 700 | 505 | 510 | 407.26 | 0 | 0 | No
2030-05-31 03:00 | 2030 33% ECP | 700 | 505 | 510 | 208.32 | 0 | 0 | No
2030-05-31 04:00 | 2030 33% ECP | 700 | 300 | 352.4 | 508.32 | 0 | 0 | No
2030-05-31 05:00 | 2030 33% ECP | 700 | 0 | 52.4 | 208.32 | 0 | 0 | No
2030-05-31 06:00 | 2030 33% ECP | 700 | -300 | -247.6 | -91.68 | 0 | 0 | No
2030-05-31 07:00 | 2030 33% ECP | 554.41 | -526 | -510 | -391.68 | 0 | 0 | No
2030-05-31 08:00 | 2030 33% ECP | 134.41 | -526 | -510 | -237.19 | 0 | 0 | No
2030-05-31 09:00 | 2030 33% ECP | -285.59 | -526 | -510 | -58.71 | 0 | 0 | Yes
2030-05-31 10:00 | 2030 33% ECP | -700 | -526 | -510 | -252.69 | 0 | 0 | Yes
2030-05-31 11:00 | 2030 33% ECP | -700 | -526 | -510 | -144.36 | 0 | 0 | Yes
2030-05-31 12:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-31 13:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-31 14:00 | 2030 33% ECP | -700 | -526 | -510 | 140.66 | 0 | 0 | Yes
2030-05-31 15:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-31 16:00 | 2030 33% ECP | -280 | -526 | -510 | 185.56 | 0 | 0 | No
2030-05-31 17:00 | 2030 33% ECP | 140 | -526 | -510 | 474.76 | 0 | 0 | No
2030-05-31 18:00 | 2030 33% ECP | 560 | -526 | -510 | 510 | 0 | 0 | No
2030-05-31 19:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-31 20:00 | 2030 33% ECP | 700 | -300 | -510 | 479.1 | 0 | 0 | No
2030-05-31 21:00 | 2030 33% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-05-31 22:00 | 2030 33% ECP | 700 | -300 | -510 | 510 | 0 | 0 | No
2030-05-31 23:00 | 2030 33% ECP | 700 | -300 | -510 | 505.9 | 0 | 0 | No
2030-06-01 | 2030 33% ECP | 700 | 0 | -245.21 | 205.9 | 0 | 0 | No
2030-06-01 01:00 | 2030 33% ECP | 700 | 0 | 0 | 82.37 | 0 | 0 | No
2030-06-01 02:00 | 2030 33% ECP | 700 | -198 | -300 | -150.63 | 0 | 0 | No
2030-06-01 03:00 | 2030 33% ECP | 700 | -115.69 | -510 | -168.35 | 0 | 0 | No
2030-06-01 04:00 | 2030 33% ECP | 700 | 0 | -510 | -70.57 | 0 | 0 | No
2030-06-01 05:00 | 2030 33% ECP | 700 | -226 | -510 | -70.86 | 0 | 0 | No
2030-06-01 06:00 | 2030 33% ECP | 700 | -526 | -510 | -84.98 | 0 | 0 | No
2030-06-01 07:00 | 2030 33% ECP | 374.33 | -526 | -510 | -28.6 | 0 | 0 | No
2030-06-01 08:00 | 2030 33% ECP | -45.67 | -526 | -510 | -40.28 | 0 | 0 | No
2030-06-01 09:00 | 2030 33% ECP | -465.67 | -526 | -510 | -40.68 | 0 | 0 | No
2030-06-01 10:00 | 2030 33% ECP | -700 | -526 | -510 | -58.91 | 0 | 0 | No
2030-06-01 11:00 | 2030 33% ECP | -700 | -526 | -510 | -23.35 | 0 | 0 | No
2030-06-01 12:00 | 2030 33% ECP | -700 | -526 | -510 | -21.22 | 0 | 0 | No
2030-06-01 13:00 | 2030 33% ECP | -700 | -526 | -510 | -67.54 | 0 | 0 | No
2030-06-01 14:00 | 2030 33% ECP | -700 | -526 | -510 | -65.13 | 0 | 0 | No
2030-06-01 15:00 | 2030 33% ECP | -332 | -526 | -510 | -47.67 | 0 | 0 | No
2030-06-01 16:00 | 2030 33% ECP | 88 | -526 | -510 | 45.43 | 0 | 0 | No
2030-06-01 17:00 | 2030 33% ECP | 508 | -526 | -510 | 129.46 | 0 | 0 | No
2030-06-01 18:00 | 2030 33% ECP | 700 | -526 | -510 | 162.22 | 0 | 0 | No
2030-06-01 19:00 | 2030 33% ECP | 700 | -226 | -463.91 | 162.22 | 0 | 0 | No
2030-06-01 20:00 | 2030 33% ECP | 700 | 0 | -399.13 | 261.91 | 0 | 0 | No
2030-06-01 21:00 | 2030 33% ECP | 700 | 0 | -489.34 | 192.61 | 0 | 0 | No
2030-06-01 22:00 | 2030 33% ECP | 700 | 0 | -311.1 | 266.13 | 0 | 0 | No
2030-06-01 23:00 | 2030 33% ECP | 700 | 0 | -11.1 | 217.34 | 0 | 0 | No
2030-06-02 | 2030 33% ECP | 700 | 0 | -48.29 | 127.56 | 0 | 0 | No
2030-06-02 01:00 | 2030 33% ECP | 700 | 0 | -300 | 163.78 | 0 | 0 | No
2030-06-02 02:00 | 2030 33% ECP | 700 | 0 | 0 | 150.68 | 0 | 0 | No
2030-06-02 03:00 | 2030 33% ECP | 700 | 0 | -20.58 | 122.88 | 0 | 0 | No
2030-06-02 04:00 | 2030 33% ECP | 700 | 0 | -320.58 | 92.7 | 0 | 0 | No
2030-06-02 05:00 | 2030 33% ECP | 700 | -91.98 | -320.58 | 56.12 | 0 | 0 | No
2030-06-02 06:00 | 2030 33% ECP | 581.32 | -391.98 | -510 | 55.7 | 0 | 0 | No
2030-06-02 07:00 | 2030 33% ECP | 161.32 | -526 | -510 | 33.25 | 0 | 0 | No
2030-06-02 08:00 | 2030 33% ECP | -258.68 | -526 | -510 | -32.44 | 0 | 0 | No
2030-06-02 09:00 | 2030 33% ECP | -678.68 | -526 | -510 | -84.24 | 0 | 0 | Yes
2030-06-02 10:00 | 2030 33% ECP | -700 | -526 | -510 | -61.65 | 0 | 0 | Yes
2030-06-02 11:00 | 2030 33% ECP | -700 | -526 | -510 | -31.48 | 0 | 0 | Yes
2030-06-02 12:00 | 2030 33% ECP | -700 | -526 | -510 | -25.11 | 0 | 0 | Yes
2030-06-02 13:00 | 2030 33% ECP | -700 | -526 | -510 | -16.99 | 0 | 0 | Yes
2030-06-02 14:00 | 2030 33% ECP | -700 | -526 | -510 | -22.05 | 0 | 0 | No
2030-06-02 15:00 | 2030 33% ECP | -700 | -526 | -510 | -71.06 | 0 | 0 | No
2030-06-02 16:00 | 2030 33% ECP | -280 | -526 | -510 | -9.06 | 0 | 0 | No
2030-06-02 17:00 | 2030 33% ECP | 140 | -526 | -510 | -204.15 | 0 | 0 | No
2030-06-02 18:00 | 2030 33% ECP | 560 | -526 | -510 | -504.15 | 0 | 0 | No
2030-06-02 19:00 | 2030 33% ECP | 700 | -526 | -510 | -370.23 | 0 | 0 | No
2030-06-02 20:00 | 2030 33% ECP | 700 | -526 | -510 | -254.15 | 0 | 0 | No
2030-06-02 21:00 | 2030 33% ECP | 280 | -526 | -510 | 45.85 | 0 | 0 | No
2030-06-02 22:00 | 2030 33% ECP | 700 | -526 | -510 | 161.38 | 0 | 0 | No
2030-06-02 23:00 | 2030 33% ECP | 700 | -526 | -510 | 43.95 | 0 | 0 | No
2030-06-03 | 2030 33% ECP | 700 | -526 | -510 | 18.17 | 0 | 0 | No
2030-06-03 01:00 | 2030 33% ECP | 700 | -337.05 | -510 | -34.9 | 0 | 0 | No
2030-06-03 02:00 | 2030 33% ECP | 560 | -37.05 | -210 | 12.68 | 0 | 0 | No
2030-06-03 03:00 | 2030 33% ECP | 140 | 262.95 | 90 | 234.94 | 0 | 0 | No
2030-06-03 04:00 | 2030 33% ECP | -280 | 505 | 390 | 128.67 | 0 | 0 | Yes
2030-06-03 05:00 | 2030 33% ECP | -700 | 505 | 510 | 428.67 | 0 | 0 | Yes
2030-06-03 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 14:00 | 2030 33% ECP | -700 | 374 | 224.45 | 300 | 0 | 0 | Yes
2030-06-03 15:00 | 2030 33% ECP | -700 | 74 | -75.55 | 0 | 0 | 0 | Yes
2030-06-03 16:00 | 2030 33% ECP | -700 | -226 | -375.55 | -300 | 0 | 0 | Yes
2030-06-03 17:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-03 18:00 | 2030 33% ECP | -700 | -300 | -373.13 | -300 | 0 | 0 | No
2030-06-03 19:00 | 2030 33% ECP | -280 | 0 | -73.13 | 0 | 0 | 0 | No
2030-06-03 20:00 | 2030 33% ECP | 140 | 300 | 226.87 | 300 | 0 | 0 | No
2030-06-03 21:00 | 2030 33% ECP | 560 | 438.18 | 510 | 455.77 | 0 | 0 | No
2030-06-03 22:00 | 2030 33% ECP | 700 | 505 | 510 | 312.62 | 0 | 0 | No
2030-06-03 23:00 | 2030 33% ECP | 700 | 505 | 510 | 116.99 | 0 | 0 | No
2030-06-04 | 2030 33% ECP | 700 | 505 | 510 | 416.99 | 0 | 0 | No
2030-06-04 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-04 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-04 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-04 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-04 05:00 | 2030 33% ECP | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-06-04 06:00 | 2030 33% ECP | 700 | -95 | -90 | 219.42 | 0 | 0 | No
2030-06-04 07:00 | 2030 33% ECP | 700 | -395 | -390 | 219.42 | 0 | 0 | No
2030-06-04 08:00 | 2030 33% ECP | 700 | -526 | -510 | 365.67 | 0 | 0 | No
2030-06-04 09:00 | 2030 33% ECP | 700 | -526 | -510 | 301.17 | 0 | 0 | No
2030-06-04 10:00 | 2030 33% ECP | 700 | -526 | -510 | 238.13 | 0 | 0 | No
2030-06-04 11:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-04 12:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-04 13:00 | 2030 33% ECP | 700 | -526 | -510 | 31.24 | 0 | 0 | No
2030-06-04 14:00 | 2030 33% ECP | 700 | -526 | -510 | -171.74 | 0 | 0 | No
2030-06-04 15:00 | 2030 33% ECP | 700 | -526 | -510 | -294.04 | 0 | 0 | No
2030-06-04 16:00 | 2030 33% ECP | 700 | -526 | -510 | -110.84 | 0 | 0 | No
2030-06-04 17:00 | 2030 33% ECP | 700 | -526 | -510 | -95.71 | 0 | 0 | No
2030-06-04 18:00 | 2030 33% ECP | 700 | -526 | -510 | -63.07 | 0 | 0 | No
2030-06-04 19:00 | 2030 33% ECP | 700 | -526 | -510 | -363.07 | 0 | 0 | No
2030-06-04 20:00 | 2030 33% ECP | 700 | -526 | -510 | -124.97 | 0 | 0 | No
2030-06-04 21:00 | 2030 33% ECP | 280 | -526 | -510 | -193.1 | 0 | 0 | No
2030-06-04 22:00 | 2030 33% ECP | 700 | -526 | -510 | -149.42 | 0 | 0 | No
2030-06-04 23:00 | 2030 33% ECP | 700 | -526 | -510 | -13.26 | 0 | 0 | No
2030-06-05 | 2030 33% ECP | 700 | -226 | -210 | 0 | 0 | 0 | No
2030-06-05 01:00 | 2030 33% ECP | 700 | 74 | 90 | 210 | 0 | 0 | No
2030-06-05 02:00 | 2030 33% ECP | 700 | 374 | 390 | 510 | 0 | 0 | No
2030-06-05 03:00 | 2030 33% ECP | 311.71 | 505 | 510 | 510 | 0 | 0 | No
2030-06-05 04:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-06-05 05:00 | 2030 33% ECP | 0 | 505 | 510 | 483.28 | 0 | 0 | No
2030-06-05 06:00 | 2030 33% ECP | 0 | 402.43 | 510 | 183.28 | 0 | 0 | No
2030-06-05 07:00 | 2030 33% ECP | -280 | 102.43 | 276.83 | 166.89 | 0 | 0 | No
2030-06-05 08:00 | 2030 33% ECP | -700 | 402.43 | 510 | 466.89 | 0 | 0 | Yes
2030-06-05 09:00 | 2030 33% ECP | -700 | 505 | 510 | 252.61 | 0 | 0 | Yes
2030-06-05 10:00 | 2030 33% ECP | -700 | 505 | 510 | 166.56 | 0 | 0 | Yes
2030-06-05 11:00 | 2030 33% ECP | -700 | 505 | 510 | 79.69 | 0 | 0 | Yes
2030-06-05 12:00 | 2030 33% ECP | -700 | 505 | 510 | 208.57 | 0 | 0 | Yes
2030-06-05 13:00 | 2030 33% ECP | -700 | 505 | 510 | 92.58 | 0 | 0 | Yes
2030-06-05 14:00 | 2030 33% ECP | -700 | 505 | 510 | 60.03 | 0 | 0 | Yes
2030-06-05 15:00 | 2030 33% ECP | -700 | 505 | 510 | 55.08 | 0 | 0 | Yes
2030-06-05 16:00 | 2030 33% ECP | -700 | 505 | 510 | 165.85 | 0 | 0 | Yes
2030-06-05 17:00 | 2030 33% ECP | -700 | 505 | 510 | 306.05 | 0 | 0 | Yes
2030-06-05 18:00 | 2030 33% ECP | -700 | 505 | 510 | 232.62 | 0 | 0 | Yes
2030-06-05 19:00 | 2030 33% ECP | -700 | 505 | 510 | 201.76 | 0 | 0 | Yes
2030-06-05 20:00 | 2030 33% ECP | -700 | 505 | 510 | 216.99 | 0 | 0 | Yes
2030-06-05 21:00 | 2030 33% ECP | -700 | 505 | 510 | 197.35 | 0 | 0 | Yes
2030-06-05 22:00 | 2030 33% ECP | -700 | 505 | 510 | 71.12 | 0 | 0 | Yes
2030-06-05 23:00 | 2030 33% ECP | -700 | 505 | 510 | -13.7 | 0 | 0 | Yes
2030-06-06 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-06 01:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-06 02:00 | 2030 33% ECP | -700 | 505 | 510 | 51.81 | 0 | 0 | Yes
2030-06-06 03:00 | 2030 33% ECP | -700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-06-06 04:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-06 05:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-06 06:00 | 2030 33% ECP | -700 | 505 | 510 | 47.75 | 0 | 0 | Yes
2030-06-06 07:00 | 2030 33% ECP | -700 | 505 | 510 | 188.17 | 0 | 0 | Yes
2030-06-06 08:00 | 2030 33% ECP | -700 | 505 | 510 | 418.33 | 0 | 0 | Yes
2030-06-06 09:00 | 2030 33% ECP | -700 | 505 | 510 | 232.52 | 0 | 0 | Yes
2030-06-06 10:00 | 2030 33% ECP | -700 | 505 | 510 | 344.23 | 0 | 0 | Yes
2030-06-06 11:00 | 2030 33% ECP | -700 | 505 | 510 | 365.59 | 0 | 0 | Yes
2030-06-06 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-06 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-06 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-06 15:00 | 2030 33% ECP | -700 | 374 | 296.52 | 510 | 0 | 0 | Yes
2030-06-06 16:00 | 2030 33% ECP | -700 | 74 | -3.48 | 510 | 0 | 0 | Yes
2030-06-06 17:00 | 2030 33% ECP | -648.27 | -226 | -303.48 | 292.09 | 0 | 0 | No
2030-06-06 18:00 | 2030 33% ECP | -228.27 | -526 | -510 | -7.91 | 0 | 0 | No
2030-06-06 19:00 | 2030 33% ECP | 191.73 | -526 | -510 | -307.91 | 0 | 0 | No
2030-06-06 20:00 | 2030 33% ECP | 611.73 | -526 | -510 | -510 | 0 | 0 | No
2030-06-06 21:00 | 2030 33% ECP | 700 | -395 | -390 | -510 | 0 | 0 | No
2030-06-06 22:00 | 2030 33% ECP | 532.32 | -95 | -90 | -362.58 | 0 | 0 | No
2030-06-06 23:00 | 2030 33% ECP | 112.32 | 205 | 210 | -62.58 | 0 | 0 | No
2030-06-07 | 2030 33% ECP | 381.68 | 505 | 510 | 237.42 | 0 | 0 | Yes
2030-06-07 01:00 | 2030 33% ECP | 578.61 | 505 | 510 | 225.74 | 0 | 0 | Yes
2030-06-07 02:00 | 2030 33% ECP | 246.98 | 505 | 510 | 47.65 | 0 | 0 | Yes
2030-06-07 03:00 | 2030 33% ECP | 223.37 | 505 | 510 | 347.65 | 0 | 0 | Yes
2030-06-07 04:00 | 2030 33% ECP | 223.37 | 505 | 510 | 337 | 0 | 0 | Yes
2030-06-07 05:00 | 2030 33% ECP | 231.25 | 205 | 210 | 90 | 0 | 0 | No
2030-06-07 06:00 | 2030 33% ECP | -188.75 | -95 | -90 | -210 | 0 | 0 | No
2030-06-07 07:00 | 2030 33% ECP | -608.75 | -395 | -390 | -510 | 0 | 0 | No
2030-06-07 08:00 | 2030 33% ECP | -280 | -226 | -510 | -441.54 | 0 | 0 | No
2030-06-07 09:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 10:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 11:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 12:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 13:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 14:00 | 2030 33% ECP | -700 | -322.78 | -510 | -510 | 0 | 0 | No
2030-06-07 15:00 | 2030 33% ECP | -426.76 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 16:00 | 2030 33% ECP | -6.76 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 17:00 | 2030 33% ECP | 413.24 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 18:00 | 2030 33% ECP | -6.76 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 19:00 | 2030 33% ECP | 413.24 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 20:00 | 2030 33% ECP | 700 | -442.52 | -510 | -510 | 0 | 0 | No
2030-06-07 21:00 | 2030 33% ECP | 700 | -142.52 | -510 | -210 | 0 | 0 | No
2030-06-07 22:00 | 2030 33% ECP | 700 | -84.77 | -510 | -445.67 | 0 | 0 | No
2030-06-07 23:00 | 2030 33% ECP | 700 | -25.26 | -510 | -145.67 | 0 | 0 | No
2030-06-08 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-08 01:00 | 2030 33% ECP | 700 | 0 | -485.4 | 0 | 0 | 0 | No
2030-06-08 02:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-08 03:00 | 2030 33% ECP | 700 | 0 | -241.94 | 0 | 0 | 0 | No
2030-06-08 04:00 | 2030 33% ECP | 652.78 | 0 | -510 | 0 | 0 | 0 | No
2030-06-08 05:00 | 2030 33% ECP | 232.78 | 0 | -510 | 0 | 0 | 0 | No
2030-06-08 06:00 | 2030 33% ECP | -187.22 | -226 | -510 | 0 | 0 | 0 | No
2030-06-08 07:00 | 2030 33% ECP | -607.22 | -526 | -510 | -56.16 | 0 | 0 | No
2030-06-08 08:00 | 2030 33% ECP | -409.16 | -526 | -510 | -70.01 | 0 | 0 | No
2030-06-08 09:00 | 2030 33% ECP | -700 | -526 | -510 | -59.08 | 0 | 0 | No
2030-06-08 10:00 | 2030 33% ECP | -700 | -526 | -510 | -12.25 | 0 | 0 | No
2030-06-08 11:00 | 2030 33% ECP | -700 | -526 | -510 | 5.14 | 0 | 0 | No
2030-06-08 12:00 | 2030 33% ECP | -700 | -526 | -510 | -15.12 | 0 | 0 | No
2030-06-08 13:00 | 2030 33% ECP | -700 | -526 | -510 | -4.09 | 0 | 0 | No
2030-06-08 14:00 | 2030 33% ECP | -700 | -526 | -510 | -4.09 | 0 | 0 | No
2030-06-08 15:00 | 2030 33% ECP | -560 | -526 | -510 | -70.87 | 0 | 0 | No
2030-06-08 16:00 | 2030 33% ECP | -140 | -526 | -510 | 0 | 0 | 0 | No
2030-06-08 17:00 | 2030 33% ECP | 280 | -526 | -510 | 71.85 | 0 | 0 | No
2030-06-08 18:00 | 2030 33% ECP | 700 | -526 | -510 | -228.15 | 0 | 0 | No
2030-06-08 19:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-08 20:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-08 21:00 | 2030 33% ECP | 700 | -526 | -510 | -211.73 | 0 | 0 | No
2030-06-08 22:00 | 2030 33% ECP | 700 | -226 | -210 | 88.27 | 0 | 0 | No
2030-06-08 23:00 | 2030 33% ECP | 700 | 0 | 90 | 4.56 | 0 | 0 | No
2030-06-09 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-09 01:00 | 2030 33% ECP | 700 | 0 | 300 | 20.12 | 0 | 0 | No
2030-06-09 02:00 | 2030 33% ECP | 700 | 0 | 187.7 | 41.45 | 0 | 0 | No
2030-06-09 03:00 | 2030 33% ECP | 700 | 0 | 379.78 | 19 | 0 | 0 | No
2030-06-09 04:00 | 2030 33% ECP | 700 | 0 | 79.78 | 0 | 0 | 0 | No
2030-06-09 05:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-09 06:00 | 2030 33% ECP | 700 | 0 | -18.72 | 0 | 0 | 0 | No
2030-06-09 07:00 | 2030 33% ECP | 700 | -226 | -255.59 | 0 | 0 | 0 | No
2030-06-09 08:00 | 2030 33% ECP | 700 | -526 | -510 | -28.3 | 0 | 0 | No
2030-06-09 09:00 | 2030 33% ECP | 700 | -526 | -510 | -9.51 | 0 | 0 | No
2030-06-09 10:00 | 2030 33% ECP | 700 | -526 | -510 | 5.51 | 0 | 0 | No
2030-06-09 11:00 | 2030 33% ECP | 700 | -526 | -510 | 47.35 | 0 | 0 | No
2030-06-09 12:00 | 2030 33% ECP | 700 | -526 | -510 | 72.32 | 0 | 0 | No
2030-06-09 13:00 | 2030 33% ECP | 700 | -526 | -510 | 79.39 | 0 | 0 | No
2030-06-09 14:00 | 2030 33% ECP | 700 | -526 | -510 | 51.19 | 0 | 0 | No
2030-06-09 15:00 | 2030 33% ECP | 700 | -526 | -510 | 103.2 | 0 | 0 | No
2030-06-09 16:00 | 2030 33% ECP | 700 | -526 | -510 | 162.83 | 0 | 0 | No
2030-06-09 17:00 | 2030 33% ECP | 700 | -404.17 | -510 | 188.16 | 0 | 0 | No
2030-06-09 18:00 | 2030 33% ECP | 700 | -104.17 | -510 | 121.55 | 0 | 0 | No
2030-06-09 19:00 | 2030 33% ECP | 700 | 0 | -210 | 69.44 | 0 | 0 | No
2030-06-09 20:00 | 2030 33% ECP | 700 | 0 | -510 | 15.12 | 0 | 0 | No
2030-06-09 21:00 | 2030 33% ECP | 700 | 0 | -400.67 | 62.88 | 0 | 0 | No
2030-06-09 22:00 | 2030 33% ECP | 700 | 0 | -225.69 | 20.13 | 0 | 0 | No
2030-06-09 23:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-10 | 2030 33% ECP | 700 | 0 | -300 | 24.24 | 0 | 0 | No
2030-06-10 01:00 | 2030 33% ECP | 700 | 0 | -510 | 19.52 | 0 | 0 | No
2030-06-10 02:00 | 2030 33% ECP | 700 | 0 | -510 | -138.73 | 0 | 0 | No
2030-06-10 03:00 | 2030 33% ECP | 700 | 0 | -510 | -194.04 | 0 | 0 | No
2030-06-10 04:00 | 2030 33% ECP | 700 | 0 | -510 | -190.47 | 0 | 0 | No
2030-06-10 05:00 | 2030 33% ECP | 700 | 0 | -510 | -17.82 | 0 | 0 | No
2030-06-10 06:00 | 2030 33% ECP | 700 | -33.55 | -510 | 73.58 | 0 | 0 | No
2030-06-10 07:00 | 2030 33% ECP | 700 | -226 | -510 | 195.23 | 0 | 0 | No
2030-06-10 08:00 | 2030 33% ECP | 700 | -526 | -510 | 272.21 | 0 | 0 | No
2030-06-10 09:00 | 2030 33% ECP | 700 | -526 | -510 | 186.24 | 0 | 0 | No
2030-06-10 10:00 | 2030 33% ECP | 700 | -526 | -510 | 252.31 | 0 | 0 | No
2030-06-10 11:00 | 2030 33% ECP | 700 | -526 | -510 | 257.87 | 0 | 0 | No
2030-06-10 12:00 | 2030 33% ECP | 700 | -526 | -510 | 155.94 | 0 | 0 | No
2030-06-10 13:00 | 2030 33% ECP | 700 | -526 | -510 | 170.76 | 0 | 0 | No
2030-06-10 14:00 | 2030 33% ECP | 700 | -526 | -510 | 210.94 | 0 | 0 | No
2030-06-10 15:00 | 2030 33% ECP | 700 | -526 | -510 | 228.79 | 0 | 0 | No
2030-06-10 16:00 | 2030 33% ECP | 700 | -526 | -510 | 300.58 | 0 | 0 | No
2030-06-10 17:00 | 2030 33% ECP | 700 | -526 | -510 | 253.05 | 0 | 0 | No
2030-06-10 18:00 | 2030 33% ECP | 678.72 | -526 | -510 | 95.94 | 0 | 0 | No
2030-06-10 19:00 | 2030 33% ECP | 678.72 | -526 | -510 | -11.79 | 0 | 0 | No
2030-06-10 20:00 | 2030 33% ECP | 258.72 | -395 | -390 | -42.1 | 0 | 0 | No
2030-06-10 21:00 | 2030 33% ECP | 632.38 | -95 | -90 | -142 | 0 | 0 | No
2030-06-10 22:00 | 2030 33% ECP | 560 | 205 | 210 | -263.75 | 0 | 0 | No
2030-06-10 23:00 | 2030 33% ECP | 140 | 505 | 510 | 36.25 | 0 | 0 | Yes
2030-06-11 | 2030 33% ECP | -280 | 505 | 510 | 115.68 | 0 | 0 | Yes
2030-06-11 01:00 | 2030 33% ECP | -700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-06-11 02:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-11 03:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-11 04:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-11 05:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-11 06:00 | 2030 33% ECP | -700 | 505 | 510 | 58.69 | 0 | 0 | Yes
2030-06-11 07:00 | 2030 33% ECP | -700 | 505 | 510 | 110.55 | 0 | 0 | Yes
2030-06-11 08:00 | 2030 33% ECP | -700 | 505 | 510 | 394.79 | 0 | 0 | Yes
2030-06-11 09:00 | 2030 33% ECP | -700 | 505 | 510 | 141.47 | 0 | 0 | Yes
2030-06-11 10:00 | 2030 33% ECP | -700 | 505 | 510 | 120.61 | 0 | 0 | Yes
2030-06-11 11:00 | 2030 33% ECP | -700 | 505 | 510 | 271.13 | 0 | 0 | Yes
2030-06-11 12:00 | 2030 33% ECP | -700 | 505 | 510 | 280.95 | 0 | 0 | Yes
2030-06-11 13:00 | 2030 33% ECP | -700 | 505 | 510 | 358.66 | 0 | 0 | Yes
2030-06-11 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 17:00 | 2030 33% ECP | -700 | 300 | 510 | 510 | 0 | 0 | Yes
2030-06-11 18:00 | 2030 33% ECP | -700 | 0 | 263.57 | 210 | 0 | 0 | No
2030-06-11 19:00 | 2030 33% ECP | -700 | 209.21 | 510 | 443.33 | 0 | 0 | No
2030-06-11 20:00 | 2030 33% ECP | -289.41 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 21:00 | 2030 33% ECP | -420 | 505 | 510 | 416.91 | 0 | 0 | Yes
2030-06-11 22:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 23:00 | 2030 33% ECP | 0 | 505 | 510 | 437.56 | 0 | 0 | Yes
2030-06-12 | 2030 33% ECP | -262.85 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-12 01:00 | 2030 33% ECP | -682.85 | 505 | 510 | 211.6 | 0 | 0 | Yes
2030-06-12 02:00 | 2030 33% ECP | -467.68 | 505 | 510 | 91.53 | 0 | 0 | Yes
2030-06-12 03:00 | 2030 33% ECP | -595.07 | 505 | 510 | 391.53 | 0 | 0 | Yes
2030-06-12 04:00 | 2030 33% ECP | -700 | 505 | 510 | 91.53 | 0 | 0 | Yes
2030-06-12 05:00 | 2030 33% ECP | -700 | 505 | 510 | 63.09 | 0 | 0 | Yes
2030-06-12 06:00 | 2030 33% ECP | -700 | 505 | 510 | 327.72 | 0 | 0 | Yes
2030-06-12 07:00 | 2030 33% ECP | -700 | 505 | 510 | 217.05 | 0 | 0 | Yes
2030-06-12 08:00 | 2030 33% ECP | -700 | 205 | 510 | 166 | 0 | 0 | Yes
2030-06-12 09:00 | 2030 33% ECP | -700 | 505 | 510 | 327.07 | 0 | 0 | Yes
2030-06-12 10:00 | 2030 33% ECP | -700 | 505 | 510 | 339.85 | 0 | 0 | Yes
2030-06-12 11:00 | 2030 33% ECP | -700 | 505 | 510 | 280.04 | 0 | 0 | Yes
2030-06-12 12:00 | 2030 33% ECP | -700 | 505 | 510 | 333.84 | 0 | 0 | Yes
2030-06-12 13:00 | 2030 33% ECP | -700 | 505 | 454.85 | 366.31 | 0 | 0 | Yes
2030-06-12 14:00 | 2030 33% ECP | -700 | 505 | 154.85 | 90 | 0 | 0 | Yes
2030-06-12 15:00 | 2030 33% ECP | -560 | 205 | -145.15 | -210 | 0 | 0 | Yes
2030-06-12 16:00 | 2030 33% ECP | -140 | -95 | -445.15 | -510 | 0 | 0 | No
2030-06-12 17:00 | 2030 33% ECP | 280 | -169.31 | -394.5 | -210 | 0 | 0 | No
2030-06-12 18:00 | 2030 33% ECP | 700 | -469.31 | -510 | -328.94 | 0 | 0 | No
2030-06-12 19:00 | 2030 33% ECP | 700 | -496.92 | -510 | -493.45 | 0 | 0 | No
2030-06-12 20:00 | 2030 33% ECP | 700 | -196.92 | -510 | -493.45 | 0 | 0 | No
2030-06-12 21:00 | 2030 33% ECP | 700 | 0 | -510 | -493.45 | 0 | 0 | No
2030-06-12 22:00 | 2030 33% ECP | 700 | 0 | -300 | -253.88 | 0 | 0 | No
2030-06-12 23:00 | 2030 33% ECP | 700 | 252.7 | 0 | 46.12 | 0 | 0 | No
2030-06-13 | 2030 33% ECP | 700 | 0 | 300 | 346.12 | 0 | 0 | No
2030-06-13 01:00 | 2030 33% ECP | 700 | 33.36 | 0 | 376.8 | 0 | 0 | No
2030-06-13 02:00 | 2030 33% ECP | 700 | -266.64 | -300 | 76.8 | 0 | 0 | No
2030-06-13 03:00 | 2030 33% ECP | 700 | -78.41 | -510 | 253.36 | 0 | 0 | No
2030-06-13 04:00 | 2030 33% ECP | 700 | -355.11 | -510 | 177.62 | 0 | 0 | No
2030-06-13 05:00 | 2030 33% ECP | 700 | -55.11 | -510 | -64.63 | 0 | 0 | No
2030-06-13 06:00 | 2030 33% ECP | 700 | -355.11 | -510 | -41.48 | 0 | 0 | No
2030-06-13 07:00 | 2030 33% ECP | 700 | -526 | -510 | -186.95 | 0 | 0 | No
2030-06-13 08:00 | 2030 33% ECP | 700 | -526 | -510 | -2.14 | 0 | 0 | No
2030-06-13 09:00 | 2030 33% ECP | 700 | -526 | -510 | 96.5 | 0 | 0 | No
2030-06-13 10:00 | 2030 33% ECP | 700 | -526 | -510 | 396.5 | 0 | 0 | No
2030-06-13 11:00 | 2030 33% ECP | 700 | -526 | -510 | 127.04 | 0 | 0 | No
2030-06-13 12:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-13 13:00 | 2030 33% ECP | 700 | -526 | -510 | 181.45 | 0 | 0 | No
2030-06-13 14:00 | 2030 33% ECP | 700 | -526 | -510 | -115.02 | 0 | 0 | No
2030-06-13 15:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-13 16:00 | 2030 33% ECP | 700 | -526 | -510 | -59.96 | 0 | 0 | No
2030-06-13 17:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-13 18:00 | 2030 33% ECP | 585.19 | -300 | -510 | 4.65 | 0 | 0 | No
2030-06-13 19:00 | 2030 33% ECP | 700 | 0 | -501.5 | 0 | 0 | 0 | No
2030-06-13 20:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-13 21:00 | 2030 33% ECP | 700 | 0 | -510 | 300 | 0 | 0 | No
2030-06-13 22:00 | 2030 33% ECP | 700 | 0 | -247.62 | 300 | 0 | 0 | No
2030-06-13 23:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-14 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-14 01:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-14 02:00 | 2030 33% ECP | 700 | 0 | -449.18 | 0 | 0 | 0 | No
2030-06-14 03:00 | 2030 33% ECP | 700 | 0 | -149.18 | 0 | 0 | 0 | No
2030-06-14 04:00 | 2030 33% ECP | 700 | 0 | -449.18 | 0 | 0 | 0 | No
2030-06-14 05:00 | 2030 33% ECP | 700 | 0 | -510 | -66.89 | 0 | 0 | No
2030-06-14 06:00 | 2030 33% ECP | 700 | -226 | -510 | -101.16 | 0 | 0 | No
2030-06-14 07:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-14 08:00 | 2030 33% ECP | 700 | -526 | -510 | 43.15 | 0 | 0 | No
2030-06-14 09:00 | 2030 33% ECP | 325.9 | -526 | -510 | 0 | 0 | 0 | No
2030-06-14 10:00 | 2030 33% ECP | 700 | -526 | -510 | -267.78 | 0 | 0 | No
2030-06-14 11:00 | 2030 33% ECP | 331.7 | -526 | -510 | -338.75 | 0 | 0 | No
2030-06-14 12:00 | 2030 33% ECP | 331.7 | -526 | -510 | -278.05 | 0 | 0 | No
2030-06-14 13:00 | 2030 33% ECP | 454.37 | -526 | -510 | -160.73 | 0 | 0 | No
2030-06-14 14:00 | 2030 33% ECP | 280 | -526 | -510 | 52.74 | 0 | 0 | No
2030-06-14 15:00 | 2030 33% ECP | 700 | -526 | -510 | 39.38 | 0 | 0 | No
2030-06-14 16:00 | 2030 33% ECP | 700 | -526 | -510 | -230.68 | 0 | 0 | No
2030-06-14 17:00 | 2030 33% ECP | 280 | -526 | -510 | -274.26 | 0 | 0 | No
2030-06-14 18:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-14 19:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-14 20:00 | 2030 33% ECP | 700 | -526 | -510 | -469.19 | 0 | 0 | No
2030-06-14 21:00 | 2030 33% ECP | 700 | -439.6 | -510 | -169.19 | 0 | 0 | No
2030-06-14 22:00 | 2030 33% ECP | 700 | -139.6 | -210 | 130.81 | 0 | 0 | No
2030-06-14 23:00 | 2030 33% ECP | 700 | 0 | 90 | 294.19 | 0 | 0 | No
2030-06-15 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-15 01:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-15 02:00 | 2030 33% ECP | 700 | 0 | -7.97 | 0 | 0 | 0 | No
2030-06-15 03:00 | 2030 33% ECP | 700 | 0 | -157.1 | 0 | 0 | 0 | No
2030-06-15 04:00 | 2030 33% ECP | 700 | 0 | -140.26 | 0 | 0 | 0 | No
2030-06-15 05:00 | 2030 33% ECP | 700 | 0 | -440.26 | 0 | 0 | 0 | No
2030-06-15 06:00 | 2030 33% ECP | 281.61 | -226 | -210 | -210 | 0 | 0 | No
2030-06-15 07:00 | 2030 33% ECP | -138.39 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 08:00 | 2030 33% ECP | 166.5 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 09:00 | 2030 33% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 10:00 | 2030 33% ECP | -306.04 | -526 | -510 | -399.1 | 0 | 0 | No
2030-06-15 11:00 | 2030 33% ECP | -423.25 | -526 | -510 | -99.1 | 0 | 0 | No
2030-06-15 12:00 | 2030 33% ECP | -667.7 | -526 | -510 | -125.24 | 0 | 0 | No
2030-06-15 13:00 | 2030 33% ECP | -247.7 | -526 | -510 | -82.35 | 0 | 0 | No
2030-06-15 14:00 | 2030 33% ECP | -48.41 | -526 | -510 | -294.64 | 0 | 0 | No
2030-06-15 15:00 | 2030 33% ECP | 79.09 | -526 | -510 | -292.03 | 0 | 0 | No
2030-06-15 16:00 | 2030 33% ECP | 499.09 | -526 | -510 | -210 | 0 | 0 | No
2030-06-15 17:00 | 2030 33% ECP | 79.09 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 18:00 | 2030 33% ECP | 499.09 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 19:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 20:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 21:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 22:00 | 2030 33% ECP | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-06-15 23:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-16 | 2030 33% ECP | 700 | 0 | -83.78 | 0 | 0 | 0 | No
2030-06-16 01:00 | 2030 33% ECP | 700 | 0 | -96.36 | 0 | 0 | 0 | No
2030-06-16 02:00 | 2030 33% ECP | 700 | 0 | -142.43 | 0 | 0 | 0 | No
2030-06-16 03:00 | 2030 33% ECP | 700 | 0 | -221.49 | 0 | 0 | 0 | No
2030-06-16 04:00 | 2030 33% ECP | 700 | 0 | -123.98 | 0 | 0 | 0 | No
2030-06-16 05:00 | 2030 33% ECP | 700 | 0 | -412.44 | 0 | 0 | 0 | No
2030-06-16 06:00 | 2030 33% ECP | 700 | -226 | -510 | -35.01 | 0 | 0 | No
2030-06-16 07:00 | 2030 33% ECP | 700 | -526 | -510 | 192.38 | 0 | 0 | No
2030-06-16 08:00 | 2030 33% ECP | 700 | -526 | -510 | 168.65 | 0 | 0 | No
2030-06-16 09:00 | 2030 33% ECP | 700 | -526 | -510 | 141.48 | 0 | 0 | No
2030-06-16 10:00 | 2030 33% ECP | 432.7 | -526 | -510 | 138.94 | 0 | 0 | No
2030-06-16 11:00 | 2030 33% ECP | 432.7 | -526 | -510 | -161.06 | 0 | 0 | No
2030-06-16 12:00 | 2030 33% ECP | 12.7 | -526 | -510 | -224.76 | 0 | 0 | No
2030-06-16 13:00 | 2030 33% ECP | 420 | -526 | -510 | -210.72 | 0 | 0 | No
2030-06-16 14:00 | 2030 33% ECP | 0 | -526 | -510 | -246.03 | 0 | 0 | No
2030-06-16 15:00 | 2030 33% ECP | 420 | -526 | -510 | 53.97 | 0 | 0 | No
2030-06-16 16:00 | 2030 33% ECP | 700 | -526 | -510 | 140.97 | 0 | 0 | No
2030-06-16 17:00 | 2030 33% ECP | 700 | -526 | -510 | 107.92 | 0 | 0 | No
2030-06-16 18:00 | 2030 33% ECP | 700 | -226 | -510 | 231.74 | 0 | 0 | No
2030-06-16 19:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-16 20:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-16 21:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-16 22:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-16 23:00 | 2030 33% ECP | 700 | 0 | -510 | 89.93 | 0 | 0 | No
2030-06-17 | 2030 33% ECP | 700 | 0 | -417.47 | 32.34 | 0 | 0 | No
2030-06-17 01:00 | 2030 33% ECP | 700 | 0 | -117.47 | 0 | 0 | 0 | No
2030-06-17 02:00 | 2030 33% ECP | 700 | 0 | -47.95 | 55.94 | 0 | 0 | No
2030-06-17 03:00 | 2030 33% ECP | 700 | 0 | -347.95 | 0 | 0 | 0 | No
2030-06-17 04:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-17 05:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-17 06:00 | 2030 33% ECP | 700 | 0 | -308.07 | 0 | 0 | 0 | No
2030-06-17 07:00 | 2030 33% ECP | 700 | -226 | -510 | 100.93 | 0 | 0 | No
2030-06-17 08:00 | 2030 33% ECP | 700 | -526 | -510 | 260.26 | 0 | 0 | No
2030-06-17 09:00 | 2030 33% ECP | 700 | -526 | -510 | 305.02 | 0 | 0 | No
2030-06-17 10:00 | 2030 33% ECP | 700 | -526 | -510 | 291.04 | 0 | 0 | No
2030-06-17 11:00 | 2030 33% ECP | 700 | -526 | -510 | 329.28 | 0 | 0 | No
2030-06-17 12:00 | 2030 33% ECP | 700 | -526 | -510 | 298.33 | 0 | 0 | No
2030-06-17 13:00 | 2030 33% ECP | 700 | -526 | -510 | 222.47 | 0 | 0 | No
2030-06-17 14:00 | 2030 33% ECP | 700 | -526 | -510 | 254.31 | 0 | 0 | No
2030-06-17 15:00 | 2030 33% ECP | 700 | -526 | -510 | 261.47 | 0 | 0 | No
2030-06-17 16:00 | 2030 33% ECP | 700 | -526 | -510 | 319.01 | 0 | 0 | No
2030-06-17 17:00 | 2030 33% ECP | 387.29 | -300 | -425.48 | 405.81 | 0 | 0 | No
2030-06-17 18:00 | 2030 33% ECP | 700 | 0 | -125.48 | 429.43 | 0 | 0 | No
2030-06-17 19:00 | 2030 33% ECP | 700 | 0 | 0 | 314.76 | 0 | 0 | No
2030-06-17 20:00 | 2030 33% ECP | 700 | 0 | 90.62 | 312.76 | 0 | 0 | No
2030-06-17 21:00 | 2030 33% ECP | 700 | 0 | 390.62 | 295.55 | 0 | 0 | No
2030-06-17 22:00 | 2030 33% ECP | 700 | 0 | 90.62 | 241.56 | 0 | 0 | No
2030-06-17 23:00 | 2030 33% ECP | 700 | 0 | 0 | 120.58 | 0 | 0 | No
2030-06-18 | 2030 33% ECP | 700 | 0 | 300 | 86.35 | 0 | 0 | No
2030-06-18 01:00 | 2030 33% ECP | 700 | 0 | 93.59 | 91.5 | 0 | 0 | No
2030-06-18 02:00 | 2030 33% ECP | 700 | 0 | 263.96 | 98.7 | 0 | 0 | No
2030-06-18 03:00 | 2030 33% ECP | 700 | 0 | 85.21 | 88.63 | 0 | 0 | No
2030-06-18 04:00 | 2030 33% ECP | 700 | 0 | 241.09 | 56.02 | 0 | 0 | No
2030-06-18 05:00 | 2030 33% ECP | 700 | 0 | 14.03 | 32 | 0 | 0 | No
2030-06-18 06:00 | 2030 33% ECP | 700 | 0 | 3.13 | 93.41 | 0 | 0 | No
2030-06-18 07:00 | 2030 33% ECP | 331.18 | 0 | 0 | 222.31 | 0 | 0 | No
2030-06-18 08:00 | 2030 33% ECP | -88.82 | -300 | -300 | 248.59 | 0 | 0 | No
2030-06-18 09:00 | 2030 33% ECP | -508.82 | -526 | -510 | 248.77 | 0 | 0 | No
2030-06-18 10:00 | 2030 33% ECP | -700 | -526 | -510 | 209.93 | 0 | 0 | No
2030-06-18 11:00 | 2030 33% ECP | -700 | -526 | -510 | 233.04 | 0 | 0 | No
2030-06-18 12:00 | 2030 33% ECP | -700 | -526 | -510 | 237.37 | 0 | 0 | No
2030-06-18 13:00 | 2030 33% ECP | -508.54 | -526 | -510 | 187.7 | 0 | 0 | No
2030-06-18 14:00 | 2030 33% ECP | -211.25 | -526 | -510 | 192.96 | 0 | 0 | No
2030-06-18 15:00 | 2030 33% ECP | 208.75 | -244.31 | -510 | 185.35 | 0 | 0 | No
2030-06-18 16:00 | 2030 33% ECP | 628.75 | 0 | -267.94 | 227.25 | 0 | 0 | No
2030-06-18 17:00 | 2030 33% ECP | 700 | 0 | 32.06 | 182.62 | 0 | 0 | No
2030-06-18 18:00 | 2030 33% ECP | 700 | 0 | 296.03 | 235.13 | 0 | 0 | No
2030-06-18 19:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-18 20:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-18 21:00 | 2030 33% ECP | 700 | 0 | -1.96 | 0 | 0 | 0 | No
2030-06-18 22:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-18 23:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-19 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-19 01:00 | 2030 33% ECP | 700 | 0 | -224.26 | 0 | 0 | 0 | No
2030-06-19 02:00 | 2030 33% ECP | 700 | 0 | -203.58 | 0 | 0 | 0 | No
2030-06-19 03:00 | 2030 33% ECP | 700 | 0 | -51.96 | 0 | 0 | 0 | No
2030-06-19 04:00 | 2030 33% ECP | 700 | 0 | -312.02 | 0 | 0 | 0 | No
2030-06-19 05:00 | 2030 33% ECP | 700 | 0 | -332.94 | 0 | 0 | 0 | No
2030-06-19 06:00 | 2030 33% ECP | 700 | 0 | -422.44 | 0 | 0 | 0 | No
2030-06-19 07:00 | 2030 33% ECP | 700 | 0 | -203.13 | 115.77 | 0 | 0 | No
2030-06-19 08:00 | 2030 33% ECP | 700 | 0 | -316.18 | 126.62 | 0 | 0 | No
2030-06-19 09:00 | 2030 33% ECP | 539.85 | -300 | -510 | 251.22 | 0 | 0 | No
2030-06-19 10:00 | 2030 33% ECP | 140 | -126.13 | -437.23 | 119.91 | 0 | 0 | No
2030-06-19 11:00 | 2030 33% ECP | -280 | -426.13 | -510 | 290.26 | 0 | 0 | No
2030-06-19 12:00 | 2030 33% ECP | -700 | -526 | -510 | 244.28 | 0 | 0 | No
2030-06-19 13:00 | 2030 33% ECP | -700 | -526 | -510 | 217.35 | 0 | 0 | No
2030-06-19 14:00 | 2030 33% ECP | -700 | -526 | -510 | 219.19 | 0 | 0 | No
2030-06-19 15:00 | 2030 33% ECP | -700 | -526 | -510 | 230.92 | 0 | 0 | No
2030-06-19 16:00 | 2030 33% ECP | -596.61 | -526 | -510 | 54.71 | 0 | 0 | No
2030-06-19 17:00 | 2030 33% ECP | -176.61 | -226 | -500.32 | 3.35 | 0 | 0 | No
2030-06-19 18:00 | 2030 33% ECP | 243.39 | 0 | -200.32 | 93.26 | 0 | 0 | No
2030-06-19 19:00 | 2030 33% ECP | 663.39 | 0 | 0 | 212.49 | 0 | 0 | No
2030-06-19 20:00 | 2030 33% ECP | 700 | 0 | 0 | 258.03 | 0 | 0 | No
2030-06-19 21:00 | 2030 33% ECP | 532.92 | 0 | 0 | 292.25 | 0 | 0 | No
2030-06-19 22:00 | 2030 33% ECP | 700 | 0 | 0 | 161.77 | 0 | 0 | No
2030-06-19 23:00 | 2030 33% ECP | 700 | 0 | 0 | 140.22 | 0 | 0 | No
2030-06-20 | 2030 33% ECP | 700 | 0 | 0 | 67.28 | 0 | 0 | No
2030-06-20 01:00 | 2030 33% ECP | 700 | 0 | -87.06 | 137.52 | 0 | 0 | No
2030-06-20 02:00 | 2030 33% ECP | 700 | 0 | -387.06 | 127.39 | 0 | 0 | No
2030-06-20 03:00 | 2030 33% ECP | 560 | -104.14 | -510 | 78.68 | 0 | 0 | No
2030-06-20 04:00 | 2030 33% ECP | 140 | 0 | -373.39 | 62.67 | 0 | 0 | No
2030-06-20 05:00 | 2030 33% ECP | -280 | -226 | -430 | 0 | 0 | 0 | No
2030-06-20 06:00 | 2030 33% ECP | -700 | -526 | -510 | 38.76 | 0 | 0 | No
2030-06-20 07:00 | 2030 33% ECP | -692.3 | -526 | -510 | 120.76 | 0 | 0 | No
2030-06-20 08:00 | 2030 33% ECP | -700 | -526 | -510 | 42.02 | 0 | 0 | Yes
2030-06-20 09:00 | 2030 33% ECP | -700 | -526 | -510 | -121.11 | 0 | 0 | Yes
2030-06-20 10:00 | 2030 33% ECP | -700 | -526 | -510 | -82.26 | 0 | 0 | Yes
2030-06-20 11:00 | 2030 33% ECP | -700 | -526 | -510 | -288.57 | 0 | 0 | Yes
2030-06-20 12:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 13:00 | 2030 33% ECP | -700 | -526 | -510 | -501.41 | 0 | 0 | Yes
2030-06-20 14:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 15:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 16:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 17:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 18:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-20 19:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-20 20:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-20 21:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-20 22:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-06-20 23:00 | 2030 33% ECP | -700 | 74 | 90 | 55.57 | 0 | 0 | Yes
2030-06-21 | 2030 33% ECP | -492.87 | 374 | 390 | 355.57 | 0 | 0 | Yes
2030-06-21 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-21 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 15:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-06-21 16:00 | 2030 33% ECP | -700 | 74 | 90 | 499.86 | 0 | 0 | Yes
2030-06-21 17:00 | 2030 33% ECP | -280 | -226 | -210 | 199.86 | 0 | 0 | Yes
2030-06-21 18:00 | 2030 33% ECP | 140 | -526 | -510 | 0 | 0 | 0 | No
2030-06-21 19:00 | 2030 33% ECP | 560 | -526 | -510 | 275.53 | 0 | 0 | No
2030-06-21 20:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-06-21 21:00 | 2030 33% ECP | 591.81 | -526 | -510 | 410.49 | 0 | 0 | No
2030-06-21 22:00 | 2030 33% ECP | 372.06 | -526 | -510 | 374.8 | 0 | 0 | No
2030-06-21 23:00 | 2030 33% ECP | 700 | -526 | -510 | 379.41 | 0 | 0 | No
2030-06-22 | 2030 33% ECP | 280 | -526 | -510 | 291.96 | 0 | 0 | No
2030-06-22 01:00 | 2030 33% ECP | 650.34 | -226 | -210 | 244.34 | 0 | 0 | No
2030-06-22 02:00 | 2030 33% ECP | 464.79 | 0 | 0 | 239.53 | 0 | 0 | No
2030-06-22 03:00 | 2030 33% ECP | 44.79 | 0 | -195.21 | 440.55 | 0 | 0 | No
2030-06-22 04:00 | 2030 33% ECP | -237.39 | -226 | -210 | 140.55 | 0 | 0 | No
2030-06-22 05:00 | 2030 33% ECP | -657.39 | -526 | -510 | -159.45 | 0 | 0 | No
2030-06-22 06:00 | 2030 33% ECP | -700 | -526 | -510 | -459.45 | 0 | 0 | No
2030-06-22 07:00 | 2030 33% ECP | -497.97 | -526 | -510 | -510 | 0 | 0 | No
2030-06-22 08:00 | 2030 33% ECP | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-06-22 09:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-06-22 10:00 | 2030 33% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-06-22 11:00 | 2030 33% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-06-22 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 16:00 | 2030 33% ECP | -700 | 505 | 510 | 426.15 | 0 | 0 | Yes
2030-06-22 17:00 | 2030 33% ECP | -700 | 300 | 295.38 | 126.15 | 0 | 0 | Yes
2030-06-22 18:00 | 2030 33% ECP | -700 | 0 | -4.62 | -173.85 | 0 | 0 | Yes
2030-06-22 19:00 | 2030 33% ECP | -700 | 300 | 295.38 | 126.15 | 0 | 0 | Yes
2030-06-22 20:00 | 2030 33% ECP | -465.05 | 505 | 510 | 426.15 | 0 | 0 | Yes
2030-06-22 21:00 | 2030 33% ECP | -45.05 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 22:00 | 2030 33% ECP | 197.41 | 505 | 510 | 510 | 0 | 0 | No
2030-06-22 23:00 | 2030 33% ECP | 617.41 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 06:00 | 2030 33% ECP | 700 | 205 | 246 | 210 | 0 | 0 | No
2030-06-23 07:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 08:00 | 2030 33% ECP | 700 | 456.58 | 510 | 510 | 0 | 0 | No
2030-06-23 09:00 | 2030 33% ECP | 700 | 156.58 | 210 | 304.41 | 0 | 0 | No
2030-06-23 10:00 | 2030 33% ECP | 700 | 0 | 282.95 | 378.45 | 0 | 0 | No
2030-06-23 11:00 | 2030 33% ECP | 700 | 205 | 401.28 | 360.24 | 0 | 0 | No
2030-06-23 12:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 13:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 14:00 | 2030 33% ECP | 700 | 300 | 284.66 | 510 | 0 | 0 | No
2030-06-23 15:00 | 2030 33% ECP | 700 | 0 | -15.34 | 510 | 0 | 0 | No
2030-06-23 16:00 | 2030 33% ECP | 700 | -300 | -315.34 | 362.24 | 0 | 0 | No
2030-06-23 17:00 | 2030 33% ECP | 700 | -526 | -510 | 176.14 | 0 | 0 | No
2030-06-23 18:00 | 2030 33% ECP | 700 | -526 | -510 | 10.66 | 0 | 0 | No
2030-06-23 19:00 | 2030 33% ECP | 700 | -283.33 | -510 | 240.63 | 0 | 0 | No
2030-06-23 20:00 | 2030 33% ECP | 700 | -283.33 | -510 | 0 | 0 | 0 | No
2030-06-23 21:00 | 2030 33% ECP | 700 | -432.36 | -510 | 250.62 | 0 | 0 | No
2030-06-23 22:00 | 2030 33% ECP | 700 | -132.36 | -510 | 214.55 | 0 | 0 | No
2030-06-23 23:00 | 2030 33% ECP | 700 | -33.86 | -510 | 0 | 0 | 0 | No
2030-06-24 | 2030 33% ECP | 700 | 0 | -292.68 | 255.04 | 0 | 0 | No
2030-06-24 01:00 | 2030 33% ECP | 700 | 0 | 0 | 335.91 | 0 | 0 | No
2030-06-24 02:00 | 2030 33% ECP | 700 | 190.84 | 273.4 | 375.21 | 0 | 0 | No
2030-06-24 03:00 | 2030 33% ECP | 700 | 490.84 | 510 | 510 | 0 | 0 | No
2030-06-24 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-24 05:00 | 2030 33% ECP | 700 | 205 | 210 | 312.89 | 0 | 0 | No
2030-06-24 06:00 | 2030 33% ECP | 700 | 0 | 375.61 | 364.06 | 0 | 0 | No
2030-06-24 07:00 | 2030 33% ECP | 700 | 207.51 | 510 | 510 | 0 | 0 | No
2030-06-24 08:00 | 2030 33% ECP | 700 | 116.67 | 210 | 510 | 0 | 0 | No
2030-06-24 09:00 | 2030 33% ECP | 360.92 | -183.33 | -90 | 510 | 0 | 0 | No
2030-06-24 10:00 | 2030 33% ECP | 700 | -483.33 | -390 | 510 | 0 | 0 | No
2030-06-24 11:00 | 2030 33% ECP | 280 | -526 | -510 | 448.68 | 0 | 0 | No
2030-06-24 12:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-06-24 13:00 | 2030 33% ECP | 298.1 | -526 | -510 | 510 | 0 | 0 | No
2030-06-24 14:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-06-24 15:00 | 2030 33% ECP | 700 | -526 | -510 | 499.01 | 0 | 0 | No
2030-06-24 16:00 | 2030 33% ECP | 700 | -526 | -510 | 460.48 | 0 | 0 | No
2030-06-24 17:00 | 2030 33% ECP | 700 | -526 | -510 | 450.08 | 0 | 0 | No
2030-06-24 18:00 | 2030 33% ECP | 700 | -226 | -410.7 | 450.08 | 0 | 0 | No
2030-06-24 19:00 | 2030 33% ECP | 700 | 0 | -506.51 | 407.73 | 0 | 0 | No
2030-06-24 20:00 | 2030 33% ECP | 700 | 0 | -206.51 | 407.73 | 0 | 0 | No
2030-06-24 21:00 | 2030 33% ECP | 700 | 0 | 0 | 407.73 | 0 | 0 | No
2030-06-24 22:00 | 2030 33% ECP | 700 | 16.83 | 210 | 323.52 | 0 | 0 | No
2030-06-24 23:00 | 2030 33% ECP | 700 | 316.83 | 510 | 510 | 0 | 0 | No
2030-06-25 | 2030 33% ECP | 700 | 16.83 | 210 | 210 | 0 | 0 | No
2030-06-25 01:00 | 2030 33% ECP | 700 | 0 | -90 | 350.33 | 0 | 0 | No
2030-06-25 02:00 | 2030 33% ECP | 700 | 0 | -178.38 | 320.68 | 0 | 0 | No
2030-06-25 03:00 | 2030 33% ECP | 700 | 0 | -178.38 | 237.23 | 0 | 0 | No
2030-06-25 04:00 | 2030 33% ECP | 700 | 0 | -70.01 | 237.23 | 0 | 0 | No
2030-06-25 05:00 | 2030 33% ECP | 700 | 0 | -370.01 | 279.24 | 0 | 0 | No
2030-06-25 06:00 | 2030 33% ECP | 700 | -284.86 | -510 | 330.43 | 0 | 0 | No
2030-06-25 07:00 | 2030 33% ECP | 700 | -526 | -510 | 406.12 | 0 | 0 | No
2030-06-25 08:00 | 2030 33% ECP | 700 | -526 | -510 | 447.31 | 0 | 0 | No
2030-06-25 09:00 | 2030 33% ECP | 420 | -526 | -510 | 451.15 | 0 | 0 | No
2030-06-25 10:00 | 2030 33% ECP | 0 | -526 | -510 | 313.01 | 0 | 0 | No
2030-06-25 11:00 | 2030 33% ECP | 348.43 | -526 | -510 | 405.8 | 0 | 0 | No
2030-06-25 12:00 | 2030 33% ECP | 348.43 | -226 | -210 | 510 | 0 | 0 | No
2030-06-25 13:00 | 2030 33% ECP | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-06-25 14:00 | 2030 33% ECP | 280 | 0 | 0 | 510 | 0 | 0 | No
2030-06-25 15:00 | 2030 33% ECP | 700 | 0 | -164.07 | 510 | 0 | 0 | No
2030-06-25 16:00 | 2030 33% ECP | 700 | -300 | -464.07 | 399.39 | 0 | 0 | No
2030-06-25 17:00 | 2030 33% ECP | 700 | 0 | -164.07 | 510 | 0 | 0 | No
2030-06-25 18:00 | 2030 33% ECP | 700 | 0 | 135.93 | 510 | 0 | 0 | No
2030-06-25 19:00 | 2030 33% ECP | 700 | 0 | 435.93 | 449.4 | 0 | 0 | No
2030-06-25 20:00 | 2030 33% ECP | 700 | 0 | 510 | 492.53 | 0 | 0 | No
2030-06-25 21:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-06-25 22:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-06-25 23:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-06-26 | 2030 33% ECP | 700 | 0 | 434.57 | 431.38 | 0 | 0 | No
2030-06-26 01:00 | 2030 33% ECP | 700 | 0 | 344.9 | 456.79 | 0 | 0 | No
2030-06-26 02:00 | 2030 33% ECP | 700 | 0 | 283.29 | 453.65 | 0 | 0 | No
2030-06-26 03:00 | 2030 33% ECP | 700 | 0 | 77.52 | 422.58 | 0 | 0 | No
2030-06-26 04:00 | 2030 33% ECP | 700 | 0 | 0 | 281.95 | 0 | 0 | No
2030-06-26 05:00 | 2030 33% ECP | 700 | 0 | 0 | 47.36 | 0 | 0 | No
2030-06-26 06:00 | 2030 33% ECP | 700 | -27.64 | -300 | 241.6 | 0 | 0 | No
2030-06-26 07:00 | 2030 33% ECP | 303.92 | -290.73 | -510 | 468.57 | 0 | 0 | No
2030-06-26 08:00 | 2030 33% ECP | -116.08 | -526 | -510 | 504.41 | 0 | 0 | No
2030-06-26 09:00 | 2030 33% ECP | 303.92 | -526 | -510 | 246.23 | 0 | 0 | No
2030-06-26 10:00 | 2030 33% ECP | -43.35 | -526 | -510 | 138.01 | 0 | 0 | No
2030-06-26 11:00 | 2030 33% ECP | 0 | -226 | -224.27 | 438.01 | 0 | 0 | No
2030-06-26 12:00 | 2030 33% ECP | 0 | 0 | -367.91 | 510 | 0 | 0 | No
2030-06-26 13:00 | 2030 33% ECP | -167.87 | -300 | -510 | 338.03 | 0 | 0 | No
2030-06-26 14:00 | 2030 33% ECP | 252.13 | 0 | -210 | 510 | 0 | 0 | No
2030-06-26 15:00 | 2030 33% ECP | 672.13 | 94.02 | 0 | 510 | 0 | 0 | No
2030-06-26 16:00 | 2030 33% ECP | 252.13 | -205.98 | -300 | 275.39 | 0 | 0 | No
2030-06-26 17:00 | 2030 33% ECP | 253.42 | -505.98 | -510 | 482.09 | 0 | 0 | No
2030-06-26 18:00 | 2030 33% ECP | 496.27 | -526 | -510 | 323.33 | 0 | 0 | No
2030-06-26 19:00 | 2030 33% ECP | 700 | -526 | -510 | 470.13 | 0 | 0 | No
2030-06-26 20:00 | 2030 33% ECP | 700 | -526 | -510 | 441.78 | 0 | 0 | No
2030-06-26 21:00 | 2030 33% ECP | 700 | -526 | -510 | 248.58 | 0 | 0 | No
2030-06-26 22:00 | 2030 33% ECP | 700 | -395 | -390 | 235.1 | 0 | 0 | No
2030-06-26 23:00 | 2030 33% ECP | 700 | -95 | -90 | 30.48 | 0 | 0 | No
2030-06-27 | 2030 33% ECP | 494.21 | 205 | 210 | 330.48 | 0 | 0 | No
2030-06-27 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 05:00 | 2030 33% ECP | 700 | 300 | 228.2 | 452.76 | 0 | 0 | No
2030-06-27 06:00 | 2030 33% ECP | 700 | 0 | -71.8 | 152.76 | 0 | 0 | No
2030-06-27 07:00 | 2030 33% ECP | 700 | -159.15 | -164.28 | 124.66 | 0 | 0 | No
2030-06-27 08:00 | 2030 33% ECP | 280 | 0 | 135.72 | 210 | 0 | 0 | No
2030-06-27 09:00 | 2030 33% ECP | -140 | 300 | 435.72 | 510 | 0 | 0 | No
2030-06-27 10:00 | 2030 33% ECP | -560 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 20:00 | 2030 33% ECP | -700 | 505 | 510 | 471.8 | 0 | 0 | Yes
2030-06-27 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 02:00 | 2030 33% ECP | -700 | 505 | 510 | 456.38 | 0 | 0 | Yes
2030-06-28 03:00 | 2030 33% ECP | -700 | 505 | 510 | 436.38 | 0 | 0 | Yes
2030-06-28 04:00 | 2030 33% ECP | -700 | 505 | 510 | 184.14 | 0 | 0 | Yes
2030-06-28 05:00 | 2030 33% ECP | -700 | 505 | 510 | 159.99 | 0 | 0 | Yes
2030-06-28 06:00 | 2030 33% ECP | -700 | 505 | 510 | 242.68 | 0 | 0 | Yes
2030-06-28 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 13:00 | 2030 33% ECP | -700 | 505 | 510 | 435.53 | 0 | 0 | Yes
2030-06-28 14:00 | 2030 33% ECP | -700 | 505 | 510 | 415.38 | 0 | 0 | Yes
2030-06-28 15:00 | 2030 33% ECP | -700 | 505 | 510 | 341.34 | 0 | 0 | Yes
2030-06-28 16:00 | 2030 33% ECP | -700 | 505 | 510 | 384.41 | 0 | 0 | Yes
2030-06-28 17:00 | 2030 33% ECP | -700 | 505 | 510 | 413.13 | 0 | 0 | Yes
2030-06-28 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 19:00 | 2030 33% ECP | -700 | 505 | 510 | 421.5 | 0 | 0 | Yes
2030-06-28 20:00 | 2030 33% ECP | -700 | 505 | 510 | 465.17 | 0 | 0 | Yes
2030-06-28 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 23:00 | 2030 33% ECP | -700 | 505 | 510 | 489.05 | 0 | 0 | Yes
2030-06-29 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 18:00 | 2030 33% ECP | -420 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 19:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 20:00 | 2030 33% ECP | 420 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 21:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 22:00 | 2030 33% ECP | 420 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 07:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 08:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 09:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 10:00 | 2030 33% ECP | 700 | 205 | 381.34 | 510 | 0 | 0 | No
2030-06-30 11:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 12:00 | 2030 33% ECP | 700 | 300 | 381.39 | 510 | 0 | 0 | No
2030-06-30 13:00 | 2030 33% ECP | 700 | 0 | 81.39 | 510 | 0 | 0 | No
2030-06-30 14:00 | 2030 33% ECP | 700 | -300 | -218.61 | 510 | 0 | 0 | No
2030-06-30 15:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-06-30 16:00 | 2030 33% ECP | 700 | -437.45 | -510 | 510 | 0 | 0 | No
2030-06-30 17:00 | 2030 33% ECP | 700 | -137.45 | -210 | 510 | 0 | 0 | No
2030-06-30 18:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-06-30 19:00 | 2030 33% ECP | 700 | 0 | 210.09 | 510 | 0 | 0 | No
2030-06-30 20:00 | 2030 33% ECP | 700 | 0 | 210.09 | 510 | 0 | 0 | No
2030-06-30 21:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-06-30 22:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-06-30 23:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-07-01 | 2030 33% ECP | 700 | 0 | 300 | 210 | 0 | 0 | No
2030-07-01 01:00 | 2030 33% ECP | 700 | 0 | 7.39 | 109.62 | 0 | 0 | No
2030-07-01 02:00 | 2030 33% ECP | 700 | 0 | 7.39 | 126.8 | 0 | 0 | No
2030-07-01 03:00 | 2030 33% ECP | 700 | 0 | 307.39 | 109.96 | 0 | 0 | No
2030-07-01 04:00 | 2030 33% ECP | 700 | 0 | 294.09 | 15.47 | 0 | 0 | No
2030-07-01 05:00 | 2030 33% ECP | 700 | 0 | 294.09 | 0 | 0 | 0 | No
2030-07-01 06:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-01 07:00 | 2030 33% ECP | 700 | 0 | 0 | 157.16 | 0 | 0 | No
2030-07-01 08:00 | 2030 33% ECP | 700 | -3.23 | -210 | 248.43 | 0 | 0 | No
2030-07-01 09:00 | 2030 33% ECP | 700 | -303.23 | -510 | 299.23 | 0 | 0 | No
2030-07-01 10:00 | 2030 33% ECP | 700 | -526 | -510 | 253.06 | 0 | 0 | No
2030-07-01 11:00 | 2030 33% ECP | 700 | -526 | -510 | 289.3 | 0 | 0 | No
2030-07-01 12:00 | 2030 33% ECP | 700 | -526 | -510 | 238.75 | 0 | 0 | No
2030-07-01 13:00 | 2030 33% ECP | 700 | -526 | -510 | 177.86 | 0 | 0 | No
2030-07-01 14:00 | 2030 33% ECP | 700 | -526 | -510 | 161.53 | 0 | 0 | No
2030-07-01 15:00 | 2030 33% ECP | 700 | -526 | -510 | 138.39 | 0 | 0 | No
2030-07-01 16:00 | 2030 33% ECP | 700 | -526 | -510 | 113.17 | 0 | 0 | No
2030-07-01 17:00 | 2030 33% ECP | 700 | -461.4 | -510 | 137.13 | 0 | 0 | No
2030-07-01 18:00 | 2030 33% ECP | 700 | -161.4 | -255.5 | 192.75 | 0 | 0 | No
2030-07-01 19:00 | 2030 33% ECP | 700 | 0 | 0 | 181.56 | 0 | 0 | No
2030-07-01 20:00 | 2030 33% ECP | 700 | 0 | 0 | 156.68 | 0 | 0 | No
2030-07-01 21:00 | 2030 33% ECP | 700 | 0 | -78.55 | 182.57 | 0 | 0 | No
2030-07-01 22:00 | 2030 33% ECP | 700 | 0 | 0 | 218.32 | 0 | 0 | No
2030-07-01 23:00 | 2030 33% ECP | 700 | 0 | 0 | 172.35 | 0 | 0 | No
2030-07-02 | 2030 33% ECP | 700 | 0 | -31.9 | 112.17 | 0 | 0 | No
2030-07-02 01:00 | 2030 33% ECP | 700 | 0 | -298.35 | 111.19 | 0 | 0 | No
2030-07-02 02:00 | 2030 33% ECP | 700 | 0 | -341.84 | 95.1 | 0 | 0 | No
2030-07-02 03:00 | 2030 33% ECP | 700 | 0 | -510 | 85.87 | 0 | 0 | No
2030-07-02 04:00 | 2030 33% ECP | 700 | 0 | -510 | 72.71 | 0 | 0 | No
2030-07-02 05:00 | 2030 33% ECP | 700 | -122.91 | -510 | 40.8 | 0 | 0 | No
2030-07-02 06:00 | 2030 33% ECP | 453.96 | 0 | -355.45 | 66.43 | 0 | 0 | No
2030-07-02 07:00 | 2030 33% ECP | 33.96 | -226 | -408.75 | 138.1 | 0 | 0 | No
2030-07-02 08:00 | 2030 33% ECP | -386.04 | -526 | -510 | 145.17 | 0 | 0 | No
2030-07-02 09:00 | 2030 33% ECP | -700 | -526 | -510 | -16.07 | 0 | 0 | No
2030-07-02 10:00 | 2030 33% ECP | -700 | -526 | -510 | -194.4 | 0 | 0 | No
2030-07-02 11:00 | 2030 33% ECP | -700 | -526 | -510 | -144.68 | 0 | 0 | No
2030-07-02 12:00 | 2030 33% ECP | -700 | -526 | -510 | 79.86 | 0 | 0 | No
2030-07-02 13:00 | 2030 33% ECP | -700 | -526 | -510 | 2.05 | 0 | 0 | No
2030-07-02 14:00 | 2030 33% ECP | -428.64 | -526 | -510 | 51.17 | 0 | 0 | No
2030-07-02 15:00 | 2030 33% ECP | -8.64 | -526 | -510 | 73.32 | 0 | 0 | No
2030-07-02 16:00 | 2030 33% ECP | -428.64 | -526 | -510 | 207.8 | 0 | 0 | No
2030-07-02 17:00 | 2030 33% ECP | -8.64 | -226 | -399.52 | 353.16 | 0 | 0 | No
2030-07-02 18:00 | 2030 33% ECP | 411.36 | 0 | -99.52 | 382.33 | 0 | 0 | No
2030-07-02 19:00 | 2030 33% ECP | 700 | 0 | -99.52 | 330.91 | 0 | 0 | No
2030-07-02 20:00 | 2030 33% ECP | 700 | 0 | 0 | 241.81 | 0 | 0 | No
2030-07-02 21:00 | 2030 33% ECP | 700 | 0 | -300 | 220.58 | 0 | 0 | No
2030-07-02 22:00 | 2030 33% ECP | 553.32 | -226 | -510 | 273.93 | 0 | 0 | No
2030-07-02 23:00 | 2030 33% ECP | 133.32 | -526 | -510 | 137.5 | 0 | 0 | No
2030-07-03 | 2030 33% ECP | 205.21 | -526 | -510 | -109.5 | 0 | 0 | No
2030-07-03 01:00 | 2030 33% ECP | 625.21 | -526 | -510 | -51.09 | 0 | 0 | No
2030-07-03 02:00 | 2030 33% ECP | 205.21 | -496.04 | -510 | -230.4 | 0 | 0 | No
2030-07-03 03:00 | 2030 33% ECP | 0 | -206.27 | -300 | -235.86 | 0 | 0 | No
2030-07-03 04:00 | 2030 33% ECP | -280 | 0 | 0 | 0 | 0 | 0 | No
2030-07-03 05:00 | 2030 33% ECP | -700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-03 06:00 | 2030 33% ECP | -480.53 | 0 | 0 | 0 | 0 | 0 | No
2030-07-03 07:00 | 2030 33% ECP | -480.53 | 0 | 0 | 99.01 | 0 | 0 | No
2030-07-03 08:00 | 2030 33% ECP | -280 | 205 | 210 | 399.01 | 0 | 0 | No
2030-07-03 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 11:00 | 2030 33% ECP | -675.2 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 12:00 | 2030 33% ECP | -442.87 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 13:00 | 2030 33% ECP | -82.42 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 14:00 | 2030 33% ECP | 209.03 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 15:00 | 2030 33% ECP | 601.54 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 16:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 17:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 18:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 19:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 20:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 21:00 | 2030 33% ECP | 280 | 205 | 210 | 288.54 | 0 | 0 | No
2030-07-03 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 05:00 | 2030 33% ECP | 700 | 481.6 | 390 | 510 | 0 | 0 | No
2030-07-04 06:00 | 2030 33% ECP | 700 | 181.6 | 90 | 302.42 | 0 | 0 | No
2030-07-04 07:00 | 2030 33% ECP | 700 | -118.4 | -210 | 420.55 | 0 | 0 | No
2030-07-04 08:00 | 2030 33% ECP | 700 | -418.4 | -510 | 510 | 0 | 0 | No
2030-07-04 09:00 | 2030 33% ECP | 700 | -118.4 | -300 | 510 | 0 | 0 | No
2030-07-04 10:00 | 2030 33% ECP | 700 | 181.6 | 0 | 510 | 0 | 0 | No
2030-07-04 11:00 | 2030 33% ECP | 280 | 300 | 10.02 | 510 | 0 | 0 | No
2030-07-04 12:00 | 2030 33% ECP | 0 | 0 | -289.98 | 510 | 0 | 0 | No
2030-07-04 13:00 | 2030 33% ECP | 0 | 0 | -86.87 | 510 | 0 | 0 | No
2030-07-04 14:00 | 2030 33% ECP | -68.88 | -85.97 | -310.07 | 510 | 0 | 0 | No
2030-07-04 15:00 | 2030 33% ECP | 189.98 | -385.97 | -510 | 510 | 0 | 0 | No
2030-07-04 16:00 | 2030 33% ECP | 609.98 | -526 | -510 | 505.06 | 0 | 0 | No
2030-07-04 17:00 | 2030 33% ECP | 700 | -526 | -510 | 370.38 | 0 | 0 | No
2030-07-04 18:00 | 2030 33% ECP | 457.99 | -526 | -510 | 70.38 | 0 | 0 | No
2030-07-04 19:00 | 2030 33% ECP | 140 | -526 | -510 | -229.62 | 0 | 0 | No
2030-07-04 20:00 | 2030 33% ECP | -280 | -291.7 | -510 | -510 | 0 | 0 | No
2030-07-04 21:00 | 2030 33% ECP | -700 | 8.3 | -210 | -210 | 0 | 0 | No
2030-07-04 22:00 | 2030 33% ECP | -700 | 308.3 | 90 | 90 | 0 | 0 | Yes
2030-07-04 23:00 | 2030 33% ECP | -700 | 505 | 390 | 200.7 | 0 | 0 | Yes
2030-07-05 | 2030 33% ECP | -700 | 505 | 510 | 56.14 | 0 | 0 | Yes
2030-07-05 01:00 | 2030 33% ECP | -700 | 505 | 510 | 73.48 | 0 | 0 | Yes
2030-07-05 02:00 | 2030 33% ECP | -700 | 505 | 510 | -11.05 | 0 | 0 | Yes
2030-07-05 03:00 | 2030 33% ECP | -700 | 505 | 510 | 219.67 | 0 | 0 | Yes
2030-07-05 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 05:00 | 2030 33% ECP | -700 | 505 | 510 | 266.02 | 0 | 0 | Yes
2030-07-05 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 10:00 | 2030 33% ECP | -700 | 505 | 510 | 479.2 | 0 | 0 | Yes
2030-07-05 11:00 | 2030 33% ECP | -700 | 505 | 507.77 | 179.2 | 0 | 0 | Yes
2030-07-05 12:00 | 2030 33% ECP | -700 | 505 | 447 | -120.8 | 0 | 0 | Yes
2030-07-05 13:00 | 2030 33% ECP | -700 | 505 | 510 | 10.05 | 0 | 0 | Yes
2030-07-05 14:00 | 2030 33% ECP | -700 | 505 | 370.91 | 0 | 0 | 0 | Yes
2030-07-05 15:00 | 2030 33% ECP | -700 | 505 | 510 | -29.91 | 0 | 0 | Yes
2030-07-05 16:00 | 2030 33% ECP | -700 | 481.76 | 510 | 118.5 | 0 | 0 | Yes
2030-07-05 17:00 | 2030 33% ECP | -700 | 505 | 510 | 265.54 | 0 | 0 | Yes
2030-07-05 18:00 | 2030 33% ECP | -700 | 505 | 510 | 200.67 | 0 | 0 | Yes
2030-07-05 19:00 | 2030 33% ECP | -700 | 505 | 510 | 275.32 | 0 | 0 | Yes
2030-07-05 20:00 | 2030 33% ECP | -700 | 505 | 510 | 445.01 | 0 | 0 | Yes
2030-07-05 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 22:00 | 2030 33% ECP | -700 | 505 | 510 | 366.95 | 0 | 0 | Yes
2030-07-05 23:00 | 2030 33% ECP | -700 | 505 | 510 | 499.18 | 0 | 0 | Yes
2030-07-06 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 01:00 | 2030 33% ECP | -700 | 505 | 510 | 290.08 | 0 | 0 | Yes
2030-07-06 02:00 | 2030 33% ECP | -700 | 505 | 510 | 158.3 | 0 | 0 | Yes
2030-07-06 03:00 | 2030 33% ECP | -700 | 505 | 510 | 458.3 | 0 | 0 | Yes
2030-07-06 04:00 | 2030 33% ECP | -700 | 505 | 510 | 486.1 | 0 | 0 | Yes
2030-07-06 05:00 | 2030 33% ECP | -700 | 505 | 510 | 478.13 | 0 | 0 | Yes
2030-07-06 06:00 | 2030 33% ECP | -700 | 505 | 510 | 178.13 | 0 | 0 | Yes
2030-07-06 07:00 | 2030 33% ECP | -700 | 505 | 510 | 413.05 | 0 | 0 | Yes
2030-07-06 08:00 | 2030 33% ECP | -700 | 505 | 510 | 447.87 | 0 | 0 | Yes
2030-07-06 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 10:00 | 2030 33% ECP | -700 | 505 | 510 | 473.24 | 0 | 0 | Yes
2030-07-06 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 12:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-07-06 13:00 | 2030 33% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-07-06 14:00 | 2030 33% ECP | -700 | -226 | -210 | 284.44 | 0 | 0 | Yes
2030-07-06 15:00 | 2030 33% ECP | -292.44 | -526 | -510 | -15.56 | 0 | 0 | No
2030-07-06 16:00 | 2030 33% ECP | 127.56 | -526 | -510 | 0 | 0 | 0 | No
2030-07-06 17:00 | 2030 33% ECP | 547.56 | -526 | -510 | 0 | 0 | 0 | No
2030-07-06 18:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-06 19:00 | 2030 33% ECP | 700 | -321.21 | -510 | 0 | 0 | 0 | No
2030-07-06 20:00 | 2030 33% ECP | 700 | -21.21 | -510 | 297.68 | 0 | 0 | No
2030-07-06 21:00 | 2030 33% ECP | 700 | 0 | -510 | 333.95 | 0 | 0 | No
2030-07-06 22:00 | 2030 33% ECP | 700 | -3.24 | -390 | 459.64 | 0 | 0 | No
2030-07-06 23:00 | 2030 33% ECP | 700 | -3.24 | -90 | 339.14 | 0 | 0 | No
2030-07-07 | 2030 33% ECP | 427.72 | 205 | 210 | 347.13 | 0 | 0 | No
2030-07-07 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-07 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-07 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-07 04:00 | 2030 33% ECP | 700 | 300 | 300 | 510 | 0 | 0 | No
2030-07-07 05:00 | 2030 33% ECP | 700 | 0 | 0 | 210 | 0 | 0 | No
2030-07-07 06:00 | 2030 33% ECP | 700 | -300 | -300 | -19.39 | 0 | 0 | No
2030-07-07 07:00 | 2030 33% ECP | 700 | -526 | -510 | 48.81 | 0 | 0 | No
2030-07-07 08:00 | 2030 33% ECP | 700 | -526 | -510 | 96.67 | 0 | 0 | No
2030-07-07 09:00 | 2030 33% ECP | 700 | -526 | -510 | 183.31 | 0 | 0 | No
2030-07-07 10:00 | 2030 33% ECP | 700 | -526 | -510 | 297.05 | 0 | 0 | No
2030-07-07 11:00 | 2030 33% ECP | 700 | -526 | -510 | 339.47 | 0 | 0 | No
2030-07-07 12:00 | 2030 33% ECP | 700 | -526 | -510 | 364.51 | 0 | 0 | No
2030-07-07 13:00 | 2030 33% ECP | 700 | -526 | -510 | 482.05 | 0 | 0 | No
2030-07-07 14:00 | 2030 33% ECP | 700 | -526 | -510 | 442.48 | 0 | 0 | No
2030-07-07 15:00 | 2030 33% ECP | 700 | -526 | -510 | 370.45 | 0 | 0 | No
2030-07-07 16:00 | 2030 33% ECP | 700 | -526 | -510 | 371 | 0 | 0 | No
2030-07-07 17:00 | 2030 33% ECP | 700 | -526 | -510 | 408.26 | 0 | 0 | No
2030-07-07 18:00 | 2030 33% ECP | 700 | -226 | -510 | 108.66 | 0 | 0 | No
2030-07-07 19:00 | 2030 33% ECP | 700 | 0 | -510 | 93.19 | 0 | 0 | No
2030-07-07 20:00 | 2030 33% ECP | 700 | 0 | -510 | 92.82 | 0 | 0 | No
2030-07-07 21:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-07-07 22:00 | 2030 33% ECP | 700 | 0 | -448.82 | 3.45 | 0 | 0 | No
2030-07-07 23:00 | 2030 33% ECP | 700 | 0 | -148.82 | 0 | 0 | 0 | No
2030-07-08 | 2030 33% ECP | 700 | 0 | -448.82 | 0 | 0 | 0 | No
2030-07-08 01:00 | 2030 33% ECP | 700 | 0 | -288.59 | 18.98 | 0 | 0 | No
2030-07-08 02:00 | 2030 33% ECP | 700 | 0 | -153.66 | 12.48 | 0 | 0 | No
2030-07-08 03:00 | 2030 33% ECP | 700 | 0 | -453.66 | 0 | 0 | 0 | No
2030-07-08 04:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-07-08 05:00 | 2030 33% ECP | 700 | 0 | -212.64 | 0 | 0 | 0 | No
2030-07-08 06:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-07-08 07:00 | 2030 33% ECP | 700 | -226 | -510 | 127.35 | 0 | 0 | No
2030-07-08 08:00 | 2030 33% ECP | 700 | -526 | -510 | 163.63 | 0 | 0 | No
2030-07-08 09:00 | 2030 33% ECP | 700 | -526 | -510 | 179.08 | 0 | 0 | No
2030-07-08 10:00 | 2030 33% ECP | 700 | -526 | -510 | 174.42 | 0 | 0 | No
2030-07-08 11:00 | 2030 33% ECP | 700 | -526 | -510 | 198.32 | 0 | 0 | No
2030-07-08 12:00 | 2030 33% ECP | 700 | -526 | -510 | 227.98 | 0 | 0 | No
2030-07-08 13:00 | 2030 33% ECP | 700 | -526 | -510 | 193.97 | 0 | 0 | No
2030-07-08 14:00 | 2030 33% ECP | 700 | -526 | -510 | 227.1 | 0 | 0 | No
2030-07-08 15:00 | 2030 33% ECP | 700 | -526 | -510 | 245.97 | 0 | 0 | No
2030-07-08 16:00 | 2030 33% ECP | 700 | -526 | -510 | 303.34 | 0 | 0 | No
2030-07-08 17:00 | 2030 33% ECP | 700 | -386.61 | -510 | 389.83 | 0 | 0 | No
2030-07-08 18:00 | 2030 33% ECP | 700 | -86.61 | -510 | 316.21 | 0 | 0 | No
2030-07-08 19:00 | 2030 33% ECP | 700 | -62.22 | -510 | 262.85 | 0 | 0 | No
2030-07-08 20:00 | 2030 33% ECP | 700 | -62.22 | -510 | 150.57 | 0 | 0 | No
2030-07-08 21:00 | 2030 33% ECP | 700 | 0 | -510 | -94.92 | 0 | 0 | No
2030-07-08 22:00 | 2030 33% ECP | 700 | -125.92 | -510 | 7.67 | 0 | 0 | No
2030-07-08 23:00 | 2030 33% ECP | 700 | -125.92 | -210 | -90 | 0 | 0 | No
2030-07-09 | 2030 33% ECP | 700 | 174.08 | 90 | 210 | 0 | 0 | No
2030-07-09 01:00 | 2030 33% ECP | 700 | 474.08 | 390 | 510 | 0 | 0 | No
2030-07-09 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-09 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-09 04:00 | 2030 33% ECP | 700 | 427.16 | 390 | 510 | 0 | 0 | No
2030-07-09 05:00 | 2030 33% ECP | 280 | 127.16 | 90 | 242.3 | 0 | 0 | No
2030-07-09 06:00 | 2030 33% ECP | -140 | -172.84 | -210 | 294.9 | 0 | 0 | No
2030-07-09 07:00 | 2030 33% ECP | 280 | -472.84 | -510 | 408.09 | 0 | 0 | No
2030-07-09 08:00 | 2030 33% ECP | 700 | -526 | -510 | 337.87 | 0 | 0 | No
2030-07-09 09:00 | 2030 33% ECP | 700 | -526 | -510 | 337.87 | 0 | 0 | No
2030-07-09 10:00 | 2030 33% ECP | 700 | -526 | -510 | 87.99 | 0 | 0 | No
2030-07-09 11:00 | 2030 33% ECP | 700 | -526 | -510 | -212.01 | 0 | 0 | No
2030-07-09 12:00 | 2030 33% ECP | 700 | -526 | -510 | -347.31 | 0 | 0 | No
2030-07-09 13:00 | 2030 33% ECP | 700 | -526 | -510 | -263.08 | 0 | 0 | No
2030-07-09 14:00 | 2030 33% ECP | 550.21 | -526 | -510 | -269.68 | 0 | 0 | No
2030-07-09 15:00 | 2030 33% ECP | 700 | -526 | -510 | -158.24 | 0 | 0 | No
2030-07-09 16:00 | 2030 33% ECP | 700 | -526 | -510 | -263.49 | 0 | 0 | No
2030-07-09 17:00 | 2030 33% ECP | 700 | -526 | -510 | -137.11 | 0 | 0 | No
2030-07-09 18:00 | 2030 33% ECP | 700 | -526 | -510 | -116.31 | 0 | 0 | No
2030-07-09 19:00 | 2030 33% ECP | 280 | -526 | -510 | 183.69 | 0 | 0 | No
2030-07-09 20:00 | 2030 33% ECP | 0 | -526 | -510 | 337.4 | 0 | 0 | No
2030-07-09 21:00 | 2030 33% ECP | 244.56 | -526 | -510 | 370.51 | 0 | 0 | No
2030-07-09 22:00 | 2030 33% ECP | 280 | -526 | -510 | 510 | 0 | 0 | No
2030-07-09 23:00 | 2030 33% ECP | 700 | -526 | -510 | 357.8 | 0 | 0 | No
2030-07-10 | 2030 33% ECP | 700 | -461.06 | -510 | 248.41 | 0 | 0 | No
2030-07-10 01:00 | 2030 33% ECP | 700 | -403.09 | -510 | 346 | 0 | 0 | No
2030-07-10 02:00 | 2030 33% ECP | 700 | -526 | -510 | 309.05 | 0 | 0 | No
2030-07-10 03:00 | 2030 33% ECP | 700 | -309.71 | -510 | 298.98 | 0 | 0 | No
2030-07-10 04:00 | 2030 33% ECP | 700 | -385.32 | -510 | 0 | 0 | 0 | No
2030-07-10 05:00 | 2030 33% ECP | 700 | -516.26 | -510 | 52.24 | 0 | 0 | No
2030-07-10 06:00 | 2030 33% ECP | 700 | -526 | -510 | 352.24 | 0 | 0 | No
2030-07-10 07:00 | 2030 33% ECP | 383.36 | -526 | -510 | 238.37 | 0 | 0 | No
2030-07-10 08:00 | 2030 33% ECP | -36.64 | -526 | -510 | 286.98 | 0 | 0 | No
2030-07-10 09:00 | 2030 33% ECP | -456.64 | -526 | -510 | 0 | 0 | 0 | No
2030-07-10 10:00 | 2030 33% ECP | -700 | -526 | -510 | 16.96 | 0 | 0 | Yes
2030-07-10 11:00 | 2030 33% ECP | -700 | -526 | -510 | -283.04 | 0 | 0 | Yes
2030-07-10 12:00 | 2030 33% ECP | -700 | -526 | -510 | -192.89 | 0 | 0 | Yes
2030-07-10 13:00 | 2030 33% ECP | -700 | -526 | -510 | -177.6 | 0 | 0 | Yes
2030-07-10 14:00 | 2030 33% ECP | -700 | -526 | -510 | -379.6 | 0 | 0 | Yes
2030-07-10 15:00 | 2030 33% ECP | -304.28 | -526 | -510 | -488.85 | 0 | 0 | Yes
2030-07-10 16:00 | 2030 33% ECP | 115.72 | -526 | -510 | -510 | 0 | 0 | No
2030-07-10 17:00 | 2030 33% ECP | 535.72 | -526 | -510 | -210 | 0 | 0 | No
2030-07-10 18:00 | 2030 33% ECP | 280 | -345.95 | -510 | -48.67 | 0 | 0 | No
2030-07-10 19:00 | 2030 33% ECP | 700 | -45.95 | -210 | 131.94 | 0 | 0 | No
2030-07-10 20:00 | 2030 33% ECP | 700 | 0 | 0 | 132.25 | 0 | 0 | No
2030-07-10 21:00 | 2030 33% ECP | 700 | 0 | -212.53 | 432.25 | 0 | 0 | No
2030-07-10 22:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-07-10 23:00 | 2030 33% ECP | 700 | 0 | 0 | 350 | 0 | 0 | No
2030-07-11 | 2030 33% ECP | 700 | 0 | -71.17 | 50 | 0 | 0 | No
2030-07-11 01:00 | 2030 33% ECP | 700 | 0 | 0 | 25.84 | 0 | 0 | No
2030-07-11 02:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-11 03:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-11 04:00 | 2030 33% ECP | 700 | 0 | -119.39 | 3.51 | 0 | 0 | No
2030-07-11 05:00 | 2030 33% ECP | 700 | 0 | -154.57 | 0 | 0 | 0 | No
2030-07-11 06:00 | 2030 33% ECP | 700 | -147.52 | -454.57 | 0 | 0 | 0 | No
2030-07-11 07:00 | 2030 33% ECP | 280 | -447.52 | -510 | -7.63 | 0 | 0 | No
2030-07-11 08:00 | 2030 33% ECP | 700 | -526 | -510 | 21.54 | 0 | 0 | No
2030-07-11 09:00 | 2030 33% ECP | 280 | -526 | -510 | 7.8 | 0 | 0 | No
2030-07-11 10:00 | 2030 33% ECP | -140 | -526 | -510 | -33.8 | 0 | 0 | No
2030-07-11 11:00 | 2030 33% ECP | -140 | -526 | -510 | -6.37 | 0 | 0 | No
2030-07-11 12:00 | 2030 33% ECP | 0 | -526 | -510 | 99.27 | 0 | 0 | No
2030-07-11 13:00 | 2030 33% ECP | -97.71 | -526 | -510 | 72.88 | 0 | 0 | No
2030-07-11 14:00 | 2030 33% ECP | 0 | -526 | -510 | 56.56 | 0 | 0 | No
2030-07-11 15:00 | 2030 33% ECP | 280.46 | -526 | -510 | 142.33 | 0 | 0 | No
2030-07-11 16:00 | 2030 33% ECP | 700 | -526 | -510 | 166.12 | 0 | 0 | No
2030-07-11 17:00 | 2030 33% ECP | 700 | -526 | -510 | 256.75 | 0 | 0 | No
2030-07-11 18:00 | 2030 33% ECP | 700 | -226 | -247.99 | 309.92 | 0 | 0 | No
2030-07-11 19:00 | 2030 33% ECP | 700 | 0 | 0 | 331.71 | 0 | 0 | No
2030-07-11 20:00 | 2030 33% ECP | 700 | 0 | -232.26 | 319.13 | 0 | 0 | No
2030-07-11 21:00 | 2030 33% ECP | 700 | 0 | 0 | 306.35 | 0 | 0 | No
2030-07-11 22:00 | 2030 33% ECP | 700 | 0 | 0 | 245.28 | 0 | 0 | No
2030-07-11 23:00 | 2030 33% ECP | 700 | 0 | -300 | 156.03 | 0 | 0 | No
2030-07-12 | 2030 33% ECP | 700 | 0 | -127.4 | 14.35 | 0 | 0 | No
2030-07-12 01:00 | 2030 33% ECP | 700 | 0 | -427.4 | 69.15 | 0 | 0 | No
2030-07-12 02:00 | 2030 33% ECP | 700 | 0 | -510 | 43.76 | 0 | 0 | No
2030-07-12 03:00 | 2030 33% ECP | 700 | -15.46 | -510 | 24.93 | 0 | 0 | No
2030-07-12 04:00 | 2030 33% ECP | 700 | -315.46 | -510 | 9.72 | 0 | 0 | No
2030-07-12 05:00 | 2030 33% ECP | 700 | -526 | -510 | -27.47 | 0 | 0 | No
2030-07-12 06:00 | 2030 33% ECP | 592.94 | -526 | -510 | -20.78 | 0 | 0 | No
2030-07-12 07:00 | 2030 33% ECP | 172.94 | -526 | -510 | -20.12 | 0 | 0 | No
2030-07-12 08:00 | 2030 33% ECP | -247.06 | -526 | -510 | -98.06 | 0 | 0 | No
2030-07-12 09:00 | 2030 33% ECP | -667.06 | -526 | -510 | -170.74 | 0 | 0 | No
2030-07-12 10:00 | 2030 33% ECP | -700 | -526 | -510 | -143.62 | 0 | 0 | No
2030-07-12 11:00 | 2030 33% ECP | -700 | -526 | -510 | -210.07 | 0 | 0 | Yes
2030-07-12 12:00 | 2030 33% ECP | -700 | -526 | -510 | -162.58 | 0 | 0 | Yes
2030-07-12 13:00 | 2030 33% ECP | -700 | -526 | -510 | -369.7 | 0 | 0 | No
2030-07-12 14:00 | 2030 33% ECP | -335.94 | -526 | -510 | -329.83 | 0 | 0 | No
2030-07-12 15:00 | 2030 33% ECP | 84.06 | -526 | -510 | -384.15 | 0 | 0 | No
2030-07-12 16:00 | 2030 33% ECP | 504.06 | -526 | -510 | -316.06 | 0 | 0 | No
2030-07-12 17:00 | 2030 33% ECP | 700 | -526 | -510 | -171.9 | 0 | 0 | No
2030-07-12 18:00 | 2030 33% ECP | 325.82 | -526 | -510 | 19.99 | 0 | 0 | No
2030-07-12 19:00 | 2030 33% ECP | 325.82 | -526 | -510 | 63.24 | 0 | 0 | No
2030-07-12 20:00 | 2030 33% ECP | 700 | -526 | -510 | -73.24 | 0 | 0 | No
2030-07-12 21:00 | 2030 33% ECP | 700 | -526 | -510 | -2.41 | 0 | 0 | No
2030-07-12 22:00 | 2030 33% ECP | 700 | -526 | -510 | -7.8 | 0 | 0 | No
2030-07-12 23:00 | 2030 33% ECP | 700 | -300 | -267.7 | -76.37 | 0 | 0 | No
2030-07-13 | 2030 33% ECP | 368.77 | 0 | 4.01 | 143.26 | 0 | 0 | No
2030-07-13 01:00 | 2030 33% ECP | 700 | 300 | 304.01 | 443.26 | 0 | 0 | No
2030-07-13 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-13 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-13 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-13 05:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-07-13 06:00 | 2030 33% ECP | 700 | -95 | -90 | -90 | 0 | 0 | No
2030-07-13 07:00 | 2030 33% ECP | 700 | -395 | -390 | -390 | 0 | 0 | No
2030-07-13 08:00 | 2030 33% ECP | 700 | -526 | -510 | -394.21 | 0 | 0 | No
2030-07-13 09:00 | 2030 33% ECP | 700 | -526 | -510 | -94.21 | 0 | 0 | No
2030-07-13 10:00 | 2030 33% ECP | 280 | -226 | -210 | 205.79 | 0 | 0 | No
2030-07-13 11:00 | 2030 33% ECP | 0 | 0 | 0 | 153.2 | 0 | 0 | No
2030-07-13 12:00 | 2030 33% ECP | 0 | 0 | 210 | 86.25 | 0 | 0 | No
2030-07-13 13:00 | 2030 33% ECP | 0 | 300 | 510 | 386.25 | 0 | 0 | No
2030-07-13 14:00 | 2030 33% ECP | 0 | 112.95 | 214.04 | 510 | 0 | 0 | No
2030-07-13 15:00 | 2030 33% ECP | 395.06 | 0 | -85.96 | 229.99 | 0 | 0 | No
2030-07-13 16:00 | 2030 33% ECP | 700 | -300 | -385.96 | -70.01 | 0 | 0 | No
2030-07-13 17:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-13 18:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-13 19:00 | 2030 33% ECP | 700 | -226 | -510 | 31.67 | 0 | 0 | No
2030-07-13 20:00 | 2030 33% ECP | 700 | -226 | -510 | 97.52 | 0 | 0 | No
2030-07-13 21:00 | 2030 33% ECP | 700 | 0 | -510 | 30.5 | 0 | 0 | No
2030-07-13 22:00 | 2030 33% ECP | 700 | -177.21 | -510 | 262.19 | 0 | 0 | No
2030-07-13 23:00 | 2030 33% ECP | 700 | 0 | -483.5 | 28.34 | 0 | 0 | No
2030-07-14 | 2030 33% ECP | 700 | 0 | -183.5 | 313.06 | 0 | 0 | No
2030-07-14 01:00 | 2030 33% ECP | 700 | 0 | 116.5 | 285.53 | 0 | 0 | No
2030-07-14 02:00 | 2030 33% ECP | 700 | 300 | 416.5 | 510 | 0 | 0 | No
2030-07-14 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-14 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-14 05:00 | 2030 33% ECP | 700 | 442.97 | 390 | 510 | 0 | 0 | No
2030-07-14 06:00 | 2030 33% ECP | 700 | 142.97 | 90 | 210 | 0 | 0 | No
2030-07-14 07:00 | 2030 33% ECP | 700 | -157.03 | -210 | 268 | 0 | 0 | No
2030-07-14 08:00 | 2030 33% ECP | 700 | -457.03 | -510 | -32 | 0 | 0 | No
2030-07-14 09:00 | 2030 33% ECP | 700 | -526 | -510 | 8.78 | 0 | 0 | No
2030-07-14 10:00 | 2030 33% ECP | 700 | -526 | -510 | 308.2 | 0 | 0 | No
2030-07-14 11:00 | 2030 33% ECP | 700 | -526 | -510 | 282.9 | 0 | 0 | No
2030-07-14 12:00 | 2030 33% ECP | 700 | -526 | -510 | 282.9 | 0 | 0 | No
2030-07-14 13:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 14:00 | 2030 33% ECP | 700 | -526 | -510 | 122.11 | 0 | 0 | No
2030-07-14 15:00 | 2030 33% ECP | 700 | -526 | -510 | 180.76 | 0 | 0 | No
2030-07-14 16:00 | 2030 33% ECP | 700 | -526 | -510 | 177.01 | 0 | 0 | No
2030-07-14 17:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 18:00 | 2030 33% ECP | 280 | -526 | -510 | 212.67 | 0 | 0 | No
2030-07-14 19:00 | 2030 33% ECP | -140 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 20:00 | 2030 33% ECP | -560 | -526 | -510 | 226.59 | 0 | 0 | No
2030-07-14 21:00 | 2030 33% ECP | -349.62 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 22:00 | 2030 33% ECP | -349.62 | -526 | -510 | 58.42 | 0 | 0 | No
2030-07-14 23:00 | 2030 33% ECP | -349.62 | -526 | -510 | 67.71 | 0 | 0 | No
2030-07-15 | 2030 33% ECP | 0 | -526 | -510 | 2.09 | 0 | 0 | No
2030-07-15 01:00 | 2030 33% ECP | -208.65 | -526 | -510 | 159.32 | 0 | 0 | No
2030-07-15 02:00 | 2030 33% ECP | -175.77 | -526 | -510 | 31.24 | 0 | 0 | No
2030-07-15 03:00 | 2030 33% ECP | 244.23 | -526 | -510 | 54.42 | 0 | 0 | No
2030-07-15 04:00 | 2030 33% ECP | 664.23 | -526 | -510 | -64.39 | 0 | 0 | No
2030-07-15 05:00 | 2030 33% ECP | 700 | -526 | -510 | 40.46 | 0 | 0 | No
2030-07-15 06:00 | 2030 33% ECP | 700 | -526 | -510 | -56.32 | 0 | 0 | No
2030-07-15 07:00 | 2030 33% ECP | 280 | -526 | -510 | 25.8 | 0 | 0 | No
2030-07-15 08:00 | 2030 33% ECP | -140 | -526 | -510 | -24.52 | 0 | 0 | No
2030-07-15 09:00 | 2030 33% ECP | -560 | -526 | -510 | -95.12 | 0 | 0 | No
2030-07-15 10:00 | 2030 33% ECP | -700 | -526 | -510 | -209.49 | 0 | 0 | No
2030-07-15 11:00 | 2030 33% ECP | -700 | -526 | -510 | -136.16 | 0 | 0 | No
2030-07-15 12:00 | 2030 33% ECP | -700 | -526 | -510 | -171.79 | 0 | 0 | No
2030-07-15 13:00 | 2030 33% ECP | -700 | -526 | -510 | -355.39 | 0 | 0 | No
2030-07-15 14:00 | 2030 33% ECP | -673.31 | -526 | -510 | -190.84 | 0 | 0 | No
2030-07-15 15:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-15 16:00 | 2030 33% ECP | -700 | -526 | -510 | -60.73 | 0 | 0 | No
2030-07-15 17:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-15 18:00 | 2030 33% ECP | -280 | -526 | -510 | -125.38 | 0 | 0 | No
2030-07-15 19:00 | 2030 33% ECP | 121.94 | -526 | -510 | -95.46 | 0 | 0 | No
2030-07-15 20:00 | 2030 33% ECP | 541.94 | -526 | -510 | 133.81 | 0 | 0 | No
2030-07-15 21:00 | 2030 33% ECP | 700 | -526 | -510 | 159.74 | 0 | 0 | No
2030-07-15 22:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-15 23:00 | 2030 33% ECP | 588.94 | -300 | -397.6 | 0 | 0 | 0 | No
2030-07-16 | 2030 33% ECP | 280 | 0 | -97.6 | 210 | 0 | 0 | No
2030-07-16 01:00 | 2030 33% ECP | 700 | 300 | 202.4 | 510 | 0 | 0 | No
2030-07-16 02:00 | 2030 33% ECP | 700 | 0 | 125.91 | 510 | 0 | 0 | No
2030-07-16 03:00 | 2030 33% ECP | 700 | 0 | 0 | 210 | 0 | 0 | No
2030-07-16 04:00 | 2030 33% ECP | 700 | 0 | -210 | 265.06 | 0 | 0 | No
2030-07-16 05:00 | 2030 33% ECP | 700 | -226 | -510 | 290.13 | 0 | 0 | No
2030-07-16 06:00 | 2030 33% ECP | 560 | -526 | -510 | 380.27 | 0 | 0 | No
2030-07-16 07:00 | 2030 33% ECP | 140 | -504.64 | -510 | 510 | 0 | 0 | No
2030-07-16 08:00 | 2030 33% ECP | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-07-16 09:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-16 10:00 | 2030 33% ECP | -700 | -526 | -510 | 480.4 | 0 | 0 | No
2030-07-16 11:00 | 2030 33% ECP | -700 | -526 | -510 | 379.68 | 0 | 0 | No
2030-07-16 12:00 | 2030 33% ECP | -700 | -526 | -510 | 159.19 | 0 | 0 | No
2030-07-16 13:00 | 2030 33% ECP | -700 | -526 | -510 | 7.14 | 0 | 0 | No
2030-07-16 14:00 | 2030 33% ECP | -700 | -526 | -510 | -190.9 | 0 | 0 | No
2030-07-16 15:00 | 2030 33% ECP | -700 | -526 | -510 | -490.9 | 0 | 0 | No
2030-07-16 16:00 | 2030 33% ECP | -700 | -526 | -510 | -190.9 | 0 | 0 | No
2030-07-16 17:00 | 2030 33% ECP | -700 | -526 | -510 | 109.1 | 0 | 0 | No
2030-07-16 18:00 | 2030 33% ECP | -386.43 | -526 | -510 | 12.14 | 0 | 0 | No
2030-07-16 19:00 | 2030 33% ECP | 33.57 | -526 | -510 | 306.74 | 0 | 0 | No
2030-07-16 20:00 | 2030 33% ECP | 366.55 | -526 | -510 | 377.85 | 0 | 0 | No
2030-07-16 21:00 | 2030 33% ECP | 0 | -526 | -510 | 323.42 | 0 | 0 | No
2030-07-16 22:00 | 2030 33% ECP | 355.49 | -526 | -510 | 401.72 | 0 | 0 | No
2030-07-16 23:00 | 2030 33% ECP | 355.49 | -526 | -510 | 235.39 | 0 | 0 | No
2030-07-17 | 2030 33% ECP | 552.76 | -234.08 | -510 | 264.38 | 0 | 0 | No
2030-07-17 01:00 | 2030 33% ECP | 132.76 | 0 | -303.66 | 66.54 | 0 | 0 | No
2030-07-17 02:00 | 2030 33% ECP | 0 | 0 | -3.66 | 244.16 | 0 | 0 | No
2030-07-17 03:00 | 2030 33% ECP | 0 | 0 | 0 | 136.47 | 0 | 0 | No
2030-07-17 04:00 | 2030 33% ECP | 160.1 | 0 | -210 | 0 | 0 | 0 | No
2030-07-17 05:00 | 2030 33% ECP | 464.07 | -300 | -510 | -51.73 | 0 | 0 | No
2030-07-17 06:00 | 2030 33% ECP | 140 | -311.2 | -510 | -24.67 | 0 | 0 | No
2030-07-17 07:00 | 2030 33% ECP | -280 | -333.62 | -510 | 184.7 | 0 | 0 | No
2030-07-17 08:00 | 2030 33% ECP | -700 | -526 | -510 | 473.13 | 0 | 0 | No
2030-07-17 09:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 10:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 11:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 12:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 13:00 | 2030 33% ECP | -700 | -526 | -510 | 484.8 | 0 | 0 | No
2030-07-17 14:00 | 2030 33% ECP | -700 | -526 | -510 | 460.69 | 0 | 0 | No
2030-07-17 15:00 | 2030 33% ECP | -700 | -526 | -510 | 473.12 | 0 | 0 | No
2030-07-17 16:00 | 2030 33% ECP | -356.73 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 17:00 | 2030 33% ECP | 63.27 | -226 | -510 | 510 | 0 | 0 | No
2030-07-17 18:00 | 2030 33% ECP | 483.27 | 0 | -510 | 502.25 | 0 | 0 | No
2030-07-17 19:00 | 2030 33% ECP | 700 | 0 | -510 | 506.09 | 0 | 0 | No
2030-07-17 20:00 | 2030 33% ECP | 700 | 0 | -510 | 498.86 | 0 | 0 | No
2030-07-17 21:00 | 2030 33% ECP | 700 | 0 | -510 | 484.31 | 0 | 0 | No
2030-07-17 22:00 | 2030 33% ECP | 700 | 0 | -510 | 444.11 | 0 | 0 | No
2030-07-17 23:00 | 2030 33% ECP | 700 | 0 | -470.02 | 294.74 | 0 | 0 | No
2030-07-18 | 2030 33% ECP | 700 | 0 | -170.02 | 190.72 | 0 | 0 | No
2030-07-18 01:00 | 2030 33% ECP | 700 | 0 | 0 | 253 | 0 | 0 | No
2030-07-18 02:00 | 2030 33% ECP | 585.92 | 0 | 0 | 231.31 | 0 | 0 | No
2030-07-18 03:00 | 2030 33% ECP | 700 | 0 | 0 | 175.98 | 0 | 0 | No
2030-07-18 04:00 | 2030 33% ECP | 700 | 0 | -209.44 | 143.97 | 0 | 0 | No
2030-07-18 05:00 | 2030 33% ECP | 700 | 0 | -377.25 | 39.94 | 0 | 0 | Yes
2030-07-18 06:00 | 2030 33% ECP | 700 | 0 | -77.25 | 117.14 | 0 | 0 | No
2030-07-18 07:00 | 2030 33% ECP | 700 | -15.86 | -377.25 | 221.82 | 0 | 0 | No
2030-07-18 08:00 | 2030 33% ECP | 280 | -315.86 | -510 | 183.33 | 0 | 0 | No
2030-07-18 09:00 | 2030 33% ECP | 700 | -526 | -510 | -17.31 | 0 | 0 | No
2030-07-18 10:00 | 2030 33% ECP | 602.01 | -526 | -510 | 215.43 | 0 | 0 | No
2030-07-18 11:00 | 2030 33% ECP | 182.01 | -526 | -510 | 77.34 | 0 | 0 | No
2030-07-18 12:00 | 2030 33% ECP | 0 | -526 | -510 | -215.33 | 0 | 0 | No
2030-07-18 13:00 | 2030 33% ECP | 0 | -526 | -510 | -180.29 | 0 | 0 | No
2030-07-18 14:00 | 2030 33% ECP | 22.67 | -526 | -510 | -43.75 | 0 | 0 | No
2030-07-18 15:00 | 2030 33% ECP | 442.67 | -526 | -510 | -206.21 | 0 | 0 | No
2030-07-18 16:00 | 2030 33% ECP | 700 | -526 | -510 | 93.79 | 0 | 0 | No
2030-07-18 17:00 | 2030 33% ECP | 700 | -526 | -510 | 114.83 | 0 | 0 | No
2030-07-18 18:00 | 2030 33% ECP | 700 | -226 | -510 | 138.47 | 0 | 0 | No
2030-07-18 19:00 | 2030 33% ECP | 700 | 0 | -510 | 313.25 | 0 | 0 | No
2030-07-18 20:00 | 2030 33% ECP | 700 | 0 | -499.22 | 193 | 0 | 0 | No
2030-07-18 21:00 | 2030 33% ECP | 700 | 0 | -199.22 | 259.71 | 0 | 0 | No
2030-07-18 22:00 | 2030 33% ECP | 700 | 0 | -499.22 | 315.44 | 0 | 0 | No
2030-07-18 23:00 | 2030 33% ECP | 700 | 0 | -255.12 | 237.96 | 0 | 0 | No
2030-07-19 | 2030 33% ECP | 700 | 0 | -271.81 | 122.09 | 0 | 0 | No
2030-07-19 01:00 | 2030 33% ECP | 700 | 0 | -492.08 | 93.73 | 0 | 0 | No
2030-07-19 02:00 | 2030 33% ECP | 700 | 0 | -342.02 | 65.55 | 0 | 0 | No
2030-07-19 03:00 | 2030 33% ECP | 700 | 0 | -407.17 | 140.43 | 0 | 0 | No
2030-07-19 04:00 | 2030 33% ECP | 700 | 0 | -107.17 | 110.93 | 0 | 0 | No
2030-07-19 05:00 | 2030 33% ECP | 575.84 | 0 | -300.68 | 68.24 | 0 | 0 | No
2030-07-19 06:00 | 2030 33% ECP | 155.84 | -226 | -510 | 163.42 | 0 | 0 | No
2030-07-19 07:00 | 2030 33% ECP | -264.16 | -526 | -510 | 143.39 | 0 | 0 | No
2030-07-19 08:00 | 2030 33% ECP | 155.84 | -526 | -510 | -156.61 | 0 | 0 | No
2030-07-19 09:00 | 2030 33% ECP | -161.12 | -526 | -510 | -161.48 | 0 | 0 | No
2030-07-19 10:00 | 2030 33% ECP | -581.12 | -526 | -510 | 55.48 | 0 | 0 | No
2030-07-19 11:00 | 2030 33% ECP | -700 | -526 | -510 | -244.52 | 0 | 0 | No
2030-07-19 12:00 | 2030 33% ECP | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-07-19 13:00 | 2030 33% ECP | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-07-19 14:00 | 2030 33% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-07-19 15:00 | 2030 33% ECP | 254.23 | -526 | -510 | -479.8 | 0 | 0 | No
2030-07-19 16:00 | 2030 33% ECP | 674.23 | -526 | -510 | -251.67 | 0 | 0 | No
2030-07-19 17:00 | 2030 33% ECP | 700 | -526 | -510 | -226.23 | 0 | 0 | No
2030-07-19 18:00 | 2030 33% ECP | 700 | -233.68 | -510 | -199.13 | 0 | 0 | No
2030-07-19 19:00 | 2030 33% ECP | 700 | 0 | -300 | 100.87 | 0 | 0 | No
2030-07-19 20:00 | 2030 33% ECP | 700 | 0 | 0 | 244.15 | 0 | 0 | No
2030-07-19 21:00 | 2030 33% ECP | 700 | 0 | 0 | 278.44 | 0 | 0 | No
2030-07-19 22:00 | 2030 33% ECP | 700 | 0 | -300 | 132.26 | 0 | 0 | No
2030-07-19 23:00 | 2030 33% ECP | 700 | 0 | 0 | 123.42 | 0 | 0 | No
2030-07-20 | 2030 33% ECP | 700 | 0 | -291.66 | 53.92 | 0 | 0 | No
2030-07-20 01:00 | 2030 33% ECP | 700 | 0 | 0 | 141.26 | 0 | 0 | No
2030-07-20 02:00 | 2030 33% ECP | 700 | 0 | 0 | 109.13 | 0 | 0 | No
2030-07-20 03:00 | 2030 33% ECP | 700 | 0 | 0 | 19.12 | 0 | 0 | No
2030-07-20 04:00 | 2030 33% ECP | 700 | 0 | 0 | 128.1 | 0 | 0 | No
2030-07-20 05:00 | 2030 33% ECP | 700 | 0 | -277.1 | 108.41 | 0 | 0 | No
2030-07-20 06:00 | 2030 33% ECP | 700 | -226 | -510 | 42.47 | 0 | 0 | No
2030-07-20 07:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-20 08:00 | 2030 33% ECP | 280 | -526 | -510 | -92.41 | 0 | 0 | No
2030-07-20 09:00 | 2030 33% ECP | -75.73 | -526 | -510 | -117.42 | 0 | 0 | No
2030-07-20 10:00 | 2030 33% ECP | -463.06 | -526 | -510 | -178.27 | 0 | 0 | No
2030-07-20 11:00 | 2030 33% ECP | -700 | -526 | -510 | -151.33 | 0 | 0 | No
2030-07-20 12:00 | 2030 33% ECP | -700 | -526 | -510 | -76.06 | 0 | 0 | No
2030-07-20 13:00 | 2030 33% ECP | -510.33 | -526 | -510 | -54.56 | 0 | 0 | No
2030-07-20 14:00 | 2030 33% ECP | -90.33 | -526 | -510 | -231.22 | 0 | 0 | No
2030-07-20 15:00 | 2030 33% ECP | 280 | -526 | -510 | -194.92 | 0 | 0 | No
2030-07-20 16:00 | 2030 33% ECP | 700 | -526 | -510 | -30.98 | 0 | 0 | No
2030-07-20 17:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-20 18:00 | 2030 33% ECP | 700 | -226 | -216.46 | 126.16 | 0 | 0 | No
2030-07-20 19:00 | 2030 33% ECP | 700 | 0 | 0 | 131.32 | 0 | 0 | No
2030-07-20 20:00 | 2030 33% ECP | 700 | 0 | 0 | 192.63 | 0 | 0 | No
2030-07-20 21:00 | 2030 33% ECP | 700 | 0 | 0 | 207.8 | 0 | 0 | No
2030-07-20 22:00 | 2030 33% ECP | 700 | 0 | 0 | 264.8 | 0 | 0 | No
2030-07-20 23:00 | 2030 33% ECP | 700 | 0 | 0 | 275.24 | 0 | 0 | No
2030-07-21 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-21 01:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-21 02:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-21 03:00 | 2030 33% ECP | 700 | 0 | -22.54 | 0 | 0 | 0 | No
2030-07-21 04:00 | 2030 33% ECP | 700 | 0 | -207.39 | 0 | 0 | 0 | No
2030-07-21 05:00 | 2030 33% ECP | 700 | 0 | -242.85 | 86.96 | 0 | 0 | No
2030-07-21 06:00 | 2030 33% ECP | 700 | -226 | -510 | 69.58 | 0 | 0 | No
2030-07-21 07:00 | 2030 33% ECP | 569.2 | -526 | -510 | 36.88 | 0 | 0 | No
2030-07-21 08:00 | 2030 33% ECP | 149.2 | -526 | -510 | 21.68 | 0 | 0 | No
2030-07-21 09:00 | 2030 33% ECP | -270.8 | -526 | -510 | 28.84 | 0 | 0 | No
2030-07-21 10:00 | 2030 33% ECP | -690.8 | -526 | -510 | 64.91 | 0 | 0 | No
2030-07-21 11:00 | 2030 33% ECP | -700 | -526 | -510 | 125.36 | 0 | 0 | No
2030-07-21 12:00 | 2030 33% ECP | -700 | -526 | -510 | 129.99 | 0 | 0 | No
2030-07-21 13:00 | 2030 33% ECP | -700 | -526 | -510 | 116.81 | 0 | 0 | No
2030-07-21 14:00 | 2030 33% ECP | -280 | -526 | -510 | 60.88 | 0 | 0 | No
2030-07-21 15:00 | 2030 33% ECP | 140 | -526 | -510 | 60.34 | 0 | 0 | No
2030-07-21 16:00 | 2030 33% ECP | 560 | -526 | -510 | 177.71 | 0 | 0 | No
2030-07-21 17:00 | 2030 33% ECP | 700 | -526 | -510 | 230.14 | 0 | 0 | No
2030-07-21 18:00 | 2030 33% ECP | 700 | -526 | -510 | 293.69 | 0 | 0 | No
2030-07-21 19:00 | 2030 33% ECP | 700 | -300 | -510 | 306.94 | 0 | 0 | No
2030-07-21 20:00 | 2030 33% ECP | 700 | 0 | -510 | 285.31 | 0 | 0 | No
2030-07-21 21:00 | 2030 33% ECP | 700 | -287.75 | -510 | 227.03 | 0 | 0 | No
2030-07-21 22:00 | 2030 33% ECP | 700 | -236.82 | -510 | 214.32 | 0 | 0 | No
2030-07-21 23:00 | 2030 33% ECP | 700 | -456.56 | -510 | 95.96 | 0 | 0 | No
2030-07-22 | 2030 33% ECP | 700 | -330.79 | -510 | -65.49 | 0 | 0 | No
2030-07-22 01:00 | 2030 33% ECP | 700 | -330.79 | -510 | 101.57 | 0 | 0 | No
2030-07-22 02:00 | 2030 33% ECP | 700 | -526 | -510 | -31.12 | 0 | 0 | No
2030-07-22 03:00 | 2030 33% ECP | 700 | -526 | -510 | -139.4 | 0 | 0 | No
2030-07-22 04:00 | 2030 33% ECP | 700 | -526 | -510 | -256.45 | 0 | 0 | No
2030-07-22 05:00 | 2030 33% ECP | 700 | -526 | -510 | -357.48 | 0 | 0 | No
2030-07-22 06:00 | 2030 33% ECP | 700 | -526 | -510 | -414.84 | 0 | 0 | No
2030-07-22 07:00 | 2030 33% ECP | 700 | -526 | -510 | -114.84 | 0 | 0 | No
2030-07-22 08:00 | 2030 33% ECP | 700 | -526 | -510 | -263.91 | 0 | 0 | No
2030-07-22 09:00 | 2030 33% ECP | 700 | -526 | -510 | 8.25 | 0 | 0 | No
2030-07-22 10:00 | 2030 33% ECP | 700 | -526 | -510 | 195.53 | 0 | 0 | No
2030-07-22 11:00 | 2030 33% ECP | 700 | -526 | -510 | 213.98 | 0 | 0 | No
2030-07-22 12:00 | 2030 33% ECP | 700 | -526 | -510 | 68.59 | 0 | 0 | No
2030-07-22 13:00 | 2030 33% ECP | 700 | -526 | -510 | 308.63 | 0 | 0 | No
2030-07-22 14:00 | 2030 33% ECP | 700 | -526 | -510 | 36.72 | 0 | 0 | No
2030-07-22 15:00 | 2030 33% ECP | 700 | -526 | -510 | 152 | 0 | 0 | No
2030-07-22 16:00 | 2030 33% ECP | 700 | -526 | -510 | 398.15 | 0 | 0 | No
2030-07-22 17:00 | 2030 33% ECP | 700 | -526 | -510 | 491.21 | 0 | 0 | No
2030-07-22 18:00 | 2030 33% ECP | 700 | -526 | -510 | 499.04 | 0 | 0 | No
2030-07-22 19:00 | 2030 33% ECP | 700 | -526 | -510 | 465.34 | 0 | 0 | No
2030-07-22 20:00 | 2030 33% ECP | 700 | -526 | -510 | 337 | 0 | 0 | No
2030-07-22 21:00 | 2030 33% ECP | 700 | -524.78 | -510 | 409.24 | 0 | 0 | No
2030-07-22 22:00 | 2030 33% ECP | 700 | -224.78 | -510 | 158.57 | 0 | 0 | No
2030-07-22 23:00 | 2030 33% ECP | 700 | -524.78 | -510 | 138.24 | 0 | 0 | No
2030-07-23 | 2030 33% ECP | 700 | -224.78 | -295.38 | 0 | 0 | 0 | No
2030-07-23 01:00 | 2030 33% ECP | 700 | 0 | -395.25 | 0 | 0 | 0 | No
2030-07-23 02:00 | 2030 33% ECP | 700 | 0 | -283.61 | 0 | 0 | 0 | No
2030-07-23 03:00 | 2030 33% ECP | 700 | 0 | -283.61 | 0 | 0 | 0 | No
2030-07-23 04:00 | 2030 33% ECP | 700 | 0 | -92.62 | 0 | 0 | 0 | No
2030-07-23 05:00 | 2030 33% ECP | 700 | 0 | -117.03 | 0 | 0 | 0 | No
2030-07-23 06:00 | 2030 33% ECP | 700 | 0 | 0 | 155.15 | 0 | 0 | No
2030-07-23 07:00 | 2030 33% ECP | 700 | 0 | -69.9 | 290.97 | 0 | 0 | No
2030-07-23 08:00 | 2030 33% ECP | 700 | -48 | -210 | 406.82 | 0 | 0 | No
2030-07-23 09:00 | 2030 33% ECP | 700 | -348 | -510 | 275.25 | 0 | 0 | No
2030-07-23 10:00 | 2030 33% ECP | 280 | -526 | -510 | 269.06 | 0 | 0 | No
2030-07-23 11:00 | 2030 33% ECP | -140 | -526 | -510 | 271.53 | 0 | 0 | No
2030-07-23 12:00 | 2030 33% ECP | -149.81 | -526 | -510 | 301.32 | 0 | 0 | No
2030-07-23 13:00 | 2030 33% ECP | 270.19 | -526 | -510 | 281.04 | 0 | 0 | No
2030-07-23 14:00 | 2030 33% ECP | 690.19 | -526 | -510 | 250.9 | 0 | 0 | No
2030-07-23 15:00 | 2030 33% ECP | 700 | -526 | -510 | 134.75 | 0 | 0 | No
2030-07-23 16:00 | 2030 33% ECP | 700 | -526 | -510 | 251.68 | 0 | 0 | No
2030-07-23 17:00 | 2030 33% ECP | 700 | -226 | -239.53 | 343.83 | 0 | 0 | No
2030-07-23 18:00 | 2030 33% ECP | 700 | 0 | 60.47 | 510 | 0 | 0 | No
2030-07-23 19:00 | 2030 33% ECP | 700 | 0 | 360.47 | 510 | 0 | 0 | No
2030-07-23 20:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-23 21:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-23 22:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-23 23:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-24 | 2030 33% ECP | 700 | 5.7 | 510 | 510 | 0 | 0 | No
2030-07-24 01:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-24 02:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-24 03:00 | 2030 33% ECP | 700 | 148.31 | 510 | 510 | 0 | 0 | No
2030-07-24 04:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-24 05:00 | 2030 33% ECP | 700 | 1.07 | 421.2 | 510 | 0 | 0 | No
2030-07-24 06:00 | 2030 33% ECP | 700 | 0 | 121.2 | 510 | 0 | 0 | No
2030-07-24 07:00 | 2030 33% ECP | 700 | -226 | -178.8 | 510 | 0 | 0 | No
2030-07-24 08:00 | 2030 33% ECP | 280 | -526 | -478.8 | 413.99 | 0 | 0 | No
2030-07-24 09:00 | 2030 33% ECP | 700 | -526 | -510 | 402.23 | 0 | 0 | No
2030-07-24 10:00 | 2030 33% ECP | 280 | -526 | -510 | 320.59 | 0 | 0 | No
2030-07-24 11:00 | 2030 33% ECP | 262.57 | -526 | -510 | 393.42 | 0 | 0 | No
2030-07-24 12:00 | 2030 33% ECP | -157.43 | -526 | -510 | 287.28 | 0 | 0 | No
2030-07-24 13:00 | 2030 33% ECP | 262.57 | -526 | -510 | 159.93 | 0 | 0 | No
2030-07-24 14:00 | 2030 33% ECP | 682.57 | -526 | -510 | 0 | 0 | 0 | No
2030-07-24 15:00 | 2030 33% ECP | 700 | -526 | -510 | 162.66 | 0 | 0 | No
2030-07-24 16:00 | 2030 33% ECP | 700 | -526 | -510 | 295.29 | 0 | 0 | No
2030-07-24 17:00 | 2030 33% ECP | 280 | -526 | -510 | 510 | 0 | 0 | No
2030-07-24 18:00 | 2030 33% ECP | 700 | -526 | -510 | 394.28 | 0 | 0 | No
2030-07-24 19:00 | 2030 33% ECP | 280 | -526 | -510 | 338.72 | 0 | 0 | No
2030-07-24 20:00 | 2030 33% ECP | 0 | -395 | -390 | 38.72 | 0 | 0 | No
2030-07-24 21:00 | 2030 33% ECP | 95.99 | -95 | -90 | -33.96 | 0 | 0 | No
2030-07-24 22:00 | 2030 33% ECP | 280 | 205 | 210 | 210 | 0 | 0 | No
2030-07-24 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 07:00 | 2030 33% ECP | 700 | 205 | 386.28 | 510 | 0 | 0 | No
2030-07-25 08:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 09:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 10:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 11:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 12:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 13:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 14:00 | 2030 33% ECP | 700 | 505 | 475.25 | 510 | 0 | 0 | No
2030-07-25 15:00 | 2030 33% ECP | 700 | 205 | 175.25 | 510 | 0 | 0 | No
2030-07-25 16:00 | 2030 33% ECP | 700 | -95 | -124.75 | 510 | 0 | 0 | No
2030-07-25 17:00 | 2030 33% ECP | 700 | -395 | -424.75 | 510 | 0 | 0 | No
2030-07-25 18:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-25 19:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-25 20:00 | 2030 33% ECP | 700 | -425.82 | -510 | 510 | 0 | 0 | No
2030-07-25 21:00 | 2030 33% ECP | 700 | -125.82 | -390 | 510 | 0 | 0 | No
2030-07-25 22:00 | 2030 33% ECP | 700 | -95 | -90 | 510 | 0 | 0 | No
2030-07-25 23:00 | 2030 33% ECP | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-07-26 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 05:00 | 2030 33% ECP | 700 | 293.31 | 510 | 510 | 0 | 0 | No
2030-07-26 06:00 | 2030 33% ECP | 700 | 216.4 | 510 | 510 | 0 | 0 | No
2030-07-26 07:00 | 2030 33% ECP | 700 | 64.58 | 510 | 510 | 0 | 0 | No
2030-07-26 08:00 | 2030 33% ECP | 420 | 170.37 | 300 | 510 | 0 | 0 | No
2030-07-26 09:00 | 2030 33% ECP | 0 | -98.26 | 0 | 510 | 0 | 0 | No
2030-07-26 10:00 | 2030 33% ECP | -416.33 | 0 | 0 | 510 | 0 | 0 | No
2030-07-26 11:00 | 2030 33% ECP | -700 | -207.43 | -123.77 | 510 | 0 | 0 | No
2030-07-26 12:00 | 2030 33% ECP | -700 | 0 | 176.23 | 510 | 0 | 0 | No
2030-07-26 13:00 | 2030 33% ECP | -700 | 300 | 476.23 | 510 | 0 | 0 | No
2030-07-26 14:00 | 2030 33% ECP | -700 | 430.11 | 300 | 510 | 0 | 0 | No
2030-07-26 15:00 | 2030 33% ECP | -467.69 | 147.93 | 0 | 510 | 0 | 0 | No
2030-07-26 16:00 | 2030 33% ECP | -47.69 | -152.07 | -300 | 345.57 | 0 | 0 | No
2030-07-26 17:00 | 2030 33% ECP | 266.66 | -452.07 | -510 | 321.17 | 0 | 0 | No
2030-07-26 18:00 | 2030 33% ECP | 686.66 | -152.07 | -363.7 | 384.76 | 0 | 0 | No
2030-07-26 19:00 | 2030 33% ECP | 700 | 0 | -363.7 | 510 | 0 | 0 | No
2030-07-26 20:00 | 2030 33% ECP | 700 | 0 | -155.94 | 510 | 0 | 0 | No
2030-07-26 21:00 | 2030 33% ECP | 700 | 0 | -90 | 510 | 0 | 0 | No
2030-07-26 22:00 | 2030 33% ECP | 700 | 205 | 210 | 485.48 | 0 | 0 | No
2030-07-26 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 06:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 07:00 | 2030 33% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 08:00 | 2030 33% ECP | -560 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 11:00 | 2030 33% ECP | -700 | 505 | 510 | 261.98 | 0 | 0 | Yes
2030-07-27 12:00 | 2030 33% ECP | -700 | 505 | 510 | 107.32 | 0 | 0 | Yes
2030-07-27 13:00 | 2030 33% ECP | -700 | 505 | 510 | 92.56 | 0 | 0 | Yes
2030-07-27 14:00 | 2030 33% ECP | -700 | 505 | 510 | 225.95 | 0 | 0 | Yes
2030-07-27 15:00 | 2030 33% ECP | -700 | 505 | 510 | 386.03 | 0 | 0 | Yes
2030-07-27 16:00 | 2030 33% ECP | -700 | 505 | 510 | 382.4 | 0 | 0 | Yes
2030-07-27 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 18:00 | 2030 33% ECP | -700 | 505 | 510 | 294.38 | 0 | 0 | Yes
2030-07-27 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 20:00 | 2030 33% ECP | -420 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 21:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 22:00 | 2030 33% ECP | 0 | 505 | 510 | 506.41 | 0 | 0 | Yes
2030-07-27 23:00 | 2030 33% ECP | -420 | 505 | 510 | 347 | 0 | 0 | Yes
2030-07-28 | 2030 33% ECP | 0 | 505 | 510 | 239.02 | 0 | 0 | Yes
2030-07-28 01:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 02:00 | 2030 33% ECP | 312.68 | 505 | 510 | 491.84 | 0 | 0 | Yes
2030-07-28 03:00 | 2030 33% ECP | 0 | 505 | 510 | 430.71 | 0 | 0 | Yes
2030-07-28 04:00 | 2030 33% ECP | 0 | 505 | 510 | 451.97 | 0 | 0 | Yes
2030-07-28 05:00 | 2030 33% ECP | 0 | 505 | 510 | 452.21 | 0 | 0 | Yes
2030-07-28 06:00 | 2030 33% ECP | -280 | 505 | 510 | 371.68 | 0 | 0 | Yes
2030-07-28 07:00 | 2030 33% ECP | -700 | 505 | 510 | 253.27 | 0 | 0 | Yes
2030-07-28 08:00 | 2030 33% ECP | -700 | 505 | 510 | 14.84 | 0 | 0 | Yes
2030-07-28 09:00 | 2030 33% ECP | -700 | 505 | 510 | 116.38 | 0 | 0 | Yes
2030-07-28 10:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-07-28 11:00 | 2030 33% ECP | -700 | 505 | 510 | 222.23 | 0 | 0 | Yes
2030-07-28 12:00 | 2030 33% ECP | -700 | 505 | 510 | 460.15 | 0 | 0 | Yes
2030-07-28 13:00 | 2030 33% ECP | -700 | 505 | 510 | 391.49 | 0 | 0 | Yes
2030-07-28 14:00 | 2030 33% ECP | -700 | 505 | 510 | 470.83 | 0 | 0 | Yes
2030-07-28 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 17:00 | 2030 33% ECP | -467.39 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 18:00 | 2030 33% ECP | -47.39 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 19:00 | 2030 33% ECP | 372.61 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 20:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 07:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 08:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 09:00 | 2030 33% ECP | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-07-29 10:00 | 2030 33% ECP | 700 | -95 | -90 | 396.83 | 0 | 0 | No
2030-07-29 11:00 | 2030 33% ECP | 700 | -395 | -390 | 435.68 | 0 | 0 | No
2030-07-29 12:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-29 13:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-29 14:00 | 2030 33% ECP | 700 | -472.5 | -510 | 510 | 0 | 0 | No
2030-07-29 15:00 | 2030 33% ECP | 700 | -465.46 | -510 | 510 | 0 | 0 | No
2030-07-29 16:00 | 2030 33% ECP | 700 | -285.85 | -510 | 506.18 | 0 | 0 | No
2030-07-29 17:00 | 2030 33% ECP | 700 | -526 | -510 | 506.18 | 0 | 0 | No
2030-07-29 18:00 | 2030 33% ECP | 700 | -526 | -510 | 433.16 | 0 | 0 | No
2030-07-29 19:00 | 2030 33% ECP | 700 | -526 | -510 | 433.16 | 0 | 0 | No
2030-07-29 20:00 | 2030 33% ECP | 700 | -526 | -510 | 371.09 | 0 | 0 | No
2030-07-29 21:00 | 2030 33% ECP | 700 | -399.47 | -510 | 395.6 | 0 | 0 | No
2030-07-29 22:00 | 2030 33% ECP | 700 | -526 | -510 | 219.52 | 0 | 0 | No
2030-07-29 23:00 | 2030 33% ECP | 700 | -526 | -510 | 175.92 | 0 | 0 | No
2030-07-30 | 2030 33% ECP | 700 | -526 | -510 | 52.9 | 0 | 0 | No
2030-07-30 01:00 | 2030 33% ECP | 700 | -526 | -510 | -7.51 | 0 | 0 | No
2030-07-30 02:00 | 2030 33% ECP | 700 | -526 | -510 | -112.92 | 0 | 0 | No
2030-07-30 03:00 | 2030 33% ECP | 700 | -526 | -510 | -104.23 | 0 | 0 | No
2030-07-30 04:00 | 2030 33% ECP | 700 | -526 | -510 | -129.8 | 0 | 0 | No
2030-07-30 05:00 | 2030 33% ECP | 700 | -526 | -510 | 12.44 | 0 | 0 | No
2030-07-30 06:00 | 2030 33% ECP | 700 | -526 | -510 | 98.01 | 0 | 0 | No
2030-07-30 07:00 | 2030 33% ECP | 700 | -526 | -510 | 163.76 | 0 | 0 | No
2030-07-30 08:00 | 2030 33% ECP | 700 | -526 | -510 | 229.83 | 0 | 0 | No
2030-07-30 09:00 | 2030 33% ECP | 700 | -526 | -510 | 189.52 | 0 | 0 | No
2030-07-30 10:00 | 2030 33% ECP | 700 | -526 | -510 | 153.41 | 0 | 0 | No
2030-07-30 11:00 | 2030 33% ECP | 700 | -526 | -510 | 24.3 | 0 | 0 | No
2030-07-30 12:00 | 2030 33% ECP | 700 | -526 | -510 | 176.7 | 0 | 0 | No
2030-07-30 13:00 | 2030 33% ECP | 700 | -526 | -510 | 148.63 | 0 | 0 | No
2030-07-30 14:00 | 2030 33% ECP | 366.33 | -526 | -510 | 282.27 | 0 | 0 | No
2030-07-30 15:00 | 2030 33% ECP | 700 | -526 | -510 | 218.91 | 0 | 0 | No
2030-07-30 16:00 | 2030 33% ECP | 700 | -526 | -510 | 100.41 | 0 | 0 | No
2030-07-30 17:00 | 2030 33% ECP | 661.53 | -526 | -510 | -98.77 | 0 | 0 | No
2030-07-30 18:00 | 2030 33% ECP | 241.53 | -526 | -510 | -398.77 | 0 | 0 | No
2030-07-30 19:00 | 2030 33% ECP | 280 | -526 | -510 | -98.77 | 0 | 0 | No
2030-07-30 20:00 | 2030 33% ECP | 700 | -526 | -510 | -141.44 | 0 | 0 | No
2030-07-30 21:00 | 2030 33% ECP | 700 | -526 | -510 | -150.88 | 0 | 0 | No
2030-07-30 22:00 | 2030 33% ECP | 700 | -382.21 | -390 | 31.1 | 0 | 0 | No
2030-07-30 23:00 | 2030 33% ECP | 700 | -82.21 | -90 | 210 | 0 | 0 | No
2030-07-31 | 2030 33% ECP | 420 | 217.79 | 210 | 510 | 0 | 0 | No
2030-07-31 01:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 02:00 | 2030 33% ECP | 344.23 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 03:00 | 2030 33% ECP | 248.84 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 04:00 | 2030 33% ECP | 603.82 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 05:00 | 2030 33% ECP | 494.59 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 07:00 | 2030 33% ECP | 351.49 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 08:00 | 2030 33% ECP | 0 | 361.85 | 510 | 510 | 0 | 0 | No
2030-07-31 09:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 10:00 | 2030 33% ECP | -70.09 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 11:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 12:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 13:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 14:00 | 2030 33% ECP | -352.91 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 15:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 16:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 17:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 18:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 19:00 | 2030 33% ECP | 700 | 407.58 | 510 | 510 | 0 | 0 | No
2030-07-31 20:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 05:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-08-01 06:00 | 2030 33% ECP | 700 | -95 | -90 | 268.22 | 0 | 0 | No
2030-08-01 07:00 | 2030 33% ECP | 700 | -395 | -390 | 363.22 | 0 | 0 | No
2030-08-01 08:00 | 2030 33% ECP | 700 | -526 | -510 | 309.1 | 0 | 0 | No
2030-08-01 09:00 | 2030 33% ECP | 700 | -526 | -510 | 384.53 | 0 | 0 | No
2030-08-01 10:00 | 2030 33% ECP | 700 | -526 | -510 | 364.36 | 0 | 0 | No
2030-08-01 11:00 | 2030 33% ECP | 700 | -526 | -510 | 411.91 | 0 | 0 | No
2030-08-01 12:00 | 2030 33% ECP | 700 | -526 | -510 | 412.57 | 0 | 0 | No
2030-08-01 13:00 | 2030 33% ECP | 700 | -526 | -510 | 343.59 | 0 | 0 | No
2030-08-01 14:00 | 2030 33% ECP | 700 | -526 | -510 | 463.49 | 0 | 0 | No
2030-08-01 15:00 | 2030 33% ECP | 700 | -526 | -510 | 435.55 | 0 | 0 | No
2030-08-01 16:00 | 2030 33% ECP | 700 | -526 | -510 | 355.37 | 0 | 0 | No
2030-08-01 17:00 | 2030 33% ECP | 700 | -226 | -510 | 444.93 | 0 | 0 | No
2030-08-01 18:00 | 2030 33% ECP | 700 | 0 | -420.38 | 444.93 | 0 | 0 | No
2030-08-01 19:00 | 2030 33% ECP | 700 | 0 | -327.29 | 284.96 | 0 | 0 | No
2030-08-01 20:00 | 2030 33% ECP | 700 | 0 | -27.29 | 284.96 | 0 | 0 | No
2030-08-01 21:00 | 2030 33% ECP | 700 | 0 | -27.29 | 427.4 | 0 | 0 | No
2030-08-01 22:00 | 2030 33% ECP | 700 | 0 | -165.5 | 499.09 | 0 | 0 | No
2030-08-01 23:00 | 2030 33% ECP | 700 | 0 | -165.5 | 372.72 | 0 | 0 | No
2030-08-02 | 2030 33% ECP | 700 | 0 | -408.72 | 272.22 | 0 | 0 | No
2030-08-02 01:00 | 2030 33% ECP | 700 | 0 | -268.12 | 211.85 | 0 | 0 | No
2030-08-02 02:00 | 2030 33% ECP | 700 | 0 | -87.29 | 172.58 | 0 | 0 | No
2030-08-02 03:00 | 2030 33% ECP | 700 | 0 | -299.26 | 179.25 | 0 | 0 | No
2030-08-02 04:00 | 2030 33% ECP | 700 | 0 | -406.31 | 139.44 | 0 | 0 | No
2030-08-02 05:00 | 2030 33% ECP | 700 | 0 | -507.32 | 170.93 | 0 | 0 | No
2030-08-02 06:00 | 2030 33% ECP | 700 | 0 | -207.32 | 239.85 | 0 | 0 | No
2030-08-02 07:00 | 2030 33% ECP | 700 | -226 | -506.3 | 323.88 | 0 | 0 | No
2030-08-02 08:00 | 2030 33% ECP | 700 | -526 | -510 | 407.42 | 0 | 0 | No
2030-08-02 09:00 | 2030 33% ECP | 700 | -526 | -510 | 405.55 | 0 | 0 | No
2030-08-02 10:00 | 2030 33% ECP | 700 | -526 | -510 | 283.79 | 0 | 0 | No
2030-08-02 11:00 | 2030 33% ECP | 700 | -526 | -510 | 329.91 | 0 | 0 | No
2030-08-02 12:00 | 2030 33% ECP | 700 | -526 | -510 | 303.74 | 0 | 0 | No
2030-08-02 13:00 | 2030 33% ECP | 700 | -526 | -510 | 319.05 | 0 | 0 | No
2030-08-02 14:00 | 2030 33% ECP | 700 | -526 | -510 | 262.6 | 0 | 0 | No
2030-08-02 15:00 | 2030 33% ECP | 700 | -526 | -510 | 342.84 | 0 | 0 | No
2030-08-02 16:00 | 2030 33% ECP | 653.19 | -526 | -510 | 380.69 | 0 | 0 | No
2030-08-02 17:00 | 2030 33% ECP | 233.19 | -526 | -510 | 350.02 | 0 | 0 | No
2030-08-02 18:00 | 2030 33% ECP | 304.49 | -300 | -510 | 446.19 | 0 | 0 | No
2030-08-02 19:00 | 2030 33% ECP | 700 | 0 | -210 | 466.17 | 0 | 0 | No
2030-08-02 20:00 | 2030 33% ECP | 700 | 0 | -464.63 | 413.99 | 0 | 0 | No
2030-08-02 21:00 | 2030 33% ECP | 700 | 0 | -164.63 | 464.54 | 0 | 0 | No
2030-08-02 22:00 | 2030 33% ECP | 700 | 0 | 0 | 458.53 | 0 | 0 | No
2030-08-02 23:00 | 2030 33% ECP | 700 | 0 | 0 | 358.51 | 0 | 0 | No
2030-08-03 | 2030 33% ECP | 700 | 0 | 0 | 252.29 | 0 | 0 | No
2030-08-03 01:00 | 2030 33% ECP | 700 | 0 | 0 | 268.2 | 0 | 0 | No
2030-08-03 02:00 | 2030 33% ECP | 700 | 0 | 0 | 238.68 | 0 | 0 | No
2030-08-03 03:00 | 2030 33% ECP | 700 | 0 | 0 | 177.51 | 0 | 0 | No
2030-08-03 04:00 | 2030 33% ECP | 700 | 0 | 0 | 194.85 | 0 | 0 | No
2030-08-03 05:00 | 2030 33% ECP | 700 | 0 | 0 | 195.66 | 0 | 0 | No
2030-08-03 06:00 | 2030 33% ECP | 332.49 | 0 | -164.97 | 200.85 | 0 | 0 | No
2030-08-03 07:00 | 2030 33% ECP | -87.51 | -226 | -210 | 215.08 | 0 | 0 | No
2030-08-03 08:00 | 2030 33% ECP | -507.51 | -526 | -510 | 79.44 | 0 | 0 | No
2030-08-03 09:00 | 2030 33% ECP | -87.51 | -526 | -510 | 69.13 | 0 | 0 | No
2030-08-03 10:00 | 2030 33% ECP | 108.1 | -526 | -510 | 151.44 | 0 | 0 | No
2030-08-03 11:00 | 2030 33% ECP | -176.07 | -526 | -510 | 70.35 | 0 | 0 | No
2030-08-03 12:00 | 2030 33% ECP | 23.26 | -526 | -510 | 165.26 | 0 | 0 | No
2030-08-03 13:00 | 2030 33% ECP | 313.81 | -526 | -510 | 121.33 | 0 | 0 | No
2030-08-03 14:00 | 2030 33% ECP | 700 | -526 | -510 | 98.34 | 0 | 0 | No
2030-08-03 15:00 | 2030 33% ECP | 700 | -526 | -510 | 183.38 | 0 | 0 | No
2030-08-03 16:00 | 2030 33% ECP | 700 | -526 | -510 | 250.52 | 0 | 0 | No
2030-08-03 17:00 | 2030 33% ECP | 700 | -526 | -510 | 352.34 | 0 | 0 | No
2030-08-03 18:00 | 2030 33% ECP | 700 | -226 | -210 | 393.62 | 0 | 0 | No
2030-08-03 19:00 | 2030 33% ECP | 700 | 0 | -188.08 | 412.55 | 0 | 0 | No
2030-08-03 20:00 | 2030 33% ECP | 700 | 0 | -77.13 | 387.65 | 0 | 0 | No
2030-08-03 21:00 | 2030 33% ECP | 700 | 0 | -377.13 | 398.88 | 0 | 0 | No
2030-08-03 22:00 | 2030 33% ECP | 700 | 0 | -466.49 | 348.87 | 0 | 0 | No
2030-08-03 23:00 | 2030 33% ECP | 319.31 | -226 | -510 | 213.79 | 0 | 0 | No
2030-08-04 | 2030 33% ECP | 187.65 | -436.94 | -510 | 124.69 | 0 | 0 | No
2030-08-04 01:00 | 2030 33% ECP | -232.35 | -303.73 | -510 | 0 | 0 | 0 | No
2030-08-04 02:00 | 2030 33% ECP | -652.35 | -526 | -510 | 43.92 | 0 | 0 | No
2030-08-04 03:00 | 2030 33% ECP | -280 | -526 | -510 | -1.56 | 0 | 0 | No
2030-08-04 04:00 | 2030 33% ECP | 140 | -526 | -510 | -301.56 | 0 | 0 | No
2030-08-04 05:00 | 2030 33% ECP | 560 | -526 | -510 | -510 | 0 | 0 | No
2030-08-04 06:00 | 2030 33% ECP | 140 | -526 | -510 | -510 | 0 | 0 | No
2030-08-04 07:00 | 2030 33% ECP | -280 | -395 | -475.02 | -419.93 | 0 | 0 | No
2030-08-04 08:00 | 2030 33% ECP | -700 | -95 | -175.02 | -119.93 | 0 | 0 | Yes
2030-08-04 09:00 | 2030 33% ECP | -700 | 205 | 124.98 | 180.07 | 0 | 0 | Yes
2030-08-04 10:00 | 2030 33% ECP | -700 | 505 | 424.98 | 398.02 | 0 | 0 | Yes
2030-08-04 11:00 | 2030 33% ECP | -700 | 505 | 510 | 430.85 | 0 | 0 | Yes
2030-08-04 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 13:00 | 2030 33% ECP | -700 | 505 | 510 | 371.19 | 0 | 0 | Yes
2030-08-04 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 16:00 | 2030 33% ECP | -700 | 505 | 510 | 415.58 | 0 | 0 | Yes
2030-08-04 17:00 | 2030 33% ECP | -700 | 505 | 510 | 493.97 | 0 | 0 | Yes
2030-08-04 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 20:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-04 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-05 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 01:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 02:00 | 2030 33% ECP | 172.32 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 03:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 04:00 | 2030 33% ECP | 106.04 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 05:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 06:00 | 2030 33% ECP | 36.18 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 07:00 | 2030 33% ECP | 36.18 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 08:00 | 2030 33% ECP | 77.06 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 09:00 | 2030 33% ECP | 478.97 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 10:00 | 2030 33% ECP | 96.95 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 11:00 | 2030 33% ECP | -323.05 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 15:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 16:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 17:00 | 2030 33% ECP | 560 | 300 | 300 | 510 | 0 | 0 | No
2030-08-05 18:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-08-05 19:00 | 2030 33% ECP | 700 | 0 | 0 | 508.81 | 0 | 0 | No
2030-08-05 20:00 | 2030 33% ECP | 700 | 0 | 0 | 459.56 | 0 | 0 | No
2030-08-05 21:00 | 2030 33% ECP | 700 | 0 | 28.9 | 494.74 | 0 | 0 | No
2030-08-05 22:00 | 2030 33% ECP | 700 | 0 | 300 | 474.33 | 0 | 0 | No
2030-08-05 23:00 | 2030 33% ECP | 700 | 0 | 0 | 370.56 | 0 | 0 | No
2030-08-06 | 2030 33% ECP | 700 | 0 | 0 | 213.15 | 0 | 0 | No
2030-08-06 01:00 | 2030 33% ECP | 700 | 0 | 0 | 262.66 | 0 | 0 | No
2030-08-06 02:00 | 2030 33% ECP | 700 | 0 | 0 | 266.29 | 0 | 0 | No
2030-08-06 03:00 | 2030 33% ECP | 700 | 0 | -94.57 | 215.4 | 0 | 0 | No
2030-08-06 04:00 | 2030 33% ECP | 700 | -176.71 | -394.57 | 211.94 | 0 | 0 | No
2030-08-06 05:00 | 2030 33% ECP | 700 | -67.79 | -510 | 185.01 | 0 | 0 | No
2030-08-06 06:00 | 2030 33% ECP | 700 | -291.01 | -510 | 161.94 | 0 | 0 | No
2030-08-06 07:00 | 2030 33% ECP | 700 | -526 | -510 | 124.85 | 0 | 0 | No
2030-08-06 08:00 | 2030 33% ECP | 700 | -526 | -510 | 1.4 | 0 | 0 | No
2030-08-06 09:00 | 2030 33% ECP | 280 | -526 | -510 | -86.38 | 0 | 0 | No
2030-08-06 10:00 | 2030 33% ECP | -114.12 | -526 | -510 | -172.74 | 0 | 0 | No
2030-08-06 11:00 | 2030 33% ECP | -420 | -526 | -510 | -472.74 | 0 | 0 | No
2030-08-06 12:00 | 2030 33% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-08-06 13:00 | 2030 33% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-08-06 14:00 | 2030 33% ECP | 0 | -526 | -510 | -340.17 | 0 | 0 | No
2030-08-06 15:00 | 2030 33% ECP | 216.76 | -526 | -510 | -105 | 0 | 0 | No
2030-08-06 16:00 | 2030 33% ECP | 636.76 | -526 | -510 | 195 | 0 | 0 | No
2030-08-06 17:00 | 2030 33% ECP | 700 | -526 | -510 | 214.96 | 0 | 0 | No
2030-08-06 18:00 | 2030 33% ECP | 280 | -526 | -510 | 211.07 | 0 | 0 | No
2030-08-06 19:00 | 2030 33% ECP | 700 | -526 | -510 | 209.48 | 0 | 0 | No
2030-08-06 20:00 | 2030 33% ECP | 700 | -526 | -510 | 144.99 | 0 | 0 | No
2030-08-06 21:00 | 2030 33% ECP | 459.66 | -526 | -510 | 233.55 | 0 | 0 | No
2030-08-06 22:00 | 2030 33% ECP | 700 | -526 | -510 | 48.21 | 0 | 0 | No
2030-08-06 23:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-08-07 | 2030 33% ECP | 700 | -526 | -510 | -55.92 | 0 | 0 | No
2030-08-07 01:00 | 2030 33% ECP | 700 | -526 | -510 | -90.28 | 0 | 0 | No
2030-08-07 02:00 | 2030 33% ECP | 700 | -526 | -510 | -39.48 | 0 | 0 | No
2030-08-07 03:00 | 2030 33% ECP | 700 | -526 | -510 | -91.5 | 0 | 0 | No
2030-08-07 04:00 | 2030 33% ECP | 700 | -526 | -510 | -40.88 | 0 | 0 | No
2030-08-07 05:00 | 2030 33% ECP | 700 | -526 | -510 | -125.5 | 0 | 0 | No
2030-08-07 06:00 | 2030 33% ECP | 700 | -526 | -510 | -40.56 | 0 | 0 | No
2030-08-07 07:00 | 2030 33% ECP | 700 | -526 | -510 | -76.41 | 0 | 0 | No
2030-08-07 08:00 | 2030 33% ECP | 700 | -526 | -510 | 43.05 | 0 | 0 | No
2030-08-07 09:00 | 2030 33% ECP | 700 | -526 | -510 | -80.8 | 0 | 0 | No
2030-08-07 10:00 | 2030 33% ECP | 700 | -526 | -510 | -157.84 | 0 | 0 | No
2030-08-07 11:00 | 2030 33% ECP | 700 | -526 | -510 | 98.17 | 0 | 0 | No
2030-08-07 12:00 | 2030 33% ECP | 700 | -526 | -510 | 217.2 | 0 | 0 | No
2030-08-07 13:00 | 2030 33% ECP | 700 | -526 | -510 | -32.96 | 0 | 0 | No
2030-08-07 14:00 | 2030 33% ECP | 700 | -526 | -510 | -10.93 | 0 | 0 | No
2030-08-07 15:00 | 2030 33% ECP | 700 | -526 | -510 | 194.67 | 0 | 0 | No
2030-08-07 16:00 | 2030 33% ECP | 700 | -526 | -510 | 494.67 | 0 | 0 | No
2030-08-07 17:00 | 2030 33% ECP | 700 | -300 | -340.44 | 410.35 | 0 | 0 | No
2030-08-07 18:00 | 2030 33% ECP | 700 | 0 | -40.44 | 475.58 | 0 | 0 | No
2030-08-07 19:00 | 2030 33% ECP | 700 | 0 | 68.2 | 510 | 0 | 0 | No
2030-08-07 20:00 | 2030 33% ECP | 700 | 0 | 368.2 | 338.15 | 0 | 0 | No
2030-08-07 21:00 | 2030 33% ECP | 700 | 0 | 368.2 | 380.14 | 0 | 0 | No
2030-08-07 22:00 | 2030 33% ECP | 700 | 0 | 68.2 | 307.65 | 0 | 0 | No
2030-08-07 23:00 | 2030 33% ECP | 700 | 0 | 237.04 | 180.05 | 0 | 0 | No
2030-08-08 | 2030 33% ECP | 700 | 0 | 61.44 | 83.85 | 0 | 0 | No
2030-08-08 01:00 | 2030 33% ECP | 700 | 0 | 361.44 | 108.15 | 0 | 0 | No
2030-08-08 02:00 | 2030 33% ECP | 700 | 0 | 335.24 | 97.01 | 0 | 0 | No
2030-08-08 03:00 | 2030 33% ECP | 700 | 0 | 35.24 | 69.93 | 0 | 0 | No
2030-08-08 04:00 | 2030 33% ECP | 700 | 0 | 309.66 | 22.47 | 0 | 0 | No
2030-08-08 05:00 | 2030 33% ECP | 700 | 0 | 9.66 | 26.75 | 0 | 0 | No
2030-08-08 06:00 | 2030 33% ECP | 700 | 0 | -58.48 | 76.64 | 0 | 0 | No
2030-08-08 07:00 | 2030 33% ECP | 700 | -300 | -358.48 | 188.06 | 0 | 0 | No
2030-08-08 08:00 | 2030 33% ECP | 700 | -526 | -510 | 245.1 | 0 | 0 | No
2030-08-08 09:00 | 2030 33% ECP | 291.73 | -526 | -510 | 209.03 | 0 | 0 | No
2030-08-08 10:00 | 2030 33% ECP | 0 | -526 | -510 | 160.06 | 0 | 0 | No
2030-08-08 11:00 | 2030 33% ECP | 0 | -526 | -510 | 160.73 | 0 | 0 | No
2030-08-08 12:00 | 2030 33% ECP | 0 | -526 | -510 | 151.32 | 0 | 0 | No
2030-08-08 13:00 | 2030 33% ECP | 0 | -526 | -510 | 98.19 | 0 | 0 | No
2030-08-08 14:00 | 2030 33% ECP | 0 | -526 | -510 | 61.46 | 0 | 0 | No
2030-08-08 15:00 | 2030 33% ECP | 296.64 | -526 | -510 | 50.49 | 0 | 0 | No
2030-08-08 16:00 | 2030 33% ECP | 700 | -526 | -510 | 152.94 | 0 | 0 | No
2030-08-08 17:00 | 2030 33% ECP | 700 | -514.93 | -510 | 227.3 | 0 | 0 | No
2030-08-08 18:00 | 2030 33% ECP | 700 | -214.93 | -210 | 302.66 | 0 | 0 | No
2030-08-08 19:00 | 2030 33% ECP | 700 | 0 | 38.33 | 254.71 | 0 | 0 | No
2030-08-08 20:00 | 2030 33% ECP | 700 | 0 | 338.33 | 224.15 | 0 | 0 | No
2030-08-08 21:00 | 2030 33% ECP | 700 | 0 | 181.58 | 187.89 | 0 | 0 | No
2030-08-08 22:00 | 2030 33% ECP | 700 | 0 | 481.58 | 6.29 | 0 | 0 | No
2030-08-08 23:00 | 2030 33% ECP | 700 | 0 | 181.58 | 0 | 0 | 0 | No
2030-08-09 | 2030 33% ECP | 700 | 0 | 46.16 | 0 | 0 | 0 | No
2030-08-09 01:00 | 2030 33% ECP | 700 | 0 | 51.32 | 0 | 0 | 0 | No
2030-08-09 02:00 | 2030 33% ECP | 700 | 32.08 | 351.32 | 203.83 | 0 | 0 | No
2030-08-09 03:00 | 2030 33% ECP | 700 | 332.08 | 510 | 503.83 | 0 | 0 | No
2030-08-09 04:00 | 2030 33% ECP | 700 | 212.67 | 210 | 203.83 | 0 | 0 | No
2030-08-09 05:00 | 2030 33% ECP | 700 | -87.33 | -90 | -96.17 | 0 | 0 | No
2030-08-09 06:00 | 2030 33% ECP | 700 | -19.98 | -390 | -396.17 | 0 | 0 | No
2030-08-09 07:00 | 2030 33% ECP | 700 | -226 | -510 | -345.13 | 0 | 0 | No
2030-08-09 08:00 | 2030 33% ECP | 700 | -526 | -510 | -243.39 | 0 | 0 | No
2030-08-09 09:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-08-09 10:00 | 2030 33% ECP | 700 | -526 | -510 | 96.07 | 0 | 0 | No
2030-08-09 11:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-08-09 12:00 | 2030 33% ECP | 638.08 | -526 | -510 | 0 | 0 | 0 | No
2030-08-09 13:00 | 2030 33% ECP | 700 | -526 | -510 | 84.27 | 0 | 0 | No
2030-08-09 14:00 | 2030 33% ECP | 663.16 | -526 | -510 | 0 | 0 | 0 | No
2030-08-09 15:00 | 2030 33% ECP | 663.16 | -526 | -510 | 110.9 | 0 | 0 | No
2030-08-09 16:00 | 2030 33% ECP | 700 | -526 | -510 | 233.45 | 0 | 0 | No
2030-08-09 17:00 | 2030 33% ECP | 700 | -518.35 | -510 | 191.69 | 0 | 0 | No
2030-08-09 18:00 | 2030 33% ECP | 700 | -218.35 | -210 | 363.53 | 0 | 0 | No
2030-08-09 19:00 | 2030 33% ECP | 700 | 0 | 0 | 165.32 | 0 | 0 | No
2030-08-09 20:00 | 2030 33% ECP | 700 | 0 | 182.12 | 165.32 | 0 | 0 | No
2030-08-09 21:00 | 2030 33% ECP | 700 | 0 | 322.5 | 287.29 | 0 | 0 | No
2030-08-09 22:00 | 2030 33% ECP | 700 | 0 | 510 | 78.91 | 0 | 0 | No
2030-08-09 23:00 | 2030 33% ECP | 700 | 0 | 210 | 114.74 | 0 | 0 | No
2030-08-10 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-10 01:00 | 2030 33% ECP | 700 | 0 | -2.44 | -194.7 | 0 | 0 | No
2030-08-10 02:00 | 2030 33% ECP | 700 | 0 | -0.27 | 0 | 0 | 0 | No
2030-08-10 03:00 | 2030 33% ECP | 700 | 0 | 0 | -10.72 | 0 | 0 | No
2030-08-10 04:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-10 05:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-10 06:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-10 07:00 | 2030 33% ECP | 700 | -226 | -264.2 | 0 | 0 | 0 | No
2030-08-10 08:00 | 2030 33% ECP | 700 | -526 | -510 | 70.82 | 0 | 0 | No
2030-08-10 09:00 | 2030 33% ECP | 700 | -526 | -510 | 112.06 | 0 | 0 | No
2030-08-10 10:00 | 2030 33% ECP | 700 | -526 | -510 | 49.35 | 0 | 0 | No
2030-08-10 11:00 | 2030 33% ECP | 700 | -526 | -510 | 135.79 | 0 | 0 | No
2030-08-10 12:00 | 2030 33% ECP | 700 | -526 | -510 | 193.05 | 0 | 0 | No
2030-08-10 13:00 | 2030 33% ECP | 700 | -526 | -510 | 113.07 | 0 | 0 | No
2030-08-10 14:00 | 2030 33% ECP | 700 | -526 | -510 | 114.6 | 0 | 0 | No
2030-08-10 15:00 | 2030 33% ECP | 700 | -526 | -510 | 135.87 | 0 | 0 | No
2030-08-10 16:00 | 2030 33% ECP | 700 | -526 | -510 | 181.91 | 0 | 0 | No
2030-08-10 17:00 | 2030 33% ECP | 700 | -226 | -338.7 | 80.74 | 0 | 0 | No
2030-08-10 18:00 | 2030 33% ECP | 700 | 0 | -38.7 | 169.93 | 0 | 0 | No
2030-08-10 19:00 | 2030 33% ECP | 700 | 0 | -38.7 | 0 | 0 | 0 | No
2030-08-10 20:00 | 2030 33% ECP | 700 | 0 | 0 | 160.95 | 0 | 0 | No
2030-08-10 21:00 | 2030 33% ECP | 700 | 0 | -205.18 | 178.45 | 0 | 0 | No
2030-08-10 22:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-10 23:00 | 2030 33% ECP | 700 | 0 | 0 | 88.8 | 0 | 0 | No
2030-08-11 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-11 01:00 | 2030 33% ECP | 700 | 0 | 0 | 37.37 | 0 | 0 | No
2030-08-11 02:00 | 2030 33% ECP | 700 | 0 | -10.57 | 19.74 | 0 | 0 | No
2030-08-11 03:00 | 2030 33% ECP | 700 | 0 | -10.57 | 3.83 | 0 | 0 | No
2030-08-11 04:00 | 2030 33% ECP | 700 | 0 | 0 | 15.64 | 0 | 0 | No
2030-08-11 05:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-11 06:00 | 2030 33% ECP | 700 | -226 | -237.98 | 0 | 0 | 0 | No
2030-08-11 07:00 | 2030 33% ECP | 700 | -526 | -510 | -36.17 | 0 | 0 | No
2030-08-11 08:00 | 2030 33% ECP | 687.17 | -526 | -510 | -74.39 | 0 | 0 | No
2030-08-11 09:00 | 2030 33% ECP | 267.17 | -526 | -510 | -132.74 | 0 | 0 | No
2030-08-11 10:00 | 2030 33% ECP | -152.83 | -526 | -510 | -194.75 | 0 | 0 | No
2030-08-11 11:00 | 2030 33% ECP | -572.83 | -526 | -510 | -176.29 | 0 | 0 | No
2030-08-11 12:00 | 2030 33% ECP | -700 | -526 | -510 | -144.31 | 0 | 0 | No
2030-08-11 13:00 | 2030 33% ECP | -619.37 | -526 | -510 | -38.32 | 0 | 0 | No
2030-08-11 14:00 | 2030 33% ECP | -199.37 | -526 | -510 | -43.45 | 0 | 0 | No
2030-08-11 15:00 | 2030 33% ECP | 220.63 | -526 | -510 | -42.53 | 0 | 0 | No
2030-08-11 16:00 | 2030 33% ECP | 640.63 | -526 | -510 | 34.47 | 0 | 0 | No
2030-08-11 17:00 | 2030 33% ECP | 485.14 | -300 | -510 | 123.43 | 0 | 0 | No
2030-08-11 18:00 | 2030 33% ECP | 700 | 0 | -243.55 | 159.4 | 0 | 0 | No
2030-08-11 19:00 | 2030 33% ECP | 700 | 0 | 0 | 164.1 | 0 | 0 | No
2030-08-11 20:00 | 2030 33% ECP | 700 | 0 | -14.31 | 169.92 | 0 | 0 | No
2030-08-11 21:00 | 2030 33% ECP | 700 | 0 | -14.31 | 204.35 | 0 | 0 | No
2030-08-11 22:00 | 2030 33% ECP | 700 | 0 | 0 | 154.93 | 0 | 0 | No
2030-08-11 23:00 | 2030 33% ECP | 700 | 0 | 0 | 54.52 | 0 | 0 | No
2030-08-12 | 2030 33% ECP | 700 | 0 | -27.6 | 38.22 | 0 | 0 | No
2030-08-12 01:00 | 2030 33% ECP | 700 | 0 | -272.95 | 0 | 0 | 0 | No
2030-08-12 02:00 | 2030 33% ECP | 700 | 0 | -29.22 | 0 | 0 | 0 | No
2030-08-12 03:00 | 2030 33% ECP | 700 | 0 | -329.22 | 0 | 0 | 0 | No
2030-08-12 04:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-12 05:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-12 06:00 | 2030 33% ECP | 700 | 0 | -510 | 1.04 | 0 | 0 | No
2030-08-12 07:00 | 2030 33% ECP | 700 | -233.76 | -510 | 89.84 | 0 | 0 | No
2030-08-12 08:00 | 2030 33% ECP | 700 | -526 | -510 | 177.32 | 0 | 0 | No
2030-08-12 09:00 | 2030 33% ECP | 700 | -526 | -510 | 120.4 | 0 | 0 | No
2030-08-12 10:00 | 2030 33% ECP | 700 | -526 | -510 | -33.32 | 0 | 0 | No
2030-08-12 11:00 | 2030 33% ECP | 470.32 | -526 | -510 | -41.84 | 0 | 0 | No
2030-08-12 12:00 | 2030 33% ECP | 470.32 | -526 | -510 | -59.25 | 0 | 0 | No
2030-08-12 13:00 | 2030 33% ECP | 141.77 | -526 | -510 | -48.12 | 0 | 0 | No
2030-08-12 14:00 | 2030 33% ECP | 561.77 | -526 | -510 | -43.36 | 0 | 0 | No
2030-08-12 15:00 | 2030 33% ECP | 700 | -526 | -510 | -82.47 | 0 | 0 | No
2030-08-12 16:00 | 2030 33% ECP | 700 | -526 | -510 | 79.33 | 0 | 0 | No
2030-08-12 17:00 | 2030 33% ECP | 700 | -416.13 | -510 | 122.97 | 0 | 0 | No
2030-08-12 18:00 | 2030 33% ECP | 700 | -116.13 | -510 | -12.04 | 0 | 0 | No
2030-08-12 19:00 | 2030 33% ECP | 700 | -273.9 | -510 | -120.48 | 0 | 0 | No
2030-08-12 20:00 | 2030 33% ECP | 700 | 0 | -510 | -228.71 | 0 | 0 | No
2030-08-12 21:00 | 2030 33% ECP | 700 | 0 | -510 | -108.77 | 0 | 0 | No
2030-08-12 22:00 | 2030 33% ECP | 700 | 0 | -510 | -73.14 | 0 | 0 | No
2030-08-12 23:00 | 2030 33% ECP | 700 | -59.2 | -510 | 19.5 | 0 | 0 | No
2030-08-13 | 2030 33% ECP | 700 | -59.2 | -510 | -0.85 | 0 | 0 | No
2030-08-13 01:00 | 2030 33% ECP | 700 | 0 | -510 | 14.2 | 0 | 0 | No
2030-08-13 02:00 | 2030 33% ECP | 700 | 0 | -510 | 57.52 | 0 | 0 | No
2030-08-13 03:00 | 2030 33% ECP | 700 | 0 | -510 | 0.56 | 0 | 0 | No
2030-08-13 04:00 | 2030 33% ECP | 700 | -150.14 | -510 | -25.46 | 0 | 0 | No
2030-08-13 05:00 | 2030 33% ECP | 700 | -435.36 | -510 | -219.35 | 0 | 0 | No
2030-08-13 06:00 | 2030 33% ECP | 700 | -444.01 | -510 | -153.44 | 0 | 0 | No
2030-08-13 07:00 | 2030 33% ECP | 700 | -287.92 | -510 | 146.56 | 0 | 0 | No
2030-08-13 08:00 | 2030 33% ECP | 700 | -526 | -510 | 205.36 | 0 | 0 | No
2030-08-13 09:00 | 2030 33% ECP | 280 | -526 | -510 | 109.85 | 0 | 0 | No
2030-08-13 10:00 | 2030 33% ECP | -140 | -526 | -510 | 69.6 | 0 | 0 | No
2030-08-13 11:00 | 2030 33% ECP | -560 | -526 | -510 | 144.18 | 0 | 0 | No
2030-08-13 12:00 | 2030 33% ECP | -700 | -526 | -510 | 56.6 | 0 | 0 | No
2030-08-13 13:00 | 2030 33% ECP | -560 | -526 | -510 | -56.51 | 0 | 0 | No
2030-08-13 14:00 | 2030 33% ECP | -140 | -526 | -510 | -188.45 | 0 | 0 | No
2030-08-13 15:00 | 2030 33% ECP | 280 | -526 | -510 | -324.94 | 0 | 0 | No
2030-08-13 16:00 | 2030 33% ECP | 700 | -526 | -510 | -144.78 | 0 | 0 | No
2030-08-13 17:00 | 2030 33% ECP | 700 | -226 | -434.93 | 155.22 | 0 | 0 | No
2030-08-13 18:00 | 2030 33% ECP | 700 | 0 | -134.93 | 211.01 | 0 | 0 | No
2030-08-13 19:00 | 2030 33% ECP | 700 | 0 | 0 | 21.06 | 0 | 0 | No
2030-08-13 20:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-13 21:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-13 22:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-13 23:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-14 | 2030 33% ECP | 700 | 0 | 59.73 | 0 | 0 | 0 | No
2030-08-14 01:00 | 2030 33% ECP | 700 | 0 | 165.11 | 0 | 0 | 0 | No
2030-08-14 02:00 | 2030 33% ECP | 700 | 0 | 465.11 | 0 | 0 | 0 | No
2030-08-14 03:00 | 2030 33% ECP | 700 | 0 | 269.85 | 0 | 0 | 0 | No
2030-08-14 04:00 | 2030 33% ECP | 700 | 0 | 404.54 | 0 | 0 | 0 | No
2030-08-14 05:00 | 2030 33% ECP | 700 | 0 | 310.07 | 0 | 0 | 0 | No
2030-08-14 06:00 | 2030 33% ECP | 700 | 0 | 90 | 0 | 0 | 0 | No
2030-08-14 07:00 | 2030 33% ECP | 700 | -86.03 | -210 | 0 | 0 | 0 | No
2030-08-14 08:00 | 2030 33% ECP | 700 | -386.03 | -510 | 125.58 | 0 | 0 | No
2030-08-14 09:00 | 2030 33% ECP | 700 | -526 | -510 | 233.52 | 0 | 0 | No
2030-08-14 10:00 | 2030 33% ECP | 700 | -526 | -510 | 168.63 | 0 | 0 | No
2030-08-14 11:00 | 2030 33% ECP | 700 | -526 | -510 | 166.72 | 0 | 0 | No
2030-08-14 12:00 | 2030 33% ECP | 700 | -526 | -510 | 145.4 | 0 | 0 | No
2030-08-14 13:00 | 2030 33% ECP | 700 | -526 | -510 | 104.25 | 0 | 0 | No
2030-08-14 14:00 | 2030 33% ECP | 700 | -526 | -510 | 115.08 | 0 | 0 | No
2030-08-14 15:00 | 2030 33% ECP | 700 | -526 | -510 | 155.52 | 0 | 0 | No
2030-08-14 16:00 | 2030 33% ECP | 700 | -511.89 | -510 | 235.56 | 0 | 0 | No
2030-08-14 17:00 | 2030 33% ECP | 700 | -211.89 | -268.95 | 382.2 | 0 | 0 | No
2030-08-14 18:00 | 2030 33% ECP | 700 | 59.53 | 0 | 510 | 0 | 0 | No
2030-08-14 19:00 | 2030 33% ECP | 700 | -240.47 | -300 | 375.27 | 0 | 0 | No
2030-08-14 20:00 | 2030 33% ECP | 700 | -67.94 | -90 | 366.38 | 0 | 0 | No
2030-08-14 21:00 | 2030 33% ECP | 700 | 232.06 | 210 | 510 | 0 | 0 | No
2030-08-14 22:00 | 2030 33% ECP | 700 | 452.43 | 510 | 510 | 0 | 0 | No
2030-08-14 23:00 | 2030 33% ECP | 700 | 152.43 | 510 | 510 | 0 | 0 | No
2030-08-15 | 2030 33% ECP | 700 | 0 | 510 | 210 | 0 | 0 | No
2030-08-15 01:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-08-15 02:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-08-15 03:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-08-15 04:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-08-15 05:00 | 2030 33% ECP | 700 | 0 | 390 | 0 | 0 | 0 | No
2030-08-15 06:00 | 2030 33% ECP | 700 | 0 | 90 | 211.7 | 0 | 0 | No
2030-08-15 07:00 | 2030 33% ECP | 700 | -175.52 | -210 | 210.66 | 0 | 0 | No
2030-08-15 08:00 | 2030 33% ECP | 700 | -475.52 | -510 | 210.66 | 0 | 0 | No
2030-08-15 09:00 | 2030 33% ECP | 700 | -526 | -510 | 161.32 | 0 | 0 | No
2030-08-15 10:00 | 2030 33% ECP | 700 | -526 | -510 | 182 | 0 | 0 | No
2030-08-15 11:00 | 2030 33% ECP | 700 | -526 | -510 | 151.75 | 0 | 0 | No
2030-08-15 12:00 | 2030 33% ECP | 700 | -526 | -510 | 159.24 | 0 | 0 | No
2030-08-15 13:00 | 2030 33% ECP | 700 | -526 | -510 | 151.4 | 0 | 0 | No
2030-08-15 14:00 | 2030 33% ECP | 700 | -526 | -510 | 169.2 | 0 | 0 | No
2030-08-15 15:00 | 2030 33% ECP | 700 | -526 | -510 | 191.93 | 0 | 0 | No
2030-08-15 16:00 | 2030 33% ECP | 700 | -459.66 | -510 | -108.07 | 0 | 0 | No
2030-08-15 17:00 | 2030 33% ECP | 700 | -526 | -510 | -408.07 | 0 | 0 | No
2030-08-15 18:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-15 19:00 | 2030 33% ECP | 700 | -300 | -267.19 | -300 | 0 | 0 | No
2030-08-15 20:00 | 2030 33% ECP | 700 | 0 | 32.81 | 0 | 0 | 0 | No
2030-08-15 21:00 | 2030 33% ECP | 700 | 300 | 332.81 | 300 | 0 | 0 | No
2030-08-15 22:00 | 2030 33% ECP | 700 | 269.84 | 510 | 202.54 | 0 | 0 | No
2030-08-15 23:00 | 2030 33% ECP | 700 | 81.09 | 410.86 | 186.46 | 0 | 0 | No
2030-08-16 | 2030 33% ECP | 700 | 0 | 329.37 | 0 | 0 | 0 | No
2030-08-16 01:00 | 2030 33% ECP | 700 | 0 | 383.35 | 0 | 0 | 0 | No
2030-08-16 02:00 | 2030 33% ECP | 700 | 0 | 510 | 21.85 | 0 | 0 | No
2030-08-16 03:00 | 2030 33% ECP | 700 | 0 | 210 | 0 | 0 | 0 | No
2030-08-16 04:00 | 2030 33% ECP | 700 | 0 | 28.53 | 0 | 0 | 0 | No
2030-08-16 05:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 06:00 | 2030 33% ECP | 700 | 0 | 140.86 | 0 | 0 | 0 | No
2030-08-16 07:00 | 2030 33% ECP | 700 | 0 | 85.21 | 0 | 0 | 0 | No
2030-08-16 08:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 09:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 10:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 11:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 12:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 13:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 14:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 15:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 16:00 | 2030 33% ECP | 700 | 0 | -210 | -7.3 | 0 | 0 | No
2030-08-16 17:00 | 2030 33% ECP | 700 | -300 | -510 | -307.3 | 0 | 0 | No
2030-08-16 18:00 | 2030 33% ECP | 700 | -300 | -390 | -455.55 | 0 | 0 | No
2030-08-16 19:00 | 2030 33% ECP | 700 | 0 | -90 | -155.55 | 0 | 0 | No
2030-08-16 20:00 | 2030 33% ECP | 700 | 300 | 210 | 144.45 | 0 | 0 | No
2030-08-16 21:00 | 2030 33% ECP | 700 | 505 | 510 | 140.19 | 0 | 0 | No
2030-08-16 22:00 | 2030 33% ECP | 700 | 505 | 510 | 323.72 | 0 | 0 | No
2030-08-16 23:00 | 2030 33% ECP | 700 | 440.5 | 510 | 259.47 | 0 | 0 | No
2030-08-17 | 2030 33% ECP | 700 | 140.5 | 510 | 0 | 0 | 0 | No
2030-08-17 01:00 | 2030 33% ECP | 700 | 0 | 510 | -106.15 | 0 | 0 | No
2030-08-17 02:00 | 2030 33% ECP | 700 | 0 | 510 | -26.41 | 0 | 0 | No
2030-08-17 03:00 | 2030 33% ECP | 700 | 0 | 510 | -137.67 | 0 | 0 | No
2030-08-17 04:00 | 2030 33% ECP | 700 | 0 | 466.52 | -85.63 | 0 | 0 | No
2030-08-17 05:00 | 2030 33% ECP | 700 | 0 | 423.43 | 0 | 0 | 0 | No
2030-08-17 06:00 | 2030 33% ECP | 700 | 0 | 227.67 | -275.5 | 0 | 0 | No
2030-08-17 07:00 | 2030 33% ECP | 700 | 0 | 459.38 | 0 | 0 | 0 | No
2030-08-17 08:00 | 2030 33% ECP | 700 | 0 | 386.55 | 0 | 0 | 0 | No
2030-08-17 09:00 | 2030 33% ECP | 700 | 0 | 352.98 | 89.64 | 0 | 0 | No
2030-08-17 10:00 | 2030 33% ECP | 700 | 0 | 265.36 | 0 | 0 | 0 | No
2030-08-17 11:00 | 2030 33% ECP | 700 | 0 | 148.55 | 89.55 | 0 | 0 | No
2030-08-17 12:00 | 2030 33% ECP | 700 | 0 | 116.32 | 2.84 | 0 | 0 | No
2030-08-17 13:00 | 2030 33% ECP | 700 | 0 | -183.68 | 0 | 0 | 0 | No
2030-08-17 14:00 | 2030 33% ECP | 700 | 0 | -391.32 | 0 | 0 | 0 | No
2030-08-17 15:00 | 2030 33% ECP | 700 | 0 | -388.64 | 0 | 0 | 0 | No
2030-08-17 16:00 | 2030 33% ECP | 700 | 0 | -99.18 | 36.45 | 0 | 0 | No
2030-08-17 17:00 | 2030 33% ECP | 700 | 0 | 200.82 | 302.15 | 0 | 0 | No
2030-08-17 18:00 | 2030 33% ECP | 700 | 0 | 500.82 | 510 | 0 | 0 | No
2030-08-17 19:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-17 20:00 | 2030 33% ECP | 700 | 0 | 510 | 432.79 | 0 | 0 | No
2030-08-17 21:00 | 2030 33% ECP | 700 | 0 | 510 | 442.34 | 0 | 0 | No
2030-08-17 22:00 | 2030 33% ECP | 700 | 0 | 510 | 396.78 | 0 | 0 | No
2030-08-17 23:00 | 2030 33% ECP | 700 | 0 | 490.51 | 97.67 | 0 | 0 | No
2030-08-18 | 2030 33% ECP | 700 | 0 | 310 | 0 | 0 | 0 | No
2030-08-18 01:00 | 2030 33% ECP | 700 | 0 | 355.03 | 0 | 0 | 0 | No
2030-08-18 02:00 | 2030 33% ECP | 700 | 0 | 345.93 | 9.29 | 0 | 0 | No
2030-08-18 03:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-08-18 04:00 | 2030 33% ECP | 700 | 0 | 327.23 | 95.36 | 0 | 0 | No
2030-08-18 05:00 | 2030 33% ECP | 700 | 0 | 278.99 | 70.31 | 0 | 0 | No
2030-08-18 06:00 | 2030 33% ECP | 700 | 0 | 90 | 76.08 | 0 | 0 | No
2030-08-18 07:00 | 2030 33% ECP | 700 | -113.34 | -210 | 116.75 | 0 | 0 | No
2030-08-18 08:00 | 2030 33% ECP | 700 | -413.34 | -510 | 108.84 | 0 | 0 | No
2030-08-18 09:00 | 2030 33% ECP | 700 | -526 | -510 | 149.08 | 0 | 0 | No
2030-08-18 10:00 | 2030 33% ECP | 700 | -526 | -510 | 163.77 | 0 | 0 | No
2030-08-18 11:00 | 2030 33% ECP | 700 | -526 | -510 | 187.91 | 0 | 0 | No
2030-08-18 12:00 | 2030 33% ECP | 700 | -526 | -510 | 300.07 | 0 | 0 | No
2030-08-18 13:00 | 2030 33% ECP | 700 | -526 | -510 | 271.99 | 0 | 0 | No
2030-08-18 14:00 | 2030 33% ECP | 700 | -526 | -510 | 258.79 | 0 | 0 | No
2030-08-18 15:00 | 2030 33% ECP | 700 | -526 | -510 | 245.07 | 0 | 0 | No
2030-08-18 16:00 | 2030 33% ECP | 700 | -526 | -510 | 275 | 0 | 0 | No
2030-08-18 17:00 | 2030 33% ECP | 700 | -300 | -352.59 | 357.06 | 0 | 0 | No
2030-08-18 18:00 | 2030 33% ECP | 700 | 0 | -52.59 | 314.98 | 0 | 0 | No
2030-08-18 19:00 | 2030 33% ECP | 700 | 0 | 247.41 | 124.32 | 0 | 0 | No
2030-08-18 20:00 | 2030 33% ECP | 700 | 0 | 510 | 339.91 | 0 | 0 | No
2030-08-18 21:00 | 2030 33% ECP | 700 | 0 | 510 | 393.78 | 0 | 0 | No
2030-08-18 22:00 | 2030 33% ECP | 700 | 0 | 510 | 336.85 | 0 | 0 | No
2030-08-18 23:00 | 2030 33% ECP | 700 | 0 | 510 | 244.36 | 0 | 0 | No
2030-08-19 | 2030 33% ECP | 700 | 0 | 423.16 | 263.14 | 0 | 0 | No
2030-08-19 01:00 | 2030 33% ECP | 700 | 0 | 123.16 | 222.28 | 0 | 0 | No
2030-08-19 02:00 | 2030 33% ECP | 700 | 0 | 364.6 | 201.71 | 0 | 0 | No
2030-08-19 03:00 | 2030 33% ECP | 700 | 0 | 122.79 | 185.37 | 0 | 0 | No
2030-08-19 04:00 | 2030 33% ECP | 700 | 0 | 0 | 67.2 | 0 | 0 | No
2030-08-19 05:00 | 2030 33% ECP | 700 | 0 | 300 | 66.24 | 0 | 0 | No
2030-08-19 06:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-19 07:00 | 2030 33% ECP | 700 | 0 | -67.72 | 72.26 | 0 | 0 | No
2030-08-19 08:00 | 2030 33% ECP | 700 | -226 | -210 | 0 | 0 | 0 | No
2030-08-19 09:00 | 2030 33% ECP | 700 | -526 | -510 | -8.94 | 0 | 0 | No
2030-08-19 10:00 | 2030 33% ECP | 700 | -526 | -510 | 115.91 | 0 | 0 | No
2030-08-19 11:00 | 2030 33% ECP | 674.86 | -226 | -210 | 77.81 | 0 | 0 | No
2030-08-19 12:00 | 2030 33% ECP | 254.86 | 74 | 90 | 377.81 | 0 | 0 | No
2030-08-19 13:00 | 2030 33% ECP | -165.14 | 374 | 390 | 451.44 | 0 | 0 | Yes
2030-08-19 14:00 | 2030 33% ECP | -585.14 | 505 | 510 | 268.79 | 0 | 0 | Yes
2030-08-19 15:00 | 2030 33% ECP | -390.11 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-19 16:00 | 2030 33% ECP | 0 | 505 | 510 | 426.32 | 0 | 0 | Yes
2030-08-19 17:00 | 2030 33% ECP | 0 | 505 | 510 | 342.35 | 0 | 0 | Yes
2030-08-19 18:00 | 2030 33% ECP | 0 | 505 | 510 | 204.93 | 0 | 0 | Yes
2030-08-19 19:00 | 2030 33% ECP | -282.86 | 505 | 510 | 176.76 | 0 | 0 | Yes
2030-08-19 20:00 | 2030 33% ECP | -700 | 505 | 510 | 147.38 | 0 | 0 | Yes
2030-08-19 21:00 | 2030 33% ECP | -700 | 505 | 510 | 301.11 | 0 | 0 | Yes
2030-08-19 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-19 23:00 | 2030 33% ECP | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-08-20 | 2030 33% ECP | -700 | 505 | 510 | -90 | 0 | 0 | Yes
2030-08-20 01:00 | 2030 33% ECP | -700 | 505 | 510 | -63.3 | 0 | 0 | Yes
2030-08-20 02:00 | 2030 33% ECP | -700 | 505 | 510 | -80.76 | 0 | 0 | Yes
2030-08-20 03:00 | 2030 33% ECP | -700 | 505 | 510 | -115.65 | 0 | 0 | Yes
2030-08-20 04:00 | 2030 33% ECP | -700 | 505 | 510 | -95.69 | 0 | 0 | Yes
2030-08-20 05:00 | 2030 33% ECP | -700 | 505 | 510 | 51.19 | 0 | 0 | Yes
2030-08-20 06:00 | 2030 33% ECP | -700 | 505 | 510 | 68.86 | 0 | 0 | Yes
2030-08-20 07:00 | 2030 33% ECP | -700 | 505 | 510 | 119.42 | 0 | 0 | Yes
2030-08-20 08:00 | 2030 33% ECP | -700 | 505 | 510 | 203.33 | 0 | 0 | Yes
2030-08-20 09:00 | 2030 33% ECP | -700 | 505 | 510 | 200 | 0 | 0 | Yes
2030-08-20 10:00 | 2030 33% ECP | -700 | 505 | 510 | 160.69 | 0 | 0 | Yes
2030-08-20 11:00 | 2030 33% ECP | -700 | 505 | 510 | 184.02 | 0 | 0 | Yes
2030-08-20 12:00 | 2030 33% ECP | -700 | 505 | 510 | 362.99 | 0 | 0 | Yes
2030-08-20 13:00 | 2030 33% ECP | -700 | 505 | 510 | 416.75 | 0 | 0 | Yes
2030-08-20 14:00 | 2030 33% ECP | -700 | 505 | 510 | 116.75 | 0 | 0 | Yes
2030-08-20 15:00 | 2030 33% ECP | -700 | 505 | 510 | 71.57 | 0 | 0 | Yes
2030-08-20 16:00 | 2030 33% ECP | -700 | 505 | 510 | 248.03 | 0 | 0 | Yes
2030-08-20 17:00 | 2030 33% ECP | -700 | 505 | 510 | 277.27 | 0 | 0 | Yes
2030-08-20 18:00 | 2030 33% ECP | -700 | 341.54 | 510 | 200.66 | 0 | 0 | Yes
2030-08-20 19:00 | 2030 33% ECP | -700 | 41.54 | 210 | -99.34 | 0 | 0 | Yes
2030-08-20 20:00 | 2030 33% ECP | -700 | 341.54 | 510 | 200.66 | 0 | 0 | Yes
2030-08-20 21:00 | 2030 33% ECP | -700 | 505 | 510 | 160.66 | 0 | 0 | Yes
2030-08-20 22:00 | 2030 33% ECP | -700 | 505 | 510 | 45.76 | 0 | 0 | Yes
2030-08-20 23:00 | 2030 33% ECP | -700 | 505 | 510 | -62.61 | 0 | 0 | Yes
2030-08-21 | 2030 33% ECP | -700 | 505 | 510 | 108.51 | 0 | 0 | Yes
2030-08-21 01:00 | 2030 33% ECP | -700 | 505 | 510 | 408.51 | 0 | 0 | Yes
2030-08-21 02:00 | 2030 33% ECP | -700 | 505 | 510 | 294.96 | 0 | 0 | Yes
2030-08-21 03:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-21 04:00 | 2030 33% ECP | -700 | 505 | 510 | 222.12 | 0 | 0 | Yes
2030-08-21 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 18:00 | 2030 33% ECP | -410.59 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 19:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 20:00 | 2030 33% ECP | -420 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 21:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 22:00 | 2030 33% ECP | -184.69 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 23:00 | 2030 33% ECP | -604.69 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 | 2030 33% ECP | -439.21 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 01:00 | 2030 33% ECP | -19.21 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 02:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 03:00 | 2030 33% ECP | -374.16 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 04:00 | 2030 33% ECP | -185.72 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 05:00 | 2030 33% ECP | -587.08 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 06:00 | 2030 33% ECP | -488.83 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 16:00 | 2030 33% ECP | -625.31 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 17:00 | 2030 33% ECP | -205.31 | 300 | 421.62 | 510 | 0 | 0 | No
2030-08-22 18:00 | 2030 33% ECP | 214.69 | 0 | 121.62 | 457.65 | 0 | 0 | No
2030-08-22 19:00 | 2030 33% ECP | 202.85 | -300 | -178.38 | 476.28 | 0 | 0 | No
2030-08-22 20:00 | 2030 33% ECP | 280 | -300 | -390 | 323.75 | 0 | 0 | No
2030-08-22 21:00 | 2030 33% ECP | 700 | 0 | -90 | 510 | 0 | 0 | No
2030-08-22 22:00 | 2030 33% ECP | 700 | 300 | 210 | 510 | 0 | 0 | No
2030-08-22 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 06:00 | 2030 33% ECP | 700 | 205 | 210 | 413.04 | 0 | 0 | No
2030-08-23 07:00 | 2030 33% ECP | 700 | 0 | -55.56 | 422.38 | 0 | 0 | No
2030-08-23 08:00 | 2030 33% ECP | 700 | -226 | -355.56 | 257.67 | 0 | 0 | No
2030-08-23 09:00 | 2030 33% ECP | 700 | -526 | -510 | 246.37 | 0 | 0 | No
2030-08-23 10:00 | 2030 33% ECP | 700 | -526 | -510 | 395.63 | 0 | 0 | No
2030-08-23 11:00 | 2030 33% ECP | 520.98 | -526 | -510 | 395.63 | 0 | 0 | No
2030-08-23 12:00 | 2030 33% ECP | 100.98 | -526 | -510 | 337.65 | 0 | 0 | No
2030-08-23 13:00 | 2030 33% ECP | 450.35 | -526 | -510 | 461.67 | 0 | 0 | No
2030-08-23 14:00 | 2030 33% ECP | 700 | -526 | -510 | 416.52 | 0 | 0 | No
2030-08-23 15:00 | 2030 33% ECP | 700 | -526 | -510 | 421.74 | 0 | 0 | No
2030-08-23 16:00 | 2030 33% ECP | 700 | -526 | -510 | 283.93 | 0 | 0 | No
2030-08-23 17:00 | 2030 33% ECP | 280 | -372.53 | -510 | 341.88 | 0 | 0 | No
2030-08-23 18:00 | 2030 33% ECP | 700 | -72.53 | -210 | 356.07 | 0 | 0 | No
2030-08-23 19:00 | 2030 33% ECP | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-08-23 20:00 | 2030 33% ECP | 700 | 0 | 390 | 264.61 | 0 | 0 | No
2030-08-23 21:00 | 2030 33% ECP | 700 | 0 | 510 | 468.48 | 0 | 0 | No
2030-08-23 22:00 | 2030 33% ECP | 700 | 0 | 510 | 468.48 | 0 | 0 | No
2030-08-23 23:00 | 2030 33% ECP | 700 | 0 | 510 | 468.48 | 0 | 0 | No
2030-08-24 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-24 01:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-24 02:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-24 03:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-24 04:00 | 2030 33% ECP | 700 | 0 | 510 | 320.03 | 0 | 0 | No
2030-08-24 05:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-24 06:00 | 2030 33% ECP | 700 | 0 | 300 | 510 | 0 | 0 | No
2030-08-24 07:00 | 2030 33% ECP | 700 | 0 | 0 | 390.81 | 0 | 0 | No
2030-08-24 08:00 | 2030 33% ECP | 362.31 | -300 | -300 | 457.62 | 0 | 0 | No
2030-08-24 09:00 | 2030 33% ECP | 700 | -526 | -510 | 195.57 | 0 | 0 | No
2030-08-24 10:00 | 2030 33% ECP | 700 | -526 | -510 | 16.35 | 0 | 0 | No
2030-08-24 11:00 | 2030 33% ECP | 280 | -526 | -510 | 27.18 | 0 | 0 | No
2030-08-24 12:00 | 2030 33% ECP | 700 | -526 | -510 | 106.47 | 0 | 0 | No
2030-08-24 13:00 | 2030 33% ECP | 337.95 | -526 | -510 | 106.47 | 0 | 0 | No
2030-08-24 14:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-08-24 15:00 | 2030 33% ECP | 592.48 | -526 | -510 | 66.35 | 0 | 0 | No
2030-08-24 16:00 | 2030 33% ECP | 172.48 | -526 | -510 | 0 | 0 | 0 | No
2030-08-24 17:00 | 2030 33% ECP | 0 | -526 | -510 | -240.48 | 0 | 0 | No
2030-08-24 18:00 | 2030 33% ECP | 350.87 | -526 | -510 | -510 | 0 | 0 | No
2030-08-24 19:00 | 2030 33% ECP | 0 | -526 | -510 | -417.61 | 0 | 0 | No
2030-08-24 20:00 | 2030 33% ECP | 0 | -526 | -510 | -117.61 | 0 | 0 | No
2030-08-24 21:00 | 2030 33% ECP | -73.19 | -526 | -510 | -272.09 | 0 | 0 | No
2030-08-24 22:00 | 2030 33% ECP | -493.19 | -526 | -510 | -260.95 | 0 | 0 | No
2030-08-24 23:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-25 | 2030 33% ECP | -663.21 | -526 | -510 | -510 | 0 | 0 | No
2030-08-25 01:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-08-25 02:00 | 2030 33% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-08-25 03:00 | 2030 33% ECP | -700 | 374 | 390 | 0 | 0 | 0 | Yes
2030-08-25 04:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 05:00 | 2030 33% ECP | -700 | 505 | 510 | -208.73 | 0 | 0 | Yes
2030-08-25 06:00 | 2030 33% ECP | -700 | 505 | 510 | -223.38 | 0 | 0 | Yes
2030-08-25 07:00 | 2030 33% ECP | -700 | 505 | 510 | -174.61 | 0 | 0 | Yes
2030-08-25 08:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 09:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 10:00 | 2030 33% ECP | -700 | 505 | 510 | 18.6 | 0 | 0 | Yes
2030-08-25 11:00 | 2030 33% ECP | -700 | 505 | 510 | -12.14 | 0 | 0 | Yes
2030-08-25 12:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 13:00 | 2030 33% ECP | -700 | 505 | 510 | -37.79 | 0 | 0 | Yes
2030-08-25 14:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 15:00 | 2030 33% ECP | -700 | 505 | 510 | 233.64 | 0 | 0 | Yes
2030-08-25 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 19:00 | 2030 33% ECP | -700 | 505 | 510 | 339.45 | 0 | 0 | Yes
2030-08-25 20:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-26 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 01:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 02:00 | 2030 33% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 07:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 08:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 09:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 10:00 | 2030 33% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 11:00 | 2030 33% ECP | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 13:00 | 2030 33% ECP | -508.25 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 14:00 | 2030 33% ECP | -88.25 | 205 | 210 | 510 | 0 | 0 | No
2030-08-26 15:00 | 2030 33% ECP | 321.31 | -95 | -90 | 459.87 | 0 | 0 | No
2030-08-26 16:00 | 2030 33% ECP | 700 | -395 | -390 | 510 | 0 | 0 | No
2030-08-26 17:00 | 2030 33% ECP | 700 | -95 | -510 | 461.8 | 0 | 0 | No
2030-08-26 18:00 | 2030 33% ECP | 700 | 0 | -321.65 | 364.18 | 0 | 0 | No
2030-08-26 19:00 | 2030 33% ECP | 700 | 0 | -21.65 | 364.18 | 0 | 0 | No
2030-08-26 20:00 | 2030 33% ECP | 700 | 0 | 0 | 430.84 | 0 | 0 | No
2030-08-26 21:00 | 2030 33% ECP | 700 | 0 | 0 | 486.94 | 0 | 0 | No
2030-08-26 22:00 | 2030 33% ECP | 700 | 0 | 0 | 446.38 | 0 | 0 | No
2030-08-26 23:00 | 2030 33% ECP | 700 | 0 | 0 | 318.47 | 0 | 0 | No
2030-08-27 | 2030 33% ECP | 700 | 0 | 300 | 53.47 | 0 | 0 | No
2030-08-27 01:00 | 2030 33% ECP | 700 | 0 | 273.58 | 55.1 | 0 | 0 | No
2030-08-27 02:00 | 2030 33% ECP | 700 | 0 | 124.64 | 15.47 | 0 | 0 | No
2030-08-27 03:00 | 2030 33% ECP | 700 | 0 | -175.36 | 25.46 | 0 | 0 | No
2030-08-27 04:00 | 2030 33% ECP | 700 | 0 | -222.7 | 12.02 | 0 | 0 | No
2030-08-27 05:00 | 2030 33% ECP | 700 | 0 | -269.85 | 29.77 | 0 | 0 | No
2030-08-27 06:00 | 2030 33% ECP | 700 | 0 | -362.4 | 99.34 | 0 | 0 | No
2030-08-27 07:00 | 2030 33% ECP | 700 | 0 | -62.4 | 167.67 | 0 | 0 | No
2030-08-27 08:00 | 2030 33% ECP | 700 | 0 | 237.6 | 272.17 | 0 | 0 | No
2030-08-27 09:00 | 2030 33% ECP | 700 | 0 | 353.66 | 353.05 | 0 | 0 | No
2030-08-27 10:00 | 2030 33% ECP | 700 | 0 | 58.63 | 313.56 | 0 | 0 | No
2030-08-27 11:00 | 2030 33% ECP | 700 | 0 | -239.51 | 261.65 | 0 | 0 | No
2030-08-27 12:00 | 2030 33% ECP | 700 | 0 | -246.17 | 261.65 | 0 | 0 | No
2030-08-27 13:00 | 2030 33% ECP | 700 | 0 | -331.01 | 168.56 | 0 | 0 | No
2030-08-27 14:00 | 2030 33% ECP | 700 | -171.28 | -510 | 380.81 | 0 | 0 | No
2030-08-27 15:00 | 2030 33% ECP | 700 | 0 | -259.38 | 361.72 | 0 | 0 | No
2030-08-27 16:00 | 2030 33% ECP | 700 | 0 | 40.56 | 417.14 | 0 | 0 | No
2030-08-27 17:00 | 2030 33% ECP | 700 | 0 | 340.56 | 426.99 | 0 | 0 | No
2030-08-27 18:00 | 2030 33% ECP | 700 | 0 | 510 | 426.99 | 0 | 0 | No
2030-08-27 19:00 | 2030 33% ECP | 700 | 0 | 510 | 407.23 | 0 | 0 | No
2030-08-27 20:00 | 2030 33% ECP | 700 | 0 | 510 | 351.08 | 0 | 0 | No
2030-08-27 21:00 | 2030 33% ECP | 700 | 0 | 510 | 275.85 | 0 | 0 | No
2030-08-27 22:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-08-27 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 01:00 | 2030 33% ECP | 700 | 505 | 510 | 382.24 | 0 | 0 | No
2030-08-28 02:00 | 2030 33% ECP | 639.15 | 505 | 510 | 242.19 | 0 | 0 | Yes
2030-08-28 03:00 | 2030 33% ECP | 375.65 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-28 04:00 | 2030 33% ECP | 0 | 505 | 510 | 300 | 0 | 0 | Yes
2030-08-28 05:00 | 2030 33% ECP | 0 | 505 | 510 | 51.39 | 0 | 0 | Yes
2030-08-28 06:00 | 2030 33% ECP | 0 | 505 | 510 | 351.39 | 0 | 0 | Yes
2030-08-28 07:00 | 2030 33% ECP | 140 | 505 | 510 | 280.47 | 0 | 0 | Yes
2030-08-28 08:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 18:00 | 2030 33% ECP | -280 | 300 | 383.19 | 300 | 0 | 0 | No
2030-08-28 19:00 | 2030 33% ECP | -420 | 0 | 83.19 | 0 | 0 | 0 | No
2030-08-28 20:00 | 2030 33% ECP | 0 | 205 | 210 | 210 | 0 | 0 | No
2030-08-28 21:00 | 2030 33% ECP | 360.61 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 03:00 | 2030 33% ECP | 618.05 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 04:00 | 2030 33% ECP | 618.05 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 05:00 | 2030 33% ECP | 283.06 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 06:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 07:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 16:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 17:00 | 2030 33% ECP | 140 | 300 | 482.31 | 435.13 | 0 | 0 | No
2030-08-29 18:00 | 2030 33% ECP | 560 | 0 | 182.31 | 135.13 | 0 | 0 | No
2030-08-29 19:00 | 2030 33% ECP | 140 | 0 | -117.69 | -20.76 | 0 | 0 | No
2030-08-29 20:00 | 2030 33% ECP | 280 | 0 | 182.31 | 195.73 | 0 | 0 | No
2030-08-29 21:00 | 2030 33% ECP | 700 | 300 | 482.31 | 495.73 | 0 | 0 | No
2030-08-29 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 06:00 | 2030 33% ECP | 700 | 205 | 300 | 210 | 0 | 0 | No
2030-08-30 07:00 | 2030 33% ECP | 700 | 0 | 0 | 131.78 | 0 | 0 | No
2030-08-30 08:00 | 2030 33% ECP | 340.02 | -300 | -300 | -134.79 | 0 | 0 | No
2030-08-30 09:00 | 2030 33% ECP | 700 | -526 | -510 | -180.49 | 0 | 0 | No
2030-08-30 10:00 | 2030 33% ECP | 700 | -526 | -510 | -133.46 | 0 | 0 | No
2030-08-30 11:00 | 2030 33% ECP | 280 | -526 | -510 | 166.54 | 0 | 0 | No
2030-08-30 12:00 | 2030 33% ECP | 700 | -526 | -510 | 169.68 | 0 | 0 | No
2030-08-30 13:00 | 2030 33% ECP | 700 | -526 | -510 | 137.81 | 0 | 0 | No
2030-08-30 14:00 | 2030 33% ECP | 700 | -526 | -510 | 107.43 | 0 | 0 | No
2030-08-30 15:00 | 2030 33% ECP | 700 | -526 | -510 | 146.31 | 0 | 0 | No
2030-08-30 16:00 | 2030 33% ECP | 700 | -226 | -300 | -8.92 | 0 | 0 | No
2030-08-30 17:00 | 2030 33% ECP | 700 | 74 | 0 | 109.01 | 0 | 0 | No
2030-08-30 18:00 | 2030 33% ECP | 700 | -92.92 | -300 | -190.99 | 0 | 0 | No
2030-08-30 19:00 | 2030 33% ECP | 700 | -35.08 | -425.96 | -473.32 | 0 | 0 | No
2030-08-30 20:00 | 2030 33% ECP | 700 | 0 | -125.96 | -173.32 | 0 | 0 | No
2030-08-30 21:00 | 2030 33% ECP | 700 | 300 | 174.04 | 126.68 | 0 | 0 | No
2030-08-30 22:00 | 2030 33% ECP | 700 | 363.74 | 474.04 | 426.68 | 0 | 0 | No
2030-08-30 23:00 | 2030 33% ECP | 700 | 244.48 | 510 | 329.29 | 0 | 0 | No
2030-08-31 | 2030 33% ECP | 700 | 0 | 363.44 | 29.29 | 0 | 0 | No
2030-08-31 01:00 | 2030 33% ECP | 700 | 0 | 278.36 | 0 | 0 | 0 | No
2030-08-31 02:00 | 2030 33% ECP | 700 | 0 | -21.64 | 0 | 0 | 0 | No
2030-08-31 03:00 | 2030 33% ECP | 700 | 0 | -319.18 | 0 | 0 | 0 | No
2030-08-31 04:00 | 2030 33% ECP | 700 | 0 | -510 | -10.36 | 0 | 0 | No
2030-08-31 05:00 | 2030 33% ECP | 644.73 | 0 | -482.82 | -140.28 | 0 | 0 | No
2030-08-31 06:00 | 2030 33% ECP | 224.73 | 0 | -182.82 | 0 | 0 | 0 | No
2030-08-31 07:00 | 2030 33% ECP | -195.27 | -226 | -260.61 | -210 | 0 | 0 | No
2030-08-31 08:00 | 2030 33% ECP | -615.27 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 09:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 10:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 11:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 12:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 13:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 14:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 15:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 16:00 | 2030 33% ECP | -433.53 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 17:00 | 2030 33% ECP | -13.53 | -526 | -510 | -359.63 | 0 | 0 | No
2030-08-31 18:00 | 2030 33% ECP | 406.47 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 19:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 20:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 21:00 | 2030 33% ECP | 700 | -230.7 | -510 | -321.11 | 0 | 0 | No
2030-08-31 22:00 | 2030 33% ECP | 700 | -1.47 | -510 | -321.11 | 0 | 0 | No
2030-08-31 23:00 | 2030 33% ECP | 700 | -301.47 | -510 | -26.89 | 0 | 0 | No
2030-09-01 | 2030 33% ECP | 700 | -526 | -510 | -109.11 | 0 | 0 | No
2030-09-01 01:00 | 2030 33% ECP | 700 | -250.23 | -510 | -84 | 0 | 0 | No
2030-09-01 02:00 | 2030 33% ECP | 700 | -526 | -510 | -75.56 | 0 | 0 | No
2030-09-01 03:00 | 2030 33% ECP | 700 | -526 | -510 | -92.68 | 0 | 0 | No
2030-09-01 04:00 | 2030 33% ECP | 700 | -526 | -510 | -139.03 | 0 | 0 | No
2030-09-01 05:00 | 2030 33% ECP | 700 | -337.57 | -510 | -319.45 | 0 | 0 | No
2030-09-01 06:00 | 2030 33% ECP | 700 | -213.55 | -510 | -135.64 | 0 | 0 | No
2030-09-01 07:00 | 2030 33% ECP | 700 | -306.22 | -510 | -38.8 | 0 | 0 | No
2030-09-01 08:00 | 2030 33% ECP | 700 | -526 | -510 | -24.38 | 0 | 0 | No
2030-09-01 09:00 | 2030 33% ECP | 700 | -526 | -510 | -82.33 | 0 | 0 | No
2030-09-01 10:00 | 2030 33% ECP | 700 | -526 | -510 | -98.2 | 0 | 0 | No
2030-09-01 11:00 | 2030 33% ECP | 700 | -526 | -510 | -165.5 | 0 | 0 | No
2030-09-01 12:00 | 2030 33% ECP | 700 | -526 | -510 | -57.53 | 0 | 0 | No
2030-09-01 13:00 | 2030 33% ECP | 700 | -526 | -510 | -144.69 | 0 | 0 | No
2030-09-01 14:00 | 2030 33% ECP | 700 | -526 | -510 | -55.65 | 0 | 0 | No
2030-09-01 15:00 | 2030 33% ECP | 700 | -526 | -510 | -226.01 | 0 | 0 | No
2030-09-01 16:00 | 2030 33% ECP | 700 | -526 | -510 | 48.77 | 0 | 0 | No
2030-09-01 17:00 | 2030 33% ECP | 280 | -526 | -510 | 130.37 | 0 | 0 | No
2030-09-01 18:00 | 2030 33% ECP | -67.38 | -526 | -510 | 164.16 | 0 | 0 | No
2030-09-01 19:00 | 2030 33% ECP | -10.85 | -526 | -510 | 42.9 | 0 | 0 | No
2030-09-01 20:00 | 2030 33% ECP | -10.85 | -526 | -510 | 42.9 | 0 | 0 | No
2030-09-01 21:00 | 2030 33% ECP | -405.18 | -526 | -510 | 67.57 | 0 | 0 | No
2030-09-01 22:00 | 2030 33% ECP | 14.82 | -526 | -510 | -232.43 | 0 | 0 | No
2030-09-01 23:00 | 2030 33% ECP | 434.82 | -526 | -510 | -245.14 | 0 | 0 | No
2030-09-02 | 2030 33% ECP | 14.82 | -526 | -510 | -387.02 | 0 | 0 | No
2030-09-02 01:00 | 2030 33% ECP | -376.61 | -526 | -510 | -310.11 | 0 | 0 | No
2030-09-02 02:00 | 2030 33% ECP | -426.48 | -364.47 | -510 | -238.69 | 0 | 0 | No
2030-09-02 03:00 | 2030 33% ECP | -700 | -64.47 | -510 | -162.36 | 0 | 0 | No
2030-09-02 04:00 | 2030 33% ECP | -700 | -166.31 | -510 | -462.36 | 0 | 0 | No
2030-09-02 05:00 | 2030 33% ECP | -700 | -304.06 | -510 | -510 | 0 | 0 | No
2030-09-02 06:00 | 2030 33% ECP | -700 | -95 | -268.37 | -210 | 0 | 0 | No
2030-09-02 07:00 | 2030 33% ECP | -700 | 205 | 31.63 | 90 | 0 | 0 | No
2030-09-02 08:00 | 2030 33% ECP | -700 | 505 | 331.63 | 390 | 0 | 0 | No
2030-09-02 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 20:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 | 2030 33% ECP | -287.44 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 01:00 | 2030 33% ECP | -207.16 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 02:00 | 2030 33% ECP | -627.16 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 03:00 | 2030 33% ECP | -207.16 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 04:00 | 2030 33% ECP | 14.37 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 05:00 | 2030 33% ECP | 434.37 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 06:00 | 2030 33% ECP | 185.2 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 07:00 | 2030 33% ECP | 27.3 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 08:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 17:00 | 2030 33% ECP | -359.29 | 300 | 387.07 | 300 | 0 | 0 | No
2030-09-03 18:00 | 2030 33% ECP | 0 | 0 | 87.07 | 0 | 0 | 0 | No
2030-09-03 19:00 | 2030 33% ECP | 0 | -300 | -212.93 | -300 | 0 | 0 | No
2030-09-03 20:00 | 2030 33% ECP | 0 | 0 | 0 | 0 | 0 | 0 | No
2030-09-03 21:00 | 2030 33% ECP | 280 | 300 | 300 | 300 | 0 | 0 | No
2030-09-03 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 05:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 06:00 | 2030 33% ECP | 57.21 | 205 | 210 | 210 | 0 | 0 | No
2030-09-04 07:00 | 2030 33% ECP | 0 | 0 | 65.98 | -16.55 | 0 | 0 | No
2030-09-04 08:00 | 2030 33% ECP | -194.51 | 200.35 | 210 | 210 | 0 | 0 | No
2030-09-04 09:00 | 2030 33% ECP | -280 | 500.35 | 510 | 510 | 0 | 0 | No
2030-09-04 10:00 | 2030 33% ECP | -700 | 200.35 | 510 | 269.17 | 0 | 0 | Yes
2030-09-04 11:00 | 2030 33% ECP | -700 | 0 | 210 | 19.31 | 0 | 0 | Yes
2030-09-04 12:00 | 2030 33% ECP | -700 | 300 | 510 | 319.31 | 0 | 0 | Yes
2030-09-04 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 14:00 | 2030 33% ECP | -700 | 505 | 499.03 | 510 | 0 | 0 | Yes
2030-09-04 15:00 | 2030 33% ECP | -700 | 505 | 199.03 | 213.59 | 0 | 0 | Yes
2030-09-04 16:00 | 2030 33% ECP | -700 | 300 | -100.97 | -86.41 | 0 | 0 | No
2030-09-04 17:00 | 2030 33% ECP | -280 | 0 | -400.97 | -386.41 | 0 | 0 | No
2030-09-04 18:00 | 2030 33% ECP | 140 | -300 | -510 | -510 | 0 | 0 | No
2030-09-04 19:00 | 2030 33% ECP | 560 | -395 | -390 | -240.02 | 0 | 0 | No
2030-09-04 20:00 | 2030 33% ECP | 700 | -95 | -90 | -90 | 0 | 0 | No
2030-09-04 21:00 | 2030 33% ECP | 677.61 | 205 | 210 | 210 | 0 | 0 | No
2030-09-04 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 23:00 | 2030 33% ECP | 533.05 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 06:00 | 2030 33% ECP | 299.72 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 07:00 | 2030 33% ECP | 0 | 205 | 313.92 | 210 | 0 | 0 | No
2030-09-05 08:00 | 2030 33% ECP | -261.78 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 09:00 | 2030 33% ECP | -681.78 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 10:00 | 2030 33% ECP | -700 | 505 | 348.1 | 510 | 0 | 0 | No
2030-09-05 11:00 | 2030 33% ECP | -700 | 205 | 48.1 | 480.17 | 0 | 0 | No
2030-09-05 12:00 | 2030 33% ECP | -700 | -95 | -251.9 | 180.17 | 0 | 0 | No
2030-09-05 13:00 | 2030 33% ECP | -700 | 0 | -348.47 | 480.17 | 0 | 0 | No
2030-09-05 14:00 | 2030 33% ECP | -489.87 | -226 | -210 | 510 | 0 | 0 | No
2030-09-05 15:00 | 2030 33% ECP | -69.87 | -526 | -510 | 510 | 0 | 0 | No
2030-09-05 16:00 | 2030 33% ECP | 75.08 | -526 | -510 | 510 | 0 | 0 | No
2030-09-05 17:00 | 2030 33% ECP | 495.08 | -226 | -510 | 510 | 0 | 0 | No
2030-09-05 18:00 | 2030 33% ECP | 700 | 0 | -480.99 | 510 | 0 | 0 | No
2030-09-05 19:00 | 2030 33% ECP | 700 | 0 | -480.99 | 510 | 0 | 0 | No
2030-09-05 20:00 | 2030 33% ECP | 700 | 0 | -222.98 | 510 | 0 | 0 | No
2030-09-05 21:00 | 2030 33% ECP | 700 | 0 | -222.98 | 510 | 0 | 0 | No
2030-09-05 22:00 | 2030 33% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-09-05 23:00 | 2030 33% ECP | 700 | 0 | -300.82 | 469 | 0 | 0 | No
2030-09-06 | 2030 33% ECP | 454.75 | 0 | -0.82 | 296.35 | 0 | 0 | No
2030-09-06 01:00 | 2030 33% ECP | 584.72 | 0 | 0 | 296.35 | 0 | 0 | No
2030-09-06 02:00 | 2030 33% ECP | 700 | 0 | -165.26 | 0 | 0 | 0 | No
2030-09-06 03:00 | 2030 33% ECP | 700 | 0 | -358.05 | 0 | 0 | 0 | No
2030-09-06 04:00 | 2030 33% ECP | 700 | 0 | -419.09 | 0 | 0 | 0 | No
2030-09-06 05:00 | 2030 33% ECP | 700 | -125.04 | -510 | 0 | 0 | 0 | No
2030-09-06 06:00 | 2030 33% ECP | 700 | 0 | -486.6 | 29.76 | 0 | 0 | No
2030-09-06 07:00 | 2030 33% ECP | 700 | 0 | -259.3 | 218.82 | 0 | 0 | No
2030-09-06 08:00 | 2030 33% ECP | 700 | -59.61 | -285.67 | 329.83 | 0 | 0 | No
2030-09-06 09:00 | 2030 33% ECP | 280 | -359.61 | -510 | 311.31 | 0 | 0 | No
2030-09-06 10:00 | 2030 33% ECP | -140 | -526 | -510 | 218.59 | 0 | 0 | No
2030-09-06 11:00 | 2030 33% ECP | -512.45 | -526 | -510 | 243.13 | 0 | 0 | No
2030-09-06 12:00 | 2030 33% ECP | -92.45 | -526 | -510 | 251.67 | 0 | 0 | No
2030-09-06 13:00 | 2030 33% ECP | -512.45 | -526 | -510 | 166.22 | 0 | 0 | No
2030-09-06 14:00 | 2030 33% ECP | -506.13 | -526 | -510 | 136.82 | 0 | 0 | No
2030-09-06 15:00 | 2030 33% ECP | -86.13 | -526 | -510 | 147.55 | 0 | 0 | No
2030-09-06 16:00 | 2030 33% ECP | 333.87 | -526 | -510 | -152.45 | 0 | 0 | No
2030-09-06 17:00 | 2030 33% ECP | 700 | -226 | -510 | -452.45 | 0 | 0 | No
2030-09-06 18:00 | 2030 33% ECP | 700 | 0 | -510 | -251.63 | 0 | 0 | No
2030-09-06 19:00 | 2030 33% ECP | 700 | 0 | -510 | -488.39 | 0 | 0 | No
2030-09-06 20:00 | 2030 33% ECP | 700 | 0 | -510 | -411.72 | 0 | 0 | No
2030-09-06 21:00 | 2030 33% ECP | 700 | 0 | -300 | -111.72 | 0 | 0 | No
2030-09-06 22:00 | 2030 33% ECP | 700 | 0 | 0 | 188.28 | 0 | 0 | No
2030-09-06 23:00 | 2030 33% ECP | 700 | -274.89 | -300 | -111.72 | 0 | 0 | No
2030-09-07 | 2030 33% ECP | 700 | -280.99 | -510 | -200.95 | 0 | 0 | No
2030-09-07 01:00 | 2030 33% ECP | 500.44 | -526 | -510 | -158.21 | 0 | 0 | No
2030-09-07 02:00 | 2030 33% ECP | 407.96 | -526 | -510 | -49.17 | 0 | 0 | No
2030-09-07 03:00 | 2030 33% ECP | 0 | -526 | -510 | -17.2 | 0 | 0 | No
2030-09-07 04:00 | 2030 33% ECP | -294.93 | -526 | -510 | -231.36 | 0 | 0 | No
2030-09-07 05:00 | 2030 33% ECP | -521.38 | -526 | -510 | -180.36 | 0 | 0 | No
2030-09-07 06:00 | 2030 33% ECP | -511.78 | -526 | -510 | -180.85 | 0 | 0 | No
2030-09-07 07:00 | 2030 33% ECP | -511.78 | -526 | -510 | 51.17 | 0 | 0 | No
2030-09-07 08:00 | 2030 33% ECP | -700 | -526 | -510 | 144.58 | 0 | 0 | No
2030-09-07 09:00 | 2030 33% ECP | -700 | -526 | -510 | 95.38 | 0 | 0 | No
2030-09-07 10:00 | 2030 33% ECP | -700 | -395 | -392.54 | 168.3 | 0 | 0 | No
2030-09-07 11:00 | 2030 33% ECP | -700 | -95 | -92.54 | 468.3 | 0 | 0 | No
2030-09-07 12:00 | 2030 33% ECP | -700 | 205 | 207.46 | 510 | 0 | 0 | No
2030-09-07 13:00 | 2030 33% ECP | -700 | 505 | 507.46 | 510 | 0 | 0 | No
2030-09-07 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-07 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-07 16:00 | 2030 33% ECP | -372.73 | 205 | 374.01 | 381.28 | 0 | 0 | No
2030-09-07 17:00 | 2030 33% ECP | 0 | 300 | 74.01 | 272.81 | 0 | 0 | No
2030-09-07 18:00 | 2030 33% ECP | 0 | 0 | -225.99 | -27.19 | 0 | 0 | No
2030-09-07 19:00 | 2030 33% ECP | 0 | -289.25 | -90 | -90 | 0 | 0 | No
2030-09-07 20:00 | 2030 33% ECP | 0 | 10.75 | 210 | 210 | 0 | 0 | No
2030-09-07 21:00 | 2030 33% ECP | 280 | 310.75 | 510 | 510 | 0 | 0 | No
2030-09-07 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-07 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 06:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-09-08 07:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 08:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 09:00 | 2030 33% ECP | 515.95 | 205 | 210 | 510 | 0 | 0 | No
2030-09-08 10:00 | 2030 33% ECP | 95.95 | -95 | -90 | 510 | 0 | 0 | No
2030-09-08 11:00 | 2030 33% ECP | 0 | -200.76 | -300 | 510 | 0 | 0 | No
2030-09-08 12:00 | 2030 33% ECP | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-09-08 13:00 | 2030 33% ECP | 0 | 0 | 300 | 510 | 0 | 0 | No
2030-09-08 14:00 | 2030 33% ECP | 0 | 0 | 393.52 | 510 | 0 | 0 | No
2030-09-08 15:00 | 2030 33% ECP | 0 | 0 | 510 | 500.83 | 0 | 0 | No
2030-09-08 16:00 | 2030 33% ECP | 0 | 0 | 484.95 | 339.11 | 0 | 0 | No
2030-09-08 17:00 | 2030 33% ECP | 420 | 0 | 485.48 | 268.15 | 0 | 0 | No
2030-09-08 18:00 | 2030 33% ECP | 0 | 0 | 218.99 | 0 | 0 | 0 | No
2030-09-08 19:00 | 2030 33% ECP | -144.18 | 205 | 210 | 210 | 0 | 0 | No
2030-09-08 20:00 | 2030 33% ECP | 275.82 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 21:00 | 2030 33% ECP | 695.82 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 04:00 | 2030 33% ECP | 643.7 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 06:00 | 2030 33% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 07:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 08:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 15:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 16:00 | 2030 33% ECP | 140 | 300 | 374.6 | 510 | 0 | 0 | No
2030-09-09 17:00 | 2030 33% ECP | 560 | 0 | 74.6 | 336.41 | 0 | 0 | No
2030-09-09 18:00 | 2030 33% ECP | 700 | 0 | 356.74 | 510 | 0 | 0 | No
2030-09-09 19:00 | 2030 33% ECP | 700 | 0 | 507.34 | 510 | 0 | 0 | No
2030-09-09 20:00 | 2030 33% ECP | 700 | 0 | 507.34 | 510 | 0 | 0 | No
2030-09-09 21:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-09 22:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-09 23:00 | 2030 33% ECP | 700 | 0 | 355.69 | 510 | 0 | 0 | No
2030-09-10 | 2030 33% ECP | 700 | 0 | 510 | 256.95 | 0 | 0 | No
2030-09-10 01:00 | 2030 33% ECP | 700 | 0 | 510 | 229.26 | 0 | 0 | No
2030-09-10 02:00 | 2030 33% ECP | 700 | 0 | 510 | 190.54 | 0 | 0 | No
2030-09-10 03:00 | 2030 33% ECP | 700 | 0 | 510 | 171.17 | 0 | 0 | No
2030-09-10 04:00 | 2030 33% ECP | 700 | 0 | 263.13 | 183.38 | 0 | 0 | No
2030-09-10 05:00 | 2030 33% ECP | 700 | 0 | 289.24 | 225.1 | 0 | 0 | No
2030-09-10 06:00 | 2030 33% ECP | 700 | 0 | 0 | 324.3 | 0 | 0 | No
2030-09-10 07:00 | 2030 33% ECP | 589.31 | -247.97 | -300 | 350.25 | 0 | 0 | No
2030-09-10 08:00 | 2030 33% ECP | 169.31 | -226 | -210 | 503.4 | 0 | 0 | No
2030-09-10 09:00 | 2030 33% ECP | -250.69 | -526 | -510 | 510 | 0 | 0 | No
2030-09-10 10:00 | 2030 33% ECP | -670.69 | -526 | -510 | 381 | 0 | 0 | No
2030-09-10 11:00 | 2030 33% ECP | -700 | -526 | -510 | 355.04 | 0 | 0 | No
2030-09-10 12:00 | 2030 33% ECP | -700 | -526 | -510 | 166.65 | 0 | 0 | No
2030-09-10 13:00 | 2030 33% ECP | -403.24 | -526 | -510 | 176.12 | 0 | 0 | No
2030-09-10 14:00 | 2030 33% ECP | 16.76 | -526 | -510 | 210.29 | 0 | 0 | No
2030-09-10 15:00 | 2030 33% ECP | 436.76 | -526 | -510 | 288.87 | 0 | 0 | No
2030-09-10 16:00 | 2030 33% ECP | 289.78 | -300 | -510 | 489.09 | 0 | 0 | No
2030-09-10 17:00 | 2030 33% ECP | 700 | 0 | -339.89 | 460.63 | 0 | 0 | No
2030-09-10 18:00 | 2030 33% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-09-10 19:00 | 2030 33% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-09-10 20:00 | 2030 33% ECP | 700 | 0 | -510 | 392.03 | 0 | 0 | No
2030-09-10 21:00 | 2030 33% ECP | 700 | 0 | -390 | 388.84 | 0 | 0 | No
2030-09-10 22:00 | 2030 33% ECP | 610.47 | -275.99 | -90 | 275.66 | 0 | 0 | No
2030-09-10 23:00 | 2030 33% ECP | 560 | 24.01 | 210 | 210 | 0 | 0 | No
2030-09-11 | 2030 33% ECP | 140 | 324.01 | 510 | 510 | 0 | 0 | No
2030-09-11 01:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 15:00 | 2030 33% ECP | -295.14 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 16:00 | 2030 33% ECP | 124.86 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 17:00 | 2030 33% ECP | 544.86 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 18:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-09-11 19:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-11 20:00 | 2030 33% ECP | 700 | 0 | 6.81 | 109.75 | 0 | 0 | No
2030-09-11 21:00 | 2030 33% ECP | 700 | 205 | 306.81 | 293.73 | 0 | 0 | No
2030-09-11 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 07:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 08:00 | 2030 33% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 09:00 | 2030 33% ECP | -560 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-12 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-12 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-12 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-12 13:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-09-12 14:00 | 2030 33% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-09-12 15:00 | 2030 33% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-09-12 16:00 | 2030 33% ECP | -700 | -526 | -510 | 286.01 | 0 | 0 | Yes
2030-09-12 17:00 | 2030 33% ECP | -700 | -526 | -510 | 84.05 | 0 | 0 | No
2030-09-12 18:00 | 2030 33% ECP | -700 | -526 | -510 | -153.79 | 0 | 0 | No
2030-09-12 19:00 | 2030 33% ECP | -700 | -526 | -510 | -243.15 | 0 | 0 | No
2030-09-12 20:00 | 2030 33% ECP | -700 | -526 | -510 | -328.55 | 0 | 0 | No
2030-09-12 21:00 | 2030 33% ECP | -700 | -226 | -210 | -28.55 | 0 | 0 | No
2030-09-12 22:00 | 2030 33% ECP | -700 | 74 | 90 | 271.45 | 0 | 0 | Yes
2030-09-12 23:00 | 2030 33% ECP | -700 | 374 | 390 | 373.68 | 0 | 0 | Yes
2030-09-13 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-13 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-13 02:00 | 2030 33% ECP | -700 | 505 | 300 | 510 | 0 | 0 | Yes
2030-09-13 03:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 04:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 05:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 06:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 07:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 08:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 09:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 10:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 11:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 12:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 13:00 | 2030 33% ECP | -700 | 374 | 0 | 510 | 0 | 0 | Yes
2030-09-13 14:00 | 2030 33% ECP | -700 | 74 | 0 | 510 | 0 | 0 | Yes
2030-09-13 15:00 | 2030 33% ECP | -700 | -226 | 0 | 510 | 0 | 0 | Yes
2030-09-13 16:00 | 2030 33% ECP | -700 | -526 | 0 | 416.46 | 0 | 0 | Yes
2030-09-13 17:00 | 2030 33% ECP | -700 | -526 | 0 | 203.51 | 0 | 0 | No
2030-09-13 18:00 | 2030 33% ECP | -280 | -526 | 0 | 503.51 | 0 | 0 | No
2030-09-13 19:00 | 2030 33% ECP | 0 | -526 | 0 | 510 | 0 | 0 | No
2030-09-13 20:00 | 2030 33% ECP | 0 | -526 | 0 | 510 | 0 | 0 | No
2030-09-13 21:00 | 2030 33% ECP | 0 | -526 | 0 | 510 | 0 | 0 | No
2030-09-13 22:00 | 2030 33% ECP | 280 | -526 | 0 | 432.99 | 0 | 0 | No
2030-09-13 23:00 | 2030 33% ECP | 700 | -428.85 | 0 | 272.19 | 0 | 0 | No
2030-09-14 | 2030 33% ECP | 398.02 | -128.85 | 0 | 510 | 0 | 0 | No
2030-09-14 01:00 | 2030 33% ECP | 700 | 74 | 0 | 510 | 0 | 0 | No
2030-09-14 02:00 | 2030 33% ECP | 700 | -226 | 0 | 247.92 | 0 | 0 | No
2030-09-14 03:00 | 2030 33% ECP | 700 | -526 | 0 | 13.83 | 0 | 0 | No
2030-09-14 04:00 | 2030 33% ECP | 700 | -526 | 0 | 0 | 0 | 0 | No
2030-09-14 05:00 | 2030 33% ECP | 700 | -526 | 0 | 14.48 | 0 | 0 | No
2030-09-14 06:00 | 2030 33% ECP | 580.14 | -526 | 0 | 45.98 | 0 | 0 | No
2030-09-14 07:00 | 2030 33% ECP | 700 | -526 | 0 | 139.71 | 0 | 0 | No
2030-09-14 08:00 | 2030 33% ECP | 533.79 | -526 | 0 | 172.33 | 0 | 0 | No
2030-09-14 09:00 | 2030 33% ECP | 700 | -526 | 0 | 199.85 | 0 | 0 | No
2030-09-14 10:00 | 2030 33% ECP | 700 | -526 | 0 | 224.28 | 0 | 0 | No
2030-09-14 11:00 | 2030 33% ECP | 700 | -526 | 0 | 228.23 | 0 | 0 | No
2030-09-14 12:00 | 2030 33% ECP | 700 | -526 | 0 | 223.7 | 0 | 0 | No
2030-09-14 13:00 | 2030 33% ECP | 700 | -526 | 0 | 167.81 | 0 | 0 | No
2030-09-14 14:00 | 2030 33% ECP | 700 | -526 | 0 | 146.61 | 0 | 0 | No
2030-09-14 15:00 | 2030 33% ECP | 700 | -526 | 0 | 164.2 | 0 | 0 | No
2030-09-14 16:00 | 2030 33% ECP | 700 | -526 | 0 | 177.98 | 0 | 0 | No
2030-09-14 17:00 | 2030 33% ECP | 700 | -526 | 0 | -122.02 | 0 | 0 | No
2030-09-14 18:00 | 2030 33% ECP | 700 | -526 | 0 | -146.82 | 0 | 0 | No
2030-09-14 19:00 | 2030 33% ECP | 700 | -526 | 0 | -267.63 | 0 | 0 | No
2030-09-14 20:00 | 2030 33% ECP | 700 | -526 | 0 | -105.82 | 0 | 0 | No
2030-09-14 21:00 | 2030 33% ECP | 624.63 | -526 | 0 | 194.18 | 0 | 0 | No
2030-09-14 22:00 | 2030 33% ECP | 700 | -526 | 0 | 130.02 | 0 | 0 | No
2030-09-14 23:00 | 2030 33% ECP | 700 | -526 | 0 | -147.56 | 0 | 0 | No
2030-09-15 | 2030 33% ECP | 700 | -226 | 0 | 0 | 0 | 0 | No
2030-09-15 01:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-15 02:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-15 03:00 | 2030 33% ECP | 700 | 0 | -413.16 | 0 | 0 | 0 | No
2030-09-15 04:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-15 05:00 | 2030 33% ECP | 700 | 0 | -501.2 | 0 | 0 | 0 | No
2030-09-15 06:00 | 2030 33% ECP | 700 | 0 | -211.57 | 0 | 0 | 0 | No
2030-09-15 07:00 | 2030 33% ECP | 700 | 0 | -510 | 6.78 | 0 | 0 | No
2030-09-15 08:00 | 2030 33% ECP | 700 | -226 | -510 | 0 | 0 | 0 | No
2030-09-15 09:00 | 2030 33% ECP | 700 | -526 | -510 | 23.42 | 0 | 0 | No
2030-09-15 10:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-09-15 11:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-09-15 12:00 | 2030 33% ECP | 700 | -526 | -510 | 36.79 | 0 | 0 | No
2030-09-15 13:00 | 2030 33% ECP | 700 | -526 | -510 | 57.51 | 0 | 0 | No
2030-09-15 14:00 | 2030 33% ECP | 700 | -526 | -510 | 68.25 | 0 | 0 | No
2030-09-15 15:00 | 2030 33% ECP | 700 | -526 | -510 | 91.14 | 0 | 0 | No
2030-09-15 16:00 | 2030 33% ECP | 700 | -526 | -510 | 164.34 | 0 | 0 | No
2030-09-15 17:00 | 2030 33% ECP | 700 | -226 | -388.81 | 300 | 0 | 0 | No
2030-09-15 18:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-09-15 19:00 | 2030 33% ECP | 700 | -526 | -510 | 195.01 | 0 | 0 | No
2030-09-15 20:00 | 2030 33% ECP | 700 | -226 | -210 | 495.01 | 0 | 0 | No
2030-09-15 21:00 | 2030 33% ECP | 700 | 74 | 90 | 510 | 0 | 0 | No
2030-09-15 22:00 | 2030 33% ECP | 700 | 187.53 | 390 | 510 | 0 | 0 | No
2030-09-15 23:00 | 2030 33% ECP | 700 | 0 | 510 | 234.07 | 0 | 0 | No
2030-09-16 | 2030 33% ECP | 700 | 0 | 510 | 370.83 | 0 | 0 | No
2030-09-16 01:00 | 2030 33% ECP | 700 | 0 | 510 | 151.86 | 0 | 0 | No
2030-09-16 02:00 | 2030 33% ECP | 700 | 0 | 510 | 149.04 | 0 | 0 | No
2030-09-16 03:00 | 2030 33% ECP | 700 | 0 | 510 | 109.46 | 0 | 0 | No
2030-09-16 04:00 | 2030 33% ECP | 700 | 0 | 510 | 109.52 | 0 | 0 | No
2030-09-16 05:00 | 2030 33% ECP | 700 | 0 | 510 | 140.07 | 0 | 0 | No
2030-09-16 06:00 | 2030 33% ECP | 700 | 0 | 510 | 249.11 | 0 | 0 | No
2030-09-16 07:00 | 2030 33% ECP | 700 | 0 | 510 | 347.32 | 0 | 0 | No
2030-09-16 08:00 | 2030 33% ECP | 700 | 0 | 289.6 | 297.38 | 0 | 0 | No
2030-09-16 09:00 | 2030 33% ECP | 700 | 198.94 | 510 | 510 | 0 | 0 | No
2030-09-16 10:00 | 2030 33% ECP | 700 | 293.36 | 510 | 510 | 0 | 0 | No
2030-09-16 11:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-16 12:00 | 2030 33% ECP | 700 | 336.22 | 510 | 510 | 0 | 0 | No
2030-09-16 13:00 | 2030 33% ECP | 700 | 336.22 | 510 | 510 | 0 | 0 | No
2030-09-16 14:00 | 2030 33% ECP | 700 | 36.22 | 210 | 510 | 0 | 0 | No
2030-09-16 15:00 | 2030 33% ECP | 700 | -230.69 | -90 | 510 | 0 | 0 | No
2030-09-16 16:00 | 2030 33% ECP | 700 | -300 | -362.08 | 470.22 | 0 | 0 | No
2030-09-16 17:00 | 2030 33% ECP | 700 | 0 | -62.08 | 483.1 | 0 | 0 | No
2030-09-16 18:00 | 2030 33% ECP | 700 | 0 | 191.79 | 445.09 | 0 | 0 | No
2030-09-16 19:00 | 2030 33% ECP | 700 | 0 | 481.46 | 439.7 | 0 | 0 | No
2030-09-16 20:00 | 2030 33% ECP | 700 | 0 | 510 | 489.06 | 0 | 0 | No
2030-09-16 21:00 | 2030 33% ECP | 700 | 0 | 510 | 333.73 | 0 | 0 | No
2030-09-16 22:00 | 2030 33% ECP | 700 | 0 | 510 | 151.15 | 0 | 0 | No
2030-09-16 23:00 | 2030 33% ECP | 700 | 0 | 510 | 196.23 | 0 | 0 | No
2030-09-17 | 2030 33% ECP | 700 | 0 | 258.31 | 0 | 0 | 0 | No
2030-09-17 01:00 | 2030 33% ECP | 700 | 0 | 428.6 | 0 | 0 | 0 | No
2030-09-17 02:00 | 2030 33% ECP | 700 | 0 | 172.09 | 0 | 0 | 0 | No
2030-09-17 03:00 | 2030 33% ECP | 700 | 0 | 120.71 | 0 | 0 | 0 | No
2030-09-17 04:00 | 2030 33% ECP | 700 | 0 | 212.26 | 0 | 0 | 0 | No
2030-09-17 05:00 | 2030 33% ECP | 700 | 0 | 81.5 | 0 | 0 | 0 | No
2030-09-17 06:00 | 2030 33% ECP | 700 | 0 | 81.5 | 0 | 0 | 0 | No
2030-09-17 07:00 | 2030 33% ECP | 700 | 0 | -141.58 | 132.77 | 0 | 0 | No
2030-09-17 08:00 | 2030 33% ECP | 700 | -300 | -441.58 | 192.86 | 0 | 0 | No
2030-09-17 09:00 | 2030 33% ECP | 700 | -526 | -510 | 240.16 | 0 | 0 | No
2030-09-17 10:00 | 2030 33% ECP | 700 | -526 | -510 | 231.45 | 0 | 0 | No
2030-09-17 11:00 | 2030 33% ECP | 700 | -526 | -510 | 250.22 | 0 | 0 | No
2030-09-17 12:00 | 2030 33% ECP | 700 | -526 | -510 | 164.07 | 0 | 0 | No
2030-09-17 13:00 | 2030 33% ECP | 700 | -526 | -510 | 207.84 | 0 | 0 | No
2030-09-17 14:00 | 2030 33% ECP | 700 | -526 | -510 | 239.8 | 0 | 0 | No
2030-09-17 15:00 | 2030 33% ECP | 700 | -526 | -510 | 245.17 | 0 | 0 | No
2030-09-17 16:00 | 2030 33% ECP | 700 | -399.54 | -510 | 361.85 | 0 | 0 | No
2030-09-17 17:00 | 2030 33% ECP | 700 | -99.54 | -210 | 466.75 | 0 | 0 | No
2030-09-17 18:00 | 2030 33% ECP | 700 | 0 | 0 | 389.61 | 0 | 0 | No
2030-09-17 19:00 | 2030 33% ECP | 700 | 0 | 0 | 351.79 | 0 | 0 | No
2030-09-17 20:00 | 2030 33% ECP | 700 | 0 | 0 | 444.76 | 0 | 0 | No
2030-09-17 21:00 | 2030 33% ECP | 700 | 0 | 129.3 | 441.41 | 0 | 0 | No
2030-09-17 22:00 | 2030 33% ECP | 700 | 0 | 0 | 271.41 | 0 | 0 | No
2030-09-17 23:00 | 2030 33% ECP | 700 | 0 | -1.76 | 177.04 | 0 | 0 | No
2030-09-18 | 2030 33% ECP | 700 | 0 | -51.01 | 335.31 | 0 | 0 | No
2030-09-18 01:00 | 2030 33% ECP | 700 | 0 | -65.88 | 103.52 | 0 | 0 | No
2030-09-18 02:00 | 2030 33% ECP | 700 | 0 | -260.3 | 47.34 | 0 | 0 | No
2030-09-18 03:00 | 2030 33% ECP | 700 | 0 | 0 | 70.62 | 0 | 0 | No
2030-09-18 04:00 | 2030 33% ECP | 700 | 0 | 0 | 17.28 | 0 | 0 | No
2030-09-18 05:00 | 2030 33% ECP | 700 | 0 | -265.03 | 81.9 | 0 | 0 | No
2030-09-18 06:00 | 2030 33% ECP | 700 | 0 | -39.13 | 200.24 | 0 | 0 | No
2030-09-18 07:00 | 2030 33% ECP | 700 | -152.7 | -210 | 371 | 0 | 0 | No
2030-09-18 08:00 | 2030 33% ECP | 700 | -452.7 | -510 | 447.91 | 0 | 0 | No
2030-09-18 09:00 | 2030 33% ECP | 700 | -526 | -510 | 388.63 | 0 | 0 | No
2030-09-18 10:00 | 2030 33% ECP | 280 | -526 | -510 | 242.73 | 0 | 0 | No
2030-09-18 11:00 | 2030 33% ECP | -119.38 | -526 | -510 | 268.45 | 0 | 0 | No
2030-09-18 12:00 | 2030 33% ECP | -515.96 | -526 | -510 | 249.45 | 0 | 0 | No
2030-09-18 13:00 | 2030 33% ECP | -515.96 | -526 | -510 | 232.33 | 0 | 0 | No
2030-09-18 14:00 | 2030 33% ECP | -214.87 | -526 | -510 | 109.23 | 0 | 0 | No
2030-09-18 15:00 | 2030 33% ECP | 205.13 | -526 | -510 | 195.46 | 0 | 0 | No
2030-09-18 16:00 | 2030 33% ECP | 625.13 | -526 | -510 | 307.75 | 0 | 0 | No
2030-09-18 17:00 | 2030 33% ECP | 689.66 | -300 | -510 | 410.73 | 0 | 0 | No
2030-09-18 18:00 | 2030 33% ECP | 700 | 0 | -210 | 491.8 | 0 | 0 | No
2030-09-18 19:00 | 2030 33% ECP | 700 | 0 | 0 | 354.75 | 0 | 0 | No
2030-09-18 20:00 | 2030 33% ECP | 700 | 0 | 0 | 185.18 | 0 | 0 | No
2030-09-18 21:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-09-18 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-18 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 05:00 | 2030 33% ECP | 280 | 205 | 210 | 210 | 0 | 0 | No
2030-09-19 06:00 | 2030 33% ECP | 700 | 0 | -33.09 | 11.45 | 0 | 0 | No
2030-09-19 07:00 | 2030 33% ECP | 445.04 | 0 | -169.25 | 243.58 | 0 | 0 | No
2030-09-19 08:00 | 2030 33% ECP | 25.04 | -226 | -469.25 | 168.84 | 0 | 0 | No
2030-09-19 09:00 | 2030 33% ECP | -394.96 | -526 | -510 | 248.42 | 0 | 0 | No
2030-09-19 10:00 | 2030 33% ECP | -700 | -526 | -510 | 473.79 | 0 | 0 | No
2030-09-19 11:00 | 2030 33% ECP | -675.76 | -526 | -510 | 510 | 0 | 0 | No
2030-09-19 12:00 | 2030 33% ECP | -255.76 | -226 | -210 | 510 | 0 | 0 | No
2030-09-19 13:00 | 2030 33% ECP | 164.24 | 74 | 90 | 510 | 0 | 0 | No
2030-09-19 14:00 | 2030 33% ECP | -43.26 | -226 | -210 | 510 | 0 | 0 | No
2030-09-19 15:00 | 2030 33% ECP | -463.26 | -526 | -510 | 510 | 0 | 0 | No
2030-09-19 16:00 | 2030 33% ECP | -43.26 | -466.32 | -510 | 510 | 0 | 0 | No
2030-09-19 17:00 | 2030 33% ECP | 376.74 | -166.32 | -210 | 510 | 0 | 0 | No
2030-09-19 18:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-09-19 19:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-09-19 20:00 | 2030 33% ECP | 700 | 0 | 0 | 390.8 | 0 | 0 | No
2030-09-19 21:00 | 2030 33% ECP | 700 | 0 | -59.21 | 459.46 | 0 | 0 | No
2030-09-19 22:00 | 2030 33% ECP | 700 | 0 | -59.21 | 510 | 0 | 0 | No
2030-09-19 23:00 | 2030 33% ECP | 700 | 0 | 0 | 361.35 | 0 | 0 | No
2030-09-20 | 2030 33% ECP | 700 | 0 | 300 | 510 | 0 | 0 | No
2030-09-20 01:00 | 2030 33% ECP | 700 | 0 | 367.02 | 365.85 | 0 | 0 | No
2030-09-20 02:00 | 2030 33% ECP | 700 | 0 | 381.4 | 510 | 0 | 0 | No
2030-09-20 03:00 | 2030 33% ECP | 700 | 43.39 | 510 | 510 | 0 | 0 | No
2030-09-20 04:00 | 2030 33% ECP | 700 | 248.47 | 300 | 510 | 0 | 0 | No
2030-09-20 05:00 | 2030 33% ECP | 700 | 0 | 0 | 210 | 0 | 0 | No
2030-09-20 06:00 | 2030 33% ECP | 700 | 0 | 33.45 | 127.26 | 0 | 0 | No
2030-09-20 07:00 | 2030 33% ECP | 569.91 | 0 | 42.74 | 274.45 | 0 | 0 | No
2030-09-20 08:00 | 2030 33% ECP | 149.91 | 0 | -210 | 413.71 | 0 | 0 | No
2030-09-20 09:00 | 2030 33% ECP | -270.09 | -300 | -510 | 381.6 | 0 | 0 | No
2030-09-20 10:00 | 2030 33% ECP | -690.09 | -526 | -510 | 268.19 | 0 | 0 | No
2030-09-20 11:00 | 2030 33% ECP | -700 | -526 | -510 | 267.41 | 0 | 0 | No
2030-09-20 12:00 | 2030 33% ECP | -541.58 | -526 | -510 | 237.96 | 0 | 0 | No
2030-09-20 13:00 | 2030 33% ECP | -121.58 | -526 | -510 | 210.07 | 0 | 0 | No
2030-09-20 14:00 | 2030 33% ECP | 298.42 | -526 | -510 | 198.14 | 0 | 0 | No
2030-09-20 15:00 | 2030 33% ECP | 700 | -526 | -510 | 224.22 | 0 | 0 | No
2030-09-20 16:00 | 2030 33% ECP | 435.2 | -300 | -450.92 | 314.65 | 0 | 0 | No
2030-09-20 17:00 | 2030 33% ECP | 700 | 0 | -150.92 | 344.14 | 0 | 0 | No
2030-09-20 18:00 | 2030 33% ECP | 700 | -300 | -450.92 | 44.14 | 0 | 0 | No
2030-09-20 19:00 | 2030 33% ECP | 700 | -95 | -150.92 | 135.31 | 0 | 0 | No
2030-09-20 20:00 | 2030 33% ECP | 700 | 205 | 149.08 | 435.31 | 0 | 0 | No
2030-09-20 21:00 | 2030 33% ECP | 700 | 505 | 449.08 | 510 | 0 | 0 | No
2030-09-20 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-20 23:00 | 2030 33% ECP | 700 | 205 | 510 | 490.5 | 0 | 0 | No
2030-09-21 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-21 01:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-21 02:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-21 03:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-21 04:00 | 2030 33% ECP | 700 | 0 | 510 | 210 | 0 | 0 | No
2030-09-21 05:00 | 2030 33% ECP | 700 | 0 | 487.65 | 11.56 | 0 | 0 | No
2030-09-21 06:00 | 2030 33% ECP | 700 | 0 | 390 | 274.56 | 0 | 0 | No
2030-09-21 07:00 | 2030 33% ECP | 474.47 | 1.15 | 90 | 510 | 0 | 0 | No
2030-09-21 08:00 | 2030 33% ECP | 54.47 | -226 | -210 | 406.99 | 0 | 0 | No
2030-09-21 09:00 | 2030 33% ECP | -365.53 | -526 | -510 | 229.43 | 0 | 0 | No
2030-09-21 10:00 | 2030 33% ECP | -700 | -526 | -510 | 186.12 | 0 | 0 | No
2030-09-21 11:00 | 2030 33% ECP | -280 | -526 | -510 | 37.65 | 0 | 0 | No
2030-09-21 12:00 | 2030 33% ECP | 140 | -526 | -510 | 26.21 | 0 | 0 | No
2030-09-21 13:00 | 2030 33% ECP | 560 | -526 | -510 | 0 | 0 | 0 | No
2030-09-21 14:00 | 2030 33% ECP | 700 | -526 | -510 | 42.95 | 0 | 0 | No
2030-09-21 15:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-09-21 16:00 | 2030 33% ECP | 280 | -526 | -510 | 88.75 | 0 | 0 | No
2030-09-21 17:00 | 2030 33% ECP | 700 | -526 | -510 | -211.25 | 0 | 0 | No
2030-09-21 18:00 | 2030 33% ECP | 700 | -526 | -510 | -390 | 0 | 0 | No
2030-09-21 19:00 | 2030 33% ECP | 700 | -300 | -471.54 | -90 | 0 | 0 | No
2030-09-21 20:00 | 2030 33% ECP | 700 | 0 | -171.54 | 210 | 0 | 0 | No
2030-09-21 21:00 | 2030 33% ECP | 700 | 300 | 128.46 | 510 | 0 | 0 | No
2030-09-21 22:00 | 2030 33% ECP | 700 | 144.26 | 428.46 | 510 | 0 | 0 | No
2030-09-21 23:00 | 2030 33% ECP | 700 | 0 | 144.31 | 300 | 0 | 0 | No
2030-09-22 | 2030 33% ECP | 700 | -12.75 | -155.69 | 0 | 0 | 0 | No
2030-09-22 01:00 | 2030 33% ECP | 700 | 0 | -453.72 | 0 | 0 | 0 | No
2030-09-22 02:00 | 2030 33% ECP | 700 | -128.57 | -510 | 69.78 | 0 | 0 | No
2030-09-22 03:00 | 2030 33% ECP | 632.32 | -428.57 | -510 | -136.11 | 0 | 0 | No
2030-09-22 04:00 | 2030 33% ECP | 700 | -526 | -510 | -180.83 | 0 | 0 | No
2030-09-22 05:00 | 2030 33% ECP | 700 | -526 | -510 | -247.3 | 0 | 0 | No
2030-09-22 06:00 | 2030 33% ECP | 280 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 07:00 | 2030 33% ECP | -140 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 08:00 | 2030 33% ECP | -218.87 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 09:00 | 2030 33% ECP | -638.87 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 10:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-09-22 11:00 | 2030 33% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-09-22 12:00 | 2030 33% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-09-22 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-22 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-22 15:00 | 2030 33% ECP | -578.86 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-22 16:00 | 2030 33% ECP | -158.86 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 17:00 | 2030 33% ECP | 261.14 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 18:00 | 2030 33% ECP | 681.14 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 19:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 20:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 05:00 | 2030 33% ECP | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-09-23 06:00 | 2030 33% ECP | 700 | 0 | 464.8 | 230.45 | 0 | 0 | No
2030-09-23 07:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-23 08:00 | 2030 33% ECP | 700 | 38.86 | 510 | 510 | 0 | 0 | No
2030-09-23 09:00 | 2030 33% ECP | 700 | 0 | 210.63 | 510 | 0 | 0 | No
2030-09-23 10:00 | 2030 33% ECP | 700 | -19.82 | -89.37 | 510 | 0 | 0 | No
2030-09-23 11:00 | 2030 33% ECP | 700 | -226 | -389.37 | 449.22 | 0 | 0 | No
2030-09-23 12:00 | 2030 33% ECP | 700 | -526 | -510 | 472.42 | 0 | 0 | No
2030-09-23 13:00 | 2030 33% ECP | 700 | -526 | -510 | 361.03 | 0 | 0 | No
2030-09-23 14:00 | 2030 33% ECP | 700 | -526 | -510 | 383.08 | 0 | 0 | No
2030-09-23 15:00 | 2030 33% ECP | 700 | -226 | -210 | 510 | 0 | 0 | No
2030-09-23 16:00 | 2030 33% ECP | 700 | 74 | 90 | 510 | 0 | 0 | No
2030-09-23 17:00 | 2030 33% ECP | 700 | 19.88 | 390 | 510 | 0 | 0 | No
2030-09-23 18:00 | 2030 33% ECP | 700 | 19.88 | 510 | 510 | 0 | 0 | No
2030-09-23 19:00 | 2030 33% ECP | 700 | 19.88 | 510 | 510 | 0 | 0 | No
2030-09-23 20:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-23 21:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-23 22:00 | 2030 33% ECP | 700 | 60.7 | 210 | 270.83 | 0 | 0 | No
2030-09-23 23:00 | 2030 33% ECP | 543.56 | 360.7 | 510 | 510 | 0 | 0 | No
2030-09-24 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 06:00 | 2030 33% ECP | 700 | 205 | 210 | 216.14 | 0 | 0 | No
2030-09-24 07:00 | 2030 33% ECP | 700 | -95 | -90 | -83.86 | 0 | 0 | No
2030-09-24 08:00 | 2030 33% ECP | 700 | -395 | -390 | -383.86 | 0 | 0 | No
2030-09-24 09:00 | 2030 33% ECP | 700 | -526 | -510 | -133.84 | 0 | 0 | No
2030-09-24 10:00 | 2030 33% ECP | 700 | -226 | -210 | 166.16 | 0 | 0 | No
2030-09-24 11:00 | 2030 33% ECP | 280 | 0 | 84.76 | 466.16 | 0 | 0 | No
2030-09-24 12:00 | 2030 33% ECP | 0 | 0 | -215.24 | 166.16 | 0 | 0 | No
2030-09-24 13:00 | 2030 33% ECP | 0 | 0 | -460.87 | 106.12 | 0 | 0 | No
2030-09-24 14:00 | 2030 33% ECP | 0 | -300 | -510 | 0 | 0 | 0 | No
2030-09-24 15:00 | 2030 33% ECP | 0 | -526 | -510 | 86.61 | 0 | 0 | No
2030-09-24 16:00 | 2030 33% ECP | 419.32 | -526 | -510 | 210 | 0 | 0 | No
2030-09-24 17:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-24 18:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-24 19:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-24 20:00 | 2030 33% ECP | 700 | -285.28 | -489.69 | 510 | 0 | 0 | No
2030-09-24 21:00 | 2030 33% ECP | 700 | 0 | -189.69 | 510 | 0 | 0 | No
2030-09-24 22:00 | 2030 33% ECP | 585.83 | 205 | 110.31 | 510 | 0 | 0 | No
2030-09-24 23:00 | 2030 33% ECP | 165.83 | 505 | 410.31 | 510 | 0 | 0 | No
2030-09-25 | 2030 33% ECP | -135.23 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 01:00 | 2030 33% ECP | -462.23 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 16:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 17:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 18:00 | 2030 33% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 19:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 20:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 07:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 08:00 | 2030 33% ECP | 426.47 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 09:00 | 2030 33% ECP | 6.47 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 10:00 | 2030 33% ECP | -413.53 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 14:00 | 2030 33% ECP | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 15:00 | 2030 33% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 16:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 17:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 18:00 | 2030 33% ECP | 700 | 205 | 254.68 | 389.75 | 0 | 0 | No
2030-09-26 19:00 | 2030 33% ECP | 700 | 205 | 263.86 | 352.06 | 0 | 0 | No
2030-09-26 20:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 07:00 | 2030 33% ECP | 700 | 205 | 302.58 | 510 | 0 | 0 | No
2030-09-27 08:00 | 2030 33% ECP | 700 | 354.64 | 510 | 510 | 0 | 0 | No
2030-09-27 09:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 10:00 | 2030 33% ECP | 700 | 300 | 390 | 510 | 0 | 0 | No
2030-09-27 11:00 | 2030 33% ECP | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-09-27 12:00 | 2030 33% ECP | 700 | -300 | -210 | 284.21 | 0 | 0 | No
2030-09-27 13:00 | 2030 33% ECP | 700 | -526 | -510 | 326.6 | 0 | 0 | No
2030-09-27 14:00 | 2030 33% ECP | 700 | -526 | -510 | 348.51 | 0 | 0 | No
2030-09-27 15:00 | 2030 33% ECP | 700 | -526 | -510 | 397.4 | 0 | 0 | No
2030-09-27 16:00 | 2030 33% ECP | 700 | -395.55 | -510 | 496.05 | 0 | 0 | No
2030-09-27 17:00 | 2030 33% ECP | 700 | -95.55 | -210.19 | 510 | 0 | 0 | No
2030-09-27 18:00 | 2030 33% ECP | 700 | 0 | -168.69 | 510 | 0 | 0 | No
2030-09-27 19:00 | 2030 33% ECP | 700 | 0 | -168.69 | 510 | 0 | 0 | No
2030-09-27 20:00 | 2030 33% ECP | 700 | 0 | -168.69 | 510 | 0 | 0 | No
2030-09-27 21:00 | 2030 33% ECP | 700 | 0 | -168.69 | 235.11 | 0 | 0 | No
2030-09-27 22:00 | 2030 33% ECP | 700 | 0 | -168.69 | 252.49 | 0 | 0 | No
2030-09-27 23:00 | 2030 33% ECP | 700 | 0 | -350.49 | 201.77 | 0 | 0 | No
2030-09-28 | 2030 33% ECP | 700 | -229.9 | -510 | 100.98 | 0 | 0 | No
2030-09-28 01:00 | 2030 33% ECP | 700 | -242.7 | -510 | 83.34 | 0 | 0 | No
2030-09-28 02:00 | 2030 33% ECP | 700 | -526 | -510 | 87.38 | 0 | 0 | No
2030-09-28 03:00 | 2030 33% ECP | 700 | -226 | -488.25 | 122.04 | 0 | 0 | No
2030-09-28 04:00 | 2030 33% ECP | 700 | 0 | -320.27 | 51.35 | 0 | 0 | No
2030-09-28 05:00 | 2030 33% ECP | 700 | 0 | -277.79 | 75.25 | 0 | 0 | No
2030-09-28 06:00 | 2030 33% ECP | 700 | 0 | -277.79 | 21.17 | 0 | 0 | No
2030-09-28 07:00 | 2030 33% ECP | 700 | 0 | -40.58 | 158.94 | 0 | 0 | No
2030-09-28 08:00 | 2030 33% ECP | 306.51 | 0 | -67.79 | 281.71 | 0 | 0 | No
2030-09-28 09:00 | 2030 33% ECP | -113.49 | -226 | -323.18 | 335.57 | 0 | 0 | No
2030-09-28 10:00 | 2030 33% ECP | -533.49 | -526 | -510 | 301.52 | 0 | 0 | No
2030-09-28 11:00 | 2030 33% ECP | -700 | -526 | -510 | 304.95 | 0 | 0 | No
2030-09-28 12:00 | 2030 33% ECP | -700 | -526 | -510 | 263.6 | 0 | 0 | No
2030-09-28 13:00 | 2030 33% ECP | -280 | -526 | -510 | -36.4 | 0 | 0 | No
2030-09-28 14:00 | 2030 33% ECP | 140 | -526 | -510 | -336.4 | 0 | 0 | No
2030-09-28 15:00 | 2030 33% ECP | 560 | -526 | -510 | -209.92 | 0 | 0 | No
2030-09-28 16:00 | 2030 33% ECP | 700 | -526 | -510 | 54.7 | 0 | 0 | No
2030-09-28 17:00 | 2030 33% ECP | 700 | -226 | -210 | 27.32 | 0 | 0 | No
2030-09-28 18:00 | 2030 33% ECP | 700 | 0 | 11.9 | 242.31 | 0 | 0 | No
2030-09-28 19:00 | 2030 33% ECP | 700 | 0 | 72.98 | 374.4 | 0 | 0 | No
2030-09-28 20:00 | 2030 33% ECP | 700 | 0 | 372.98 | 477.2 | 0 | 0 | No
2030-09-28 21:00 | 2030 33% ECP | 700 | 0 | 510 | 392.32 | 0 | 0 | No
2030-09-28 22:00 | 2030 33% ECP | 700 | 0 | 510 | 334.65 | 0 | 0 | No
2030-09-28 23:00 | 2030 33% ECP | 700 | 0 | 510 | 277.6 | 0 | 0 | No
2030-09-29 | 2030 33% ECP | 700 | 0 | 510 | 239.21 | 0 | 0 | No
2030-09-29 01:00 | 2030 33% ECP | 700 | 0 | 510 | 279.29 | 0 | 0 | No
2030-09-29 02:00 | 2030 33% ECP | 700 | 0 | 510 | 265.08 | 0 | 0 | No
2030-09-29 03:00 | 2030 33% ECP | 700 | 0 | 405.74 | 234.66 | 0 | 0 | No
2030-09-29 04:00 | 2030 33% ECP | 700 | 0 | 105.74 | 225.56 | 0 | 0 | No
2030-09-29 05:00 | 2030 33% ECP | 700 | 0 | 3.99 | 204.35 | 0 | 0 | No
2030-09-29 06:00 | 2030 33% ECP | 700 | 0 | 0 | 234.41 | 0 | 0 | No
2030-09-29 07:00 | 2030 33% ECP | 700 | 0 | 0 | 287.88 | 0 | 0 | No
2030-09-29 08:00 | 2030 33% ECP | 317.41 | -194.41 | -261.47 | 275.54 | 0 | 0 | No
2030-09-29 09:00 | 2030 33% ECP | -102.59 | -494.41 | -510 | 248.06 | 0 | 0 | No
2030-09-29 10:00 | 2030 33% ECP | -522.59 | -526 | -510 | 215.83 | 0 | 0 | No
2030-09-29 11:00 | 2030 33% ECP | -700 | -526 | -510 | 123.92 | 0 | 0 | No
2030-09-29 12:00 | 2030 33% ECP | -700 | -526 | -510 | 148.2 | 0 | 0 | No
2030-09-29 13:00 | 2030 33% ECP | -280 | -526 | -510 | 111.87 | 0 | 0 | No
2030-09-29 14:00 | 2030 33% ECP | 140 | -526 | -510 | 23.25 | 0 | 0 | No
2030-09-29 15:00 | 2030 33% ECP | 560 | -526 | -510 | 23.25 | 0 | 0 | No
2030-09-29 16:00 | 2030 33% ECP | 231.75 | -526 | -510 | 243.44 | 0 | 0 | No
2030-09-29 17:00 | 2030 33% ECP | -188.25 | -526 | -510 | 191.03 | 0 | 0 | No
2030-09-29 18:00 | 2030 33% ECP | -608.25 | -526 | -510 | 170.79 | 0 | 0 | No
2030-09-29 19:00 | 2030 33% ECP | -700 | -526 | -510 | 207.23 | 0 | 0 | No
2030-09-29 20:00 | 2030 33% ECP | -700 | -526 | -510 | 35.3 | 0 | 0 | No
2030-09-29 21:00 | 2030 33% ECP | -700 | -526 | -510 | -264.7 | 0 | 0 | No
2030-09-29 22:00 | 2030 33% ECP | -700 | -526 | -510 | -291.43 | 0 | 0 | No
2030-09-29 23:00 | 2030 33% ECP | -700 | -395 | -405.94 | -237.25 | 0 | 0 | No
2030-09-30 | 2030 33% ECP | -280 | -95 | -105.94 | 62.75 | 0 | 0 | No
2030-09-30 01:00 | 2030 33% ECP | 140 | 205 | 194.06 | 362.75 | 0 | 0 | Yes
2030-09-30 02:00 | 2030 33% ECP | 560 | 505 | 494.06 | 510 | 0 | 0 | Yes
2030-09-30 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-30 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 07:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 08:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 09:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 10:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 11:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 12:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 13:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 14:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 15:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 16:00 | 2030 33% ECP | 700 | 426.29 | 510 | 510 | 0 | 0 | No
2030-09-30 17:00 | 2030 33% ECP | 700 | 300 | 354.59 | 510 | 0 | 0 | No
2030-09-30 18:00 | 2030 33% ECP | 700 | 0 | 54.59 | 510 | 0 | 0 | No
2030-09-30 19:00 | 2030 33% ECP | 700 | 0 | 304.03 | 510 | 0 | 0 | No
2030-09-30 20:00 | 2030 33% ECP | 700 | 205 | 224.79 | 510 | 0 | 0 | No
2030-09-30 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 05:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-10-01 06:00 | 2030 33% ECP | 700 | 0 | -16.94 | 0 | 0 | 0 | No
2030-10-01 07:00 | 2030 33% ECP | 700 | 0 | 178.55 | 114.69 | 0 | 0 | No
2030-10-01 08:00 | 2030 33% ECP | 700 | 0 | -121.45 | 180.42 | 0 | 0 | No
2030-10-01 09:00 | 2030 33% ECP | 700 | -300 | -421.45 | 180.42 | 0 | 0 | No
2030-10-01 10:00 | 2030 33% ECP | 700 | -526 | -510 | 78.08 | 0 | 0 | No
2030-10-01 11:00 | 2030 33% ECP | 633.07 | -526 | -510 | 0 | 0 | 0 | No
2030-10-01 12:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-10-01 13:00 | 2030 33% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-10-01 14:00 | 2030 33% ECP | 700 | -300 | -304.26 | 0 | 0 | 0 | No
2030-10-01 15:00 | 2030 33% ECP | 700 | 0 | -4.26 | 28.93 | 0 | 0 | No
2030-10-01 16:00 | 2030 33% ECP | 700 | 0 | 143.73 | 0 | 0 | 0 | No
2030-10-01 17:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-01 18:00 | 2030 33% ECP | 700 | -91.51 | -300 | -300 | 0 | 0 | No
2030-10-01 19:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-01 20:00 | 2030 33% ECP | 700 | 0 | 210 | 210 | 0 | 0 | No
2030-10-01 21:00 | 2030 33% ECP | 700 | 256.74 | 510 | 510 | 0 | 0 | No
2030-10-01 22:00 | 2030 33% ECP | 700 | 0 | 210 | 211.77 | 0 | 0 | No
2030-10-01 23:00 | 2030 33% ECP | 700 | -239.12 | -90 | -88.23 | 0 | 0 | No
2030-10-02 | 2030 33% ECP | 700 | -239.86 | -390 | -9.57 | 0 | 0 | No
2030-10-02 01:00 | 2030 33% ECP | 700 | -300 | -236.82 | 5.14 | 0 | 0 | No
2030-10-02 02:00 | 2030 33% ECP | 700 | 0 | 63.18 | 210 | 0 | 0 | No
2030-10-02 03:00 | 2030 33% ECP | 700 | 300 | 363.18 | 510 | 0 | 0 | No
2030-10-02 04:00 | 2030 33% ECP | 640.61 | 505 | 510 | 510 | 0 | 0 | No
2030-10-02 05:00 | 2030 33% ECP | 700 | 300 | 330.29 | 510 | 0 | 0 | No
2030-10-02 06:00 | 2030 33% ECP | 700 | 0 | 30.29 | 210 | 0 | 0 | No
2030-10-02 07:00 | 2030 33% ECP | 560 | 53.42 | 90 | 510 | 0 | 0 | No
2030-10-02 08:00 | 2030 33% ECP | 140 | -172.05 | -210 | 510 | 0 | 0 | No
2030-10-02 09:00 | 2030 33% ECP | -280 | -472.05 | -510 | 510 | 0 | 0 | No
2030-10-02 10:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-02 11:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-02 12:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-02 13:00 | 2030 33% ECP | -700 | -526 | -510 | 504.3 | 0 | 0 | No
2030-10-02 14:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-02 15:00 | 2030 33% ECP | -700 | -526 | -510 | 224.74 | 0 | 0 | No
2030-10-02 16:00 | 2030 33% ECP | -626.69 | -526 | -510 | 510 | 0 | 0 | No
2030-10-02 17:00 | 2030 33% ECP | -206.69 | -226 | -457.7 | 510 | 0 | 0 | No
2030-10-02 18:00 | 2030 33% ECP | 213.31 | 0 | -157.7 | 340.48 | 0 | 0 | No
2030-10-02 19:00 | 2030 33% ECP | 633.31 | 0 | -143.43 | 329.44 | 0 | 0 | No
2030-10-02 20:00 | 2030 33% ECP | 700 | 0 | 0 | 146.31 | 0 | 0 | No
2030-10-02 21:00 | 2030 33% ECP | 700 | 205 | 300 | 446.31 | 0 | 0 | No
2030-10-02 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-02 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 06:00 | 2030 33% ECP | 281.87 | 205 | 210 | 458.72 | 0 | 0 | No
2030-10-03 07:00 | 2030 33% ECP | 700 | 0 | -90 | 375.5 | 0 | 0 | No
2030-10-03 08:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-10-03 09:00 | 2030 33% ECP | 591.25 | 0 | 0 | 510 | 0 | 0 | No
2030-10-03 10:00 | 2030 33% ECP | 411.82 | 0 | -210 | 432.27 | 0 | 0 | No
2030-10-03 11:00 | 2030 33% ECP | -8.18 | -300 | -510 | 132.27 | 0 | 0 | No
2030-10-03 12:00 | 2030 33% ECP | -414.43 | -526 | -510 | -167.73 | 0 | 0 | No
2030-10-03 13:00 | 2030 33% ECP | -268.28 | -526 | -510 | 21.81 | 0 | 0 | No
2030-10-03 14:00 | 2030 33% ECP | -6.17 | -526 | -510 | 108.67 | 0 | 0 | No
2030-10-03 15:00 | 2030 33% ECP | 115.08 | -300 | -510 | 260.41 | 0 | 0 | No
2030-10-03 16:00 | 2030 33% ECP | 535.08 | 0 | -510 | 0 | 0 | 0 | No
2030-10-03 17:00 | 2030 33% ECP | 700 | 0 | -223.6 | 0 | 0 | 0 | No
2030-10-03 18:00 | 2030 33% ECP | 700 | 0 | -90 | 0 | 0 | 0 | No
2030-10-03 19:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-10-03 20:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-03 22:00 | 2030 33% ECP | 560 | 505 | 510 | 366.82 | 0 | 0 | Yes
2030-10-03 23:00 | 2030 33% ECP | 140 | 505 | 510 | 83.4 | 0 | 0 | Yes
2030-10-04 | 2030 33% ECP | -280 | 505 | 510 | 374.54 | 0 | 0 | Yes
2030-10-04 01:00 | 2030 33% ECP | -700 | 505 | 510 | 74.54 | 0 | 0 | Yes
2030-10-04 02:00 | 2030 33% ECP | -700 | 505 | 510 | 150.38 | 0 | 0 | Yes
2030-10-04 03:00 | 2030 33% ECP | -700 | 505 | 510 | 150.38 | 0 | 0 | Yes
2030-10-04 04:00 | 2030 33% ECP | -700 | 374 | 390 | 176.04 | 0 | 0 | Yes
2030-10-04 05:00 | 2030 33% ECP | -700 | 74 | 90 | 104.46 | 0 | 0 | Yes
2030-10-04 06:00 | 2030 33% ECP | -700 | -226 | -210 | -135.39 | 0 | 0 | Yes
2030-10-04 07:00 | 2030 33% ECP | -700 | -526 | -510 | -435.39 | 0 | 0 | No
2030-10-04 08:00 | 2030 33% ECP | -700 | -526 | -510 | -135.39 | 0 | 0 | No
2030-10-04 09:00 | 2030 33% ECP | -700 | -526 | -510 | 83.9 | 0 | 0 | No
2030-10-04 10:00 | 2030 33% ECP | -700 | -526 | -510 | 210 | 0 | 0 | Yes
2030-10-04 11:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-04 12:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-10-04 13:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-04 14:00 | 2030 33% ECP | -700 | -395.14 | -510 | 510 | 0 | 0 | No
2030-10-04 15:00 | 2030 33% ECP | -432.78 | -526 | -510 | 510 | 0 | 0 | No
2030-10-04 16:00 | 2030 33% ECP | -12.78 | -526 | -510 | 510 | 0 | 0 | No
2030-10-04 17:00 | 2030 33% ECP | 407.22 | -526 | -510 | 510 | 0 | 0 | No
2030-10-04 18:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-04 19:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-04 20:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-04 21:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-04 22:00 | 2030 33% ECP | 700 | -526 | -510 | 407.47 | 0 | 0 | No
2030-10-04 23:00 | 2030 33% ECP | 687.46 | -226 | -318.85 | 454.97 | 0 | 0 | No
2030-10-05 | 2030 33% ECP | 700 | 74 | -18.85 | 510 | 0 | 0 | No
2030-10-05 01:00 | 2030 33% ECP | 700 | 83.67 | 281.15 | 510 | 0 | 0 | No
2030-10-05 02:00 | 2030 33% ECP | 700 | 83.67 | 390 | 510 | 0 | 0 | No
2030-10-05 03:00 | 2030 33% ECP | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-10-05 04:00 | 2030 33% ECP | 700 | -226 | -210 | 343.91 | 0 | 0 | No
2030-10-05 05:00 | 2030 33% ECP | 700 | -526 | -510 | 43.91 | 0 | 0 | No
2030-10-05 06:00 | 2030 33% ECP | 700 | -526 | -510 | 244.07 | 0 | 0 | No
2030-10-05 07:00 | 2030 33% ECP | 700 | -526 | -510 | 68.71 | 0 | 0 | No
2030-10-05 08:00 | 2030 33% ECP | 700 | -526 | -510 | 249.32 | 0 | 0 | No
2030-10-05 09:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-05 10:00 | 2030 33% ECP | 700 | -526 | -510 | 417.42 | 0 | 0 | No
2030-10-05 11:00 | 2030 33% ECP | 700 | -526 | -510 | 274.89 | 0 | 0 | No
2030-10-05 12:00 | 2030 33% ECP | 700 | -526 | -510 | 218.87 | 0 | 0 | No
2030-10-05 13:00 | 2030 33% ECP | 700 | -526 | -510 | -81.13 | 0 | 0 | No
2030-10-05 14:00 | 2030 33% ECP | 700 | -526 | -510 | -168.39 | 0 | 0 | No
2030-10-05 15:00 | 2030 33% ECP | 700 | -226 | -510 | 131.61 | 0 | 0 | No
2030-10-05 16:00 | 2030 33% ECP | 700 | 0 | -510 | 236.24 | 0 | 0 | No
2030-10-05 17:00 | 2030 33% ECP | 700 | 0 | -510 | 322.83 | 0 | 0 | No
2030-10-05 18:00 | 2030 33% ECP | 700 | 0 | -210 | 50.02 | 0 | 0 | No
2030-10-05 19:00 | 2030 33% ECP | 700 | 0 | -510 | 350.02 | 0 | 0 | No
2030-10-05 20:00 | 2030 33% ECP | 700 | 0 | -308.3 | 510 | 0 | 0 | No
2030-10-05 21:00 | 2030 33% ECP | 700 | 0 | -90 | 491.9 | 0 | 0 | No
2030-10-05 22:00 | 2030 33% ECP | 682.44 | 6.47 | 210 | 454.94 | 0 | 0 | No
2030-10-05 23:00 | 2030 33% ECP | 262.44 | 306.47 | 510 | 510 | 0 | 0 | No
2030-10-06 | 2030 33% ECP | -157.56 | 505 | 510 | 510 | 0 | 0 | No
2030-10-06 01:00 | 2030 33% ECP | -444.92 | 505 | 510 | 510 | 0 | 0 | No
2030-10-06 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-06 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-06 04:00 | 2030 33% ECP | -700 | 426.45 | 390 | 510 | 0 | 0 | No
2030-10-06 05:00 | 2030 33% ECP | -408.07 | 126.45 | 90 | 510 | 0 | 0 | No
2030-10-06 06:00 | 2030 33% ECP | 11.93 | -173.55 | -210 | 386.03 | 0 | 0 | No
2030-10-06 07:00 | 2030 33% ECP | 431.93 | -473.55 | -510 | 510 | 0 | 0 | No
2030-10-06 08:00 | 2030 33% ECP | 300.64 | -173.55 | -210 | 477.82 | 0 | 0 | No
2030-10-06 09:00 | 2030 33% ECP | 0 | -304.54 | -510 | 412.09 | 0 | 0 | No
2030-10-06 10:00 | 2030 33% ECP | -280 | -209.44 | -510 | 300.95 | 0 | 0 | No
2030-10-06 11:00 | 2030 33% ECP | -700 | -226 | -421.62 | 222.02 | 0 | 0 | No
2030-10-06 12:00 | 2030 33% ECP | -700 | -526 | -510 | 478 | 0 | 0 | No
2030-10-06 13:00 | 2030 33% ECP | -700 | -526 | -510 | 178 | 0 | 0 | No
2030-10-06 14:00 | 2030 33% ECP | -700 | -226 | -333.82 | 190.22 | 0 | 0 | No
2030-10-06 15:00 | 2030 33% ECP | -700 | -226 | -396.31 | -109.78 | 0 | 0 | No
2030-10-06 16:00 | 2030 33% ECP | -292.26 | -526 | -510 | -409.78 | 0 | 0 | No
2030-10-06 17:00 | 2030 33% ECP | 127.74 | -526 | -510 | -510 | 0 | 0 | No
2030-10-06 18:00 | 2030 33% ECP | 547.74 | -526 | -510 | -510 | 0 | 0 | No
2030-10-06 19:00 | 2030 33% ECP | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-10-06 20:00 | 2030 33% ECP | 700 | 74 | 90 | 90 | 0 | 0 | No
2030-10-06 21:00 | 2030 33% ECP | 596.8 | 374 | 390 | 390 | 0 | 0 | No
2030-10-06 22:00 | 2030 33% ECP | 176.8 | 505 | 510 | 510 | 0 | 0 | No
2030-10-06 23:00 | 2030 33% ECP | 69.97 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 | 2030 33% ECP | 489.97 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 07:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 08:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 09:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 10:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 11:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 12:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 13:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 14:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 15:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 16:00 | 2030 33% ECP | 700 | 300 | 384.9 | 510 | 0 | 0 | No
2030-10-07 17:00 | 2030 33% ECP | 700 | 0 | 84.9 | 510 | 0 | 0 | No
2030-10-07 18:00 | 2030 33% ECP | 700 | 0 | -42.66 | 510 | 0 | 0 | No
2030-10-07 19:00 | 2030 33% ECP | 700 | 0 | -42.66 | 510 | 0 | 0 | No
2030-10-07 20:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-10-07 21:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-10-07 22:00 | 2030 33% ECP | 700 | 0 | 210 | 420.24 | 0 | 0 | No
2030-10-07 23:00 | 2030 33% ECP | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-10-08 | 2030 33% ECP | 700 | 174.99 | 510 | 510 | 0 | 0 | No
2030-10-08 01:00 | 2030 33% ECP | 700 | 440.14 | 510 | 510 | 0 | 0 | No
2030-10-08 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 07:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-10-08 08:00 | 2030 33% ECP | 700 | 0 | -15.99 | 510 | 0 | 0 | No
2030-10-08 09:00 | 2030 33% ECP | 700 | 0 | 115.71 | 367.44 | 0 | 0 | No
2030-10-08 10:00 | 2030 33% ECP | 700 | 300 | 415.71 | 510 | 0 | 0 | No
2030-10-08 11:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 12:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 13:00 | 2030 33% ECP | 700 | 300 | 247.99 | 510 | 0 | 0 | No
2030-10-08 14:00 | 2030 33% ECP | 700 | 0 | -52.01 | 510 | 0 | 0 | No
2030-10-08 15:00 | 2030 33% ECP | 700 | -300 | -352.01 | 210 | 0 | 0 | No
2030-10-08 16:00 | 2030 33% ECP | 700 | 0 | -510 | 415.52 | 0 | 0 | No
2030-10-08 17:00 | 2030 33% ECP | 700 | 0 | -452.49 | 510 | 0 | 0 | No
2030-10-08 18:00 | 2030 33% ECP | 700 | 0 | -384.42 | 510 | 0 | 0 | No
2030-10-08 19:00 | 2030 33% ECP | 700 | 0 | -384.42 | 510 | 0 | 0 | No
2030-10-08 20:00 | 2030 33% ECP | 700 | 0 | -510 | 426.75 | 0 | 0 | No
2030-10-08 21:00 | 2030 33% ECP | 700 | 0 | -510 | 126.75 | 0 | 0 | No
2030-10-08 22:00 | 2030 33% ECP | 700 | -73.34 | -510 | -173.25 | 0 | 0 | No
2030-10-08 23:00 | 2030 33% ECP | 700 | -210.62 | -316.88 | 9.43 | 0 | 0 | No
2030-10-09 | 2030 33% ECP | 700 | 89.38 | -16.88 | 210 | 0 | 0 | No
2030-10-09 01:00 | 2030 33% ECP | 700 | 389.38 | 283.12 | 510 | 0 | 0 | No
2030-10-09 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 04:00 | 2030 33% ECP | 583.11 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 05:00 | 2030 33% ECP | 163.11 | 205 | 210 | 210 | 0 | 0 | No
2030-10-09 06:00 | 2030 33% ECP | 0 | -95 | -90 | -90 | 0 | 0 | No
2030-10-09 07:00 | 2030 33% ECP | 0 | -395 | -390 | -390 | 0 | 0 | No
2030-10-09 08:00 | 2030 33% ECP | 0 | -305.91 | -510 | -135.08 | 0 | 0 | No
2030-10-09 09:00 | 2030 33% ECP | 0 | -5.91 | -210 | 31.07 | 0 | 0 | No
2030-10-09 10:00 | 2030 33% ECP | -420 | 294.09 | 90 | 331.07 | 0 | 0 | No
2030-10-09 11:00 | 2030 33% ECP | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-10-09 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-09 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-09 14:00 | 2030 33% ECP | -700 | 505 | 358.41 | 510 | 0 | 0 | Yes
2030-10-09 15:00 | 2030 33% ECP | -700 | 300 | 58.41 | 510 | 0 | 0 | Yes
2030-10-09 16:00 | 2030 33% ECP | -280 | 0 | -241.59 | 310.02 | 0 | 0 | No
2030-10-09 17:00 | 2030 33% ECP | 140 | 0 | -510 | 310.73 | 0 | 0 | No
2030-10-09 18:00 | 2030 33% ECP | 560 | 0 | -485.81 | 468.93 | 0 | 0 | No
2030-10-09 19:00 | 2030 33% ECP | 700 | 0 | -185.81 | 510 | 0 | 0 | No
2030-10-09 20:00 | 2030 33% ECP | 700 | 87.19 | 114.19 | 510 | 0 | 0 | No
2030-10-09 21:00 | 2030 33% ECP | 700 | 387.19 | 414.19 | 510 | 0 | 0 | No
2030-10-09 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 23:00 | 2030 33% ECP | 692.79 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 05:00 | 2030 33% ECP | 280 | 205 | 210 | 469.37 | 0 | 0 | No
2030-10-10 06:00 | 2030 33% ECP | -140 | -95 | -90 | 169.37 | 0 | 0 | No
2030-10-10 07:00 | 2030 33% ECP | -560 | -395 | -390 | -130.63 | 0 | 0 | No
2030-10-10 08:00 | 2030 33% ECP | -700 | -306.58 | -510 | 0 | 0 | 0 | No
2030-10-10 09:00 | 2030 33% ECP | -694.12 | -6.58 | -210 | 300 | 0 | 0 | No
2030-10-10 10:00 | 2030 33% ECP | -274.12 | 293.42 | 90 | 510 | 0 | 0 | No
2030-10-10 11:00 | 2030 33% ECP | 145.88 | 505 | 390 | 510 | 0 | 0 | No
2030-10-10 12:00 | 2030 33% ECP | 565.88 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 13:00 | 2030 33% ECP | 700 | 300 | 300 | 510 | 0 | 0 | No
2030-10-10 14:00 | 2030 33% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-10-10 15:00 | 2030 33% ECP | 700 | 0 | -210 | 297.99 | 0 | 0 | No
2030-10-10 16:00 | 2030 33% ECP | 519.31 | -300 | -510 | 198.82 | 0 | 0 | No
2030-10-10 17:00 | 2030 33% ECP | 700 | 0 | -215.01 | 257.57 | 0 | 0 | No
2030-10-10 18:00 | 2030 33% ECP | 700 | 0 | -158.3 | 510 | 0 | 0 | No
2030-10-10 19:00 | 2030 33% ECP | 700 | 0 | -275.22 | 510 | 0 | 0 | No
2030-10-10 20:00 | 2030 33% ECP | 700 | 0 | -275.22 | 510 | 0 | 0 | No
2030-10-10 21:00 | 2030 33% ECP | 700 | 0 | 0 | 210 | 0 | 0 | No
2030-10-10 22:00 | 2030 33% ECP | 700 | 205 | 300 | 342.21 | 0 | 0 | No
2030-10-10 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 06:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-10-11 07:00 | 2030 33% ECP | 700 | 0 | 455.09 | 276.79 | 0 | 0 | No
2030-10-11 08:00 | 2030 33% ECP | 700 | 72.6 | 328.65 | 510 | 0 | 0 | No
2030-10-11 09:00 | 2030 33% ECP | 700 | 0 | 28.65 | 390.52 | 0 | 0 | No
2030-10-11 10:00 | 2030 33% ECP | 283.05 | 0 | -210 | 285.16 | 0 | 0 | No
2030-10-11 11:00 | 2030 33% ECP | 29.28 | -300 | -510 | 204.25 | 0 | 0 | No
2030-10-11 12:00 | 2030 33% ECP | 37.19 | -526 | -510 | 264.86 | 0 | 0 | No
2030-10-11 13:00 | 2030 33% ECP | 336.28 | -526 | -510 | 267.32 | 0 | 0 | No
2030-10-11 14:00 | 2030 33% ECP | 488.31 | -526 | -510 | 210.33 | 0 | 0 | No
2030-10-11 15:00 | 2030 33% ECP | 700 | -300 | -253.03 | 286.39 | 0 | 0 | No
2030-10-11 16:00 | 2030 33% ECP | 700 | 0 | 46.97 | 510 | 0 | 0 | No
2030-10-11 17:00 | 2030 33% ECP | 700 | 258.01 | 90 | 498.83 | 0 | 0 | No
2030-10-11 18:00 | 2030 33% ECP | 700 | -41.99 | -210 | 198.83 | 0 | 0 | No
2030-10-11 19:00 | 2030 33% ECP | 700 | -341.99 | -510 | -101.17 | 0 | 0 | No
2030-10-11 20:00 | 2030 33% ECP | 700 | -41.99 | -210 | 198.83 | 0 | 0 | No
2030-10-11 21:00 | 2030 33% ECP | 700 | 258.01 | 90 | 498.83 | 0 | 0 | No
2030-10-11 22:00 | 2030 33% ECP | 700 | 0 | 91.82 | 198.83 | 0 | 0 | No
2030-10-11 23:00 | 2030 33% ECP | 700 | 0 | -195.6 | 81.61 | 0 | 0 | No
2030-10-12 | 2030 33% ECP | 700 | -45.53 | -495.6 | -39.08 | 0 | 0 | No
2030-10-12 01:00 | 2030 33% ECP | 700 | -219.92 | -510 | 8.78 | 0 | 0 | No
2030-10-12 02:00 | 2030 33% ECP | 700 | -106.6 | -510 | -111.2 | 0 | 0 | No
2030-10-12 03:00 | 2030 33% ECP | 700 | -351.55 | -510 | -100.58 | 0 | 0 | No
2030-10-12 04:00 | 2030 33% ECP | 280 | -526 | -510 | -178.43 | 0 | 0 | No
2030-10-12 05:00 | 2030 33% ECP | -140 | -526 | -510 | -128.23 | 0 | 0 | No
2030-10-12 06:00 | 2030 33% ECP | -316.88 | -526 | -510 | -30.73 | 0 | 0 | No
2030-10-12 07:00 | 2030 33% ECP | -421.84 | -526 | -510 | -330.73 | 0 | 0 | No
2030-10-12 08:00 | 2030 33% ECP | -598.65 | -526 | -510 | -442.16 | 0 | 0 | No
2030-10-12 09:00 | 2030 33% ECP | -700 | -526 | -510 | -410.2 | 0 | 0 | No
2030-10-12 10:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 11:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 12:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 13:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 14:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 15:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 16:00 | 2030 33% ECP | -700 | -526 | -510 | -360.26 | 0 | 0 | No
2030-10-12 17:00 | 2030 33% ECP | -560 | -526 | -510 | -60.26 | 0 | 0 | No
2030-10-12 18:00 | 2030 33% ECP | -140 | -526 | -510 | 239.74 | 0 | 0 | No
2030-10-12 19:00 | 2030 33% ECP | 280 | -526 | -510 | 510 | 0 | 0 | No
2030-10-12 20:00 | 2030 33% ECP | 700 | -300 | -300 | 316.47 | 0 | 0 | No
2030-10-12 21:00 | 2030 33% ECP | 700 | 0 | 0 | 316.47 | 0 | 0 | No
2030-10-12 22:00 | 2030 33% ECP | 700 | 300 | 300 | 510 | 0 | 0 | No
2030-10-12 23:00 | 2030 33% ECP | 700 | 147.22 | 510 | 510 | 0 | 0 | No
2030-10-13 | 2030 33% ECP | 700 | 447.22 | 510 | 510 | 0 | 0 | No
2030-10-13 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 05:00 | 2030 33% ECP | 700 | 300 | 252.1 | 510 | 0 | 0 | No
2030-10-13 06:00 | 2030 33% ECP | 700 | 0 | -47.9 | 436.06 | 0 | 0 | No
2030-10-13 07:00 | 2030 33% ECP | 700 | 0 | -292.76 | 136.06 | 0 | 0 | No
2030-10-13 08:00 | 2030 33% ECP | 280 | -194.2 | -510 | -163.94 | 0 | 0 | No
2030-10-13 09:00 | 2030 33% ECP | -140 | 0 | -390 | -180.23 | 0 | 0 | No
2030-10-13 10:00 | 2030 33% ECP | -560 | 300 | -90 | 119.77 | 0 | 0 | Yes
2030-10-13 11:00 | 2030 33% ECP | -700 | 505 | 210 | 419.77 | 0 | 0 | Yes
2030-10-13 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-13 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-13 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-13 15:00 | 2030 33% ECP | -679.7 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 16:00 | 2030 33% ECP | -259.7 | 505 | 510 | 510 | 0 | 0 | No
2030-10-13 17:00 | 2030 33% ECP | 160.3 | 205 | 210 | 210 | 0 | 0 | No
2030-10-13 18:00 | 2030 33% ECP | 5.99 | 0 | -84.27 | 0 | 0 | 0 | No
2030-10-13 19:00 | 2030 33% ECP | 425.99 | 300 | 215.73 | 300 | 0 | 0 | No
2030-10-13 20:00 | 2030 33% ECP | 700 | 505 | 510 | 267.17 | 0 | 0 | Yes
2030-10-13 21:00 | 2030 33% ECP | 700 | 505 | 510 | 270.88 | 0 | 0 | Yes
2030-10-13 22:00 | 2030 33% ECP | 700 | 505 | 510 | 427.15 | 0 | 0 | Yes
2030-10-13 23:00 | 2030 33% ECP | 363.34 | 505 | 510 | 471.06 | 0 | 0 | Yes
2030-10-14 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-14 02:00 | 2030 33% ECP | 700 | 505 | 510 | 370.67 | 0 | 0 | Yes
2030-10-14 03:00 | 2030 33% ECP | 700 | 505 | 510 | 170.91 | 0 | 0 | Yes
2030-10-14 04:00 | 2030 33% ECP | 700 | 505 | 510 | 373.67 | 0 | 0 | Yes
2030-10-14 05:00 | 2030 33% ECP | 700 | 505 | 510 | 495.4 | 0 | 0 | Yes
2030-10-14 06:00 | 2030 33% ECP | 700 | 505 | 510 | 195.4 | 0 | 0 | Yes
2030-10-14 07:00 | 2030 33% ECP | 700 | 505 | 510 | 207.29 | 0 | 0 | No
2030-10-14 08:00 | 2030 33% ECP | 700 | 505 | 510 | 507.29 | 0 | 0 | No
2030-10-14 09:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 10:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 11:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 12:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 13:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 14:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 15:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 16:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-10-14 17:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-10-14 18:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-10-14 19:00 | 2030 33% ECP | 700 | 0 | 455.11 | 0 | 0 | 0 | No
2030-10-14 20:00 | 2030 33% ECP | 700 | 205 | 455.11 | 210 | 0 | 0 | No
2030-10-14 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 | 2030 33% ECP | 700 | 254.77 | 510 | 510 | 0 | 0 | No
2030-10-15 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 04:00 | 2030 33% ECP | 700 | 205 | 428.64 | 210 | 0 | 0 | No
2030-10-15 05:00 | 2030 33% ECP | 700 | 0 | 449.22 | 0 | 0 | 0 | No
2030-10-15 06:00 | 2030 33% ECP | 700 | 0 | 510 | 300 | 0 | 0 | No
2030-10-15 07:00 | 2030 33% ECP | 700 | 229.56 | 510 | 510 | 0 | 0 | No
2030-10-15 08:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 09:00 | 2030 33% ECP | 700 | 300 | 313.38 | 510 | 0 | 0 | No
2030-10-15 10:00 | 2030 33% ECP | 700 | 0 | 13.38 | 382.65 | 0 | 0 | No
2030-10-15 11:00 | 2030 33% ECP | 700 | 0 | -286.62 | 368.04 | 0 | 0 | No
2030-10-15 12:00 | 2030 33% ECP | 700 | 0 | -400.84 | 359.51 | 0 | 0 | No
2030-10-15 13:00 | 2030 33% ECP | 700 | 0 | -100.84 | 292.9 | 0 | 0 | No
2030-10-15 14:00 | 2030 33% ECP | 700 | 0 | 0 | 300.92 | 0 | 0 | No
2030-10-15 15:00 | 2030 33% ECP | 700 | 0 | 0 | 318.47 | 0 | 0 | No
2030-10-15 16:00 | 2030 33% ECP | 700 | 0 | 205.75 | 445.69 | 0 | 0 | No
2030-10-15 17:00 | 2030 33% ECP | 700 | 0 | -94.25 | 145.69 | 0 | 0 | No
2030-10-15 18:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-15 19:00 | 2030 33% ECP | 700 | 300 | 300 | 300 | 0 | 0 | No
2030-10-15 20:00 | 2030 33% ECP | 700 | 474.94 | 510 | 510 | 0 | 0 | No
2030-10-15 21:00 | 2030 33% ECP | 700 | 194.03 | 510 | 510 | 0 | 0 | No
2030-10-15 22:00 | 2030 33% ECP | 700 | 102.94 | 510 | 510 | 0 | 0 | No
2030-10-15 23:00 | 2030 33% ECP | 700 | 0 | 510 | 335.81 | 0 | 0 | No
2030-10-16 | 2030 33% ECP | 700 | 0 | 210 | 35.81 | 0 | 0 | No
2030-10-16 01:00 | 2030 33% ECP | 700 | 0 | 99.81 | 0 | 0 | 0 | No
2030-10-16 02:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-16 03:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-16 04:00 | 2030 33% ECP | 700 | 0 | -80.86 | 0 | 0 | 0 | No
2030-10-16 05:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-16 06:00 | 2030 33% ECP | 700 | 0 | -100.86 | 0 | 0 | 0 | No
2030-10-16 07:00 | 2030 33% ECP | 700 | 0 | -68.85 | 0 | 0 | 0 | No
2030-10-16 08:00 | 2030 33% ECP | 700 | 0 | 231.15 | 0 | 0 | 0 | No
2030-10-16 09:00 | 2030 33% ECP | 700 | 0 | -55.83 | 0 | 0 | 0 | No
2030-10-16 10:00 | 2030 33% ECP | 700 | 0 | -253.52 | 0 | 0 | 0 | No
2030-10-16 11:00 | 2030 33% ECP | 420 | 0 | -323.4 | 0 | 0 | 0 | No
2030-10-16 12:00 | 2030 33% ECP | 0 | 0 | -23.4 | 0 | 0 | 0 | No
2030-10-16 13:00 | 2030 33% ECP | -420 | 0 | -269.53 | 0 | 0 | 0 | No
2030-10-16 14:00 | 2030 33% ECP | -140 | 0 | -510 | 0 | 0 | 0 | No
2030-10-16 15:00 | 2030 33% ECP | 280 | -226 | -390.72 | 0 | 0 | 0 | No
2030-10-16 16:00 | 2030 33% ECP | 700 | -526 | -510 | -300 | 0 | 0 | No
2030-10-16 17:00 | 2030 33% ECP | 700 | -526 | -510 | -399.88 | 0 | 0 | No
2030-10-16 18:00 | 2030 33% ECP | 280 | -526 | -510 | -325.66 | 0 | 0 | No
2030-10-16 19:00 | 2030 33% ECP | 700 | -300 | -334.63 | -25.66 | 0 | 0 | No
2030-10-16 20:00 | 2030 33% ECP | 700 | 0 | -34.63 | 274.34 | 0 | 0 | No
2030-10-16 21:00 | 2030 33% ECP | 700 | 0 | 134.1 | 0 | 0 | 0 | No
2030-10-16 22:00 | 2030 33% ECP | 700 | 0 | -8.29 | 0 | 0 | 0 | No
2030-10-16 23:00 | 2030 33% ECP | 700 | -154.1 | -308.29 | -300 | 0 | 0 | No
2030-10-17 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 01:00 | 2030 33% ECP | 700 | 0 | -510 | -121.79 | 0 | 0 | No
2030-10-17 02:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 03:00 | 2030 33% ECP | 700 | 0 | -510 | -143.38 | 0 | 0 | No
2030-10-17 04:00 | 2030 33% ECP | 700 | 0 | -510 | -319.97 | 0 | 0 | No
2030-10-17 05:00 | 2030 33% ECP | 700 | 0 | -510 | -19.97 | 0 | 0 | No
2030-10-17 06:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 07:00 | 2030 33% ECP | 700 | 0 | -300 | -92.02 | 0 | 0 | No
2030-10-17 08:00 | 2030 33% ECP | 700 | 0 | 0 | 13.04 | 0 | 0 | No
2030-10-17 09:00 | 2030 33% ECP | 700 | 0 | -300 | 0 | 0 | 0 | No
2030-10-17 10:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 11:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 12:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 13:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 14:00 | 2030 33% ECP | 700 | 0 | -510 | -147.54 | 0 | 0 | No
2030-10-17 15:00 | 2030 33% ECP | 700 | -116.76 | -510 | -156.82 | 0 | 0 | No
2030-10-17 16:00 | 2030 33% ECP | 700 | -416.76 | -510 | -285.94 | 0 | 0 | No
2030-10-17 17:00 | 2030 33% ECP | 581.51 | -526 | -510 | -510 | 0 | 0 | No
2030-10-17 18:00 | 2030 33% ECP | 280 | -526 | -510 | -406.13 | 0 | 0 | No
2030-10-17 19:00 | 2030 33% ECP | 700 | -226 | -210 | -106.13 | 0 | 0 | No
2030-10-17 20:00 | 2030 33% ECP | 700 | 74 | 90 | 193.87 | 0 | 0 | No
2030-10-17 21:00 | 2030 33% ECP | 700 | 0 | 376.54 | 177.35 | 0 | 0 | No
2030-10-17 22:00 | 2030 33% ECP | 700 | 0 | 76.54 | 0 | 0 | 0 | No
2030-10-17 23:00 | 2030 33% ECP | 700 | 0 | -223.46 | -167.47 | 0 | 0 | No
2030-10-18 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-18 01:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-18 02:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-18 03:00 | 2030 33% ECP | 700 | 0 | -253.82 | 0 | 0 | 0 | No
2030-10-18 04:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-18 05:00 | 2030 33% ECP | 700 | 0 | -300 | 0 | 0 | 0 | No
2030-10-18 06:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-10-18 07:00 | 2030 33% ECP | 700 | -61.61 | -210 | 0 | 0 | 0 | No
2030-10-18 08:00 | 2030 33% ECP | 700 | -361.61 | -510 | -300 | 0 | 0 | No
2030-10-18 09:00 | 2030 33% ECP | 700 | -403.59 | -510 | -19.77 | 0 | 0 | No
2030-10-18 10:00 | 2030 33% ECP | 700 | -103.59 | -493.17 | 61.83 | 0 | 0 | No
2030-10-18 11:00 | 2030 33% ECP | 700 | 0 | -510 | 28.43 | 0 | 0 | No
2030-10-18 12:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-18 13:00 | 2030 33% ECP | 700 | 0 | -510 | 16 | 0 | 0 | No
2030-10-18 14:00 | 2030 33% ECP | 700 | 0 | -307.36 | 0 | 0 | 0 | No
2030-10-18 15:00 | 2030 33% ECP | 700 | -115.17 | -510 | 0 | 0 | 0 | No
2030-10-18 16:00 | 2030 33% ECP | 700 | -415.17 | -510 | -300 | 0 | 0 | No
2030-10-18 17:00 | 2030 33% ECP | 342.71 | -466.73 | -510 | -357.32 | 0 | 0 | No
2030-10-18 18:00 | 2030 33% ECP | 280 | -191.43 | -510 | -57.32 | 0 | 0 | No
2030-10-18 19:00 | 2030 33% ECP | 700 | 0 | -510 | -292.02 | 0 | 0 | No
2030-10-18 20:00 | 2030 33% ECP | 700 | -300 | -510 | -257.98 | 0 | 0 | No
2030-10-18 21:00 | 2030 33% ECP | 700 | 0 | -306.28 | 0 | 0 | 0 | No
2030-10-18 22:00 | 2030 33% ECP | 700 | -226 | -510 | -77.33 | 0 | 0 | No
2030-10-18 23:00 | 2030 33% ECP | 554.37 | -526 | -510 | -5.47 | 0 | 0 | No
2030-10-19 | 2030 33% ECP | 700 | -526 | -510 | 15.04 | 0 | 0 | No
2030-10-19 01:00 | 2030 33% ECP | 700 | -226 | -230.55 | 108.01 | 0 | 0 | No
2030-10-19 02:00 | 2030 33% ECP | 700 | 74 | 69.45 | 408.01 | 0 | 0 | No
2030-10-19 03:00 | 2030 33% ECP | 609.28 | 374 | 369.45 | 510 | 0 | 0 | No
2030-10-19 04:00 | 2030 33% ECP | 189.28 | 300 | 90 | 210 | 0 | 0 | No
2030-10-19 05:00 | 2030 33% ECP | -230.72 | 0 | -210 | -90 | 0 | 0 | No
2030-10-19 06:00 | 2030 33% ECP | -650.72 | -300 | -510 | -390 | 0 | 0 | No
2030-10-19 07:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-19 08:00 | 2030 33% ECP | -700 | -517.19 | -510 | -446.27 | 0 | 0 | No
2030-10-19 09:00 | 2030 33% ECP | -280 | -217.19 | -210 | -146.27 | 0 | 0 | No
2030-10-19 10:00 | 2030 33% ECP | -700 | 82.81 | 90 | 153.73 | 0 | 0 | No
2030-10-19 11:00 | 2030 33% ECP | -700 | 382.81 | 390 | 453.73 | 0 | 0 | No
2030-10-19 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-19 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-19 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-19 15:00 | 2030 33% ECP | -420 | 300 | 371.29 | 300 | 0 | 0 | No
2030-10-19 16:00 | 2030 33% ECP | 0 | 0 | 71.29 | 0 | 0 | 0 | No
2030-10-19 17:00 | 2030 33% ECP | 420 | 0 | 0 | 0 | 0 | 0 | No
2030-10-19 18:00 | 2030 33% ECP | 250.87 | 0 | 210 | 26.97 | 0 | 0 | No
2030-10-19 19:00 | 2030 33% ECP | -169.13 | 300 | 510 | 326.97 | 0 | 0 | No
2030-10-19 20:00 | 2030 33% ECP | -589.13 | 505 | 510 | 510 | 0 | 0 | No
2030-10-19 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-19 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-19 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 01:00 | 2030 33% ECP | -700 | 505 | 510 | 362.83 | 0 | 0 | Yes
2030-10-20 02:00 | 2030 33% ECP | -700 | 505 | 510 | 475.19 | 0 | 0 | Yes
2030-10-20 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 15:00 | 2030 33% ECP | -700 | 505 | 509.67 | 258.54 | 0 | 0 | Yes
2030-10-20 16:00 | 2030 33% ECP | -700 | 205 | 209.67 | -41.46 | 0 | 0 | Yes
2030-10-20 17:00 | 2030 33% ECP | -700 | -95 | -90.33 | -341.46 | 0 | 0 | No
2030-10-20 18:00 | 2030 33% ECP | -700 | 205 | 209.67 | -41.46 | 0 | 0 | No
2030-10-20 19:00 | 2030 33% ECP | -700 | 505 | 509.67 | 258.54 | 0 | 0 | No
2030-10-20 20:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 21:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 22:00 | 2030 33% ECP | 0 | 505 | 510 | 443.12 | 0 | 0 | Yes
2030-10-20 23:00 | 2030 33% ECP | 0 | 505 | 510 | 408.03 | 0 | 0 | Yes
2030-10-21 | 2030 33% ECP | 420 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 07:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 08:00 | 2030 33% ECP | 700 | 205 | 210 | 346.91 | 0 | 0 | No
2030-10-21 09:00 | 2030 33% ECP | 700 | -95 | -90 | 510 | 0 | 0 | No
2030-10-21 10:00 | 2030 33% ECP | 700 | -395 | -390 | 454.72 | 0 | 0 | No
2030-10-21 11:00 | 2030 33% ECP | 700 | -526 | -510 | 447.98 | 0 | 0 | No
2030-10-21 12:00 | 2030 33% ECP | 700 | -526 | -510 | 276.28 | 0 | 0 | No
2030-10-21 13:00 | 2030 33% ECP | 700 | -526 | -510 | 90 | 0 | 0 | No
2030-10-21 14:00 | 2030 33% ECP | 700 | -526 | -510 | -210 | 0 | 0 | No
2030-10-21 15:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-21 16:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-21 17:00 | 2030 33% ECP | 700 | -526 | -510 | -412.02 | 0 | 0 | No
2030-10-21 18:00 | 2030 33% ECP | 700 | -395 | -409.13 | -382.53 | 0 | 0 | No
2030-10-21 19:00 | 2030 33% ECP | 700 | -95 | -109.13 | -463.04 | 0 | 0 | No
2030-10-21 20:00 | 2030 33% ECP | 700 | 205 | 190.87 | -463.04 | 0 | 0 | No
2030-10-21 21:00 | 2030 33% ECP | 700 | 505 | 490.87 | -163.04 | 0 | 0 | No
2030-10-21 22:00 | 2030 33% ECP | 700 | 505 | 510 | 136.96 | 0 | 0 | Yes
2030-10-21 23:00 | 2030 33% ECP | 663.46 | 505 | 510 | 27.26 | 0 | 0 | Yes
2030-10-22 | 2030 33% ECP | 700 | 505 | 510 | 86.29 | 0 | 0 | Yes
2030-10-22 01:00 | 2030 33% ECP | 700 | 505 | 510 | 105.24 | 0 | 0 | Yes
2030-10-22 02:00 | 2030 33% ECP | 700 | 505 | 510 | 322.24 | 0 | 0 | Yes
2030-10-22 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-22 04:00 | 2030 33% ECP | 700 | 505 | 510 | 286.05 | 0 | 0 | Yes
2030-10-22 05:00 | 2030 33% ECP | 700 | 505 | 510 | 313.86 | 0 | 0 | Yes
2030-10-22 06:00 | 2030 33% ECP | 280 | 205 | 293.33 | 13.86 | 0 | 0 | No
2030-10-22 07:00 | 2030 33% ECP | 700 | 0 | -6.67 | -106.76 | 0 | 0 | No
2030-10-22 08:00 | 2030 33% ECP | 700 | 0 | 293.33 | 4.38 | 0 | 0 | No
2030-10-22 09:00 | 2030 33% ECP | 700 | 0 | 73.6 | 304.38 | 0 | 0 | No
2030-10-22 10:00 | 2030 33% ECP | 280 | -105.87 | -226.4 | 4.38 | 0 | 0 | No
2030-10-22 11:00 | 2030 33% ECP | 0 | -307.93 | -510 | 61.95 | 0 | 0 | No
2030-10-22 12:00 | 2030 33% ECP | 0 | -491.59 | -510 | -95.81 | 0 | 0 | No
2030-10-22 13:00 | 2030 33% ECP | -41.97 | -305.7 | -510 | -16.13 | 0 | 0 | No
2030-10-22 14:00 | 2030 33% ECP | 76.3 | -5.7 | -510 | -27.66 | 0 | 0 | No
2030-10-22 15:00 | 2030 33% ECP | 496.3 | 0 | -510 | 173.55 | 0 | 0 | No
2030-10-22 16:00 | 2030 33% ECP | 428.62 | -226 | -210 | 398.22 | 0 | 0 | No
2030-10-22 17:00 | 2030 33% ECP | 8.62 | -526 | -510 | 177.6 | 0 | 0 | No
2030-10-22 18:00 | 2030 33% ECP | -411.38 | -526 | -510 | 0 | 0 | 0 | No
2030-10-22 19:00 | 2030 33% ECP | 8.62 | -526 | -510 | -21.94 | 0 | 0 | No
2030-10-22 20:00 | 2030 33% ECP | 428.62 | -526 | -510 | 0 | 0 | 0 | No
2030-10-22 21:00 | 2030 33% ECP | 182.36 | -365.37 | -510 | 96.58 | 0 | 0 | No
2030-10-22 22:00 | 2030 33% ECP | -237.64 | -526 | -510 | 16.39 | 0 | 0 | No
2030-10-22 23:00 | 2030 33% ECP | 182.36 | -526 | -510 | -80.69 | 0 | 0 | No
2030-10-23 | 2030 33% ECP | 280 | -526 | -510 | -363.55 | 0 | 0 | No
2030-10-23 01:00 | 2030 33% ECP | 700 | -526 | -510 | -161.14 | 0 | 0 | No
2030-10-23 02:00 | 2030 33% ECP | 700 | -300 | -510 | -34.14 | 0 | 0 | No
2030-10-23 03:00 | 2030 33% ECP | 700 | 0 | -210 | 265.86 | 0 | 0 | No
2030-10-23 04:00 | 2030 33% ECP | 700 | 300 | 90 | 510 | 0 | 0 | No
2030-10-23 05:00 | 2030 33% ECP | 280 | 0 | -210 | 210 | 0 | 0 | No
2030-10-23 06:00 | 2030 33% ECP | 700 | 0 | -510 | 266.73 | 0 | 0 | No
2030-10-23 07:00 | 2030 33% ECP | 700 | 0 | -510 | 355.84 | 0 | 0 | No
2030-10-23 08:00 | 2030 33% ECP | 700 | 0 | -510 | 497.79 | 0 | 0 | No
2030-10-23 09:00 | 2030 33% ECP | 425.46 | 0 | -510 | 375.54 | 0 | 0 | No
2030-10-23 10:00 | 2030 33% ECP | 5.46 | -226.94 | -510 | 510 | 0 | 0 | No
2030-10-23 11:00 | 2030 33% ECP | -280 | -492.74 | -510 | 344.53 | 0 | 0 | No
2030-10-23 12:00 | 2030 33% ECP | -700 | -526 | -510 | 44.53 | 0 | 0 | No
2030-10-23 13:00 | 2030 33% ECP | -700 | -526 | -510 | -255.47 | 0 | 0 | No
2030-10-23 14:00 | 2030 33% ECP | -455.28 | -526 | -510 | -99.51 | 0 | 0 | No
2030-10-23 15:00 | 2030 33% ECP | -35.28 | -226 | -510 | 153.81 | 0 | 0 | No
2030-10-23 16:00 | 2030 33% ECP | 384.72 | 0 | -510 | 382.01 | 0 | 0 | No
2030-10-23 17:00 | 2030 33% ECP | 700 | 0 | -510 | 377.26 | 0 | 0 | No
2030-10-23 18:00 | 2030 33% ECP | 530.75 | -204.82 | -510 | 441.2 | 0 | 0 | No
2030-10-23 19:00 | 2030 33% ECP | 110.75 | -504.82 | -510 | 391.77 | 0 | 0 | No
2030-10-23 20:00 | 2030 33% ECP | -309.25 | -526 | -510 | 285.18 | 0 | 0 | No
2030-10-23 21:00 | 2030 33% ECP | -5.32 | -526 | -510 | -0.42 | 0 | 0 | No
2030-10-23 22:00 | 2030 33% ECP | -425.32 | -368.81 | -390 | -300.42 | 0 | 0 | Yes
2030-10-23 23:00 | 2030 33% ECP | -700 | -68.81 | -90 | -0.42 | 0 | 0 | Yes
2030-10-24 | 2030 33% ECP | -700 | 231.19 | 210 | 299.58 | 0 | 0 | Yes
2030-10-24 01:00 | 2030 33% ECP | -700 | 505 | 510 | 418.04 | 0 | 0 | Yes
2030-10-24 02:00 | 2030 33% ECP | -700 | 505 | 510 | 162.41 | 0 | 0 | Yes
2030-10-24 03:00 | 2030 33% ECP | -700 | 505 | 510 | 359.17 | 0 | 0 | Yes
2030-10-24 04:00 | 2030 33% ECP | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-10-24 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-24 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-24 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-24 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 15:00 | 2030 33% ECP | -280 | 458 | 390 | 510 | 0 | 0 | Yes
2030-10-24 16:00 | 2030 33% ECP | 140 | 158 | 90 | 510 | 0 | 0 | No
2030-10-24 17:00 | 2030 33% ECP | 560 | -142 | -210 | 286.69 | 0 | 0 | No
2030-10-24 18:00 | 2030 33% ECP | 700 | -442 | -510 | 510 | 0 | 0 | No
2030-10-24 19:00 | 2030 33% ECP | 560 | -300 | -505.41 | 210 | 0 | 0 | No
2030-10-24 20:00 | 2030 33% ECP | 140 | 0 | -205.41 | 510 | 0 | 0 | No
2030-10-24 21:00 | 2030 33% ECP | -280 | 300 | 94.59 | 510 | 0 | 0 | Yes
2030-10-24 22:00 | 2030 33% ECP | -700 | 505 | 394.59 | 319.3 | 0 | 0 | Yes
2030-10-24 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 07:00 | 2030 33% ECP | -700 | 300 | 510 | 328.68 | 0 | 0 | Yes
2030-10-25 08:00 | 2030 33% ECP | -700 | 0 | 210 | 28.68 | 0 | 0 | No
2030-10-25 09:00 | 2030 33% ECP | -700 | 300 | 510 | 328.68 | 0 | 0 | No
2030-10-25 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 14:00 | 2030 33% ECP | -700 | 416.78 | 390 | 390 | 0 | 0 | Yes
2030-10-25 15:00 | 2030 33% ECP | -420 | 116.78 | 90 | 90 | 0 | 0 | No
2030-10-25 16:00 | 2030 33% ECP | 0 | -183.22 | -210 | -210 | 0 | 0 | No
2030-10-25 17:00 | 2030 33% ECP | -420 | -483.22 | -510 | -510 | 0 | 0 | No
2030-10-25 18:00 | 2030 33% ECP | 0 | -257.68 | -210 | -210 | 0 | 0 | No
2030-10-25 19:00 | 2030 33% ECP | 420 | 42.32 | 90 | 90 | 0 | 0 | No
2030-10-25 20:00 | 2030 33% ECP | 0 | 342.32 | 390 | 390 | 0 | 0 | No
2030-10-25 21:00 | 2030 33% ECP | -420 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 04:00 | 2030 33% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-10-26 05:00 | 2030 33% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-10-26 06:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-10-26 07:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-26 08:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-26 09:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-26 10:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-10-26 11:00 | 2030 33% ECP | -700 | 0 | -82.88 | 0 | 0 | 0 | Yes
2030-10-26 12:00 | 2030 33% ECP | -700 | 300 | 217.12 | 300 | 0 | 0 | Yes
2030-10-26 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 14:00 | 2030 33% ECP | -700 | 505 | 417.13 | 510 | 0 | 0 | Yes
2030-10-26 15:00 | 2030 33% ECP | -420 | 300 | 117.13 | 210 | 0 | 0 | Yes
2030-10-26 16:00 | 2030 33% ECP | 0 | 0 | -182.87 | -90 | 0 | 0 | No
2030-10-26 17:00 | 2030 33% ECP | 420 | 0 | -449.38 | 24.65 | 0 | 0 | No
2030-10-26 18:00 | 2030 33% ECP | 700 | 0 | -460.69 | 142.68 | 0 | 0 | No
2030-10-26 19:00 | 2030 33% ECP | 700 | 0 | -251.45 | 89.13 | 0 | 0 | No
2030-10-26 20:00 | 2030 33% ECP | 700 | 0 | 48.55 | 360.23 | 0 | 0 | No
2030-10-26 21:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-10-26 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-26 23:00 | 2030 33% ECP | 616.52 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 | 2030 33% ECP | 196.52 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 01:00 | 2030 33% ECP | -223.48 | 205 | 414.68 | 510 | 0 | 0 | No
2030-10-27 02:00 | 2030 33% ECP | -643.48 | 0 | 403.72 | 510 | 0 | 0 | No
2030-10-27 03:00 | 2030 33% ECP | -546.39 | 0 | 202.37 | 510 | 0 | 0 | No
2030-10-27 04:00 | 2030 33% ECP | -608.78 | 0 | 29.25 | 432.53 | 0 | 0 | No
2030-10-27 05:00 | 2030 33% ECP | -188.78 | 0 | -83.56 | 307.37 | 0 | 0 | No
2030-10-27 06:00 | 2030 33% ECP | -140 | -300 | -383.56 | 256.77 | 0 | 0 | No
2030-10-27 07:00 | 2030 33% ECP | 280 | 0 | -83.56 | 449.66 | 0 | 0 | No
2030-10-27 08:00 | 2030 33% ECP | 700 | 0 | 76.9 | 149.66 | 0 | 0 | No
2030-10-27 09:00 | 2030 33% ECP | 400.15 | 0 | 90 | 348.84 | 0 | 0 | No
2030-10-27 10:00 | 2030 33% ECP | -19.85 | -226 | -210 | 510 | 0 | 0 | No
2030-10-27 11:00 | 2030 33% ECP | -439.85 | -526 | -510 | 356.2 | 0 | 0 | No
2030-10-27 12:00 | 2030 33% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-10-27 13:00 | 2030 33% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-10-27 14:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-10-27 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-27 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-27 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 20:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 21:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-27 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 14:00 | 2030 33% ECP | -700 | 505 | 428.18 | 510 | 0 | 0 | Yes
2030-10-28 15:00 | 2030 33% ECP | -700 | 205 | 128.18 | 510 | 0 | 0 | Yes
2030-10-28 16:00 | 2030 33% ECP | -700 | -95 | -171.82 | 422.6 | 0 | 0 | No
2030-10-28 17:00 | 2030 33% ECP | -280 | -395 | -471.82 | 122.6 | 0 | 0 | No
2030-10-28 18:00 | 2030 33% ECP | 0 | -95 | -171.82 | 0 | 0 | 0 | No
2030-10-28 19:00 | 2030 33% ECP | -280 | 205 | 128.18 | 300 | 0 | 0 | No
2030-10-28 20:00 | 2030 33% ECP | -700 | 505 | 428.18 | 510 | 0 | 0 | No
2030-10-28 21:00 | 2030 33% ECP | -533.68 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-28 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 01:00 | 2030 33% ECP | -273.42 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 02:00 | 2030 33% ECP | -693.42 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 05:00 | 2030 33% ECP | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-10-29 06:00 | 2030 33% ECP | -700 | -95 | -90 | 510 | 0 | 0 | No
2030-10-29 07:00 | 2030 33% ECP | -700 | -395 | -390 | 300 | 0 | 0 | No
2030-10-29 08:00 | 2030 33% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-10-29 09:00 | 2030 33% ECP | -700 | -526 | -510 | 215.45 | 0 | 0 | No
2030-10-29 10:00 | 2030 33% ECP | -700 | -226 | -210 | 465.31 | 0 | 0 | No
2030-10-29 11:00 | 2030 33% ECP | -700 | 74 | 90 | 277.87 | 0 | 0 | No
2030-10-29 12:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-10-29 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 15:00 | 2030 33% ECP | -700 | 292.67 | 210 | 245.65 | 0 | 0 | No
2030-10-29 16:00 | 2030 33% ECP | -700 | -7.33 | -90 | -54.35 | 0 | 0 | No
2030-10-29 17:00 | 2030 33% ECP | -700 | -307.33 | -390 | -354.35 | 0 | 0 | No
2030-10-29 18:00 | 2030 33% ECP | -700 | -453.76 | -510 | -510 | 0 | 0 | No
2030-10-29 19:00 | 2030 33% ECP | -700 | -153.76 | -210 | -210 | 0 | 0 | No
2030-10-29 20:00 | 2030 33% ECP | -700 | 146.24 | 90 | 90 | 0 | 0 | No
2030-10-29 21:00 | 2030 33% ECP | -700 | 446.24 | 390 | 390 | 0 | 0 | Yes
2030-10-29 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-29 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-30 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 01:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 02:00 | 2030 33% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 05:00 | 2030 33% ECP | 297.77 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 06:00 | 2030 33% ECP | -122.23 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 07:00 | 2030 33% ECP | 208.45 | 205 | 210 | 210 | 0 | 0 | No
2030-10-30 08:00 | 2030 33% ECP | 628.45 | 0 | 510 | 465.74 | 0 | 0 | No
2030-10-30 09:00 | 2030 33% ECP | 700 | 0 | 228.6 | 508.57 | 0 | 0 | No
2030-10-30 10:00 | 2030 33% ECP | 420 | 0 | -71.4 | 316.12 | 0 | 0 | No
2030-10-30 11:00 | 2030 33% ECP | 0 | -4.03 | -371.4 | 118.05 | 0 | 0 | No
2030-10-30 12:00 | 2030 33% ECP | 0 | -214.11 | -510 | 74.03 | 0 | 0 | No
2030-10-30 13:00 | 2030 33% ECP | 0 | 0 | -327 | 148.92 | 0 | 0 | No
2030-10-30 14:00 | 2030 33% ECP | 335.81 | 0 | -27 | 95.17 | 0 | 0 | No
2030-10-30 15:00 | 2030 33% ECP | 236.96 | 0 | 198.8 | 179.76 | 0 | 0 | No
2030-10-30 16:00 | 2030 33% ECP | -183.04 | 0 | -101.2 | 176.17 | 0 | 0 | No
2030-10-30 17:00 | 2030 33% ECP | -603.04 | -300 | -401.2 | -123.83 | 0 | 0 | No
2030-10-30 18:00 | 2030 33% ECP | -700 | -526 | -510 | -423.83 | 0 | 0 | No
2030-10-30 19:00 | 2030 33% ECP | -700 | -526 | -510 | -129.26 | 0 | 0 | No
2030-10-30 20:00 | 2030 33% ECP | -577.02 | -526 | -510 | 170.74 | 0 | 0 | No
2030-10-30 21:00 | 2030 33% ECP | -625.41 | -526 | -510 | 26.84 | 0 | 0 | No
2030-10-30 22:00 | 2030 33% ECP | -700 | -526 | -510 | 57.15 | 0 | 0 | No
2030-10-30 23:00 | 2030 33% ECP | -700 | -526 | -510 | -119.01 | 0 | 0 | No
2030-10-31 | 2030 33% ECP | -700 | -526 | 0 | -419.01 | 0 | 0 | Yes
2030-10-31 01:00 | 2030 33% ECP | -700 | -226 | 0 | -119.01 | 0 | 0 | Yes
2030-10-31 02:00 | 2030 33% ECP | -700 | 74 | 0 | 0 | 0 | 0 | Yes
2030-10-31 03:00 | 2030 33% ECP | -700 | 374 | 0 | 78.77 | 0 | 0 | Yes
2030-10-31 04:00 | 2030 33% ECP | -700 | 505 | 0 | 94.94 | 0 | 0 | Yes
2030-10-31 05:00 | 2030 33% ECP | -700 | 505 | 0 | -20.32 | 0 | 0 | Yes
2030-10-31 06:00 | 2030 33% ECP | -700 | 505 | 0 | 61.29 | 0 | 0 | Yes
2030-10-31 07:00 | 2030 33% ECP | -700 | 505 | 0 | 361.29 | 0 | 0 | Yes
2030-10-31 08:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 09:00 | 2030 33% ECP | -700 | 505 | 0 | 431.35 | 0 | 0 | Yes
2030-10-31 10:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 11:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 12:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 13:00 | 2030 33% ECP | -700 | 505 | 0 | 312.82 | 0 | 0 | Yes
2030-10-31 14:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 15:00 | 2030 33% ECP | -700 | 505 | 0 | 338.57 | 0 | 0 | Yes
2030-10-31 16:00 | 2030 33% ECP | -700 | 505 | 0 | 382.68 | 0 | 0 | Yes
2030-10-31 17:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 18:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 19:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 20:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-10-31 21:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-10-31 22:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 23:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 01:00 | 2030 33% ECP | -700 | 505 | 0 | 476.13 | 0 | 0 | Yes
2030-11-01 02:00 | 2030 33% ECP | -700 | 505 | 0 | 227.48 | 0 | 0 | Yes
2030-11-01 03:00 | 2030 33% ECP | -700 | 505 | 0 | 430.41 | 0 | 0 | Yes
2030-11-01 04:00 | 2030 33% ECP | -700 | 505 | 0 | 184.14 | 0 | 0 | Yes
2030-11-01 05:00 | 2030 33% ECP | -700 | 505 | 0 | 421.03 | 0 | 0 | Yes
2030-11-01 06:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 07:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 08:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 09:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 10:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 11:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 12:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 13:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 14:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 15:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 16:00 | 2030 33% ECP | -280 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 17:00 | 2030 33% ECP | 140 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 18:00 | 2030 33% ECP | 560 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 19:00 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 20:00 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 21:00 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 22:00 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 23:00 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-02 | 2030 33% ECP | 700 | 505 | 300 | 510 | 0 | 0 | No
2030-11-02 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 02:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 03:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 04:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 05:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 06:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 07:00 | 2030 33% ECP | 0 | 205 | 372.26 | 412.2 | 0 | 0 | No
2030-11-02 08:00 | 2030 33% ECP | 0 | 0 | 510 | 411.5 | 0 | 0 | No
2030-11-02 09:00 | 2030 33% ECP | 0 | 205 | 510 | 440.89 | 0 | 0 | No
2030-11-02 10:00 | 2030 33% ECP | -203.96 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 11:00 | 2030 33% ECP | -623.96 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 12:00 | 2030 33% ECP | -623.96 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 13:00 | 2030 33% ECP | -623.96 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 14:00 | 2030 33% ECP | -623.96 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 15:00 | 2030 33% ECP | -250.66 | 205 | 210 | 510 | 0 | 0 | No
2030-11-02 16:00 | 2030 33% ECP | -280 | -95 | -90 | 298.61 | 0 | 0 | No
2030-11-02 17:00 | 2030 33% ECP | -700 | -395 | -390 | 236.12 | 0 | 0 | No
2030-11-02 18:00 | 2030 33% ECP | -588.71 | -526 | -510 | 233.76 | 0 | 0 | No
2030-11-02 19:00 | 2030 33% ECP | -168.71 | -226 | -210 | 301.4 | 0 | 0 | No
2030-11-02 20:00 | 2030 33% ECP | 251.29 | 74 | 90 | 210 | 0 | 0 | No
2030-11-02 21:00 | 2030 33% ECP | 373.2 | 374 | 390 | 510 | 0 | 0 | No
2030-11-02 22:00 | 2030 33% ECP | -46.8 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 23:00 | 2030 33% ECP | -466.8 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 | 2030 33% ECP | -46.8 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 01:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 02:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 03:00 | 2030 33% ECP | -40.94 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 04:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 05:00 | 2030 33% ECP | -234.75 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 06:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 07:00 | 2030 33% ECP | 280 | 300 | 245.75 | 439.22 | 0 | 0 | No
2030-11-03 08:00 | 2030 33% ECP | 700 | 0 | -54.25 | 139.22 | 0 | 0 | No
2030-11-03 09:00 | 2030 33% ECP | 700 | 300 | 245.75 | 439.22 | 0 | 0 | No
2030-11-03 10:00 | 2030 33% ECP | 280 | 0 | 87.36 | 442.44 | 0 | 0 | No
2030-11-03 11:00 | 2030 33% ECP | 0 | 0 | 0 | 495.46 | 0 | 0 | No
2030-11-03 12:00 | 2030 33% ECP | 0 | 0 | 0 | 357.32 | 0 | 0 | No
2030-11-03 13:00 | 2030 33% ECP | 0 | 205 | 210 | 210 | 0 | 0 | No
2030-11-03 14:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 15:00 | 2030 33% ECP | 700 | 217.53 | 510 | 510 | 0 | 0 | No
2030-11-03 16:00 | 2030 33% ECP | 700 | 0 | 210 | 492.6 | 0 | 0 | No
2030-11-03 17:00 | 2030 33% ECP | 700 | 0 | 479.44 | 408.46 | 0 | 0 | No
2030-11-03 18:00 | 2030 33% ECP | 700 | 0 | 510 | 408.46 | 0 | 0 | No
2030-11-03 19:00 | 2030 33% ECP | 700 | 0 | 510 | 408.46 | 0 | 0 | No
2030-11-03 20:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-11-03 21:00 | 2030 33% ECP | 700 | 0 | 510 | 466.32 | 0 | 0 | No
2030-11-03 22:00 | 2030 33% ECP | 700 | 0 | 510 | 402.3 | 0 | 0 | No
2030-11-03 23:00 | 2030 33% ECP | 700 | 96.06 | 510 | 510 | 0 | 0 | No
2030-11-04 | 2030 33% ECP | 700 | 0 | 255.57 | 369.61 | 0 | 0 | No
2030-11-04 01:00 | 2030 33% ECP | 700 | 250.49 | 510 | 510 | 0 | 0 | No
2030-11-04 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 07:00 | 2030 33% ECP | 280 | 205 | 210 | 210 | 0 | 0 | No
2030-11-04 08:00 | 2030 33% ECP | 700 | 0 | 300 | 280.58 | 0 | 0 | No
2030-11-04 09:00 | 2030 33% ECP | 700 | 205.32 | 0 | 271.92 | 0 | 0 | No
2030-11-04 10:00 | 2030 33% ECP | 700 | 0 | 0 | 193.15 | 0 | 0 | No
2030-11-04 11:00 | 2030 33% ECP | 536.9 | -300 | 0 | -106.85 | 0 | 0 | No
2030-11-04 12:00 | 2030 33% ECP | 318.06 | -526 | 0 | -324.68 | 0 | 0 | No
2030-11-04 13:00 | 2030 33% ECP | 424.87 | -526 | 0 | -164.86 | 0 | 0 | No
2030-11-04 14:00 | 2030 33% ECP | 678.57 | -300 | 0 | -66.15 | 0 | 0 | No
2030-11-04 15:00 | 2030 33% ECP | 700 | 0 | 0 | 233.85 | 0 | 0 | No
2030-11-04 16:00 | 2030 33% ECP | 700 | 0 | 0 | -66.15 | 0 | 0 | No
2030-11-04 17:00 | 2030 33% ECP | 700 | 0 | 0 | -227.25 | 0 | 0 | No
2030-11-04 18:00 | 2030 33% ECP | 700 | 0 | 0 | -90 | 0 | 0 | No
2030-11-04 19:00 | 2030 33% ECP | 700 | 205 | 0 | 210 | 0 | 0 | No
2030-11-04 20:00 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-04 21:00 | 2030 33% ECP | 700 | 505 | 0 | 445.25 | 0 | 0 | No
2030-11-04 22:00 | 2030 33% ECP | 700 | 444.93 | 0 | 490.69 | 0 | 0 | No
2030-11-04 23:00 | 2030 33% ECP | 700 | 144.93 | 0 | 208.93 | 0 | 0 | No
2030-11-05 | 2030 33% ECP | 700 | 205 | 0 | 210 | 0 | 0 | No
2030-11-05 01:00 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-05 02:00 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-05 03:00 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-05 04:00 | 2030 33% ECP | 700 | 333.7 | 0 | 510 | 0 | 0 | No
2030-11-05 05:00 | 2030 33% ECP | 700 | 33.7 | 0 | 210 | 0 | 0 | No
2030-11-05 06:00 | 2030 33% ECP | 576.02 | 0 | 0 | 0 | 0 | 0 | No
2030-11-05 07:00 | 2030 33% ECP | 700 | 0 | 0 | 103.47 | 0 | 0 | No
2030-11-05 08:00 | 2030 33% ECP | 700 | 263.66 | 0 | 403.47 | 0 | 0 | No
2030-11-05 09:00 | 2030 33% ECP | 700 | 379.31 | 0 | 510 | 0 | 0 | No
2030-11-05 10:00 | 2030 33% ECP | 700 | 79.31 | 0 | 213.35 | 0 | 0 | No
2030-11-05 11:00 | 2030 33% ECP | 700 | 0 | 0 | 109.75 | 0 | 0 | No
2030-11-05 12:00 | 2030 33% ECP | 291.55 | 0 | 0 | 125 | 0 | 0 | No
2030-11-05 13:00 | 2030 33% ECP | -128.45 | 0 | 0 | 126.39 | 0 | 0 | No
2030-11-05 14:00 | 2030 33% ECP | 85.67 | -107.01 | 0 | -173.61 | 0 | 0 | No
2030-11-05 15:00 | 2030 33% ECP | 505.67 | 0 | 0 | 0 | 0 | 0 | No
2030-11-05 16:00 | 2030 33% ECP | 700 | -26.38 | 0 | -210 | 0 | 0 | No
2030-11-05 17:00 | 2030 33% ECP | 700 | -326.38 | 0 | -510 | 0 | 0 | No
2030-11-05 18:00 | 2030 33% ECP | 700 | -526 | 0 | -510 | 0 | 0 | No
2030-11-05 19:00 | 2030 33% ECP | 700 | -226 | 0 | -510 | 0 | 0 | No
2030-11-05 20:00 | 2030 33% ECP | 700 | 74 | 0 | -210 | 0 | 0 | No
2030-11-05 21:00 | 2030 33% ECP | 700 | 374 | 0 | 2.23 | 0 | 0 | No
2030-11-05 22:00 | 2030 33% ECP | 700 | 224.5 | 0 | 0 | 0 | 0 | No
2030-11-05 23:00 | 2030 33% ECP | 700 | 0 | 0 | 266.78 | 0 | 0 | No
2030-11-06 | 2030 33% ECP | 700 | 0 | 0 | 156.91 | 0 | 0 | No
2030-11-06 01:00 | 2030 33% ECP | 700 | 0 | 0 | 120.76 | 0 | 0 | No
2030-11-06 02:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-11-06 03:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-11-06 04:00 | 2030 33% ECP | 684.29 | 0 | 0 | 0 | 0 | 0 | No
2030-11-06 05:00 | 2030 33% ECP | 264.29 | -226 | 0 | -210 | 0 | 0 | No
2030-11-06 06:00 | 2030 33% ECP | -155.71 | -526 | 0 | -510 | 0 | 0 | No
2030-11-06 07:00 | 2030 33% ECP | -158.36 | -526 | 0 | -510 | 0 | 0 | No
2030-11-06 08:00 | 2030 33% ECP | 261.64 | -526 | 0 | -510 | 0 | 0 | No
2030-11-06 09:00 | 2030 33% ECP | 681.64 | -526 | -510 | -349.79 | 0 | 0 | No
2030-11-06 10:00 | 2030 33% ECP | 560 | -526 | -510 | -49.79 | 0 | 0 | No
2030-11-06 11:00 | 2030 33% ECP | 140 | -226 | -210 | 250.21 | 0 | 0 | No
2030-11-06 12:00 | 2030 33% ECP | -280 | -226 | -210 | 82.47 | 0 | 0 | No
2030-11-06 13:00 | 2030 33% ECP | -700 | -526 | -510 | -217.53 | 0 | 0 | No
2030-11-06 14:00 | 2030 33% ECP | -700 | -526 | -510 | -375.88 | 0 | 0 | No
2030-11-06 15:00 | 2030 33% ECP | -621.81 | -526 | -510 | -215.62 | 0 | 0 | No
2030-11-06 16:00 | 2030 33% ECP | -201.81 | -526 | -510 | -510 | 0 | 0 | No
2030-11-06 17:00 | 2030 33% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-11-06 18:00 | 2030 33% ECP | 0 | -339.46 | -510 | -242.97 | 0 | 0 | No
2030-11-06 19:00 | 2030 33% ECP | 280 | -39.46 | -210 | 57.03 | 0 | 0 | No
2030-11-06 20:00 | 2030 33% ECP | 700 | 260.54 | 90 | 357.03 | 0 | 0 | No
2030-11-06 21:00 | 2030 33% ECP | 700 | 251.65 | 390 | 510 | 0 | 0 | No
2030-11-06 22:00 | 2030 33% ECP | 700 | 79.52 | 318.42 | 300 | 0 | 0 | No
2030-11-06 23:00 | 2030 33% ECP | 700 | 0 | 18.42 | 0 | 0 | 0 | No
2030-11-07 | 2030 33% ECP | 700 | 300 | 318.42 | 300 | 0 | 0 | No
2030-11-07 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-07 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-07 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-07 04:00 | 2030 33% ECP | 700 | 300 | 210 | 236.43 | 0 | 0 | No
2030-11-07 05:00 | 2030 33% ECP | 280 | 0 | -90 | -63.57 | 0 | 0 | No
2030-11-07 06:00 | 2030 33% ECP | -140 | -300 | -390 | -363.57 | 0 | 0 | No
2030-11-07 07:00 | 2030 33% ECP | 24.77 | 0 | -510 | -405.06 | 0 | 0 | No
2030-11-07 08:00 | 2030 33% ECP | 444.77 | 0 | -510 | -248.48 | 0 | 0 | No
2030-11-07 09:00 | 2030 33% ECP | 402.11 | -210.57 | -510 | -134.13 | 0 | 0 | No
2030-11-07 10:00 | 2030 33% ECP | 0 | -510.57 | -510 | -179.91 | 0 | 0 | No
2030-11-07 11:00 | 2030 33% ECP | -277.26 | -327.63 | -510 | -241 | 0 | 0 | No
2030-11-07 12:00 | 2030 33% ECP | -697.26 | -526 | -510 | -346.59 | 0 | 0 | No
2030-11-07 13:00 | 2030 33% ECP | -640.2 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 14:00 | 2030 33% ECP | -437.38 | -526 | -510 | -479.75 | 0 | 0 | No
2030-11-07 15:00 | 2030 33% ECP | -300.64 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 16:00 | 2030 33% ECP | -280 | -226 | -510 | -400.98 | 0 | 0 | No
2030-11-07 17:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 18:00 | 2030 33% ECP | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 19:00 | 2030 33% ECP | 140 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 20:00 | 2030 33% ECP | 560 | -226 | -510 | -510 | 0 | 0 | No
2030-11-07 21:00 | 2030 33% ECP | 560.07 | 0 | -422.27 | -300 | 0 | 0 | No
2030-11-07 22:00 | 2030 33% ECP | 700 | 0 | -122.27 | 0 | 0 | 0 | No
2030-11-07 23:00 | 2030 33% ECP | 700 | 0 | -240.09 | 0 | 0 | 0 | No
2030-11-08 | 2030 33% ECP | 700 | 0 | 59.91 | 300 | 0 | 0 | No
2030-11-08 01:00 | 2030 33% ECP | 700 | 0 | 359.91 | 0 | 0 | 0 | No
2030-11-08 02:00 | 2030 33% ECP | 700 | 0 | 510 | 34.89 | 0 | 0 | No
2030-11-08 03:00 | 2030 33% ECP | 560 | 0 | 510 | 34.89 | 0 | 0 | No
2030-11-08 04:00 | 2030 33% ECP | 140 | 0 | 510 | 71.11 | 0 | 0 | No
2030-11-08 05:00 | 2030 33% ECP | -280 | 0 | 301.88 | 36.53 | 0 | 0 | No
2030-11-08 06:00 | 2030 33% ECP | -700 | 0 | 1.88 | 36.53 | 0 | 0 | No
2030-11-08 07:00 | 2030 33% ECP | -700 | 0 | -298.12 | 0 | 0 | 0 | No
2030-11-08 08:00 | 2030 33% ECP | -665.09 | 0 | -118.2 | 0 | 0 | 0 | No
2030-11-08 09:00 | 2030 33% ECP | -248.17 | 0 | 0 | 77.58 | 0 | 0 | No
2030-11-08 10:00 | 2030 33% ECP | -503.09 | 0 | 0 | 207.15 | 0 | 0 | No
2030-11-08 11:00 | 2030 33% ECP | -700 | 0 | -48.85 | 330.52 | 0 | 0 | No
2030-11-08 12:00 | 2030 33% ECP | -700 | 0 | -287.01 | 295.46 | 0 | 0 | No
2030-11-08 13:00 | 2030 33% ECP | -700 | -58.22 | -510 | 161.7 | 0 | 0 | No
2030-11-08 14:00 | 2030 33% ECP | -280 | -358.22 | -510 | 223.68 | 0 | 0 | No
2030-11-08 15:00 | 2030 33% ECP | 0 | -526 | -510 | 215.3 | 0 | 0 | No
2030-11-08 16:00 | 2030 33% ECP | -52.47 | -526 | -510 | 73.9 | 0 | 0 | No
2030-11-08 17:00 | 2030 33% ECP | -472.47 | -526 | -510 | 329.8 | 0 | 0 | No
2030-11-08 18:00 | 2030 33% ECP | -52.47 | -526 | -510 | 329.8 | 0 | 0 | No
2030-11-08 19:00 | 2030 33% ECP | 0 | -526 | -510 | 29.8 | 0 | 0 | No
2030-11-08 20:00 | 2030 33% ECP | 198.15 | -526 | -510 | 115.59 | 0 | 0 | No
2030-11-08 21:00 | 2030 33% ECP | 618.15 | -226 | -397.39 | 415.59 | 0 | 0 | No
2030-11-08 22:00 | 2030 33% ECP | 260.62 | -526 | -510 | 217.26 | 0 | 0 | No
2030-11-08 23:00 | 2030 33% ECP | 99.22 | -526 | -510 | 132.77 | 0 | 0 | No
2030-11-09 | 2030 33% ECP | 519.22 | -226 | -210 | 366.49 | 0 | 0 | No
2030-11-09 01:00 | 2030 33% ECP | 700 | 0 | -184.38 | 111.07 | 0 | 0 | No
2030-11-09 02:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-11-09 03:00 | 2030 33% ECP | 700 | 0 | -107.8 | 0 | 0 | 0 | No
2030-11-09 04:00 | 2030 33% ECP | 420 | 0 | -300 | 0 | 0 | 0 | No
2030-11-09 05:00 | 2030 33% ECP | 0 | 0 | 0 | 0 | 0 | 0 | No
2030-11-09 06:00 | 2030 33% ECP | -420 | -226 | -300 | -168.59 | 0 | 0 | No
2030-11-09 07:00 | 2030 33% ECP | -700 | -526 | -510 | -468.59 | 0 | 0 | No
2030-11-09 08:00 | 2030 33% ECP | -347.16 | -526 | -510 | -327.79 | 0 | 0 | No
2030-11-09 09:00 | 2030 33% ECP | -158.43 | -526 | -510 | -237.2 | 0 | 0 | No
2030-11-09 10:00 | 2030 33% ECP | -420 | -433.65 | -510 | -141.2 | 0 | 0 | No
2030-11-09 11:00 | 2030 33% ECP | 0 | -133.65 | -481.34 | 0 | 0 | 0 | No
2030-11-09 12:00 | 2030 33% ECP | -46.76 | -433.65 | -510 | -24.13 | 0 | 0 | No
2030-11-09 13:00 | 2030 33% ECP | 0 | -163.66 | -510 | -93.95 | 0 | 0 | No
2030-11-09 14:00 | 2030 33% ECP | 371.25 | 0 | -510 | -153.98 | 0 | 0 | No
2030-11-09 15:00 | 2030 33% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-11-09 16:00 | 2030 33% ECP | 700 | -130.78 | -510 | 0 | 0 | 0 | No
2030-11-09 17:00 | 2030 33% ECP | 700 | -430.78 | -510 | -300 | 0 | 0 | No
2030-11-09 18:00 | 2030 33% ECP | 700 | -300 | -510 | -280.29 | 0 | 0 | No
2030-11-09 19:00 | 2030 33% ECP | 700 | 0 | -431.88 | 0 | 0 | 0 | No
2030-11-09 20:00 | 2030 33% ECP | 700 | 0 | -247.11 | 0 | 0 | 0 | No
2030-11-09 21:00 | 2030 33% ECP | 700 | 0 | 52.89 | 91.46 | 0 | 0 | No
2030-11-09 22:00 | 2030 33% ECP | 700 | 300 | 352.89 | 391.46 | 0 | 0 | No
2030-11-09 23:00 | 2030 33% ECP | 700 | 0 | 510 | 247.63 | 0 | 0 | No
2030-11-10 | 2030 33% ECP | 700 | 0 | 510 | 64.44 | 0 | 0 | No
2030-11-10 01:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-11-10 02:00 | 2030 33% ECP | 700 | 0 | 510 | 49.63 | 0 | 0 | No
2030-11-10 03:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-11-10 04:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-11-10 05:00 | 2030 33% ECP | 420 | 0 | 426.36 | 0 | 0 | 0 | No
2030-11-10 06:00 | 2030 33% ECP | 0 | 0 | 148.96 | 67.15 | 0 | 0 | No
2030-11-10 07:00 | 2030 33% ECP | -420 | 0 | -151.04 | -125.08 | 0 | 0 | No
2030-11-10 08:00 | 2030 33% ECP | -700 | 0 | -451.04 | -425.08 | 0 | 0 | No
2030-11-10 09:00 | 2030 33% ECP | -469.54 | 0 | -510 | -413.96 | 0 | 0 | No
2030-11-10 10:00 | 2030 33% ECP | -700 | -55.46 | -210 | -113.96 | 0 | 0 | No
2030-11-10 11:00 | 2030 33% ECP | -700 | -355.46 | -510 | -42.24 | 0 | 0 | No
2030-11-10 12:00 | 2030 33% ECP | -700 | -526 | -510 | -342.24 | 0 | 0 | No
2030-11-10 13:00 | 2030 33% ECP | -700 | -526 | -510 | -263.89 | 0 | 0 | No
2030-11-10 14:00 | 2030 33% ECP | -700 | -526 | -510 | -271.36 | 0 | 0 | No
2030-11-10 15:00 | 2030 33% ECP | -700 | -526 | -510 | -419.76 | 0 | 0 | No
2030-11-10 16:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-10 17:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-10 18:00 | 2030 33% ECP | -700 | -526 | -510 | -330.1 | 0 | 0 | No
2030-11-10 19:00 | 2030 33% ECP | -700 | -526 | -510 | -30.1 | 0 | 0 | No
2030-11-10 20:00 | 2030 33% ECP | -700 | -526 | -510 | -48.72 | 0 | 0 | No
2030-11-10 21:00 | 2030 33% ECP | -700 | -526 | -510 | 21 | 0 | 0 | No
2030-11-10 22:00 | 2030 33% ECP | -700 | -526 | -510 | -44.37 | 0 | 0 | No
2030-11-10 23:00 | 2030 33% ECP | -700 | -526 | -510 | 29.65 | 0 | 0 | No
2030-11-11 | 2030 33% ECP | -700 | -452.95 | -510 | -103.48 | 0 | 0 | No
2030-11-11 01:00 | 2030 33% ECP | -700 | -152.95 | -210 | 196.52 | 0 | 0 | No
2030-11-11 02:00 | 2030 33% ECP | -700 | 147.05 | 90 | 448.79 | 0 | 0 | Yes
2030-11-11 03:00 | 2030 33% ECP | -700 | 447.05 | 390 | 510 | 0 | 0 | Yes
2030-11-11 04:00 | 2030 33% ECP | -700 | 505 | 510 | 468.93 | 0 | 0 | Yes
2030-11-11 05:00 | 2030 33% ECP | -700 | 505 | 510 | 168.93 | 0 | 0 | Yes
2030-11-11 06:00 | 2030 33% ECP | -700 | 505 | 510 | 441.16 | 0 | 0 | Yes
2030-11-11 07:00 | 2030 33% ECP | -700 | 505 | 510 | 424.93 | 0 | 0 | Yes
2030-11-11 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 15:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 16:00 | 2030 33% ECP | -284.97 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 17:00 | 2030 33% ECP | 135.03 | 278.73 | 510 | 496.06 | 0 | 0 | No
2030-11-11 18:00 | 2030 33% ECP | 555.03 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 19:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 20:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-12 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-12 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-12 03:00 | 2030 33% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 04:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-12 05:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 07:00 | 2030 33% ECP | -700 | 205 | 210 | 251.57 | 0 | 0 | No
2030-11-12 08:00 | 2030 33% ECP | -700 | -95 | -90 | 393.64 | 0 | 0 | No
2030-11-12 09:00 | 2030 33% ECP | -700 | -395 | -390 | 510 | 0 | 0 | No
2030-11-12 10:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-11-12 11:00 | 2030 33% ECP | -700 | -526 | -510 | 380.49 | 0 | 0 | No
2030-11-12 12:00 | 2030 33% ECP | -700 | -526 | -510 | 80.49 | 0 | 0 | No
2030-11-12 13:00 | 2030 33% ECP | -700 | -526 | -510 | 1.44 | 0 | 0 | No
2030-11-12 14:00 | 2030 33% ECP | -700 | -526 | -510 | -267.35 | 0 | 0 | No
2030-11-12 15:00 | 2030 33% ECP | -700 | -526 | -510 | -55.6 | 0 | 0 | No
2030-11-12 16:00 | 2030 33% ECP | -700 | -526 | -510 | -58.81 | 0 | 0 | No
2030-11-12 17:00 | 2030 33% ECP | -700 | -526 | -510 | -17.62 | 0 | 0 | No
2030-11-12 18:00 | 2030 33% ECP | -700 | -395 | -390 | -51.09 | 0 | 0 | No
2030-11-12 19:00 | 2030 33% ECP | -700 | -95 | -90 | -90.42 | 0 | 0 | No
2030-11-12 20:00 | 2030 33% ECP | -394.51 | 205 | 210 | 209.58 | 0 | 0 | No
2030-11-12 21:00 | 2030 33% ECP | 25.49 | 505 | 510 | 509.58 | 0 | 0 | No
2030-11-12 22:00 | 2030 33% ECP | 445.49 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 23:00 | 2030 33% ECP | 620.43 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 03:00 | 2030 33% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 04:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 05:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 07:00 | 2030 33% ECP | -700 | 205 | 210 | 490.84 | 0 | 0 | No
2030-11-13 08:00 | 2030 33% ECP | -666.51 | -95 | -90 | 283.19 | 0 | 0 | No
2030-11-13 09:00 | 2030 33% ECP | -254.41 | 0 | 0 | 510 | 0 | 0 | No
2030-11-13 10:00 | 2030 33% ECP | -674.41 | 0 | 0 | 510 | 0 | 0 | No
2030-11-13 11:00 | 2030 33% ECP | -700 | 0 | -118.22 | 510 | 0 | 0 | No
2030-11-13 12:00 | 2030 33% ECP | -700 | 300 | 109.93 | 510 | 0 | 0 | No
2030-11-13 13:00 | 2030 33% ECP | -700 | 0 | -190.07 | 315.81 | 0 | 0 | No
2030-11-13 14:00 | 2030 33% ECP | -700 | 0 | -254.39 | 484.2 | 0 | 0 | No
2030-11-13 15:00 | 2030 33% ECP | -280 | 0 | 0 | 345.79 | 0 | 0 | No
2030-11-13 16:00 | 2030 33% ECP | -700 | 0 | 171.66 | 445.21 | 0 | 0 | No
2030-11-13 17:00 | 2030 33% ECP | -700 | 0 | 471.66 | 467.37 | 0 | 0 | No
2030-11-13 18:00 | 2030 33% ECP | -700 | 0 | 171.66 | 506.62 | 0 | 0 | No
2030-11-13 19:00 | 2030 33% ECP | -280 | 0 | 0 | 507.85 | 0 | 0 | No
2030-11-13 20:00 | 2030 33% ECP | 140 | 0 | 0 | 510 | 0 | 0 | No
2030-11-13 21:00 | 2030 33% ECP | -164.15 | 0 | 0 | 353.36 | 0 | 0 | No
2030-11-13 22:00 | 2030 33% ECP | -584.15 | 0 | -222.96 | 475.38 | 0 | 0 | No
2030-11-13 23:00 | 2030 33% ECP | -280 | 300 | 77.04 | 510 | 0 | 0 | No
2030-11-14 | 2030 33% ECP | -291.86 | 384.74 | 377.04 | 510 | 0 | 0 | No
2030-11-14 01:00 | 2030 33% ECP | -471.98 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 02:00 | 2030 33% ECP | -420 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 03:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 04:00 | 2030 33% ECP | -342.68 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 05:00 | 2030 33% ECP | -335.02 | 374 | 390 | 510 | 0 | 0 | No
2030-11-14 06:00 | 2030 33% ECP | -700 | 74 | 90 | 471.67 | 0 | 0 | No
2030-11-14 07:00 | 2030 33% ECP | -700 | -226 | -210 | 171.67 | 0 | 0 | No
2030-11-14 08:00 | 2030 33% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-11-14 09:00 | 2030 33% ECP | -280 | -226 | -210 | 510 | 0 | 0 | No
2030-11-14 10:00 | 2030 33% ECP | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-11-14 11:00 | 2030 33% ECP | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-11-14 12:00 | 2030 33% ECP | -296.14 | 0 | 0 | 510 | 0 | 0 | No
2030-11-14 13:00 | 2030 33% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-11-14 14:00 | 2030 33% ECP | -451.22 | 0 | 0 | 510 | 0 | 0 | No
2030-11-14 15:00 | 2030 33% ECP | -31.22 | 0 | -210 | 510 | 0 | 0 | No
2030-11-14 16:00 | 2030 33% ECP | -438.61 | -300 | -510 | 210 | 0 | 0 | No
2030-11-14 17:00 | 2030 33% ECP | -700 | -526 | -510 | -90 | 0 | 0 | No
2030-11-14 18:00 | 2030 33% ECP | -537.69 | -245.53 | -210 | -90 | 0 | 0 | No
2030-11-14 19:00 | 2030 33% ECP | -117.69 | 54.47 | 90 | 210 | 0 | 0 | No
2030-11-14 20:00 | 2030 33% ECP | 81.94 | 354.47 | 390 | 510 | 0 | 0 | No
2030-11-14 21:00 | 2030 33% ECP | -338.06 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-14 23:00 | 2030 33% ECP | -377.19 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 | 2030 33% ECP | 42.81 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 01:00 | 2030 33% ECP | 462.81 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 02:00 | 2030 33% ECP | 42.81 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 03:00 | 2030 33% ECP | 403.09 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 04:00 | 2030 33% ECP | 379.08 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 05:00 | 2030 33% ECP | 137.84 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 06:00 | 2030 33% ECP | 295.9 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 07:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 08:00 | 2030 33% ECP | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-11-15 09:00 | 2030 33% ECP | 700 | 399.42 | 510 | 510 | 0 | 0 | No
2030-11-15 10:00 | 2030 33% ECP | 618.15 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 11:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 12:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 13:00 | 2030 33% ECP | 700 | 450.15 | 390 | 510 | 0 | 0 | No
2030-11-15 14:00 | 2030 33% ECP | 700 | 150.15 | 90 | 510 | 0 | 0 | No
2030-11-15 15:00 | 2030 33% ECP | 700 | -149.85 | -210 | 210 | 0 | 0 | No
2030-11-15 16:00 | 2030 33% ECP | 700 | -449.85 | -510 | -90 | 0 | 0 | No
2030-11-15 17:00 | 2030 33% ECP | 280 | -526 | -510 | 47.3 | 0 | 0 | No
2030-11-15 18:00 | 2030 33% ECP | 700 | -526 | -510 | 309.44 | 0 | 0 | No
2030-11-15 19:00 | 2030 33% ECP | 698.3 | -526 | -510 | 309.44 | 0 | 0 | No
2030-11-15 20:00 | 2030 33% ECP | 278.3 | -526 | -510 | 9.44 | 0 | 0 | No
2030-11-15 21:00 | 2030 33% ECP | -141.7 | -226 | -210 | -61.09 | 0 | 0 | No
2030-11-15 22:00 | 2030 33% ECP | -561.7 | 74 | 90 | 238.91 | 0 | 0 | Yes
2030-11-15 23:00 | 2030 33% ECP | -700 | 374 | 390 | 460.13 | 0 | 0 | Yes
2030-11-16 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-16 01:00 | 2030 33% ECP | 140 | 505 | 510 | 476.82 | 0 | 0 | Yes
2030-11-16 02:00 | 2030 33% ECP | 392.17 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-16 03:00 | 2030 33% ECP | 608.63 | 505 | 510 | 357.17 | 0 | 0 | Yes
2030-11-16 04:00 | 2030 33% ECP | 188.63 | 505 | 510 | 57.17 | 0 | 0 | Yes
2030-11-16 05:00 | 2030 33% ECP | 188.63 | 505 | 510 | 275.2 | 0 | 0 | Yes
2030-11-16 06:00 | 2030 33% ECP | -213.85 | 505 | 510 | 510 | 0 | 0 | No
2030-11-16 07:00 | 2030 33% ECP | -633.85 | 505 | 510 | 510 | 0 | 0 | No
2030-11-16 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-16 09:00 | 2030 33% ECP | -577.12 | 205 | 210 | 510 | 0 | 0 | No
2030-11-16 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-16 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-16 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-16 13:00 | 2030 33% ECP | -700 | 265.65 | 210 | 510 | 0 | 0 | No
2030-11-16 14:00 | 2030 33% ECP | -700 | -34.35 | -90 | 510 | 0 | 0 | No
2030-11-16 15:00 | 2030 33% ECP | -700 | -334.35 | -390 | 327.25 | 0 | 0 | No
2030-11-16 16:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-11-16 17:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-11-16 18:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-11-16 19:00 | 2030 33% ECP | -700 | -526 | -510 | 478.2 | 0 | 0 | No
2030-11-16 20:00 | 2030 33% ECP | -700 | -526 | -510 | 407.3 | 0 | 0 | No
2030-11-16 21:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-11-16 22:00 | 2030 33% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-11-16 23:00 | 2030 33% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-11-17 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-11-17 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 13:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-11-17 14:00 | 2030 33% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-11-17 15:00 | 2030 33% ECP | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-11-17 16:00 | 2030 33% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-11-17 17:00 | 2030 33% ECP | -700 | -526 | -510 | -90 | 0 | 0 | No
2030-11-17 18:00 | 2030 33% ECP | -700 | -526 | -510 | 72 | 0 | 0 | No
2030-11-17 19:00 | 2030 33% ECP | -700 | -526 | -510 | 372 | 0 | 0 | No
2030-11-17 20:00 | 2030 33% ECP | -700 | -353.89 | -390 | 510 | 0 | 0 | No
2030-11-17 21:00 | 2030 33% ECP | -700 | -53.89 | -90 | 437.94 | 0 | 0 | Yes
2030-11-17 22:00 | 2030 33% ECP | -700 | 246.11 | 210 | 510 | 0 | 0 | Yes
2030-11-17 23:00 | 2030 33% ECP | -700 | 505 | 510 | 504.67 | 0 | 0 | Yes
2030-11-18 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 03:00 | 2030 33% ECP | -700 | 505 | 510 | 263.54 | 0 | 0 | Yes
2030-11-18 04:00 | 2030 33% ECP | -700 | 505 | 510 | 148.51 | 0 | 0 | Yes
2030-11-18 05:00 | 2030 33% ECP | -700 | 505 | 510 | 428.47 | 0 | 0 | Yes
2030-11-18 06:00 | 2030 33% ECP | -700 | 505 | 510 | 455.79 | 0 | 0 | Yes
2030-11-18 07:00 | 2030 33% ECP | -700 | 505 | 510 | 478.66 | 0 | 0 | Yes
2030-11-18 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-18 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 14:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-11-18 15:00 | 2030 33% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-11-18 16:00 | 2030 33% ECP | -700 | -226 | -210 | 413.7 | 0 | 0 | No
2030-11-18 17:00 | 2030 33% ECP | -700 | -526 | -510 | 113.7 | 0 | 0 | No
2030-11-18 18:00 | 2030 33% ECP | -700 | -526 | -510 | 193.36 | 0 | 0 | No
2030-11-18 19:00 | 2030 33% ECP | -700 | -391.39 | -390 | 493.36 | 0 | 0 | No
2030-11-18 20:00 | 2030 33% ECP | -700 | -91.39 | -90 | 510 | 0 | 0 | No
2030-11-18 21:00 | 2030 33% ECP | -700 | 208.61 | 210 | 510 | 0 | 0 | Yes
2030-11-18 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-19 07:00 | 2030 33% ECP | -700 | 205 | 210 | 375.3 | 0 | 0 | No
2030-11-19 08:00 | 2030 33% ECP | -330.51 | 0 | 410.23 | 75.3 | 0 | 0 | No
2030-11-19 09:00 | 2030 33% ECP | -81.47 | 0 | 210 | 210 | 0 | 0 | No
2030-11-19 10:00 | 2030 33% ECP | 0 | 24.04 | 510 | 510 | 0 | 0 | No
2030-11-19 11:00 | 2030 33% ECP | 0 | 0 | 510 | 363.64 | 0 | 0 | No
2030-11-19 12:00 | 2030 33% ECP | -420 | 0 | 510 | 213.86 | 0 | 0 | No
2030-11-19 13:00 | 2030 33% ECP | -700 | 205 | 510 | 225.2 | 0 | 0 | No
2030-11-19 14:00 | 2030 33% ECP | -640.11 | 505 | 510 | 510 | 0 | 0 | No
2030-11-19 15:00 | 2030 33% ECP | -220.11 | 505 | 510 | 510 | 0 | 0 | No
2030-11-19 16:00 | 2030 33% ECP | 199.89 | 205 | 210 | 210 | 0 | 0 | No
2030-11-19 17:00 | 2030 33% ECP | -220.11 | 0 | 0 | 0 | 0 | 0 | No
2030-11-19 18:00 | 2030 33% ECP | -325.07 | 0 | 0 | 0 | 0 | 0 | No
2030-11-19 19:00 | 2030 33% ECP | 94.93 | 0 | 0 | 0 | 0 | 0 | No
2030-11-19 20:00 | 2030 33% ECP | 140 | 0 | -30.3 | 0 | 0 | 0 | No
2030-11-19 21:00 | 2030 33% ECP | -280 | 0 | -330.3 | 0 | 0 | 0 | No
2030-11-19 22:00 | 2030 33% ECP | -700 | -137.17 | -510 | -51.22 | 0 | 0 | No
2030-11-19 23:00 | 2030 33% ECP | -280 | -393.37 | -510 | -218.39 | 0 | 0 | No
2030-11-20 | 2030 33% ECP | -591.13 | -93.37 | -420.36 | -132.92 | 0 | 0 | No
2030-11-20 01:00 | 2030 33% ECP | -496.25 | -389.16 | -510 | -432.92 | 0 | 0 | No
2030-11-20 02:00 | 2030 33% ECP | -467.48 | -410.79 | -510 | -418.7 | 0 | 0 | No
2030-11-20 03:00 | 2030 33% ECP | -700 | -110.79 | -510 | -325.58 | 0 | 0 | No
2030-11-20 04:00 | 2030 33% ECP | -700 | -368.36 | -510 | -318.51 | 0 | 0 | No
2030-11-20 05:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-20 06:00 | 2030 33% ECP | -700 | -526 | -510 | -493.97 | 0 | 0 | No
2030-11-20 07:00 | 2030 33% ECP | -700 | -296.65 | -510 | -396.09 | 0 | 0 | No
2030-11-20 08:00 | 2030 33% ECP | -700 | 0 | -510 | -103.71 | 0 | 0 | No
2030-11-20 09:00 | 2030 33% ECP | -700 | -190.05 | -510 | -51.24 | 0 | 0 | No
2030-11-20 10:00 | 2030 33% ECP | -700 | -418.01 | -510 | 248.76 | 0 | 0 | No
2030-11-20 11:00 | 2030 33% ECP | -700 | -526 | -510 | 477.9 | 0 | 0 | No
2030-11-20 12:00 | 2030 33% ECP | -700 | -526 | -510 | 326.2 | 0 | 0 | No
2030-11-20 13:00 | 2030 33% ECP | -700 | -526 | -510 | 26.2 | 0 | 0 | No
2030-11-20 14:00 | 2030 33% ECP | -700 | -526 | -510 | 21.42 | 0 | 0 | No
2030-11-20 15:00 | 2030 33% ECP | -700 | -526 | -510 | -188.37 | 0 | 0 | No
2030-11-20 16:00 | 2030 33% ECP | -700 | -334.29 | -510 | -434.14 | 0 | 0 | No
2030-11-20 17:00 | 2030 33% ECP | -700 | -300 | -467.9 | -134.14 | 0 | 0 | No
2030-11-20 18:00 | 2030 33% ECP | -700 | 0 | -167.9 | 112.14 | 0 | 0 | No
2030-11-20 19:00 | 2030 33% ECP | -700 | 0 | 132.1 | 41.83 | 0 | 0 | No
2030-11-20 20:00 | 2030 33% ECP | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-11-20 21:00 | 2030 33% ECP | -621.49 | 505 | 510 | 510 | 0 | 0 | No
2030-11-20 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-20 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 15:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 16:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 17:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 19:00 | 2030 33% ECP | -476.68 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 20:00 | 2030 33% ECP | -56.68 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 21:00 | 2030 33% ECP | 363.32 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 22:00 | 2030 33% ECP | 440.41 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 23:00 | 2030 33% ECP | 20.41 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 | 2030 33% ECP | 440.41 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 03:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 04:00 | 2030 33% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 05:00 | 2030 33% ECP | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 07:00 | 2030 33% ECP | -700 | 505 | 510 | 506.77 | 0 | 0 | No
2030-11-22 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 12:00 | 2030 33% ECP | -700 | 305.44 | 510 | 510 | 0 | 0 | No
2030-11-22 13:00 | 2030 33% ECP | -700 | 205 | 510 | 409.54 | 0 | 0 | No
2030-11-22 14:00 | 2030 33% ECP | -700 | 505 | 510 | 437.69 | 0 | 0 | No
2030-11-22 15:00 | 2030 33% ECP | -318.8 | 505 | 510 | 437.69 | 0 | 0 | No
2030-11-22 16:00 | 2030 33% ECP | -280 | 505 | 510 | 444.11 | 0 | 0 | No
2030-11-22 17:00 | 2030 33% ECP | -700 | 205 | 210 | 144.11 | 0 | 0 | No
2030-11-22 18:00 | 2030 33% ECP | -280 | 0 | 510 | 311.56 | 0 | 0 | No
2030-11-22 19:00 | 2030 33% ECP | 0 | 300 | 510 | 510 | 0 | 0 | No
2030-11-22 20:00 | 2030 33% ECP | 78.55 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 21:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 22:00 | 2030 33% ECP | 179.91 | 300 | 343.28 | 300 | 0 | 0 | No
2030-11-22 23:00 | 2030 33% ECP | 284.54 | 0 | 43.28 | 0 | 0 | 0 | No
2030-11-23 | 2030 33% ECP | 0 | 0 | -256.72 | -108.37 | 0 | 0 | No
2030-11-23 01:00 | 2030 33% ECP | 0 | 0 | -423.21 | 0 | 0 | 0 | No
2030-11-23 02:00 | 2030 33% ECP | 0 | 0 | -510 | -10.13 | 0 | 0 | No
2030-11-23 03:00 | 2030 33% ECP | -169.46 | -226 | -421 | 0 | 0 | 0 | No
2030-11-23 04:00 | 2030 33% ECP | -589.46 | -526 | -510 | -74.99 | 0 | 0 | No
2030-11-23 05:00 | 2030 33% ECP | -700 | -526 | -510 | -357.78 | 0 | 0 | No
2030-11-23 06:00 | 2030 33% ECP | -700 | -526 | -510 | -250.06 | 0 | 0 | No
2030-11-23 07:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-23 08:00 | 2030 33% ECP | -700 | -526 | -510 | -356.22 | 0 | 0 | No
2030-11-23 09:00 | 2030 33% ECP | -700 | -526 | -510 | -56.22 | 0 | 0 | No
2030-11-23 10:00 | 2030 33% ECP | -700 | -526 | -510 | -175.69 | 0 | 0 | No
2030-11-23 11:00 | 2030 33% ECP | -700 | -226 | -210 | -90 | 0 | 0 | No
2030-11-23 12:00 | 2030 33% ECP | -700 | 74 | 90 | 210 | 0 | 0 | No
2030-11-23 13:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-11-23 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-23 15:00 | 2030 33% ECP | -700 | 374 | 390 | 390 | 0 | 0 | No
2030-11-23 16:00 | 2030 33% ECP | -700 | 74 | 90 | 90 | 0 | 0 | No
2030-11-23 17:00 | 2030 33% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-11-23 18:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-23 19:00 | 2030 33% ECP | -700 | -226 | -360.33 | -300 | 0 | 0 | No
2030-11-23 20:00 | 2030 33% ECP | -700 | 74 | -60.33 | 0 | 0 | 0 | No
2030-11-23 21:00 | 2030 33% ECP | -700 | 374 | 239.67 | 300 | 0 | 0 | Yes
2030-11-23 22:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-23 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 14:00 | 2030 33% ECP | -650.55 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 15:00 | 2030 33% ECP | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 16:00 | 2030 33% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 17:00 | 2030 33% ECP | 280 | 205 | 210 | 510 | 0 | 0 | No
2030-11-24 18:00 | 2030 33% ECP | 700 | 225.76 | 510 | 510 | 0 | 0 | No
2030-11-24 19:00 | 2030 33% ECP | 700 | 225.76 | 510 | 510 | 0 | 0 | No
2030-11-24 20:00 | 2030 33% ECP | 700 | 457.03 | 510 | 510 | 0 | 0 | No
2030-11-24 21:00 | 2030 33% ECP | 700 | 327.55 | 510 | 510 | 0 | 0 | No
2030-11-24 22:00 | 2030 33% ECP | 700 | 301.08 | 510 | 510 | 0 | 0 | No
2030-11-24 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 06:00 | 2030 33% ECP | 280 | 205 | 210 | 210 | 0 | 0 | No
2030-11-25 07:00 | 2030 33% ECP | 617.92 | -95 | -90 | -90 | 0 | 0 | No
2030-11-25 08:00 | 2030 33% ECP | 700 | 2.7 | 210 | 210 | 0 | 0 | No
2030-11-25 09:00 | 2030 33% ECP | 700 | 0 | 510 | 470.69 | 0 | 0 | No
2030-11-25 10:00 | 2030 33% ECP | 700 | 1.3 | 308.99 | 510 | 0 | 0 | No
2030-11-25 11:00 | 2030 33% ECP | 700 | 0 | 8.99 | 229.62 | 0 | 0 | No
2030-11-25 12:00 | 2030 33% ECP | 700 | -247.07 | -291.01 | 173.3 | 0 | 0 | No
2030-11-25 13:00 | 2030 33% ECP | 280 | 0 | -182.67 | 112.35 | 0 | 0 | No
2030-11-25 14:00 | 2030 33% ECP | 280 | 0 | -31.71 | 0 | 0 | 0 | No
2030-11-25 15:00 | 2030 33% ECP | 700 | 0 | 71.37 | 0 | 0 | 0 | No
2030-11-25 16:00 | 2030 33% ECP | 700 | 0 | -228.63 | 0 | 0 | 0 | No
2030-11-25 17:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-11-25 18:00 | 2030 33% ECP | 700 | 0 | -17.29 | 0 | 0 | 0 | No
2030-11-25 19:00 | 2030 33% ECP | 700 | 0 | -17.29 | 0 | 0 | 0 | No
2030-11-25 20:00 | 2030 33% ECP | 700 | 0 | -129.28 | 0 | 0 | 0 | No
2030-11-25 21:00 | 2030 33% ECP | 700 | 0 | 170.72 | 57.04 | 0 | 0 | No
2030-11-25 22:00 | 2030 33% ECP | 700 | 300 | 470.72 | 357.04 | 0 | 0 | No
2030-11-25 23:00 | 2030 33% ECP | 700 | 0 | 510 | 182.85 | 0 | 0 | No
2030-11-26 | 2030 33% ECP | 700 | 300 | 510 | 482.85 | 0 | 0 | No
2030-11-26 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-26 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-26 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-26 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-26 05:00 | 2030 33% ECP | 280 | 300 | 324.83 | 210 | 0 | 0 | No
2030-11-26 06:00 | 2030 33% ECP | 12.14 | 0 | 24.83 | -90 | 0 | 0 | No
2030-11-26 07:00 | 2030 33% ECP | 256.68 | 0 | 0 | -55.78 | 0 | 0 | No
2030-11-26 08:00 | 2030 33% ECP | 79.99 | -226 | -296.5 | -210 | 0 | 0 | No
2030-11-26 09:00 | 2030 33% ECP | 499.99 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 10:00 | 2030 33% ECP | 498.32 | -226 | -210 | -210 | 0 | 0 | No
2030-11-26 11:00 | 2030 33% ECP | 306.72 | 0 | -210 | -210 | 0 | 0 | No
2030-11-26 12:00 | 2030 33% ECP | -113.28 | -300 | -510 | -510 | 0 | 0 | No
2030-11-26 13:00 | 2030 33% ECP | 0 | -459.5 | -510 | -510 | 0 | 0 | No
2030-11-26 14:00 | 2030 33% ECP | 0 | -200.69 | -510 | -510 | 0 | 0 | No
2030-11-26 15:00 | 2030 33% ECP | 247.52 | -226 | -510 | -240.03 | 0 | 0 | No
2030-11-26 16:00 | 2030 33% ECP | 667.52 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 17:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 18:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 19:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 20:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 21:00 | 2030 33% ECP | 700 | -300 | -316.28 | -496.24 | 0 | 0 | No
2030-11-26 22:00 | 2030 33% ECP | 700 | 0 | -16.28 | -196.24 | 0 | 0 | No
2030-11-26 23:00 | 2030 33% ECP | 700 | 0 | -255.74 | -39.22 | 0 | 0 | No
2030-11-27 | 2030 33% ECP | 700 | 300 | 44.26 | 0 | 0 | 0 | No
2030-11-27 01:00 | 2030 33% ECP | 700 | 452.75 | 344.26 | 0 | 0 | 0 | No
2030-11-27 02:00 | 2030 33% ECP | 700 | 452.75 | 510 | 0 | 0 | 0 | No
2030-11-27 03:00 | 2030 33% ECP | 700 | 463.54 | 510 | 0 | 0 | 0 | No
2030-11-27 04:00 | 2030 33% ECP | 280 | 300 | 390 | 0 | 0 | 0 | No
2030-11-27 05:00 | 2030 33% ECP | -140 | 0 | 90 | 0 | 0 | 0 | No
2030-11-27 06:00 | 2030 33% ECP | -560 | -57.86 | -210 | -210 | 0 | 0 | No
2030-11-27 07:00 | 2030 33% ECP | -664.42 | -357.86 | -510 | -510 | 0 | 0 | No
2030-11-27 08:00 | 2030 33% ECP | -244.42 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 09:00 | 2030 33% ECP | 97.34 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 10:00 | 2030 33% ECP | 515.78 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 11:00 | 2030 33% ECP | 95.78 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 12:00 | 2030 33% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 13:00 | 2030 33% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 14:00 | 2030 33% ECP | 136.12 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 15:00 | 2030 33% ECP | 556.12 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 16:00 | 2030 33% ECP | 298.03 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 17:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 18:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 19:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 20:00 | 2030 33% ECP | 700 | -300 | -499.53 | -300 | 0 | 0 | No
2030-11-27 21:00 | 2030 33% ECP | 700 | 0 | -199.53 | 0 | 0 | 0 | No
2030-11-27 22:00 | 2030 33% ECP | 700 | 0 | -156.5 | 0 | 0 | 0 | No
2030-11-27 23:00 | 2030 33% ECP | 622.14 | 0 | 0 | 0 | 0 | 0 | No
2030-11-28 | 2030 33% ECP | 700 | 300 | 300 | 300 | 0 | 0 | No
2030-11-28 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-28 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-28 03:00 | 2030 33% ECP | 496.09 | 505 | 510 | 510 | 0 | 0 | No
2030-11-28 04:00 | 2030 33% ECP | 76.09 | 505 | 510 | 510 | 0 | 0 | No
2030-11-28 05:00 | 2030 33% ECP | -343.91 | 300 | 375.14 | 210 | 0 | 0 | No
2030-11-28 06:00 | 2030 33% ECP | -700 | 0 | 75.14 | -90 | 0 | 0 | No
2030-11-28 07:00 | 2030 33% ECP | -280 | 0 | -224.86 | -390 | 0 | 0 | No
2030-11-28 08:00 | 2030 33% ECP | 0 | 0 | -492.52 | -231.11 | 0 | 0 | No
2030-11-28 09:00 | 2030 33% ECP | 420 | 0 | -510 | -488.97 | 0 | 0 | No
2030-11-28 10:00 | 2030 33% ECP | 369.62 | 0 | -210 | -188.97 | 0 | 0 | No
2030-11-28 11:00 | 2030 33% ECP | 0 | 0 | -219.2 | -57.94 | 0 | 0 | No
2030-11-28 12:00 | 2030 33% ECP | 0 | 0 | -510 | -273.86 | 0 | 0 | No
2030-11-28 13:00 | 2030 33% ECP | 0 | 0 | -473.63 | -129.98 | 0 | 0 | No
2030-11-28 14:00 | 2030 33% ECP | 0 | 0 | -173.63 | -28.86 | 0 | 0 | No
2030-11-28 15:00 | 2030 33% ECP | 191.45 | 0 | 0 | -26.94 | 0 | 0 | No
2030-11-28 16:00 | 2030 33% ECP | 477.02 | -226 | -210 | -326.94 | 0 | 0 | No
2030-11-28 17:00 | 2030 33% ECP | 122.12 | -526 | -510 | -510 | 0 | 0 | No
2030-11-28 18:00 | 2030 33% ECP | 542.12 | -526 | -510 | -510 | 0 | 0 | No
2030-11-28 19:00 | 2030 33% ECP | 700 | -226 | -478.2 | -210 | 0 | 0 | No
2030-11-28 20:00 | 2030 33% ECP | 700 | 74 | 0 | 20.4 | 0 | 0 | No
2030-11-28 21:00 | 2030 33% ECP | 700 | 374 | 0 | 0 | 0 | 0 | No
2030-11-28 22:00 | 2030 33% ECP | 700 | 392.7 | 0 | 200.4 | 0 | 0 | No
2030-11-28 23:00 | 2030 33% ECP | 700 | 325.56 | 0 | 500.4 | 0 | 0 | No
2030-11-29 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 01:00 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 02:00 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 03:00 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 04:00 | 2030 33% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 05:00 | 2030 33% ECP | 700 | 505 | 0 | 361.35 | 0 | 0 | No
2030-11-29 06:00 | 2030 33% ECP | 700 | 505 | 0 | 61.35 | 0 | 0 | No
2030-11-29 07:00 | 2030 33% ECP | 700 | 505 | 0 | -35.35 | 0 | 0 | No
2030-11-29 08:00 | 2030 33% ECP | 511.31 | 205 | 0 | -335.35 | 0 | 0 | No
2030-11-29 09:00 | 2030 33% ECP | 700 | 505 | 0 | -35.35 | 0 | 0 | No
2030-11-29 10:00 | 2030 33% ECP | 700 | 505 | 0 | 0 | 0 | 0 | No
2030-11-29 11:00 | 2030 33% ECP | 700 | 505 | 0 | 29.67 | 0 | 0 | No
2030-11-29 12:00 | 2030 33% ECP | 700 | 505 | 0 | 18.4 | 0 | 0 | No
2030-11-29 13:00 | 2030 33% ECP | 700 | 415.77 | 0 | -21.33 | 0 | 0 | No
2030-11-29 14:00 | 2030 33% ECP | 700 | 115.77 | 0 | 90 | 0 | 0 | No
2030-11-29 15:00 | 2030 33% ECP | 444.88 | -184.23 | 0 | -210 | 0 | 0 | No
2030-11-29 16:00 | 2030 33% ECP | 592.85 | -484.23 | 0 | -510 | 0 | 0 | No
2030-11-29 17:00 | 2030 33% ECP | 592.85 | -526 | 0 | -510 | 0 | 0 | No
2030-11-29 18:00 | 2030 33% ECP | 700 | -526 | 0 | -510 | 0 | 0 | No
2030-11-29 19:00 | 2030 33% ECP | 700 | -226 | 0 | -510 | 0 | 0 | No
2030-11-29 20:00 | 2030 33% ECP | 700 | 74 | 0 | -210 | 0 | 0 | No
2030-11-29 21:00 | 2030 33% ECP | 700 | 305.58 | 0 | -27.62 | 0 | 0 | No
2030-11-29 22:00 | 2030 33% ECP | 700 | 287.9 | 0 | -143.22 | 0 | 0 | No
2030-11-29 23:00 | 2030 33% ECP | 700 | 300 | 0 | 156.78 | 0 | 0 | No
2030-11-30 | 2030 33% ECP | 280 | 0 | 0 | -58.6 | 0 | 0 | No
2030-11-30 01:00 | 2030 33% ECP | 297.7 | 0 | 0 | -42.57 | 0 | 0 | No
2030-11-30 02:00 | 2030 33% ECP | 560 | 0 | 0 | -342.57 | 0 | 0 | No
2030-11-30 03:00 | 2030 33% ECP | 140 | 0 | 0 | -144.83 | 0 | 0 | No
2030-11-30 04:00 | 2030 33% ECP | -280 | -43.29 | 0 | -269.46 | 0 | 0 | No
2030-11-30 05:00 | 2030 33% ECP | -700 | -12.75 | 0 | -422.03 | 0 | 0 | No
2030-11-30 06:00 | 2030 33% ECP | -700 | -226 | 0 | -510 | 0 | 0 | No
2030-11-30 07:00 | 2030 33% ECP | -700 | -526 | 0 | -220.9 | 0 | 0 | No
2030-11-30 08:00 | 2030 33% ECP | -700 | -226 | 0 | -332.96 | 0 | 0 | No
2030-11-30 09:00 | 2030 33% ECP | -700 | -58.56 | 0 | -130.74 | 0 | 0 | No
2030-11-30 10:00 | 2030 33% ECP | -700 | 205 | 0 | 169.26 | 0 | 0 | No
2030-11-30 11:00 | 2030 33% ECP | -700 | 505 | 0 | 469.26 | 0 | 0 | No
2030-11-30 12:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 13:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 14:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 15:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 16:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 17:00 | 2030 33% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 18:00 | 2030 33% ECP | -627.27 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 19:00 | 2030 33% ECP | -207.27 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 20:00 | 2030 33% ECP | 212.73 | 505 | 300 | 510 | 0 | 0 | No
2030-11-30 21:00 | 2030 33% ECP | 632.73 | 205 | 510 | 219.07 | 0 | 0 | No
2030-11-30 22:00 | 2030 33% ECP | 700 | 111.36 | 501.82 | 381.91 | 0 | 0 | No
2030-11-30 23:00 | 2030 33% ECP | 630.59 | 411.36 | 510 | 510 | 0 | 0 | No
2030-12-01 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 06:00 | 2030 33% ECP | 700 | 205 | 510 | 392.53 | 0 | 0 | No
2030-12-01 07:00 | 2030 33% ECP | 551.21 | 0 | 510 | 285.9 | 0 | 0 | No
2030-12-01 08:00 | 2030 33% ECP | 131.21 | 0 | 510 | 229.99 | 0 | 0 | No
2030-12-01 09:00 | 2030 33% ECP | 403.94 | 0 | 510 | 493.21 | 0 | 0 | No
2030-12-01 10:00 | 2030 33% ECP | 340.66 | 0 | 510 | 510 | 0 | 0 | No
2030-12-01 11:00 | 2030 33% ECP | 0 | 126.25 | 510 | 510 | 0 | 0 | No
2030-12-01 12:00 | 2030 33% ECP | 0 | 7.78 | 510 | 510 | 0 | 0 | No
2030-12-01 13:00 | 2030 33% ECP | 141.86 | 14.2 | 510 | 510 | 0 | 0 | No
2030-12-01 14:00 | 2030 33% ECP | 561.86 | 0 | 390 | 410.42 | 0 | 0 | No
2030-12-01 15:00 | 2030 33% ECP | 141.86 | 300 | 90 | 239.81 | 0 | 0 | No
2030-12-01 16:00 | 2030 33% ECP | -278.14 | 0 | -210 | -60.19 | 0 | 0 | No
2030-12-01 17:00 | 2030 33% ECP | -698.14 | -300 | -510 | -360.19 | 0 | 0 | No
2030-12-01 18:00 | 2030 33% ECP | -278.14 | -300 | -300 | -282.52 | 0 | 0 | No
2030-12-01 19:00 | 2030 33% ECP | 141.86 | 0 | 0 | 17.48 | 0 | 0 | No
2030-12-01 20:00 | 2030 33% ECP | 561.86 | 0 | 300 | 259 | 0 | 0 | No
2030-12-01 21:00 | 2030 33% ECP | 700 | 0 | 117.17 | 0 | 0 | 0 | No
2030-12-01 22:00 | 2030 33% ECP | 524.01 | 0 | 0 | 0 | 0 | 0 | No
2030-12-01 23:00 | 2030 33% ECP | 700 | 0 | -150.81 | 0 | 0 | 0 | No
2030-12-02 | 2030 33% ECP | 700 | 0 | -192.43 | 0 | 0 | 0 | No
2030-12-02 01:00 | 2030 33% ECP | 700 | -152.61 | -492.43 | -300 | 0 | 0 | No
2030-12-02 02:00 | 2030 33% ECP | 665.05 | -452.61 | -510 | -346.85 | 0 | 0 | No
2030-12-02 03:00 | 2030 33% ECP | 420 | -226 | -510 | -359.81 | 0 | 0 | No
2030-12-02 04:00 | 2030 33% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-12-02 05:00 | 2030 33% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-12-02 06:00 | 2030 33% ECP | -280 | -300 | -314.83 | -464.55 | 0 | 0 | No
2030-12-02 07:00 | 2030 33% ECP | -700 | 0 | -14.83 | -164.55 | 0 | 0 | No
2030-12-02 08:00 | 2030 33% ECP | -700 | 300 | 285.17 | 135.45 | 0 | 0 | No
2030-12-02 09:00 | 2030 33% ECP | -700 | 505 | 510 | 435.45 | 0 | 0 | No
2030-12-02 10:00 | 2030 33% ECP | -700 | 448.06 | 510 | 282.28 | 0 | 0 | No
2030-12-02 11:00 | 2030 33% ECP | -700 | 148.06 | 300 | 249.78 | 0 | 0 | No
2030-12-02 12:00 | 2030 33% ECP | -700 | -151.94 | 0 | -50.22 | 0 | 0 | No
2030-12-02 13:00 | 2030 33% ECP | -700 | -13.51 | 0 | -133.7 | 0 | 0 | No
2030-12-02 14:00 | 2030 33% ECP | -700 | 0 | 300 | 166.3 | 0 | 0 | No
2030-12-02 15:00 | 2030 33% ECP | -700 | 0 | 498.7 | 210 | 0 | 0 | No
2030-12-02 16:00 | 2030 33% ECP | -700 | 161.61 | 510 | 510 | 0 | 0 | No
2030-12-02 17:00 | 2030 33% ECP | -700 | 205 | 510 | 389.64 | 0 | 0 | No
2030-12-02 18:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-02 19:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-02 20:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-02 21:00 | 2030 33% ECP | 51.73 | 205 | 510 | 237.61 | 0 | 0 | No
2030-12-02 22:00 | 2030 33% ECP | -368.27 | 505 | 510 | 510 | 0 | 0 | No
2030-12-02 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 01:00 | 2030 33% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 02:00 | 2030 33% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 04:00 | 2030 33% ECP | 361.56 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 05:00 | 2030 33% ECP | -58.44 | 484.28 | 510 | 270.85 | 0 | 0 | No
2030-12-03 06:00 | 2030 33% ECP | -478.44 | 505 | 510 | 268.34 | 0 | 0 | No
2030-12-03 07:00 | 2030 33% ECP | -393.7 | 505 | 510 | 402.58 | 0 | 0 | No
2030-12-03 08:00 | 2030 33% ECP | 0 | 287.25 | 510 | 510 | 0 | 0 | No
2030-12-03 09:00 | 2030 33% ECP | 0 | 0 | 210 | 210 | 0 | 0 | No
2030-12-03 10:00 | 2030 33% ECP | 253.57 | 300 | 510 | 510 | 0 | 0 | No
2030-12-03 11:00 | 2030 33% ECP | 673.57 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 12:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 13:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 14:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 15:00 | 2030 33% ECP | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-12-03 16:00 | 2030 33% ECP | 650.69 | 0 | 210 | 210 | 0 | 0 | No
2030-12-03 17:00 | 2030 33% ECP | 650.69 | 0 | -90 | -90 | 0 | 0 | No
2030-12-03 18:00 | 2030 33% ECP | 650.69 | 205 | 210 | 210 | 0 | 0 | No
2030-12-03 19:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 20:00 | 2030 33% ECP | 700 | 380.64 | 510 | 510 | 0 | 0 | No
2030-12-03 21:00 | 2030 33% ECP | 700 | 474.57 | 510 | 510 | 0 | 0 | No
2030-12-03 22:00 | 2030 33% ECP | 700 | 182.76 | 510 | 510 | 0 | 0 | No
2030-12-03 23:00 | 2030 33% ECP | 700 | 205 | 510 | 210.1 | 0 | 0 | No
2030-12-04 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-04 01:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-12-04 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-04 03:00 | 2030 33% ECP | 586.86 | 505 | 510 | 510 | 0 | 0 | No
2030-12-04 04:00 | 2030 33% ECP | 166.86 | 505 | 510 | 510 | 0 | 0 | No
2030-12-04 05:00 | 2030 33% ECP | -253.14 | 505 | 510 | 274.25 | 0 | 0 | No
2030-12-04 06:00 | 2030 33% ECP | -673.14 | 505 | 510 | -25.75 | 0 | 0 | No
2030-12-04 07:00 | 2030 33% ECP | -700 | 205 | 210 | -325.75 | 0 | 0 | No
2030-12-04 08:00 | 2030 33% ECP | -700 | -95 | -90 | -510 | 0 | 0 | No
2030-12-04 09:00 | 2030 33% ECP | -700 | -395 | -390 | -510 | 0 | 0 | No
2030-12-04 10:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-04 11:00 | 2030 33% ECP | -700 | -300 | -427.97 | -300 | 0 | 0 | No
2030-12-04 12:00 | 2030 33% ECP | -700 | 0 | -127.97 | 0 | 0 | 0 | No
2030-12-04 13:00 | 2030 33% ECP | -700 | 300 | 172.03 | 300 | 0 | 0 | No
2030-12-04 14:00 | 2030 33% ECP | -700 | 300 | 211.02 | 300 | 0 | 0 | No
2030-12-04 15:00 | 2030 33% ECP | -700 | 0 | -88.98 | 0 | 0 | 0 | No
2030-12-04 16:00 | 2030 33% ECP | -700 | -300 | -388.98 | -300 | 0 | 0 | No
2030-12-04 17:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-04 18:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-04 19:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-04 20:00 | 2030 33% ECP | -700 | -226 | -495.76 | -510 | 0 | 0 | No
2030-12-04 21:00 | 2030 33% ECP | -700 | 74 | -195.76 | -210 | 0 | 0 | No
2030-12-04 22:00 | 2030 33% ECP | -700 | 374 | 104.24 | 90 | 0 | 0 | Yes
2030-12-04 23:00 | 2030 33% ECP | -700 | 505 | 404.24 | 267.99 | 0 | 0 | Yes
2030-12-05 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-05 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-05 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-05 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-05 04:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-12-05 05:00 | 2030 33% ECP | -700 | 74 | 90 | 293.99 | 0 | 0 | Yes
2030-12-05 06:00 | 2030 33% ECP | -700 | -226 | -210 | -6.01 | 0 | 0 | Yes
2030-12-05 07:00 | 2030 33% ECP | -700 | -526 | -510 | -66.97 | 0 | 0 | No
2030-12-05 08:00 | 2030 33% ECP | -700 | -526 | -510 | 116.51 | 0 | 0 | No
2030-12-05 09:00 | 2030 33% ECP | -700 | -526 | -510 | -183.49 | 0 | 0 | No
2030-12-05 10:00 | 2030 33% ECP | -700 | -483.98 | -510 | -230.9 | 0 | 0 | No
2030-12-05 11:00 | 2030 33% ECP | -700 | -526 | -510 | 69.1 | 0 | 0 | No
2030-12-05 12:00 | 2030 33% ECP | -700 | -501.03 | -510 | 0 | 0 | 0 | No
2030-12-05 13:00 | 2030 33% ECP | -280 | -242.72 | -510 | -159.9 | 0 | 0 | No
2030-12-05 14:00 | 2030 33% ECP | 0 | 0 | -510 | -46.04 | 0 | 0 | No
2030-12-05 15:00 | 2030 33% ECP | 280.31 | 0 | -236.54 | 0 | 0 | 0 | No
2030-12-05 16:00 | 2030 33% ECP | -139.69 | 0 | -71.89 | 0 | 0 | 0 | No
2030-12-05 17:00 | 2030 33% ECP | -559.69 | -300 | -371.89 | -300 | 0 | 0 | No
2030-12-05 18:00 | 2030 33% ECP | -139.69 | -300 | -128.6 | -262.48 | 0 | 0 | No
2030-12-05 19:00 | 2030 33% ECP | 280.31 | 0 | 171.4 | 37.52 | 0 | 0 | No
2030-12-05 20:00 | 2030 33% ECP | 700 | 300 | 471.4 | 337.52 | 0 | 0 | No
2030-12-05 21:00 | 2030 33% ECP | 700 | 461.99 | 510 | 510 | 0 | 0 | No
2030-12-05 22:00 | 2030 33% ECP | 700 | 253.58 | 510 | 510 | 0 | 0 | No
2030-12-05 23:00 | 2030 33% ECP | 700 | 159.88 | 510 | 510 | 0 | 0 | No
2030-12-06 | 2030 33% ECP | 700 | 459.88 | 510 | 510 | 0 | 0 | No
2030-12-06 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-06 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-06 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-06 04:00 | 2030 33% ECP | 700 | 505 | 510 | 380.35 | 0 | 0 | No
2030-12-06 05:00 | 2030 33% ECP | 700 | 505 | 510 | 80.35 | 0 | 0 | No
2030-12-06 06:00 | 2030 33% ECP | 280 | 505 | 510 | -110 | 0 | 0 | No
2030-12-06 07:00 | 2030 33% ECP | 400.3 | 300 | 219.38 | -288.25 | 0 | 0 | No
2030-12-06 08:00 | 2030 33% ECP | 700 | 0 | -80.62 | -373.21 | 0 | 0 | No
2030-12-06 09:00 | 2030 33% ECP | 700 | 0 | 0 | -73.21 | 0 | 0 | No
2030-12-06 10:00 | 2030 33% ECP | 700 | 0 | -74.52 | 0 | 0 | 0 | No
2030-12-06 11:00 | 2030 33% ECP | 700 | 0 | -239.99 | -204.02 | 0 | 0 | No
2030-12-06 12:00 | 2030 33% ECP | 700 | -41.82 | -510 | -504.02 | 0 | 0 | No
2030-12-06 13:00 | 2030 33% ECP | 700 | -75.69 | -510 | -510 | 0 | 0 | No
2030-12-06 14:00 | 2030 33% ECP | 700 | -20.41 | -510 | -510 | 0 | 0 | No
2030-12-06 15:00 | 2030 33% ECP | 700 | -315.29 | -510 | -510 | 0 | 0 | No
2030-12-06 16:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-06 17:00 | 2030 33% ECP | 700 | -405.42 | -510 | -510 | 0 | 0 | No
2030-12-06 18:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-06 19:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-06 20:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-06 21:00 | 2030 33% ECP | 700 | -300 | -510 | -473.46 | 0 | 0 | No
2030-12-06 22:00 | 2030 33% ECP | 687.33 | 0 | -210 | -173.46 | 0 | 0 | No
2030-12-06 23:00 | 2030 33% ECP | 700 | 300 | 90 | 126.54 | 0 | 0 | No
2030-12-07 | 2030 33% ECP | 700 | 294.64 | 390 | 0 | 0 | 0 | No
2030-12-07 01:00 | 2030 33% ECP | 700 | 205 | 510 | 0 | 0 | 0 | No
2030-12-07 02:00 | 2030 33% ECP | 700 | 505 | 510 | 152.91 | 0 | 0 | No
2030-12-07 03:00 | 2030 33% ECP | 560 | 505 | 510 | 322.35 | 0 | 0 | No
2030-12-07 04:00 | 2030 33% ECP | 140 | 505 | 510 | 22.35 | 0 | 0 | No
2030-12-07 05:00 | 2030 33% ECP | -280 | 205 | 510 | 0 | 0 | 0 | No
2030-12-07 06:00 | 2030 33% ECP | -700 | 296.4 | 300 | 0 | 0 | 0 | No
2030-12-07 07:00 | 2030 33% ECP | -700 | 0 | 0 | -300 | 0 | 0 | No
2030-12-07 08:00 | 2030 33% ECP | -700 | 0 | -300 | -328.45 | 0 | 0 | No
2030-12-07 09:00 | 2030 33% ECP | -700 | 0 | -90 | -147.69 | 0 | 0 | No
2030-12-07 10:00 | 2030 33% ECP | -700 | 205 | 210 | -41.24 | 0 | 0 | No
2030-12-07 11:00 | 2030 33% ECP | -700 | 505 | 510 | 249.01 | 0 | 0 | No
2030-12-07 12:00 | 2030 33% ECP | -700 | 482.89 | 510 | 157.51 | 0 | 0 | No
2030-12-07 13:00 | 2030 33% ECP | -700 | 505 | 300 | 160.55 | 0 | 0 | No
2030-12-07 14:00 | 2030 33% ECP | -435.75 | 505 | 0 | 107.37 | 0 | 0 | No
2030-12-07 15:00 | 2030 33% ECP | -15.75 | 505 | 0 | 109.77 | 0 | 0 | No
2030-12-07 16:00 | 2030 33% ECP | -296.22 | 505 | 0 | 77.62 | 0 | 0 | No
2030-12-07 17:00 | 2030 33% ECP | 123.78 | 505 | 0 | 175.89 | 0 | 0 | No
2030-12-07 18:00 | 2030 33% ECP | 543.78 | 505 | 0 | 428.95 | 0 | 0 | No
2030-12-07 19:00 | 2030 33% ECP | 700 | 292.44 | 0 | 325.18 | 0 | 0 | No
2030-12-07 20:00 | 2030 33% ECP | 674.34 | 505 | 0 | 383.27 | 0 | 0 | No
2030-12-07 21:00 | 2030 33% ECP | 630.73 | 505 | 0 | 510 | 0 | 0 | No
2030-12-07 22:00 | 2030 33% ECP | 482.16 | 505 | 0 | 484.52 | 0 | 0 | No
2030-12-07 23:00 | 2030 33% ECP | 700 | 432.04 | 0 | 357.11 | 0 | 0 | No
2030-12-08 | 2030 33% ECP | 700 | 132.04 | 0 | 220.24 | 0 | 0 | No
2030-12-08 01:00 | 2030 33% ECP | 700 | 175.85 | 0 | 102.29 | 0 | 0 | No
2030-12-08 02:00 | 2030 33% ECP | 441.43 | 255.57 | 0 | 390 | 0 | 0 | No
2030-12-08 03:00 | 2030 33% ECP | 21.43 | 0 | 0 | 90 | 0 | 0 | No
2030-12-08 04:00 | 2030 33% ECP | -398.57 | -226 | 0 | -210 | 0 | 0 | No
2030-12-08 05:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 06:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 07:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 08:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 09:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 10:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 11:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 12:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 13:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 14:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 15:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 16:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 17:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 18:00 | 2030 33% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 19:00 | 2030 33% ECP | -472.96 | -226 | 0 | -210 | 0 | 0 | No
2030-12-08 20:00 | 2030 33% ECP | -52.96 | 74 | 0 | 90 | 0 | 0 | No
2030-12-08 21:00 | 2030 33% ECP | 245.17 | 232.98 | 0 | 381.82 | 0 | 0 | No
2030-12-08 22:00 | 2030 33% ECP | 665.17 | 0 | 0 | 81.82 | 0 | 0 | No
2030-12-08 23:00 | 2030 33% ECP | 526.81 | 0 | 0 | -218.18 | 0 | 0 | No
2030-12-09 | 2030 33% ECP | 700 | 300 | 0 | -101.12 | 0 | 0 | No
2030-12-09 01:00 | 2030 33% ECP | 700 | 281.77 | 0 | -401.12 | 0 | 0 | No
2030-12-09 02:00 | 2030 33% ECP | 700 | 143.38 | 0 | -401.12 | 0 | 0 | No
2030-12-09 03:00 | 2030 33% ECP | 700 | 202.41 | 0 | -150.52 | 0 | 0 | No
2030-12-09 04:00 | 2030 33% ECP | 700 | 67.4 | 0 | 149.48 | 0 | 0 | No
2030-12-09 05:00 | 2030 33% ECP | 700 | 0 | 0 | 256.86 | 0 | 0 | No
2030-12-09 06:00 | 2030 33% ECP | 700 | 0 | 0 | 77.98 | 0 | 0 | No
2030-12-09 07:00 | 2030 33% ECP | 585.08 | 0 | 0 | 0 | 0 | 0 | No
2030-12-09 08:00 | 2030 33% ECP | 165.08 | 0 | 0 | 78.8 | 0 | 0 | No
2030-12-09 09:00 | 2030 33% ECP | -254.92 | -226 | 0 | 242.22 | 0 | 0 | No
2030-12-09 10:00 | 2030 33% ECP | -674.92 | -526 | 0 | -57.78 | 0 | 0 | No
2030-12-09 11:00 | 2030 33% ECP | -700 | -526 | 0 | -14.54 | 0 | 0 | No
2030-12-09 12:00 | 2030 33% ECP | -280 | -257.94 | 0 | 285.46 | 0 | 0 | No
2030-12-09 13:00 | 2030 33% ECP | 140 | 0 | 0 | 60.8 | 0 | 0 | No
2030-12-09 14:00 | 2030 33% ECP | 420 | 0 | 0 | 0 | 0 | 0 | No
2030-12-09 15:00 | 2030 33% ECP | 0 | -71.91 | -210 | -86.9 | 0 | 0 | No
2030-12-09 16:00 | 2030 33% ECP | -420 | -371.91 | -510 | -386.9 | 0 | 0 | No
2030-12-09 17:00 | 2030 33% ECP | 0 | -71.91 | -210 | -86.9 | 0 | 0 | No
2030-12-09 18:00 | 2030 33% ECP | 420 | 228.09 | 90 | 213.1 | 0 | 0 | No
2030-12-09 19:00 | 2030 33% ECP | 700 | 0 | -23.25 | 20.18 | 0 | 0 | No
2030-12-09 20:00 | 2030 33% ECP | 700 | 0 | 209.21 | 31.67 | 0 | 0 | No
2030-12-09 21:00 | 2030 33% ECP | 700 | 0 | -0.32 | 0 | 0 | 0 | No
2030-12-09 22:00 | 2030 33% ECP | 466.14 | 49.23 | 210 | 210 | 0 | 0 | No
2030-12-09 23:00 | 2030 33% ECP | 700 | 349.23 | 510 | 510 | 0 | 0 | No
2030-12-10 | 2030 33% ECP | 700 | 293.7 | 510 | 510 | 0 | 0 | No
2030-12-10 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 05:00 | 2030 33% ECP | 580.47 | 205 | 210 | 210 | 0 | 0 | No
2030-12-10 06:00 | 2030 33% ECP | 700 | 0 | 510 | 244.4 | 0 | 0 | No
2030-12-10 07:00 | 2030 33% ECP | 418.77 | 267.98 | 510 | 510 | 0 | 0 | No
2030-12-10 08:00 | 2030 33% ECP | 330.03 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 09:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 10:00 | 2030 33% ECP | 0 | 344.03 | 390 | 510 | 0 | 0 | No
2030-12-10 11:00 | 2030 33% ECP | -280 | 44.03 | 90 | 510 | 0 | 0 | No
2030-12-10 12:00 | 2030 33% ECP | -700 | -255.97 | -210 | 280.91 | 0 | 0 | No
2030-12-10 13:00 | 2030 33% ECP | -700 | -526 | -510 | 71.42 | 0 | 0 | No
2030-12-10 14:00 | 2030 33% ECP | -700 | -526 | -510 | -107.9 | 0 | 0 | No
2030-12-10 15:00 | 2030 33% ECP | -700 | -344.77 | -510 | 74.49 | 0 | 0 | No
2030-12-10 16:00 | 2030 33% ECP | -700 | -325.71 | -390 | 238.73 | 0 | 0 | No
2030-12-10 17:00 | 2030 33% ECP | -700 | -25.71 | -90 | 510 | 0 | 0 | No
2030-12-10 18:00 | 2030 33% ECP | -280 | 236.62 | 210 | 510 | 0 | 0 | No
2030-12-10 19:00 | 2030 33% ECP | 140 | 419.43 | 510 | 510 | 0 | 0 | No
2030-12-10 20:00 | 2030 33% ECP | 560 | 205 | 303.77 | 482.16 | 0 | 0 | No
2030-12-10 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 05:00 | 2030 33% ECP | 578.34 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 06:00 | 2030 33% ECP | 578.34 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 07:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-12-11 08:00 | 2030 33% ECP | 342.21 | 460.02 | 510 | 510 | 0 | 0 | No
2030-12-11 09:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 10:00 | 2030 33% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 11:00 | 2030 33% ECP | 140 | 431.46 | 510 | 510 | 0 | 0 | No
2030-12-11 12:00 | 2030 33% ECP | -280 | 320.01 | 510 | 510 | 0 | 0 | No
2030-12-11 13:00 | 2030 33% ECP | -700 | 244.46 | 510 | 510 | 0 | 0 | No
2030-12-11 14:00 | 2030 33% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-12-11 15:00 | 2030 33% ECP | -700 | 74 | 90 | 273.63 | 0 | 0 | No
2030-12-11 16:00 | 2030 33% ECP | -501.04 | -226 | -210 | 412.55 | 0 | 0 | No
2030-12-11 17:00 | 2030 33% ECP | -81.04 | -526 | -510 | 376.05 | 0 | 0 | No
2030-12-11 18:00 | 2030 33% ECP | -81.04 | -526 | -510 | 300 | 0 | 0 | No
2030-12-11 19:00 | 2030 33% ECP | 280 | -526 | -510 | 0 | 0 | 0 | No
2030-12-11 20:00 | 2030 33% ECP | 700 | -385.58 | -510 | 149.39 | 0 | 0 | No
2030-12-11 21:00 | 2030 33% ECP | 700 | -85.58 | -210 | 209.46 | 0 | 0 | No
2030-12-11 22:00 | 2030 33% ECP | 700 | -152.18 | -510 | 81.54 | 0 | 0 | No
2030-12-11 23:00 | 2030 33% ECP | 700 | 0 | -469.39 | 0 | 0 | 0 | No
2030-12-12 | 2030 33% ECP | 700 | 0 | -169.39 | 0 | 0 | 0 | No
2030-12-12 01:00 | 2030 33% ECP | 700 | 0 | 130.61 | 0 | 0 | 0 | No
2030-12-12 02:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-12 03:00 | 2030 33% ECP | 700 | 0 | 59.3 | 0 | 0 | 0 | No
2030-12-12 04:00 | 2030 33% ECP | 700 | 0 | 38.1 | 0 | 0 | 0 | No
2030-12-12 05:00 | 2030 33% ECP | 628.57 | 0 | 0 | 0 | 0 | 0 | No
2030-12-12 06:00 | 2030 33% ECP | 208.57 | 0 | -210 | -177.38 | 0 | 0 | No
2030-12-12 07:00 | 2030 33% ECP | -211.43 | -300 | -510 | -477.38 | 0 | 0 | No
2030-12-12 08:00 | 2030 33% ECP | 208.57 | 0 | -510 | -437.59 | 0 | 0 | No
2030-12-12 09:00 | 2030 33% ECP | 628.57 | 0 | -510 | -317.93 | 0 | 0 | No
2030-12-12 10:00 | 2030 33% ECP | 700 | 0 | -510 | -484.08 | 0 | 0 | No
2030-12-12 11:00 | 2030 33% ECP | 700 | 0 | -510 | -191.03 | 0 | 0 | No
2030-12-12 12:00 | 2030 33% ECP | 584.51 | 0 | -494.86 | -129.17 | 0 | 0 | No
2030-12-12 13:00 | 2030 33% ECP | 700 | 0 | -194.86 | 0 | 0 | 0 | No
2030-12-12 14:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-12 15:00 | 2030 33% ECP | 700 | 54.37 | 0 | 0 | 0 | 0 | No
2030-12-12 16:00 | 2030 33% ECP | 700 | -245.63 | -300 | -300 | 0 | 0 | No
2030-12-12 17:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 18:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 19:00 | 2030 33% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 20:00 | 2030 33% ECP | 465.08 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 21:00 | 2030 33% ECP | 45.08 | -526 | -510 | -369.83 | 0 | 0 | No
2030-12-12 22:00 | 2030 33% ECP | -125.9 | -526 | -510 | -241.37 | 0 | 0 | No
2030-12-12 23:00 | 2030 33% ECP | -545.9 | -526 | -510 | -44.68 | 0 | 0 | No
2030-12-13 | 2030 33% ECP | -700 | -526 | -510 | 84.39 | 0 | 0 | No
2030-12-13 01:00 | 2030 33% ECP | -700 | -526 | -510 | -21.12 | 0 | 0 | No
2030-12-13 02:00 | 2030 33% ECP | -700 | -526 | -510 | -95.36 | 0 | 0 | No
2030-12-13 03:00 | 2030 33% ECP | -700 | -526 | -510 | -67.25 | 0 | 0 | No
2030-12-13 04:00 | 2030 33% ECP | -700 | -526 | -510 | -367.25 | 0 | 0 | No
2030-12-13 05:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-13 06:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-13 07:00 | 2030 33% ECP | -700 | -465.84 | -510 | -510 | 0 | 0 | No
2030-12-13 08:00 | 2030 33% ECP | -700 | -321.14 | -510 | -510 | 0 | 0 | No
2030-12-13 09:00 | 2030 33% ECP | -280 | -321.14 | -510 | -265.24 | 0 | 0 | No
2030-12-13 10:00 | 2030 33% ECP | -73.99 | -149.53 | -300 | 34.76 | 0 | 0 | No
2030-12-13 11:00 | 2030 33% ECP | -493.99 | 0 | 0 | 334.76 | 0 | 0 | No
2030-12-13 12:00 | 2030 33% ECP | -700 | 0 | -58.36 | 210 | 0 | 0 | No
2030-12-13 13:00 | 2030 33% ECP | -700 | 300 | 241.64 | 510 | 0 | 0 | No
2030-12-13 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-13 15:00 | 2030 33% ECP | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-12-13 16:00 | 2030 33% ECP | -700 | -95 | -90 | 370.43 | 0 | 0 | No
2030-12-13 17:00 | 2030 33% ECP | -341.69 | -395 | -390 | 376.91 | 0 | 0 | No
2030-12-13 18:00 | 2030 33% ECP | -341.69 | -526 | -510 | 477.59 | 0 | 0 | No
2030-12-13 19:00 | 2030 33% ECP | -167.26 | -526 | -510 | 427.7 | 0 | 0 | No
2030-12-13 20:00 | 2030 33% ECP | -490.65 | -300 | -390 | 191.89 | 0 | 0 | No
2030-12-13 21:00 | 2030 33% ECP | -70.65 | 0 | -90 | 248.76 | 0 | 0 | No
2030-12-13 22:00 | 2030 33% ECP | -490.65 | 300 | 210 | 510 | 0 | 0 | No
2030-12-13 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-14 | 2030 33% ECP | -422.35 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 01:00 | 2030 33% ECP | -2.35 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 02:00 | 2030 33% ECP | -420 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 03:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 04:00 | 2030 33% ECP | -163.24 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 05:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 08:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 14:00 | 2030 33% ECP | -700 | 205 | 210 | 408.92 | 0 | 0 | No
2030-12-14 15:00 | 2030 33% ECP | -700 | -95 | -90 | 379.33 | 0 | 0 | No
2030-12-14 16:00 | 2030 33% ECP | -280 | -395 | -390 | 79.33 | 0 | 0 | No
2030-12-14 17:00 | 2030 33% ECP | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-12-14 18:00 | 2030 33% ECP | 189.92 | -526 | -510 | 195.96 | 0 | 0 | No
2030-12-14 19:00 | 2030 33% ECP | 189.92 | -526 | -510 | 85.07 | 0 | 0 | No
2030-12-14 20:00 | 2030 33% ECP | 360.04 | -382.72 | -510 | 109.92 | 0 | 0 | No
2030-12-14 21:00 | 2030 33% ECP | 0 | -82.72 | -502.66 | 409.92 | 0 | 0 | No
2030-12-14 22:00 | 2030 33% ECP | 0 | 0 | -202.66 | 220.18 | 0 | 0 | No
2030-12-14 23:00 | 2030 33% ECP | 420 | 300 | 97.34 | 510 | 0 | 0 | No
2030-12-15 | 2030 33% ECP | 700 | 505 | 397.34 | 510 | 0 | 0 | No
2030-12-15 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 05:00 | 2030 33% ECP | 616.42 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 06:00 | 2030 33% ECP | 196.42 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 07:00 | 2030 33% ECP | -223.58 | 205 | 210 | 210 | 0 | 0 | No
2030-12-15 08:00 | 2030 33% ECP | -524.73 | -95 | -90 | 331.69 | 0 | 0 | No
2030-12-15 09:00 | 2030 33% ECP | -104.73 | -395 | -390 | 496.33 | 0 | 0 | No
2030-12-15 10:00 | 2030 33% ECP | 315.27 | -526 | -510 | 510 | 0 | 0 | No
2030-12-15 11:00 | 2030 33% ECP | 493.45 | -300 | -510 | 510 | 0 | 0 | No
2030-12-15 12:00 | 2030 33% ECP | 73.45 | 0 | -393.2 | 510 | 0 | 0 | No
2030-12-15 13:00 | 2030 33% ECP | 0 | -123.93 | -510 | 510 | 0 | 0 | No
2030-12-15 14:00 | 2030 33% ECP | 214.39 | -423.93 | -510 | 487.81 | 0 | 0 | No
2030-12-15 15:00 | 2030 33% ECP | 587.5 | -526 | -510 | 222.18 | 0 | 0 | No
2030-12-15 16:00 | 2030 33% ECP | 700 | -526 | -510 | 502.36 | 0 | 0 | No
2030-12-15 17:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-12-15 18:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-12-15 19:00 | 2030 33% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-12-15 20:00 | 2030 33% ECP | 427.85 | -526 | -510 | 510 | 0 | 0 | No
2030-12-15 21:00 | 2030 33% ECP | 140 | -300 | -363.46 | 460.56 | 0 | 0 | No
2030-12-15 22:00 | 2030 33% ECP | -280 | 0 | -63.46 | 510 | 0 | 0 | No
2030-12-15 23:00 | 2030 33% ECP | -700 | 0 | 89.93 | 314 | 0 | 0 | No
2030-12-16 | 2030 33% ECP | -700 | 205 | 256.69 | 383.12 | 0 | 0 | No
2030-12-16 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 02:00 | 2030 33% ECP | -700 | 505 | 510 | 300.04 | 0 | 0 | Yes
2030-12-16 03:00 | 2030 33% ECP | -700 | 505 | 510 | 0.04 | 0 | 0 | Yes
2030-12-16 04:00 | 2030 33% ECP | -700 | 505 | 510 | 249.87 | 0 | 0 | Yes
2030-12-16 05:00 | 2030 33% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-12-16 06:00 | 2030 33% ECP | -700 | 505 | 510 | 218.24 | 0 | 0 | Yes
2030-12-16 07:00 | 2030 33% ECP | -700 | 505 | 510 | 235.08 | 0 | 0 | Yes
2030-12-16 08:00 | 2030 33% ECP | -700 | 505 | 510 | 381.96 | 0 | 0 | Yes
2030-12-16 09:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 10:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 11:00 | 2030 33% ECP | -549.16 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 12:00 | 2030 33% ECP | -129.16 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 13:00 | 2030 33% ECP | 290.84 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 14:00 | 2030 33% ECP | 389.88 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 15:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 16:00 | 2030 33% ECP | 692.99 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 17:00 | 2030 33% ECP | 272.99 | 205 | 210 | 510 | 0 | 0 | No
2030-12-16 18:00 | 2030 33% ECP | 280 | 205 | 210 | 510 | 0 | 0 | No
2030-12-16 19:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 20:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 05:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 06:00 | 2030 33% ECP | -140 | 280.3 | 210 | 510 | 0 | 0 | No
2030-12-17 07:00 | 2030 33% ECP | -126.52 | -19.7 | -90 | 426.77 | 0 | 0 | No
2030-12-17 08:00 | 2030 33% ECP | -546.52 | 0 | -390 | 510 | 0 | 0 | No
2030-12-17 09:00 | 2030 33% ECP | -126.52 | 0 | -90 | 510 | 0 | 0 | No
2030-12-17 10:00 | 2030 33% ECP | 0 | -209.7 | -340.38 | 510 | 0 | 0 | No
2030-12-17 11:00 | 2030 33% ECP | -420 | -509.7 | -510 | 510 | 0 | 0 | No
2030-12-17 12:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-12-17 13:00 | 2030 33% ECP | -700 | -526 | -510 | 488.19 | 0 | 0 | No
2030-12-17 14:00 | 2030 33% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-12-17 15:00 | 2030 33% ECP | -700 | -490.14 | -510 | 510 | 0 | 0 | No
2030-12-17 16:00 | 2030 33% ECP | -700 | -526 | -510 | 447.5 | 0 | 0 | No
2030-12-17 17:00 | 2030 33% ECP | -700 | -226 | -390 | 365.15 | 0 | 0 | No
2030-12-17 18:00 | 2030 33% ECP | -280 | 0 | -390 | 65.15 | 0 | 0 | No
2030-12-17 19:00 | 2030 33% ECP | 140 | 0 | -90 | 144.28 | 0 | 0 | No
2030-12-17 20:00 | 2030 33% ECP | 126.64 | 205 | 210 | 210 | 0 | 0 | No
2030-12-17 21:00 | 2030 33% ECP | 546.64 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 01:00 | 2030 33% ECP | 521.77 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 02:00 | 2030 33% ECP | 101.77 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 03:00 | 2030 33% ECP | -34.25 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 04:00 | 2030 33% ECP | -454.25 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 05:00 | 2030 33% ECP | -629.8 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 06:00 | 2030 33% ECP | -700 | 505 | 367.99 | 510 | 0 | 0 | No
2030-12-18 07:00 | 2030 33% ECP | -700 | 205 | 67.99 | 210 | 0 | 0 | No
2030-12-18 08:00 | 2030 33% ECP | -700 | -95 | -232.01 | -90 | 0 | 0 | No
2030-12-18 09:00 | 2030 33% ECP | -700 | 0 | -90 | -90 | 0 | 0 | No
2030-12-18 10:00 | 2030 33% ECP | -700 | 159.82 | 210 | 210 | 0 | 0 | No
2030-12-18 11:00 | 2030 33% ECP | -280 | 459.82 | 510 | 510 | 0 | 0 | No
2030-12-18 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 13:00 | 2030 33% ECP | -324.05 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 14:00 | 2030 33% ECP | -203.18 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 15:00 | 2030 33% ECP | -77.95 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 16:00 | 2030 33% ECP | 250.83 | 205 | 210 | 510 | 0 | 0 | No
2030-12-18 17:00 | 2030 33% ECP | 250.83 | -95 | -90 | 510 | 0 | 0 | No
2030-12-18 18:00 | 2030 33% ECP | 670.83 | -395 | -390 | 510 | 0 | 0 | No
2030-12-18 19:00 | 2030 33% ECP | 670.83 | -300 | -183.02 | 510 | 0 | 0 | No
2030-12-18 20:00 | 2030 33% ECP | 700 | 0 | 116.98 | 510 | 0 | 0 | No
2030-12-18 21:00 | 2030 33% ECP | 696.56 | 300 | 416.98 | 510 | 0 | 0 | No
2030-12-18 22:00 | 2030 33% ECP | 276.56 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 23:00 | 2030 33% ECP | -143.44 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 01:00 | 2030 33% ECP | -70.32 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 02:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 03:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 06:00 | 2030 33% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 07:00 | 2030 33% ECP | -449.5 | 205 | 300 | 259.95 | 0 | 0 | No
2030-12-19 08:00 | 2030 33% ECP | -666.21 | 0 | 0 | 60.08 | 0 | 0 | No
2030-12-19 09:00 | 2030 33% ECP | -246.21 | 0 | 0 | 343.54 | 0 | 0 | No
2030-12-19 10:00 | 2030 33% ECP | -666.21 | 205 | 210 | 210 | 0 | 0 | No
2030-12-19 11:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 12:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 13:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 15:00 | 2030 33% ECP | -601 | 400.47 | 510 | 510 | 0 | 0 | No
2030-12-19 16:00 | 2030 33% ECP | -503.8 | 100.47 | 210 | 210 | 0 | 0 | No
2030-12-19 17:00 | 2030 33% ECP | -440.91 | -199.53 | -90 | 343.3 | 0 | 0 | No
2030-12-19 18:00 | 2030 33% ECP | -438.99 | -395 | -390 | 510 | 0 | 0 | No
2030-12-19 19:00 | 2030 33% ECP | -140 | -95 | -90 | 210 | 0 | 0 | No
2030-12-19 20:00 | 2030 33% ECP | 280 | 205 | 210 | 434.22 | 0 | 0 | No
2030-12-19 21:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 04:00 | 2030 33% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 05:00 | 2030 33% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 06:00 | 2030 33% ECP | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 08:00 | 2030 33% ECP | -700 | 205 | 210 | 494.55 | 0 | 0 | No
2030-12-20 09:00 | 2030 33% ECP | -370.56 | 0 | 0 | 510 | 0 | 0 | No
2030-12-20 10:00 | 2030 33% ECP | -280 | 0 | 274.57 | 510 | 0 | 0 | No
2030-12-20 11:00 | 2030 33% ECP | -700 | 0 | -25.43 | 332.12 | 0 | 0 | No
2030-12-20 12:00 | 2030 33% ECP | -700 | 0 | -256.04 | 256.07 | 0 | 0 | No
2030-12-20 13:00 | 2030 33% ECP | -700 | 0 | -435.25 | 344.11 | 0 | 0 | No
2030-12-20 14:00 | 2030 33% ECP | -700 | 0 | -135.25 | 373.72 | 0 | 0 | No
2030-12-20 15:00 | 2030 33% ECP | -280 | 0 | -435.25 | 172.8 | 0 | 0 | No
2030-12-20 16:00 | 2030 33% ECP | -140.95 | 0 | -510 | 0 | 0 | 0 | No
2030-12-20 17:00 | 2030 33% ECP | -420 | 0 | -404.2 | 0 | 0 | 0 | No
2030-12-20 18:00 | 2030 33% ECP | 0 | 0 | -104.2 | 0 | 0 | 0 | No
2030-12-20 19:00 | 2030 33% ECP | 420 | 0 | -390 | 0 | 0 | 0 | No
2030-12-20 20:00 | 2030 33% ECP | 700 | 0 | -90 | 0 | 0 | 0 | No
2030-12-20 21:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-12-20 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 07:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-12-21 08:00 | 2030 33% ECP | 700 | -76.95 | -90 | 342.65 | 0 | 0 | No
2030-12-21 09:00 | 2030 33% ECP | 700 | 0 | 0 | 377.38 | 0 | 0 | No
2030-12-21 10:00 | 2030 33% ECP | 700 | 0 | 190.05 | 440.68 | 0 | 0 | No
2030-12-21 11:00 | 2030 33% ECP | 700 | 0 | 0 | 440.68 | 0 | 0 | No
2030-12-21 12:00 | 2030 33% ECP | 700 | -31.75 | -300 | 382.12 | 0 | 0 | No
2030-12-21 13:00 | 2030 33% ECP | 700 | 0 | -112.57 | 487.63 | 0 | 0 | No
2030-12-21 14:00 | 2030 33% ECP | 700 | 0 | 0 | 387.05 | 0 | 0 | No
2030-12-21 15:00 | 2030 33% ECP | 700 | 0 | 0 | 348.92 | 0 | 0 | No
2030-12-21 16:00 | 2030 33% ECP | 700 | 0 | -137.96 | 303.5 | 0 | 0 | No
2030-12-21 17:00 | 2030 33% ECP | 700 | 0 | 0 | 329 | 0 | 0 | No
2030-12-21 18:00 | 2030 33% ECP | 700 | 0 | 0 | 459.6 | 0 | 0 | No
2030-12-21 19:00 | 2030 33% ECP | 700 | 0 | 143.24 | 459.6 | 0 | 0 | No
2030-12-21 20:00 | 2030 33% ECP | 700 | 0 | 143.24 | 510 | 0 | 0 | No
2030-12-21 21:00 | 2030 33% ECP | 700 | 0 | 294.66 | 510 | 0 | 0 | No
2030-12-21 22:00 | 2030 33% ECP | 700 | 205 | 210 | 390.11 | 0 | 0 | No
2030-12-21 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 01:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 02:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 03:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 04:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 05:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 06:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 07:00 | 2030 33% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-12-22 08:00 | 2030 33% ECP | 700 | 0 | 210 | 0 | 0 | 0 | No
2030-12-22 09:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-22 10:00 | 2030 33% ECP | 700 | 0 | 450.88 | 0 | 0 | 0 | No
2030-12-22 11:00 | 2030 33% ECP | 700 | 0 | 510 | 70 | 0 | 0 | No
2030-12-22 12:00 | 2030 33% ECP | 700 | 0 | 481.78 | 0 | 0 | 0 | No
2030-12-22 13:00 | 2030 33% ECP | 700 | 0 | 410.11 | 60 | 0 | 0 | No
2030-12-22 14:00 | 2030 33% ECP | 700 | 0 | 118.02 | 97.75 | 0 | 0 | No
2030-12-22 15:00 | 2030 33% ECP | 700 | 0 | -56.99 | 274.71 | 0 | 0 | No
2030-12-22 16:00 | 2030 33% ECP | 700 | -300 | -356.99 | -25.29 | 0 | 0 | No
2030-12-22 17:00 | 2030 33% ECP | 700 | -526 | -510 | -168.7 | 0 | 0 | No
2030-12-22 18:00 | 2030 33% ECP | 700 | -526 | -510 | -79.66 | 0 | 0 | No
2030-12-22 19:00 | 2030 33% ECP | 700 | -526 | -510 | -41.98 | 0 | 0 | No
2030-12-22 20:00 | 2030 33% ECP | 700 | -526 | -510 | -256.17 | 0 | 0 | No
2030-12-22 21:00 | 2030 33% ECP | 700 | -526 | -510 | 43.83 | 0 | 0 | No
2030-12-22 22:00 | 2030 33% ECP | 700 | -226 | -429.4 | 343.83 | 0 | 0 | No
2030-12-22 23:00 | 2030 33% ECP | 700 | -325.73 | -510 | 236.9 | 0 | 0 | No
2030-12-23 | 2030 33% ECP | 700 | -499.33 | -510 | 179.46 | 0 | 0 | No
2030-12-23 01:00 | 2030 33% ECP | 700 | -526 | -510 | -20.08 | 0 | 0 | No
2030-12-23 02:00 | 2030 33% ECP | 700 | -526 | -510 | 52.7 | 0 | 0 | No
2030-12-23 03:00 | 2030 33% ECP | 700 | -526 | -510 | 102.41 | 0 | 0 | No
2030-12-23 04:00 | 2030 33% ECP | 700 | -526 | -510 | 13.3 | 0 | 0 | No
2030-12-23 05:00 | 2030 33% ECP | 613.86 | -526 | -510 | 210 | 0 | 0 | No
2030-12-23 06:00 | 2030 33% ECP | 193.86 | -322.14 | -510 | 510 | 0 | 0 | No
2030-12-23 07:00 | 2030 33% ECP | 474.5 | -526 | -510 | 388.86 | 0 | 0 | No
2030-12-23 08:00 | 2030 33% ECP | 425.73 | -526 | -510 | 88.86 | 0 | 0 | No
2030-12-23 09:00 | 2030 33% ECP | 440.67 | -526 | -510 | 0 | 0 | 0 | No
2030-12-23 10:00 | 2030 33% ECP | 397.82 | -526 | -510 | -241.97 | 0 | 0 | No
2030-12-23 11:00 | 2030 33% ECP | 0 | -258.7 | -510 | -192.39 | 0 | 0 | No
2030-12-23 12:00 | 2030 33% ECP | -215.22 | -526 | -510 | 107.61 | 0 | 0 | No
2030-12-23 13:00 | 2030 33% ECP | -635.22 | -226 | -210 | 407.61 | 0 | 0 | No
2030-12-23 14:00 | 2030 33% ECP | -700 | -98.52 | -510 | 248.3 | 0 | 0 | No
2030-12-23 15:00 | 2030 33% ECP | -700 | 0 | -456.65 | 154.36 | 0 | 0 | No
2030-12-23 16:00 | 2030 33% ECP | -602.26 | -53.46 | -510 | 106.2 | 0 | 0 | No
2030-12-23 17:00 | 2030 33% ECP | -182.26 | -253.13 | -510 | 210 | 0 | 0 | No
2030-12-23 18:00 | 2030 33% ECP | 46.98 | 0 | -210 | 510 | 0 | 0 | No
2030-12-23 19:00 | 2030 33% ECP | 0 | 0 | 82.56 | 226.09 | 0 | 0 | No
2030-12-23 20:00 | 2030 33% ECP | 0 | 0 | 103 | 406.74 | 0 | 0 | No
2030-12-23 21:00 | 2030 33% ECP | -248.24 | 205 | 339.2 | 510 | 0 | 0 | No
2030-12-23 22:00 | 2030 33% ECP | -315.79 | 505 | 510 | 510 | 0 | 0 | No
2030-12-23 23:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 | 2030 33% ECP | -588.87 | 505 | 510 | 510 | 0 | 0 | No
2030-12-24 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 04:00 | 2030 33% ECP | -630.42 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 06:00 | 2030 33% ECP | -420 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 07:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 08:00 | 2030 33% ECP | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 09:00 | 2030 33% ECP | 0 | 475.62 | 510 | 345.79 | 0 | 0 | No
2030-12-24 10:00 | 2030 33% ECP | 420 | 478.06 | 510 | 510 | 0 | 0 | No
2030-12-24 11:00 | 2030 33% ECP | 0 | 178.06 | 210 | 510 | 0 | 0 | No
2030-12-24 12:00 | 2030 33% ECP | -354.99 | 0 | 0 | 510 | 0 | 0 | No
2030-12-24 13:00 | 2030 33% ECP | 0 | 0 | 168.62 | 231.36 | 0 | 0 | No
2030-12-24 14:00 | 2030 33% ECP | 0 | 0 | 107.85 | 442.56 | 0 | 0 | No
2030-12-24 15:00 | 2030 33% ECP | 420 | 0 | 345.28 | 510 | 0 | 0 | No
2030-12-24 16:00 | 2030 33% ECP | 700 | 0 | 274.48 | 383.94 | 0 | 0 | No
2030-12-24 17:00 | 2030 33% ECP | 700 | 0 | 510 | 438.59 | 0 | 0 | No
2030-12-24 18:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-12-24 19:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-12-24 20:00 | 2030 33% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-12-24 21:00 | 2030 33% ECP | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-12-24 22:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-24 23:00 | 2030 33% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-25 | 2030 33% ECP | 700 | 396.34 | 510 | 510 | 0 | 0 | No
2030-12-25 01:00 | 2030 33% ECP | 700 | 345.66 | 510 | 510 | 0 | 0 | No
2030-12-25 02:00 | 2030 33% ECP | 524.59 | 505 | 510 | 510 | 0 | 0 | No
2030-12-25 03:00 | 2030 33% ECP | 104.59 | 505 | 510 | 510 | 0 | 0 | No
2030-12-25 04:00 | 2030 33% ECP | 0 | 228 | 510 | 510 | 0 | 0 | No
2030-12-25 05:00 | 2030 33% ECP | 0 | 300 | 286.14 | 387.66 | 0 | 0 | No
2030-12-25 06:00 | 2030 33% ECP | 416.08 | 0 | -13.86 | 87.66 | 0 | 0 | No
2030-12-25 07:00 | 2030 33% ECP | 700 | 0 | -221.16 | 9.09 | 0 | 0 | No
2030-12-25 08:00 | 2030 33% ECP | 700 | 0 | -200.76 | 52.47 | 0 | 0 | No
2030-12-25 09:00 | 2030 33% ECP | 700 | 0 | -223.12 | 124.65 | 0 | 0 | No
2030-12-25 10:00 | 2030 33% ECP | 700 | 0 | -213.86 | 38.95 | 0 | 0 | No
2030-12-25 11:00 | 2030 33% ECP | 700 | 0 | -510 | 263.53 | 0 | 0 | No
2030-12-25 12:00 | 2030 33% ECP | 697.59 | -300 | -510 | 160.83 | 0 | 0 | No
2030-12-25 13:00 | 2030 33% ECP | 700 | -383.82 | -510 | 215.23 | 0 | 0 | No
2030-12-25 14:00 | 2030 33% ECP | 689.86 | -300 | -510 | 339.44 | 0 | 0 | No
2030-12-25 15:00 | 2030 33% ECP | 700 | 0 | -491.38 | 97.45 | 0 | 0 | No
2030-12-25 16:00 | 2030 33% ECP | 700 | -296.5 | -510 | 278.84 | 0 | 0 | No
2030-12-25 17:00 | 2030 33% ECP | 282.5 | -372.51 | -510 | 347.31 | 0 | 0 | No
2030-12-25 18:00 | 2030 33% ECP | 0 | -413.41 | -510 | 164.46 | 0 | 0 | No
2030-12-25 19:00 | 2030 33% ECP | -29.16 | -402.58 | -510 | 151.36 | 0 | 0 | No
2030-12-25 20:00 | 2030 33% ECP | -280 | -102.58 | -210 | -148.64 | 0 | 0 | No
2030-12-25 21:00 | 2030 33% ECP | -700 | 8.83 | 90 | -185.81 | 0 | 0 | No
2030-12-25 22:00 | 2030 33% ECP | -700 | 308.83 | 390 | -24.21 | 0 | 0 | No
2030-12-25 23:00 | 2030 33% ECP | -700 | 505 | 510 | 126.43 | 0 | 0 | Yes
2030-12-26 | 2030 33% ECP | -700 | 505 | 510 | 426.43 | 0 | 0 | Yes
2030-12-26 01:00 | 2030 33% ECP | -700 | 505 | 510 | 423.15 | 0 | 0 | Yes
2030-12-26 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-26 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 06:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 07:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 08:00 | 2030 33% ECP | -700 | 505 | 510 | 367.79 | 0 | 0 | Yes
2030-12-26 09:00 | 2030 33% ECP | -700 | 505 | 510 | 334.37 | 0 | 0 | Yes
2030-12-26 10:00 | 2030 33% ECP | -700 | 505 | 510 | 494.03 | 0 | 0 | Yes
2030-12-26 11:00 | 2030 33% ECP | -700 | 505 | 510 | 480.48 | 0 | 0 | Yes
2030-12-26 12:00 | 2030 33% ECP | -700 | 505 | 510 | 473.91 | 0 | 0 | Yes
2030-12-26 13:00 | 2030 33% ECP | -700 | 505 | 510 | 491.55 | 0 | 0 | Yes
2030-12-26 14:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 15:00 | 2030 33% ECP | -700 | 505 | 510 | 413.23 | 0 | 0 | Yes
2030-12-26 16:00 | 2030 33% ECP | -700 | 505 | 510 | 294.17 | 0 | 0 | Yes
2030-12-26 17:00 | 2030 33% ECP | -700 | 505 | 510 | 255.81 | 0 | 0 | Yes
2030-12-26 18:00 | 2030 33% ECP | -700 | 505 | 510 | 210.47 | 0 | 0 | Yes
2030-12-26 19:00 | 2030 33% ECP | -700 | 505 | 510 | 225.67 | 0 | 0 | Yes
2030-12-26 20:00 | 2030 33% ECP | -700 | 505 | 510 | 293.63 | 0 | 0 | Yes
2030-12-26 21:00 | 2030 33% ECP | -700 | 505 | 510 | 461.45 | 0 | 0 | Yes
2030-12-26 22:00 | 2030 33% ECP | -700 | 505 | 510 | 283.93 | 0 | 0 | Yes
2030-12-26 23:00 | 2030 33% ECP | -700 | 505 | 510 | 313.46 | 0 | 0 | Yes
2030-12-27 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-27 01:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-27 02:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-27 03:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-27 04:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-27 05:00 | 2030 33% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-27 06:00 | 2030 33% ECP | -700 | 224.33 | 210 | 510 | 0 | 0 | No
2030-12-27 07:00 | 2030 33% ECP | -700 | -75.67 | -90 | 474.29 | 0 | 0 | No
2030-12-27 08:00 | 2030 33% ECP | -280 | -375.67 | -390 | 174.29 | 0 | 0 | No
2030-12-27 09:00 | 2030 33% ECP | -275.91 | -526 | -510 | 324.67 | 0 | 0 | No
2030-12-27 10:00 | 2030 33% ECP | 0 | -226 | -510 | 321.41 | 0 | 0 | No
2030-12-27 11:00 | 2030 33% ECP | -151.31 | -526 | -510 | 107.33 | 0 | 0 | No
2030-12-27 12:00 | 2030 33% ECP | -2.42 | -526 | -510 | 101.36 | 0 | 0 | No
2030-12-27 13:00 | 2030 33% ECP | 0 | -291.37 | -510 | 182.55 | 0 | 0 | No
2030-12-27 14:00 | 2030 33% ECP | 0 | -526 | -510 | 202.95 | 0 | 0 | No
2030-12-27 15:00 | 2030 33% ECP | -280 | -526 | -510 | -8.56 | 0 | 0 | No
2030-12-27 16:00 | 2030 33% ECP | -700 | -526 | -510 | 291.44 | 0 | 0 | No
2030-12-27 17:00 | 2030 33% ECP | -700 | -526 | -510 | -8.56 | 0 | 0 | No
2030-12-27 18:00 | 2030 33% ECP | -700 | -526 | -510 | -308.56 | 0 | 0 | No
2030-12-27 19:00 | 2030 33% ECP | -328.15 | -526 | -510 | -8.56 | 0 | 0 | No
2030-12-27 20:00 | 2030 33% ECP | 0 | -526 | -510 | 137.9 | 0 | 0 | No
2030-12-27 21:00 | 2030 33% ECP | -280 | -526 | -510 | 348.85 | 0 | 0 | No
2030-12-27 22:00 | 2030 33% ECP | -700 | -526 | -510 | 344.46 | 0 | 0 | No
2030-12-27 23:00 | 2030 33% ECP | -700 | -526 | -510 | 272.2 | 0 | 0 | No
2030-12-28 | 2030 33% ECP | -700 | -526 | -510 | 180.64 | 0 | 0 | No
2030-12-28 01:00 | 2030 33% ECP | -700 | -526 | -510 | -119.36 | 0 | 0 | No
2030-12-28 02:00 | 2030 33% ECP | -700 | -526 | -510 | -419.36 | 0 | 0 | No
2030-12-28 03:00 | 2030 33% ECP | -700 | -526 | -510 | -380.53 | 0 | 0 | No
2030-12-28 04:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 05:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 06:00 | 2030 33% ECP | -700 | -526 | -510 | -480.24 | 0 | 0 | No
2030-12-28 07:00 | 2030 33% ECP | -700 | -526 | -510 | -180.24 | 0 | 0 | No
2030-12-28 08:00 | 2030 33% ECP | -700 | -526 | -510 | 119.76 | 0 | 0 | No
2030-12-28 09:00 | 2030 33% ECP | -700 | -526 | -510 | 32.15 | 0 | 0 | No
2030-12-28 10:00 | 2030 33% ECP | -700 | -526 | -510 | 255.84 | 0 | 0 | No
2030-12-28 11:00 | 2030 33% ECP | -700 | -526 | -510 | 434.04 | 0 | 0 | No
2030-12-28 12:00 | 2030 33% ECP | -700 | -526 | -510 | 223.5 | 0 | 0 | No
2030-12-28 13:00 | 2030 33% ECP | -700 | -526 | -510 | -76.5 | 0 | 0 | No
2030-12-28 14:00 | 2030 33% ECP | -700 | -526 | -510 | -376.5 | 0 | 0 | No
2030-12-28 15:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 16:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 17:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 18:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 19:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 20:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-28 21:00 | 2030 33% ECP | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-12-28 22:00 | 2030 33% ECP | -700 | -526 | -510 | 90 | 0 | 0 | No
2030-12-28 23:00 | 2030 33% ECP | -700 | -526 | -510 | 76.94 | 0 | 0 | No
2030-12-29 | 2030 33% ECP | -700 | -526 | -510 | -67.59 | 0 | 0 | No
2030-12-29 01:00 | 2030 33% ECP | -700 | -526 | -510 | 232.41 | 0 | 0 | No
2030-12-29 02:00 | 2030 33% ECP | -700 | -526 | -510 | 209.79 | 0 | 0 | No
2030-12-29 03:00 | 2030 33% ECP | -700 | -526 | -510 | 240.74 | 0 | 0 | No
2030-12-29 04:00 | 2030 33% ECP | -700 | -526 | -510 | -34.25 | 0 | 0 | No
2030-12-29 05:00 | 2030 33% ECP | -700 | -526 | -510 | -246.09 | 0 | 0 | No
2030-12-29 06:00 | 2030 33% ECP | -700 | -526 | -510 | -127.6 | 0 | 0 | No
2030-12-29 07:00 | 2030 33% ECP | -700 | -526 | -510 | -186.45 | 0 | 0 | No
2030-12-29 08:00 | 2030 33% ECP | -700 | -526 | -510 | -322.28 | 0 | 0 | No
2030-12-29 09:00 | 2030 33% ECP | -700 | -526 | -510 | -60 | 0 | 0 | No
2030-12-29 10:00 | 2030 33% ECP | -700 | -526 | -510 | -64.94 | 0 | 0 | No
2030-12-29 11:00 | 2030 33% ECP | -700 | -526 | -510 | 235.06 | 0 | 0 | No
2030-12-29 12:00 | 2030 33% ECP | -700 | -526 | -510 | 188 | 0 | 0 | No
2030-12-29 13:00 | 2030 33% ECP | -700 | -526 | -510 | -112 | 0 | 0 | No
2030-12-29 14:00 | 2030 33% ECP | -700 | -526 | -510 | -162.7 | 0 | 0 | No
2030-12-29 15:00 | 2030 33% ECP | -581.23 | -526 | -510 | -462.7 | 0 | 0 | No
2030-12-29 16:00 | 2030 33% ECP | -700 | -278.25 | -510 | -510 | 0 | 0 | No
2030-12-29 17:00 | 2030 33% ECP | -700 | -227.99 | -510 | -269.15 | 0 | 0 | No
2030-12-29 18:00 | 2030 33% ECP | -280 | 0 | -300 | 30.85 | 0 | 0 | No
2030-12-29 19:00 | 2030 33% ECP | 140 | 0 | 0 | 330.85 | 0 | 0 | No
2030-12-29 20:00 | 2030 33% ECP | 560 | 0 | 0 | 124.45 | 0 | 0 | No
2030-12-29 21:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-29 22:00 | 2030 33% ECP | 700 | 0 | 0 | 223.59 | 0 | 0 | No
2030-12-29 23:00 | 2030 33% ECP | 700 | 0 | 0 | 200.31 | 0 | 0 | No
2030-12-30 | 2030 33% ECP | 700 | 0 | 300 | 300 | 0 | 0 | No
2030-12-30 01:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-30 02:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-30 03:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-30 04:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-30 05:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-30 06:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-30 07:00 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-30 08:00 | 2030 33% ECP | 700 | 0 | 510 | 185.38 | 0 | 0 | No
2030-12-30 09:00 | 2030 33% ECP | 700 | 0 | 510 | 454.56 | 0 | 0 | No
2030-12-30 10:00 | 2030 33% ECP | 700 | 0 | 510 | 353.91 | 0 | 0 | No
2030-12-30 11:00 | 2030 33% ECP | 700 | 0 | 469.82 | 53.91 | 0 | 0 | No
2030-12-30 12:00 | 2030 33% ECP | 700 | 0 | 510 | 193.38 | 0 | 0 | No
2030-12-30 13:00 | 2030 33% ECP | 700 | 0 | 461.76 | 276.75 | 0 | 0 | No
2030-12-30 14:00 | 2030 33% ECP | 700 | 0 | 161.76 | 300 | 0 | 0 | No
2030-12-30 15:00 | 2030 33% ECP | 700 | 0 | -138.24 | 0 | 0 | 0 | No
2030-12-30 16:00 | 2030 33% ECP | 700 | 0 | -438.24 | -82.32 | 0 | 0 | No
2030-12-30 17:00 | 2030 33% ECP | 700 | 0 | -510 | -21.23 | 0 | 0 | No
2030-12-30 18:00 | 2030 33% ECP | 700 | 0 | -510 | -74.29 | 0 | 0 | No
2030-12-30 19:00 | 2030 33% ECP | 700 | 0 | -300 | -242.93 | 0 | 0 | No
2030-12-30 20:00 | 2030 33% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-30 21:00 | 2030 33% ECP | 700 | 128.05 | 300 | 300 | 0 | 0 | No
2030-12-30 22:00 | 2030 33% ECP | 700 | 0 | 510 | 294.18 | 0 | 0 | No
2030-12-30 23:00 | 2030 33% ECP | 700 | 0 | 510 | 195.52 | 0 | 0 | No
2030-12-31 | 2030 33% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-31 01:00 | 2030 33% ECP | 700 | 0 | 338.79 | 0 | 0 | 0 | No
2030-12-31 02:00 | 2030 33% ECP | 700 | 0 | 38.79 | 0 | 0 | 0 | No
2030-12-31 03:00 | 2030 33% ECP | 700 | 0 | 338.79 | 0 | 0 | 0 | No
2030-12-31 04:00 | 2030 33% ECP | 420 | 0 | 38.79 | 0 | 0 | 0 | No
2030-12-31 05:00 | 2030 33% ECP | 0 | 0 | 338.79 | 0 | 0 | 0 | No
2030-12-31 06:00 | 2030 33% ECP | -420 | 0 | 300 | 0 | 0 | 0 | No
2030-12-31 07:00 | 2030 33% ECP | -700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-31 08:00 | 2030 33% ECP | -700 | -261.29 | -300 | -300 | 0 | 0 | No
2030-12-31 09:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 10:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 11:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 12:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 13:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 14:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 15:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 16:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 17:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 18:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 19:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 20:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 21:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 22:00 | 2030 33% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 23:00 | 2030 33% ECP | -305.8 | -226 | -210 | -210 | 0 | 0 | No
2030-01-01 | 2030 100% ECP | -280 | -226 | -210 | -209.03 | 0 | 0 | No
2030-01-01 01:00 | 2030 100% ECP | 140 | 0 | 0 | 90.97 | 0 | 0 | No
2030-01-01 02:00 | 2030 100% ECP | 560 | 0 | -300 | 169.79 | 0 | 0 | No
2030-01-01 03:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-01 04:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-01 05:00 | 2030 100% ECP | 700 | 0 | -277.19 | 0 | 0 | 0 | No
2030-01-01 06:00 | 2030 100% ECP | 280 | 0 | -125.99 | 0 | 0 | 0 | No
2030-01-01 07:00 | 2030 100% ECP | 0 | 0 | 0 | 0 | 0 | 0 | No
2030-01-01 08:00 | 2030 100% ECP | 0 | 0 | 0 | 213.8 | 0 | 0 | No
2030-01-01 09:00 | 2030 100% ECP | -138.14 | 0 | 0 | 170.35 | 0 | 0 | No
2030-01-01 10:00 | 2030 100% ECP | -558.14 | 0 | -192.39 | 185.42 | 0 | 0 | No
2030-01-01 11:00 | 2030 100% ECP | -700 | -226 | -492.39 | 0 | 0 | 0 | No
2030-01-01 12:00 | 2030 100% ECP | -700 | -526 | -510 | -108.84 | 0 | 0 | No
2030-01-01 13:00 | 2030 100% ECP | -700 | -226 | -342.86 | 98.33 | 0 | 0 | No
2030-01-01 14:00 | 2030 100% ECP | -700 | -10.06 | -210 | 228.76 | 0 | 0 | No
2030-01-01 15:00 | 2030 100% ECP | -700 | -310.06 | -510 | 27.09 | 0 | 0 | No
2030-01-01 16:00 | 2030 100% ECP | -700 | -526 | -510 | -47.14 | 0 | 0 | No
2030-01-01 17:00 | 2030 100% ECP | -700 | -526 | -510 | -123.27 | 0 | 0 | No
2030-01-01 18:00 | 2030 100% ECP | -700 | -526 | -510 | -390.28 | 0 | 0 | No
2030-01-01 19:00 | 2030 100% ECP | -700 | -526 | -510 | -294.92 | 0 | 0 | No
2030-01-01 20:00 | 2030 100% ECP | -700 | -526 | -510 | 5.08 | 0 | 0 | Yes
2030-01-01 21:00 | 2030 100% ECP | -700 | -526 | -510 | -42.26 | 0 | 0 | Yes
2030-01-01 22:00 | 2030 100% ECP | -700 | -526 | -510 | -59.88 | 0 | 0 | Yes
2030-01-01 23:00 | 2030 100% ECP | -700 | -226 | -210 | 240.12 | 0 | 0 | Yes
2030-01-02 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-01-02 01:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-02 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 13:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-02 14:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-01-02 15:00 | 2030 100% ECP | -700 | -226 | -210 | 291.09 | 0 | 0 | Yes
2030-01-02 16:00 | 2030 100% ECP | -700 | -526 | -510 | -8.91 | 0 | 0 | Yes
2030-01-02 17:00 | 2030 100% ECP | -700 | -526 | -510 | -163.14 | 0 | 0 | No
2030-01-02 18:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-01-02 19:00 | 2030 100% ECP | -700 | -526 | -510 | -89.06 | 0 | 0 | No
2030-01-02 20:00 | 2030 100% ECP | -700 | -526 | -510 | 210.94 | 0 | 0 | No
2030-01-02 21:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-01-02 22:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-01-02 23:00 | 2030 100% ECP | -700 | 374 | 390 | 322.16 | 0 | 0 | Yes
2030-01-03 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 01:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 02:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 04:00 | 2030 100% ECP | 417.34 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 05:00 | 2030 100% ECP | -2.66 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 06:00 | 2030 100% ECP | -422.66 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 07:00 | 2030 100% ECP | -700 | 205 | 210 | 406.87 | 0 | 0 | No
2030-01-03 08:00 | 2030 100% ECP | -700 | 0 | 0 | 261.95 | 0 | 0 | No
2030-01-03 09:00 | 2030 100% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-01-03 10:00 | 2030 100% ECP | -700 | 0 | -181.19 | 510 | 0 | 0 | No
2030-01-03 11:00 | 2030 100% ECP | -700 | -226 | -228.36 | 510 | 0 | 0 | No
2030-01-03 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-01-03 13:00 | 2030 100% ECP | -700 | -467.51 | -510 | 487.29 | 0 | 0 | No
2030-01-03 14:00 | 2030 100% ECP | -700 | -167.51 | -361.02 | 235.06 | 0 | 0 | No
2030-01-03 15:00 | 2030 100% ECP | -700 | 0 | -61.02 | 389.36 | 0 | 0 | No
2030-01-03 16:00 | 2030 100% ECP | -700 | 0 | 0 | 355.25 | 0 | 0 | No
2030-01-03 17:00 | 2030 100% ECP | -700 | 0 | 0 | 502.47 | 0 | 0 | No
2030-01-03 18:00 | 2030 100% ECP | -700 | 0 | 0 | 491.8 | 0 | 0 | No
2030-01-03 19:00 | 2030 100% ECP | -700 | 0 | 0 | 300 | 0 | 0 | No
2030-01-03 20:00 | 2030 100% ECP | -700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-03 21:00 | 2030 100% ECP | -700 | 0 | 123.44 | 187.25 | 0 | 0 | No
2030-01-03 22:00 | 2030 100% ECP | -646.76 | 300 | 423.44 | 487.25 | 0 | 0 | No
2030-01-03 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-04 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 01:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 02:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 03:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 07:00 | 2030 100% ECP | -700 | 205 | 210 | 377.96 | 0 | 0 | No
2030-01-04 08:00 | 2030 100% ECP | -700 | 0 | 77.72 | 77.96 | 0 | 0 | No
2030-01-04 09:00 | 2030 100% ECP | -700 | 78 | 281.53 | 210 | 0 | 0 | No
2030-01-04 10:00 | 2030 100% ECP | -700 | 378 | 510 | 510 | 0 | 0 | No
2030-01-04 11:00 | 2030 100% ECP | -700 | 300 | 319.49 | 300 | 0 | 0 | No
2030-01-04 12:00 | 2030 100% ECP | -700 | 0 | 19.49 | 0 | 0 | 0 | No
2030-01-04 13:00 | 2030 100% ECP | -700 | 0 | 240.33 | 54.93 | 0 | 0 | No
2030-01-04 14:00 | 2030 100% ECP | -700 | 0 | 361.46 | 139.66 | 0 | 0 | No
2030-01-04 15:00 | 2030 100% ECP | -700 | 74 | 61.46 | 129.88 | 0 | 0 | No
2030-01-04 16:00 | 2030 100% ECP | -700 | -226 | -238.54 | -170.12 | 0 | 0 | No
2030-01-04 17:00 | 2030 100% ECP | -700 | -526 | -510 | -470.12 | 0 | 0 | No
2030-01-04 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-04 19:00 | 2030 100% ECP | -700 | -526 | -510 | -477.67 | 0 | 0 | No
2030-01-04 20:00 | 2030 100% ECP | -700 | -300 | -345.82 | -177.67 | 0 | 0 | No
2030-01-04 21:00 | 2030 100% ECP | -700 | 0 | -45.82 | 122.33 | 0 | 0 | No
2030-01-04 22:00 | 2030 100% ECP | -700 | -287.64 | -345.82 | -29.55 | 0 | 0 | No
2030-01-04 23:00 | 2030 100% ECP | -700 | -288.71 | -510 | 60.97 | 0 | 0 | No
2030-01-05 | 2030 100% ECP | -700 | -384.17 | -510 | -19.62 | 0 | 0 | No
2030-01-05 01:00 | 2030 100% ECP | -700 | -518.73 | -510 | 210 | 0 | 0 | No
2030-01-05 02:00 | 2030 100% ECP | -700 | -218.73 | -210 | 510 | 0 | 0 | No
2030-01-05 03:00 | 2030 100% ECP | -700 | 81.27 | 90 | 510 | 0 | 0 | No
2030-01-05 04:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-01-05 05:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | No
2030-01-05 06:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-01-05 07:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-01-05 08:00 | 2030 100% ECP | -700 | -526 | -510 | 18.32 | 0 | 0 | No
2030-01-05 09:00 | 2030 100% ECP | -700 | -526 | -510 | -195.63 | 0 | 0 | No
2030-01-05 10:00 | 2030 100% ECP | -700 | -526 | -510 | 104.37 | 0 | 0 | No
2030-01-05 11:00 | 2030 100% ECP | -700 | -526 | -510 | 27.94 | 0 | 0 | Yes
2030-01-05 12:00 | 2030 100% ECP | -700 | -526 | -510 | 302.32 | 0 | 0 | Yes
2030-01-05 13:00 | 2030 100% ECP | -700 | -526 | -510 | 302.32 | 0 | 0 | No
2030-01-05 14:00 | 2030 100% ECP | -700 | -526 | -510 | 262.03 | 0 | 0 | Yes
2030-01-05 15:00 | 2030 100% ECP | -700 | -526 | -510 | -37.97 | 0 | 0 | No
2030-01-05 16:00 | 2030 100% ECP | -700 | -526 | -510 | 240.61 | 0 | 0 | No
2030-01-05 17:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-01-05 18:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-01-05 19:00 | 2030 100% ECP | -700 | -526 | -510 | 424.89 | 0 | 0 | Yes
2030-01-05 20:00 | 2030 100% ECP | -700 | -526 | -510 | 348.64 | 0 | 0 | Yes
2030-01-05 21:00 | 2030 100% ECP | -700 | -526 | -510 | 85.7 | 0 | 0 | Yes
2030-01-05 22:00 | 2030 100% ECP | -700 | -526 | -510 | -214.3 | 0 | 0 | Yes
2030-01-05 23:00 | 2030 100% ECP | -700 | -226 | -210 | 85.7 | 0 | 0 | Yes
2030-01-06 | 2030 100% ECP | -700 | 74 | 90 | 385.7 | 0 | 0 | Yes
2030-01-06 01:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-06 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 04:00 | 2030 100% ECP | -700 | 505 | 510 | 237.75 | 0 | 0 | Yes
2030-01-06 05:00 | 2030 100% ECP | -700 | 505 | 510 | 377.62 | 0 | 0 | Yes
2030-01-06 06:00 | 2030 100% ECP | -700 | 505 | 510 | 229.67 | 0 | 0 | Yes
2030-01-06 07:00 | 2030 100% ECP | -700 | 505 | 510 | 15.13 | 0 | 0 | Yes
2030-01-06 08:00 | 2030 100% ECP | -700 | 505 | 510 | 34.56 | 0 | 0 | Yes
2030-01-06 09:00 | 2030 100% ECP | -700 | 505 | 510 | 334.56 | 0 | 0 | Yes
2030-01-06 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 14:00 | 2030 100% ECP | -700 | 505 | 210 | 510 | 0 | 0 | Yes
2030-01-06 15:00 | 2030 100% ECP | -700 | 300 | -90 | 479.71 | 0 | 0 | Yes
2030-01-06 16:00 | 2030 100% ECP | -700 | 0 | -390 | 179.71 | 0 | 0 | No
2030-01-06 17:00 | 2030 100% ECP | -700 | -300 | -510 | 479.71 | 0 | 0 | No
2030-01-06 18:00 | 2030 100% ECP | -700 | -300 | -510 | 510 | 0 | 0 | No
2030-01-06 19:00 | 2030 100% ECP | -700 | -489.91 | -510 | 510 | 0 | 0 | No
2030-01-06 20:00 | 2030 100% ECP | -700 | -189.91 | -510 | 510 | 0 | 0 | No
2030-01-06 21:00 | 2030 100% ECP | -700 | 0 | -300 | 510 | 0 | 0 | No
2030-01-06 22:00 | 2030 100% ECP | -280 | 158.74 | 0 | 510 | 0 | 0 | No
2030-01-06 23:00 | 2030 100% ECP | -700 | 458.74 | 300 | 510 | 0 | 0 | Yes
2030-01-07 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 05:00 | 2030 100% ECP | -700 | 505 | 510 | 279.46 | 0 | 0 | Yes
2030-01-07 06:00 | 2030 100% ECP | -700 | 505 | 510 | 471.53 | 0 | 0 | Yes
2030-01-07 07:00 | 2030 100% ECP | -700 | 505 | 510 | 311.27 | 0 | 0 | Yes
2030-01-07 08:00 | 2030 100% ECP | -700 | 505 | 510 | 485.47 | 0 | 0 | Yes
2030-01-07 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 17:00 | 2030 100% ECP | -700 | 205 | 398.77 | 210 | 0 | 0 | Yes
2030-01-07 18:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-08 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 01:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-08 02:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 03:00 | 2030 100% ECP | -25.22 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 04:00 | 2030 100% ECP | -445.22 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 07:00 | 2030 100% ECP | -700 | 205 | 369.68 | 274.72 | 0 | 0 | No
2030-01-08 08:00 | 2030 100% ECP | -700 | 44.3 | 438.03 | 210 | 0 | 0 | No
2030-01-08 09:00 | 2030 100% ECP | -700 | 344.3 | 510 | 510 | 0 | 0 | No
2030-01-08 10:00 | 2030 100% ECP | -700 | 482.26 | 510 | 510 | 0 | 0 | No
2030-01-08 11:00 | 2030 100% ECP | -700 | 182.26 | 210 | 210 | 0 | 0 | No
2030-01-08 12:00 | 2030 100% ECP | -700 | -82.8 | -90 | 157.79 | 0 | 0 | No
2030-01-08 13:00 | 2030 100% ECP | -700 | -77.23 | -264.17 | 147.88 | 0 | 0 | No
2030-01-08 14:00 | 2030 100% ECP | -700 | 0 | 35.83 | 386.64 | 0 | 0 | No
2030-01-08 15:00 | 2030 100% ECP | -700 | 300 | 335.83 | 422.02 | 0 | 0 | No
2030-01-08 16:00 | 2030 100% ECP | -700 | 0 | 35.83 | 122.02 | 0 | 0 | No
2030-01-08 17:00 | 2030 100% ECP | -700 | -300 | -264.17 | 147.3 | 0 | 0 | No
2030-01-08 18:00 | 2030 100% ECP | -700 | -526 | -510 | -152.7 | 0 | 0 | No
2030-01-08 19:00 | 2030 100% ECP | -700 | -526 | -510 | -345 | 0 | 0 | No
2030-01-08 20:00 | 2030 100% ECP | -700 | -526 | -510 | -45 | 0 | 0 | No
2030-01-08 21:00 | 2030 100% ECP | -420 | -526 | -510 | 62.78 | 0 | 0 | No
2030-01-08 22:00 | 2030 100% ECP | 0 | -480.49 | -510 | 172.7 | 0 | 0 | No
2030-01-08 23:00 | 2030 100% ECP | 296.02 | -357.73 | -510 | 36.81 | 0 | 0 | No
2030-01-09 | 2030 100% ECP | 700 | -57.73 | -343.28 | 0 | 0 | 0 | No
2030-01-09 01:00 | 2030 100% ECP | 700 | 0 | -43.28 | 0 | 0 | 0 | No
2030-01-09 02:00 | 2030 100% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-09 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 06:00 | 2030 100% ECP | 700 | 205 | 320.27 | 210 | 0 | 0 | No
2030-01-09 07:00 | 2030 100% ECP | 280 | 205 | 510 | 414.18 | 0 | 0 | No
2030-01-09 08:00 | 2030 100% ECP | 579.94 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 09:00 | 2030 100% ECP | 700 | 453.91 | 510 | 510 | 0 | 0 | No
2030-01-09 10:00 | 2030 100% ECP | 700 | 234.71 | 510 | 510 | 0 | 0 | No
2030-01-09 11:00 | 2030 100% ECP | 700 | 216.95 | 510 | 510 | 0 | 0 | No
2030-01-09 12:00 | 2030 100% ECP | 694.13 | 0 | 210 | 307.19 | 0 | 0 | No
2030-01-09 13:00 | 2030 100% ECP | 274.13 | 0 | 510 | 438.94 | 0 | 0 | No
2030-01-09 14:00 | 2030 100% ECP | 0 | 300 | 300 | 510 | 0 | 0 | No
2030-01-09 15:00 | 2030 100% ECP | 420 | 0 | 0 | 210 | 0 | 0 | No
2030-01-09 16:00 | 2030 100% ECP | 0 | -300 | -300 | 254.15 | 0 | 0 | No
2030-01-09 17:00 | 2030 100% ECP | -215.56 | -526 | -510 | 25.42 | 0 | 0 | No
2030-01-09 18:00 | 2030 100% ECP | 204.44 | -526 | -510 | -274.58 | 0 | 0 | No
2030-01-09 19:00 | 2030 100% ECP | 624.44 | -526 | -510 | 25.42 | 0 | 0 | No
2030-01-09 20:00 | 2030 100% ECP | 204.44 | -526 | -510 | 291.86 | 0 | 0 | No
2030-01-09 21:00 | 2030 100% ECP | -34.52 | -526 | -510 | 294.4 | 0 | 0 | No
2030-01-09 22:00 | 2030 100% ECP | 250.59 | -526 | -510 | 15.57 | 0 | 0 | No
2030-01-09 23:00 | 2030 100% ECP | 670.59 | -226 | -472.21 | 0 | 0 | 0 | No
2030-01-10 | 2030 100% ECP | 700 | 0 | -172.21 | 0 | 0 | 0 | No
2030-01-10 01:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-10 02:00 | 2030 100% ECP | 700 | 0 | 13.13 | 0 | 0 | 0 | No
2030-01-10 03:00 | 2030 100% ECP | 700 | 0 | 313.13 | 300 | 0 | 0 | No
2030-01-10 04:00 | 2030 100% ECP | 420 | 0 | 13.13 | 0 | 0 | 0 | No
2030-01-10 05:00 | 2030 100% ECP | 0 | 0 | 302.05 | 0 | 0 | 0 | No
2030-01-10 06:00 | 2030 100% ECP | -420 | 0 | 202 | 0 | 0 | 0 | No
2030-01-10 07:00 | 2030 100% ECP | -700 | 300 | 90 | 192.28 | 0 | 0 | No
2030-01-10 08:00 | 2030 100% ECP | -700 | 0 | -210 | -107.72 | 0 | 0 | No
2030-01-10 09:00 | 2030 100% ECP | -700 | -300 | -510 | -407.72 | 0 | 0 | No
2030-01-10 10:00 | 2030 100% ECP | -700 | -526 | -510 | -107.72 | 0 | 0 | No
2030-01-10 11:00 | 2030 100% ECP | -700 | -526 | -510 | -217.5 | 0 | 0 | Yes
2030-01-10 12:00 | 2030 100% ECP | -700 | -526 | -510 | -147.81 | 0 | 0 | Yes
2030-01-10 13:00 | 2030 100% ECP | -700 | -526 | -510 | -386.58 | 0 | 0 | Yes
2030-01-10 14:00 | 2030 100% ECP | -700 | -526 | -510 | -344.46 | 0 | 0 | Yes
2030-01-10 15:00 | 2030 100% ECP | -700 | -526 | -510 | -338.78 | 0 | 0 | Yes
2030-01-10 16:00 | 2030 100% ECP | -700 | -526 | -510 | -507.79 | 0 | 0 | Yes
2030-01-10 17:00 | 2030 100% ECP | -700 | -526 | -510 | -265.16 | 0 | 0 | Yes
2030-01-10 18:00 | 2030 100% ECP | -700 | -526 | -510 | -218.26 | 0 | 0 | Yes
2030-01-10 19:00 | 2030 100% ECP | -700 | -526 | -510 | -362.92 | 0 | 0 | Yes
2030-01-10 20:00 | 2030 100% ECP | -700 | -526 | -510 | -410.46 | 0 | 0 | Yes
2030-01-10 21:00 | 2030 100% ECP | -700 | -226 | -210 | -110.46 | 0 | 0 | Yes
2030-01-10 22:00 | 2030 100% ECP | -700 | 74 | 90 | 189.54 | 0 | 0 | Yes
2030-01-10 23:00 | 2030 100% ECP | -700 | 374 | 390 | 364.23 | 0 | 0 | Yes
2030-01-11 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 03:00 | 2030 100% ECP | -700 | 505 | 510 | 374.63 | 0 | 0 | Yes
2030-01-11 04:00 | 2030 100% ECP | -700 | 505 | 510 | 158.22 | 0 | 0 | Yes
2030-01-11 05:00 | 2030 100% ECP | -700 | 505 | 510 | 458.22 | 0 | 0 | Yes
2030-01-11 06:00 | 2030 100% ECP | -700 | 505 | 510 | 449.51 | 0 | 0 | Yes
2030-01-11 07:00 | 2030 100% ECP | -700 | 505 | 510 | 403.74 | 0 | 0 | Yes
2030-01-11 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 15:00 | 2030 100% ECP | -700 | 501.04 | 509.54 | 510 | 0 | 0 | No
2030-01-11 16:00 | 2030 100% ECP | -700 | 201.04 | 209.54 | 210 | 0 | 0 | No
2030-01-11 17:00 | 2030 100% ECP | -700 | 0 | -90.46 | 510 | 0 | 0 | No
2030-01-11 18:00 | 2030 100% ECP | -700 | 0 | -390.46 | 509.99 | 0 | 0 | No
2030-01-11 19:00 | 2030 100% ECP | -280 | 0 | -390 | 510 | 0 | 0 | No
2030-01-11 20:00 | 2030 100% ECP | 140 | 0 | -90 | 510 | 0 | 0 | No
2030-01-11 21:00 | 2030 100% ECP | 560 | 48.19 | 210 | 510 | 0 | 0 | No
2030-01-11 22:00 | 2030 100% ECP | 700 | 348.19 | 510 | 510 | 0 | 0 | No
2030-01-11 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 04:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 05:00 | 2030 100% ECP | 140 | 205 | 210 | 510 | 0 | 0 | No
2030-01-12 06:00 | 2030 100% ECP | -280 | -95 | -90 | 217.63 | 0 | 0 | No
2030-01-12 07:00 | 2030 100% ECP | -700 | 0 | -249.52 | 209.98 | 0 | 0 | No
2030-01-12 08:00 | 2030 100% ECP | -700 | 0 | -10.93 | 454.58 | 0 | 0 | No
2030-01-12 09:00 | 2030 100% ECP | -280 | 0 | -10.93 | 418.17 | 0 | 0 | No
2030-01-12 10:00 | 2030 100% ECP | -700 | 0 | -108.85 | 200.44 | 0 | 0 | No
2030-01-12 11:00 | 2030 100% ECP | -700 | 0 | -408.85 | 500.44 | 0 | 0 | No
2030-01-12 12:00 | 2030 100% ECP | -700 | -107.95 | -510 | 435.71 | 0 | 0 | No
2030-01-12 13:00 | 2030 100% ECP | -700 | -59.78 | -510 | 360.87 | 0 | 0 | No
2030-01-12 14:00 | 2030 100% ECP | -700 | 0 | -210 | 236.29 | 0 | 0 | No
2030-01-12 15:00 | 2030 100% ECP | -700 | 0 | -210 | 297.59 | 0 | 0 | No
2030-01-12 16:00 | 2030 100% ECP | -700 | 0 | -210 | 486.73 | 0 | 0 | No
2030-01-12 17:00 | 2030 100% ECP | -700 | 0 | -475.09 | 510 | 0 | 0 | No
2030-01-12 18:00 | 2030 100% ECP | -700 | 0 | -324.31 | 510 | 0 | 0 | No
2030-01-12 19:00 | 2030 100% ECP | -700 | 0 | -324.31 | 330.84 | 0 | 0 | No
2030-01-12 20:00 | 2030 100% ECP | -700 | 0 | -510 | 75.98 | 0 | 0 | No
2030-01-12 21:00 | 2030 100% ECP | -700 | -230.43 | -510 | 195.99 | 0 | 0 | No
2030-01-12 22:00 | 2030 100% ECP | -700 | -526 | -510 | -44.09 | 0 | 0 | No
2030-01-12 23:00 | 2030 100% ECP | -700 | -526 | -510 | 255.91 | 0 | 0 | No
2030-01-13 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-01-13 01:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-01-13 02:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-13 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 06:00 | 2030 100% ECP | -700 | 505 | 218.25 | 210 | 0 | 0 | Yes
2030-01-13 07:00 | 2030 100% ECP | -700 | 505 | 444.87 | 0 | 0 | 0 | Yes
2030-01-13 08:00 | 2030 100% ECP | -700 | 505 | 510 | 239.41 | 0 | 0 | Yes
2030-01-13 09:00 | 2030 100% ECP | -700 | 505 | 510 | 112.32 | 0 | 0 | Yes
2030-01-13 10:00 | 2030 100% ECP | -700 | 505 | 510 | 226.99 | 0 | 0 | Yes
2030-01-13 11:00 | 2030 100% ECP | -700 | 505 | 510 | 316.99 | 0 | 0 | Yes
2030-01-13 12:00 | 2030 100% ECP | -700 | 505 | 510 | 380.42 | 0 | 0 | Yes
2030-01-13 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 14:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-01-13 15:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-01-13 16:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-01-13 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-01-13 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-01-13 19:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-01-13 20:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-01-13 21:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-01-13 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 23:00 | 2030 100% ECP | -700 | 505 | 510 | 322.43 | 0 | 0 | Yes
2030-01-14 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 02:00 | 2030 100% ECP | -700 | 505 | 510 | 491.54 | 0 | 0 | Yes
2030-01-14 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 08:00 | 2030 100% ECP | -690.75 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 09:00 | 2030 100% ECP | -270.75 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 10:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 11:00 | 2030 100% ECP | -64.99 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 12:00 | 2030 100% ECP | -119.67 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 13:00 | 2030 100% ECP | -154.3 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 14:00 | 2030 100% ECP | 0 | 374 | 390 | 510 | 0 | 0 | No
2030-01-14 15:00 | 2030 100% ECP | 0 | 74 | 90 | 510 | 0 | 0 | No
2030-01-14 16:00 | 2030 100% ECP | -420 | -226 | -210 | 210 | 0 | 0 | No
2030-01-14 17:00 | 2030 100% ECP | -700 | -526 | -510 | 335.85 | 0 | 0 | No
2030-01-14 18:00 | 2030 100% ECP | -700 | -226 | -317.54 | 510 | 0 | 0 | No
2030-01-14 19:00 | 2030 100% ECP | -700 | 74 | -17.54 | 510 | 0 | 0 | No
2030-01-14 20:00 | 2030 100% ECP | -700 | 374 | 282.46 | 510 | 0 | 0 | Yes
2030-01-14 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 14:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-15 15:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-01-15 16:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-01-15 17:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-01-15 18:00 | 2030 100% ECP | -700 | -526 | -510 | 353.13 | 0 | 0 | No
2030-01-15 19:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-01-15 20:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-01-15 21:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | No
2030-01-15 22:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-15 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 07:00 | 2030 100% ECP | -700 | 300 | 510 | 463.19 | 0 | 0 | Yes
2030-01-16 08:00 | 2030 100% ECP | -700 | 0 | 210 | 163.19 | 0 | 0 | Yes
2030-01-16 09:00 | 2030 100% ECP | -700 | 205 | 221.96 | 210 | 0 | 0 | Yes
2030-01-16 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 14:00 | 2030 100% ECP | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-01-16 15:00 | 2030 100% ECP | -700 | 333.18 | 90 | 510 | 0 | 0 | Yes
2030-01-16 16:00 | 2030 100% ECP | -700 | 33.18 | -210 | 510 | 0 | 0 | Yes
2030-01-16 17:00 | 2030 100% ECP | -700 | -266.82 | -510 | 510 | 0 | 0 | No
2030-01-16 18:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-01-16 19:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-01-16 20:00 | 2030 100% ECP | -700 | -226 | -210 | 356.59 | 0 | 0 | No
2030-01-16 21:00 | 2030 100% ECP | -280 | 74 | 90 | 488.43 | 0 | 0 | No
2030-01-16 22:00 | 2030 100% ECP | 140 | 374 | 390 | 510 | 0 | 0 | No
2030-01-16 23:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 04:00 | 2030 100% ECP | 539.61 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 05:00 | 2030 100% ECP | 119.61 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 06:00 | 2030 100% ECP | -300.39 | 205 | 210 | 210 | 0 | 0 | No
2030-01-17 07:00 | 2030 100% ECP | -700 | -95 | -90 | 316 | 0 | 0 | No
2030-01-17 08:00 | 2030 100% ECP | -342.92 | 0 | 0 | 295.33 | 0 | 0 | No
2030-01-17 09:00 | 2030 100% ECP | 0 | 0 | 209.62 | 510 | 0 | 0 | No
2030-01-17 10:00 | 2030 100% ECP | -280 | 0 | 74.21 | 510 | 0 | 0 | No
2030-01-17 11:00 | 2030 100% ECP | -700 | -75.87 | -210 | 467.08 | 0 | 0 | No
2030-01-17 12:00 | 2030 100% ECP | -700 | -375.87 | -510 | 492.21 | 0 | 0 | No
2030-01-17 13:00 | 2030 100% ECP | -445.93 | -408.31 | -510 | 203.51 | 0 | 0 | No
2030-01-17 14:00 | 2030 100% ECP | -25.93 | -108.31 | -210 | 503.51 | 0 | 0 | No
2030-01-17 15:00 | 2030 100% ECP | 394.07 | 191.69 | 90 | 510 | 0 | 0 | No
2030-01-17 16:00 | 2030 100% ECP | 0 | 0 | 390 | 510 | 0 | 0 | No
2030-01-17 17:00 | 2030 100% ECP | -420 | 0 | 510 | 210 | 0 | 0 | No
2030-01-17 18:00 | 2030 100% ECP | -140 | 0 | 510 | 54.92 | 0 | 0 | No
2030-01-17 19:00 | 2030 100% ECP | 280 | 0 | 510 | 155.94 | 0 | 0 | No
2030-01-17 20:00 | 2030 100% ECP | 700 | 0 | 510 | 100.05 | 0 | 0 | No
2030-01-17 21:00 | 2030 100% ECP | 700 | 205 | 510 | 400.05 | 0 | 0 | No
2030-01-17 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 04:00 | 2030 100% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 05:00 | 2030 100% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 06:00 | 2030 100% ECP | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 08:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 09:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 15:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 16:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 17:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 18:00 | 2030 100% ECP | 280 | 205 | 510 | 210 | 0 | 0 | No
2030-01-18 19:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 20:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 21:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 23:00 | 2030 100% ECP | 700 | 466.95 | 510 | 510 | 0 | 0 | No
2030-01-19 | 2030 100% ECP | 700 | 166.95 | 465.54 | 210 | 0 | 0 | No
2030-01-19 01:00 | 2030 100% ECP | 700 | 0 | 423.71 | 0 | 0 | 0 | No
2030-01-19 02:00 | 2030 100% ECP | 700 | 0 | 123.71 | 0 | 0 | 0 | No
2030-01-19 03:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-19 04:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-19 05:00 | 2030 100% ECP | 280 | 0 | 0 | 0 | 0 | 0 | No
2030-01-19 06:00 | 2030 100% ECP | -140 | 0 | 0 | 0 | 0 | 0 | No
2030-01-19 07:00 | 2030 100% ECP | -484.4 | 0 | 0 | 0 | 0 | 0 | No
2030-01-19 08:00 | 2030 100% ECP | -700 | -226 | -300 | -266.42 | 0 | 0 | No
2030-01-19 09:00 | 2030 100% ECP | -700 | -526 | -510 | -476.7 | 0 | 0 | No
2030-01-19 10:00 | 2030 100% ECP | -614.11 | -526 | -510 | -176.7 | 0 | 0 | No
2030-01-19 11:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 13:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 14:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 15:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 16:00 | 2030 100% ECP | -280 | -226 | -210 | -160.23 | 0 | 0 | No
2030-01-19 17:00 | 2030 100% ECP | -700 | -526 | -510 | -460.23 | 0 | 0 | No
2030-01-19 18:00 | 2030 100% ECP | -700 | -526 | -510 | -258.13 | 0 | 0 | No
2030-01-19 19:00 | 2030 100% ECP | -280 | -485.46 | -510 | 41.87 | 0 | 0 | No
2030-01-19 20:00 | 2030 100% ECP | 140 | -185.46 | -294.74 | 66.84 | 0 | 0 | No
2030-01-19 21:00 | 2030 100% ECP | 208.97 | 0 | -103.66 | 4.88 | 0 | 0 | No
2030-01-19 22:00 | 2030 100% ECP | -211.03 | -226 | -403.66 | 0 | 0 | 0 | No
2030-01-19 23:00 | 2030 100% ECP | -631.03 | -526 | -510 | 16.71 | 0 | 0 | No
2030-01-20 | 2030 100% ECP | -560 | -526 | -510 | -94.36 | 0 | 0 | No
2030-01-20 01:00 | 2030 100% ECP | -140 | -226 | -210 | 72.92 | 0 | 0 | No
2030-01-20 02:00 | 2030 100% ECP | 280 | 74 | 90 | 372.92 | 0 | 0 | No
2030-01-20 03:00 | 2030 100% ECP | 700 | 374 | 390 | 510 | 0 | 0 | No
2030-01-20 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-20 05:00 | 2030 100% ECP | 280 | 205 | 210 | 510 | 0 | 0 | No
2030-01-20 06:00 | 2030 100% ECP | -140 | -95 | -90 | 210 | 0 | 0 | No
2030-01-20 07:00 | 2030 100% ECP | -560 | -395 | -390 | -44.1 | 0 | 0 | No
2030-01-20 08:00 | 2030 100% ECP | -413.82 | -526 | -510 | 89.66 | 0 | 0 | No
2030-01-20 09:00 | 2030 100% ECP | -700 | -526 | -510 | 69.06 | 0 | 0 | No
2030-01-20 10:00 | 2030 100% ECP | -700 | -526 | -510 | 348.43 | 0 | 0 | No
2030-01-20 11:00 | 2030 100% ECP | -700 | -526 | -510 | 392.61 | 0 | 0 | No
2030-01-20 12:00 | 2030 100% ECP | -700 | -526 | -510 | 449.16 | 0 | 0 | No
2030-01-20 13:00 | 2030 100% ECP | -700 | -526 | -510 | 346.88 | 0 | 0 | No
2030-01-20 14:00 | 2030 100% ECP | -700 | -526 | -510 | 46.88 | 0 | 0 | No
2030-01-20 15:00 | 2030 100% ECP | -280 | -226 | -510 | 300 | 0 | 0 | No
2030-01-20 16:00 | 2030 100% ECP | 140 | 0 | -395.94 | 0 | 0 | 0 | No
2030-01-20 17:00 | 2030 100% ECP | 0 | 0 | -95.94 | 231.07 | 0 | 0 | No
2030-01-20 18:00 | 2030 100% ECP | 280 | 0 | 0 | 435.36 | 0 | 0 | No
2030-01-20 19:00 | 2030 100% ECP | 700 | 0 | -300 | 450.29 | 0 | 0 | No
2030-01-20 20:00 | 2030 100% ECP | 700 | 0 | -300 | 355.85 | 0 | 0 | No
2030-01-20 21:00 | 2030 100% ECP | 700 | 0 | 0 | 55.85 | 0 | 0 | No
2030-01-20 22:00 | 2030 100% ECP | 700 | 0 | -300 | 55.85 | 0 | 0 | No
2030-01-20 23:00 | 2030 100% ECP | 700 | 0 | -331.26 | 214.32 | 0 | 0 | No
2030-01-21 | 2030 100% ECP | 700 | 300 | -31.26 | 510 | 0 | 0 | No
2030-01-21 01:00 | 2030 100% ECP | 700 | 505 | 268.74 | 510 | 0 | 0 | No
2030-01-21 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 06:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 07:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 08:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 09:00 | 2030 100% ECP | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-01-21 10:00 | 2030 100% ECP | 280 | 0 | 210 | 210 | 0 | 0 | No
2030-01-21 11:00 | 2030 100% ECP | 139.49 | 0 | 0 | 0 | 0 | 0 | No
2030-01-21 12:00 | 2030 100% ECP | 377.25 | 0 | 210 | 210 | 0 | 0 | No
2030-01-21 13:00 | 2030 100% ECP | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-01-21 14:00 | 2030 100% ECP | 700 | 300 | 300 | 470.11 | 0 | 0 | No
2030-01-21 15:00 | 2030 100% ECP | 280 | 0 | 0 | 170.11 | 0 | 0 | No
2030-01-21 16:00 | 2030 100% ECP | 700 | 0 | -300 | -60.85 | 0 | 0 | No
2030-01-21 17:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-01-21 18:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-01-21 19:00 | 2030 100% ECP | 700 | 0 | -390 | -231.41 | 0 | 0 | No
2030-01-21 20:00 | 2030 100% ECP | 280 | 0 | -90 | -69.51 | 0 | 0 | No
2030-01-21 21:00 | 2030 100% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-21 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 23:00 | 2030 100% ECP | 700 | 205 | 510 | 340.12 | 0 | 0 | No
2030-01-22 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 06:00 | 2030 100% ECP | 700 | 505 | 510 | 210 | 0 | 0 | No
2030-01-22 07:00 | 2030 100% ECP | 700 | 505 | 510 | 0 | 0 | 0 | No
2030-01-22 08:00 | 2030 100% ECP | 700 | 505 | 510 | 0 | 0 | 0 | No
2030-01-22 09:00 | 2030 100% ECP | 700 | 505 | 510 | 65.51 | 0 | 0 | No
2030-01-22 10:00 | 2030 100% ECP | 700 | 505 | 510 | 135.83 | 0 | 0 | No
2030-01-22 11:00 | 2030 100% ECP | 700 | 505 | 510 | 126.01 | 0 | 0 | No
2030-01-22 12:00 | 2030 100% ECP | 700 | 505 | 510 | 99.81 | 0 | 0 | No
2030-01-22 13:00 | 2030 100% ECP | 700 | 505 | 510 | 103.36 | 0 | 0 | No
2030-01-22 14:00 | 2030 100% ECP | 700 | 374 | 390 | 86.68 | 0 | 0 | No
2030-01-22 15:00 | 2030 100% ECP | 700 | 74 | 90 | 87.06 | 0 | 0 | No
2030-01-22 16:00 | 2030 100% ECP | 700 | -226 | -210 | -212.94 | 0 | 0 | No
2030-01-22 17:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-22 18:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-22 19:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-22 20:00 | 2030 100% ECP | 700 | -226 | -210 | -245.52 | 0 | 0 | No
2030-01-22 21:00 | 2030 100% ECP | 700 | 74 | 90 | 54.48 | 0 | 0 | No
2030-01-22 22:00 | 2030 100% ECP | 700 | 374 | 390 | 210 | 0 | 0 | No
2030-01-22 23:00 | 2030 100% ECP | 700 | 417.7 | 510 | 510 | 0 | 0 | No
2030-01-23 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 06:00 | 2030 100% ECP | 292.33 | 505 | 510 | 281.11 | 0 | 0 | No
2030-01-23 07:00 | 2030 100% ECP | 280 | 205 | 210 | -18.89 | 0 | 0 | No
2030-01-23 08:00 | 2030 100% ECP | 700 | 0 | 153.94 | 0 | 0 | 0 | No
2030-01-23 09:00 | 2030 100% ECP | 700 | 0 | 453.94 | 233.31 | 0 | 0 | No
2030-01-23 10:00 | 2030 100% ECP | 700 | 0 | 397.17 | 300 | 0 | 0 | No
2030-01-23 11:00 | 2030 100% ECP | 700 | 0 | 97.17 | 0 | 0 | 0 | No
2030-01-23 12:00 | 2030 100% ECP | 700 | 0 | -202.83 | -24.68 | 0 | 0 | No
2030-01-23 13:00 | 2030 100% ECP | 583.41 | 0 | 0 | 0 | 0 | 0 | No
2030-01-23 14:00 | 2030 100% ECP | 647.55 | 0 | 0 | 0 | 0 | 0 | No
2030-01-23 15:00 | 2030 100% ECP | 700 | 13.45 | 109.63 | 269.86 | 0 | 0 | No
2030-01-23 16:00 | 2030 100% ECP | 700 | 0 | -190.37 | -30.14 | 0 | 0 | No
2030-01-23 17:00 | 2030 100% ECP | 280 | -300 | -490.37 | -330.14 | 0 | 0 | No
2030-01-23 18:00 | 2030 100% ECP | 700 | -333.85 | -510 | -510 | 0 | 0 | No
2030-01-23 19:00 | 2030 100% ECP | 700 | -33.85 | -210 | -210 | 0 | 0 | No
2030-01-23 20:00 | 2030 100% ECP | 700 | 266.15 | 90 | 90 | 0 | 0 | No
2030-01-23 21:00 | 2030 100% ECP | 700 | 155.86 | 390 | 131.56 | 0 | 0 | No
2030-01-23 22:00 | 2030 100% ECP | 700 | 81.69 | 510 | 116.95 | 0 | 0 | No
2030-01-23 23:00 | 2030 100% ECP | 700 | 167.96 | 510 | 416.95 | 0 | 0 | No
2030-01-24 | 2030 100% ECP | 700 | 467.96 | 510 | 510 | 0 | 0 | No
2030-01-24 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 06:00 | 2030 100% ECP | 700 | 505 | 510 | 210 | 0 | 0 | No
2030-01-24 07:00 | 2030 100% ECP | 700 | 505 | 510 | -90 | 0 | 0 | No
2030-01-24 08:00 | 2030 100% ECP | 280 | 205 | 491.35 | -157.41 | 0 | 0 | No
2030-01-24 09:00 | 2030 100% ECP | 0 | 238.61 | 510 | -53.47 | 0 | 0 | No
2030-01-24 10:00 | 2030 100% ECP | 0 | 0 | 420.03 | -109.92 | 0 | 0 | No
2030-01-24 11:00 | 2030 100% ECP | -263.5 | 0 | 120.03 | -73.75 | 0 | 0 | No
2030-01-24 12:00 | 2030 100% ECP | 156.5 | 300 | 300 | -88.76 | 0 | 0 | No
2030-01-24 13:00 | 2030 100% ECP | -263.5 | 0 | 0 | -388.76 | 0 | 0 | No
2030-01-24 14:00 | 2030 100% ECP | 0 | 0 | -300 | -510 | 0 | 0 | No
2030-01-24 15:00 | 2030 100% ECP | 0 | -226 | -510 | -510 | 0 | 0 | No
2030-01-24 16:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 17:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 18:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 19:00 | 2030 100% ECP | 169.96 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 20:00 | 2030 100% ECP | 589.96 | -300 | -510 | -475.67 | 0 | 0 | No
2030-01-24 21:00 | 2030 100% ECP | 700 | 0 | -210 | -175.67 | 0 | 0 | No
2030-01-24 22:00 | 2030 100% ECP | 379.46 | 0 | -300 | -300 | 0 | 0 | No
2030-01-24 23:00 | 2030 100% ECP | 236.6 | 0 | 0 | 0 | 0 | 0 | No
2030-01-25 | 2030 100% ECP | 0 | -300 | -300 | -300 | 0 | 0 | No
2030-01-25 01:00 | 2030 100% ECP | 0 | -526 | -510 | -297.91 | 0 | 0 | No
2030-01-25 02:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-01-25 03:00 | 2030 100% ECP | -280 | -226.22 | -510 | -510 | 0 | 0 | No
2030-01-25 04:00 | 2030 100% ECP | -700 | -60.92 | -510 | -510 | 0 | 0 | No
2030-01-25 05:00 | 2030 100% ECP | -700 | -112.7 | -510 | -510 | 0 | 0 | No
2030-01-25 06:00 | 2030 100% ECP | -700 | 0 | -510 | -510 | 0 | 0 | No
2030-01-25 07:00 | 2030 100% ECP | -700 | 0 | -510 | -510 | 0 | 0 | No
2030-01-25 08:00 | 2030 100% ECP | -700 | 0 | -235.17 | -210 | 0 | 0 | No
2030-01-25 09:00 | 2030 100% ECP | -700 | 0 | -448.29 | 0 | 0 | 0 | No
2030-01-25 10:00 | 2030 100% ECP | -700 | 0 | -271.48 | 0 | 0 | 0 | No
2030-01-25 11:00 | 2030 100% ECP | -700 | -100.21 | -510 | -245.86 | 0 | 0 | No
2030-01-25 12:00 | 2030 100% ECP | -700 | -342.98 | -510 | -469.05 | 0 | 0 | No
2030-01-25 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-25 14:00 | 2030 100% ECP | -700 | -300 | -510 | -510 | 0 | 0 | No
2030-01-25 15:00 | 2030 100% ECP | -700 | 0 | -300 | -317.36 | 0 | 0 | No
2030-01-25 16:00 | 2030 100% ECP | -700 | 0 | 0 | -56.97 | 0 | 0 | No
2030-01-25 17:00 | 2030 100% ECP | -700 | -300 | -300 | -356.97 | 0 | 0 | No
2030-01-25 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-25 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-25 20:00 | 2030 100% ECP | -700 | -499.44 | -510 | -340.42 | 0 | 0 | No
2030-01-25 21:00 | 2030 100% ECP | -700 | -526 | -510 | -43.39 | 0 | 0 | No
2030-01-25 22:00 | 2030 100% ECP | -700 | -526 | -510 | -68.61 | 0 | 0 | No
2030-01-25 23:00 | 2030 100% ECP | -700 | -526 | -510 | -123.43 | 0 | 0 | Yes
2030-01-26 | 2030 100% ECP | -700 | -226 | -210 | 176.57 | 0 | 0 | No
2030-01-26 01:00 | 2030 100% ECP | -700 | 74 | 90 | 476.57 | 0 | 0 | Yes
2030-01-26 02:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-26 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-26 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-26 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-26 06:00 | 2030 100% ECP | -700 | 505 | 428.84 | 214.71 | 0 | 0 | Yes
2030-01-26 07:00 | 2030 100% ECP | -700 | 205 | 128.84 | -85.29 | 0 | 0 | No
2030-01-26 08:00 | 2030 100% ECP | -700 | -95 | -171.16 | 40.93 | 0 | 0 | No
2030-01-26 09:00 | 2030 100% ECP | -700 | -395 | -471.16 | 340.93 | 0 | 0 | No
2030-01-26 10:00 | 2030 100% ECP | -700 | -526 | -510 | 163.25 | 0 | 0 | No
2030-01-26 11:00 | 2030 100% ECP | -700 | -526 | -510 | -58.99 | 0 | 0 | No
2030-01-26 12:00 | 2030 100% ECP | -700 | -526 | -510 | -143.4 | 0 | 0 | No
2030-01-26 13:00 | 2030 100% ECP | -700 | -526 | -510 | 156.6 | 0 | 0 | No
2030-01-26 14:00 | 2030 100% ECP | -700 | -526 | -510 | 121.94 | 0 | 0 | No
2030-01-26 15:00 | 2030 100% ECP | -700 | -526 | -510 | 311.45 | 0 | 0 | No
2030-01-26 16:00 | 2030 100% ECP | -700 | -526 | -510 | 300 | 0 | 0 | No
2030-01-26 17:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-01-26 18:00 | 2030 100% ECP | -700 | -526 | -510 | -300 | 0 | 0 | No
2030-01-26 19:00 | 2030 100% ECP | -700 | -526 | -510 | -293.18 | 0 | 0 | No
2030-01-26 20:00 | 2030 100% ECP | -700 | -526 | -510 | 6.82 | 0 | 0 | No
2030-01-26 21:00 | 2030 100% ECP | -700 | -526 | -510 | 126.1 | 0 | 0 | No
2030-01-26 22:00 | 2030 100% ECP | -700 | -526 | -510 | -59.47 | 0 | 0 | No
2030-01-26 23:00 | 2030 100% ECP | -700 | -526 | -510 | -359.47 | 0 | 0 | No
2030-01-27 | 2030 100% ECP | -700 | -226 | -210 | -59.47 | 0 | 0 | No
2030-01-27 01:00 | 2030 100% ECP | -700 | 74 | 90 | 210 | 0 | 0 | No
2030-01-27 02:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-01-27 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 08:00 | 2030 100% ECP | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-27 09:00 | 2030 100% ECP | -700 | -95 | -90 | -90 | 0 | 0 | No
2030-01-27 10:00 | 2030 100% ECP | -700 | -395 | -390 | -33.82 | 0 | 0 | No
2030-01-27 11:00 | 2030 100% ECP | -700 | -526 | -510 | -333.82 | 0 | 0 | No
2030-01-27 12:00 | 2030 100% ECP | -700 | -526 | -510 | -96.55 | 0 | 0 | No
2030-01-27 13:00 | 2030 100% ECP | -700 | -526 | -510 | -396.55 | 0 | 0 | No
2030-01-27 14:00 | 2030 100% ECP | -700 | -450.93 | -510 | -96.55 | 0 | 0 | No
2030-01-27 15:00 | 2030 100% ECP | -280 | -150.93 | -510 | 118.75 | 0 | 0 | No
2030-01-27 16:00 | 2030 100% ECP | -280 | 0 | -510 | 369.52 | 0 | 0 | No
2030-01-27 17:00 | 2030 100% ECP | -700 | -180.04 | -510 | 369.52 | 0 | 0 | No
2030-01-27 18:00 | 2030 100% ECP | -700 | -315.87 | -510 | 412.1 | 0 | 0 | No
2030-01-27 19:00 | 2030 100% ECP | -280 | -15.87 | -510 | 412.1 | 0 | 0 | No
2030-01-27 20:00 | 2030 100% ECP | 140 | 0 | -510 | 510 | 0 | 0 | No
2030-01-27 21:00 | 2030 100% ECP | 560 | 0 | -510 | 482.91 | 0 | 0 | No
2030-01-27 22:00 | 2030 100% ECP | 700 | -106.83 | -510 | 304.95 | 0 | 0 | No
2030-01-27 23:00 | 2030 100% ECP | 700 | -179.95 | -510 | 362.93 | 0 | 0 | No
2030-01-28 | 2030 100% ECP | 420 | -179.95 | -510 | 285.27 | 0 | 0 | No
2030-01-28 01:00 | 2030 100% ECP | 0 | -453.64 | -510 | 164.42 | 0 | 0 | No
2030-01-28 02:00 | 2030 100% ECP | 0 | -207.31 | -210 | 464.42 | 0 | 0 | No
2030-01-28 03:00 | 2030 100% ECP | 0 | 49.58 | 90 | 210 | 0 | 0 | No
2030-01-28 04:00 | 2030 100% ECP | 0 | 349.58 | 390 | 510 | 0 | 0 | No
2030-01-28 05:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-28 06:00 | 2030 100% ECP | -700 | 300 | 215.16 | 510 | 0 | 0 | No
2030-01-28 07:00 | 2030 100% ECP | -700 | 0 | -84.84 | 510 | 0 | 0 | No
2030-01-28 08:00 | 2030 100% ECP | -700 | -300 | -384.84 | 448.56 | 0 | 0 | No
2030-01-28 09:00 | 2030 100% ECP | -700 | -526 | -510 | 148.56 | 0 | 0 | No
2030-01-28 10:00 | 2030 100% ECP | -700 | -526 | -510 | 448.56 | 0 | 0 | No
2030-01-28 11:00 | 2030 100% ECP | -700 | -526 | -510 | 148.56 | 0 | 0 | No
2030-01-28 12:00 | 2030 100% ECP | -700 | -526 | -510 | 162.91 | 0 | 0 | No
2030-01-28 13:00 | 2030 100% ECP | -700 | -526 | -510 | 462.91 | 0 | 0 | No
2030-01-28 14:00 | 2030 100% ECP | -700 | -526 | -510 | 505.09 | 0 | 0 | No
2030-01-28 15:00 | 2030 100% ECP | -700 | -526 | -510 | 390.93 | 0 | 0 | No
2030-01-28 16:00 | 2030 100% ECP | -700 | -526 | -510 | 239.26 | 0 | 0 | No
2030-01-28 17:00 | 2030 100% ECP | -700 | -526 | -510 | 354.64 | 0 | 0 | No
2030-01-28 18:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-01-28 19:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-01-28 20:00 | 2030 100% ECP | -700 | -300 | -328.32 | 510 | 0 | 0 | No
2030-01-28 21:00 | 2030 100% ECP | -700 | 0 | -28.32 | 510 | 0 | 0 | No
2030-01-28 22:00 | 2030 100% ECP | -700 | 300 | 271.68 | 510 | 0 | 0 | Yes
2030-01-28 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-29 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 06:00 | 2030 100% ECP | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-01-29 07:00 | 2030 100% ECP | -700 | -95 | -90 | 440.11 | 0 | 0 | No
2030-01-29 08:00 | 2030 100% ECP | -700 | -395 | -390 | 510 | 0 | 0 | No
2030-01-29 09:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-01-29 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-01-29 11:00 | 2030 100% ECP | -700 | -526 | -510 | 500.12 | 0 | 0 | No
2030-01-29 12:00 | 2030 100% ECP | -700 | -526 | -510 | 200.12 | 0 | 0 | No
2030-01-29 13:00 | 2030 100% ECP | -700 | -526 | -510 | -99.88 | 0 | 0 | No
2030-01-29 14:00 | 2030 100% ECP | -700 | -526 | -510 | -305.13 | 0 | 0 | No
2030-01-29 15:00 | 2030 100% ECP | -700 | -526 | -510 | -450.63 | 0 | 0 | No
2030-01-29 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-29 17:00 | 2030 100% ECP | -700 | -526 | -510 | -341.28 | 0 | 0 | No
2030-01-29 18:00 | 2030 100% ECP | -700 | -526 | -510 | -41.28 | 0 | 0 | No
2030-01-29 19:00 | 2030 100% ECP | -700 | -526 | -510 | 258.72 | 0 | 0 | No
2030-01-29 20:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-01-29 21:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | No
2030-01-29 22:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-01-29 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-30 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 05:00 | 2030 100% ECP | -700 | 431.46 | 390 | 510 | 0 | 0 | No
2030-01-30 06:00 | 2030 100% ECP | -700 | 131.46 | 90 | 210 | 0 | 0 | No
2030-01-30 07:00 | 2030 100% ECP | -700 | -168.54 | -210 | -90 | 0 | 0 | No
2030-01-30 08:00 | 2030 100% ECP | -700 | -468.54 | -510 | 165.28 | 0 | 0 | No
2030-01-30 09:00 | 2030 100% ECP | -700 | -526 | -510 | 165.28 | 0 | 0 | No
2030-01-30 10:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-01-30 11:00 | 2030 100% ECP | -700 | -226 | -210 | 78.28 | 0 | 0 | No
2030-01-30 12:00 | 2030 100% ECP | -700 | 74 | 90 | 240.65 | 0 | 0 | No
2030-01-30 13:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-01-30 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 16:00 | 2030 100% ECP | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-30 17:00 | 2030 100% ECP | -700 | -95 | -90 | -90 | 0 | 0 | No
2030-01-30 18:00 | 2030 100% ECP | -700 | -395 | -390 | -298.07 | 0 | 0 | No
2030-01-30 19:00 | 2030 100% ECP | -700 | -300 | -210.1 | -90 | 0 | 0 | No
2030-01-30 20:00 | 2030 100% ECP | -700 | 0 | 89.9 | 210 | 0 | 0 | No
2030-01-30 21:00 | 2030 100% ECP | -700 | 300 | 389.9 | 510 | 0 | 0 | No
2030-01-30 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 06:00 | 2030 100% ECP | -700 | 462.77 | 210 | 510 | 0 | 0 | Yes
2030-01-31 07:00 | 2030 100% ECP | -700 | 162.77 | -90 | 510 | 0 | 0 | Yes
2030-01-31 08:00 | 2030 100% ECP | -700 | -137.23 | -390 | 319.32 | 0 | 0 | Yes
2030-01-31 09:00 | 2030 100% ECP | -700 | -400 | -510 | 236.62 | 0 | 0 | No
2030-01-31 10:00 | 2030 100% ECP | -700 | -100 | -210 | 510 | 0 | 0 | No
2030-01-31 11:00 | 2030 100% ECP | -700 | 127.61 | 90 | 510 | 0 | 0 | Yes
2030-01-31 12:00 | 2030 100% ECP | -700 | 427.61 | 390 | 510 | 0 | 0 | Yes
2030-01-31 13:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-31 14:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-01-31 15:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-01-31 16:00 | 2030 100% ECP | -700 | -526 | -510 | 267.5 | 0 | 0 | Yes
2030-01-31 17:00 | 2030 100% ECP | -700 | -526 | -510 | -32.5 | 0 | 0 | Yes
2030-01-31 18:00 | 2030 100% ECP | -700 | -526 | -510 | -332.5 | 0 | 0 | Yes
2030-01-31 19:00 | 2030 100% ECP | -700 | -526 | -510 | -122.77 | 0 | 0 | Yes
2030-01-31 20:00 | 2030 100% ECP | -700 | -226 | -210 | 177.23 | 0 | 0 | Yes
2030-01-31 21:00 | 2030 100% ECP | -700 | 74 | 90 | 477.23 | 0 | 0 | Yes
2030-01-31 22:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-31 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 15:00 | 2030 100% ECP | -700 | 491.82 | 510 | 510 | 0 | 0 | Yes
2030-02-01 16:00 | 2030 100% ECP | -485.34 | 191.82 | 300 | 320.91 | 0 | 0 | No
2030-02-01 17:00 | 2030 100% ECP | -333.13 | 0 | 0 | 20.91 | 0 | 0 | No
2030-02-01 18:00 | 2030 100% ECP | -382.43 | 0 | 0 | 320.91 | 0 | 0 | No
2030-02-01 19:00 | 2030 100% ECP | 37.57 | 0 | 0 | 273.19 | 0 | 0 | No
2030-02-01 20:00 | 2030 100% ECP | 457.57 | 0 | 0 | 273.19 | 0 | 0 | No
2030-02-01 21:00 | 2030 100% ECP | 700 | 0 | -296.91 | 159.17 | 0 | 0 | No
2030-02-01 22:00 | 2030 100% ECP | 700 | 0 | -296.91 | 159.17 | 0 | 0 | No
2030-02-01 23:00 | 2030 100% ECP | 700 | -249.28 | -510 | 0 | 0 | 0 | No
2030-02-02 | 2030 100% ECP | 403.89 | -526 | -510 | 109 | 0 | 0 | No
2030-02-02 01:00 | 2030 100% ECP | 0 | -510.41 | -510 | 122.1 | 0 | 0 | No
2030-02-02 02:00 | 2030 100% ECP | 420 | -210.41 | -223.47 | 52.29 | 0 | 0 | No
2030-02-02 03:00 | 2030 100% ECP | 0 | -226 | -436.9 | 0 | 0 | 0 | No
2030-02-02 04:00 | 2030 100% ECP | -420 | -526 | -510 | -47.22 | 0 | 0 | No
2030-02-02 05:00 | 2030 100% ECP | -700 | -526 | -510 | -43.61 | 0 | 0 | No
2030-02-02 06:00 | 2030 100% ECP | -700 | -526 | -510 | -170.79 | 0 | 0 | No
2030-02-02 07:00 | 2030 100% ECP | -700 | -526 | -510 | 5.99 | 0 | 0 | No
2030-02-02 08:00 | 2030 100% ECP | -700 | -526 | -510 | 30.65 | 0 | 0 | No
2030-02-02 09:00 | 2030 100% ECP | -700 | -526 | -510 | -46.38 | 0 | 0 | No
2030-02-02 10:00 | 2030 100% ECP | -700 | -526 | -510 | 15.08 | 0 | 0 | Yes
2030-02-02 11:00 | 2030 100% ECP | -700 | -526 | -510 | 68.55 | 0 | 0 | Yes
2030-02-02 12:00 | 2030 100% ECP | -700 | -526 | -510 | 102.15 | 0 | 0 | Yes
2030-02-02 13:00 | 2030 100% ECP | -700 | -526 | -510 | 53.82 | 0 | 0 | Yes
2030-02-02 14:00 | 2030 100% ECP | -700 | -526 | -510 | -83.05 | 0 | 0 | Yes
2030-02-02 15:00 | 2030 100% ECP | -700 | -526 | -510 | -135.67 | 0 | 0 | Yes
2030-02-02 16:00 | 2030 100% ECP | -700 | -526 | -510 | -206.39 | 0 | 0 | Yes
2030-02-02 17:00 | 2030 100% ECP | -700 | -526 | -510 | 93.61 | 0 | 0 | Yes
2030-02-02 18:00 | 2030 100% ECP | -700 | -526 | -510 | 166.64 | 0 | 0 | Yes
2030-02-02 19:00 | 2030 100% ECP | -700 | -526 | -510 | -133.36 | 0 | 0 | Yes
2030-02-02 20:00 | 2030 100% ECP | -700 | -526 | -510 | 14.13 | 0 | 0 | Yes
2030-02-02 21:00 | 2030 100% ECP | -700 | -526 | -510 | 314.13 | 0 | 0 | Yes
2030-02-02 22:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-02-02 23:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-02-03 | 2030 100% ECP | -700 | 374 | 390 | 232.52 | 0 | 0 | Yes
2030-02-03 01:00 | 2030 100% ECP | -700 | 505 | 510 | 111.7 | 0 | 0 | Yes
2030-02-03 02:00 | 2030 100% ECP | -700 | 505 | 510 | 158.67 | 0 | 0 | Yes
2030-02-03 03:00 | 2030 100% ECP | -700 | 505 | 510 | 192.58 | 0 | 0 | Yes
2030-02-03 04:00 | 2030 100% ECP | -700 | 505 | 510 | 135.84 | 0 | 0 | Yes
2030-02-03 05:00 | 2030 100% ECP | -700 | 505 | 510 | 178.21 | 0 | 0 | Yes
2030-02-03 06:00 | 2030 100% ECP | -700 | 505 | 510 | 254.53 | 0 | 0 | Yes
2030-02-03 07:00 | 2030 100% ECP | -700 | 505 | 510 | 265.48 | 0 | 0 | Yes
2030-02-03 08:00 | 2030 100% ECP | -700 | 505 | 510 | 235.44 | 0 | 0 | Yes
2030-02-03 09:00 | 2030 100% ECP | -700 | 505 | 510 | 486.25 | 0 | 0 | Yes
2030-02-03 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 12:00 | 2030 100% ECP | -700 | 505 | 510 | 450.93 | 0 | 0 | Yes
2030-02-03 13:00 | 2030 100% ECP | -700 | 505 | 510 | 408.87 | 0 | 0 | Yes
2030-02-03 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 15:00 | 2030 100% ECP | -700 | 505 | 510 | 452.94 | 0 | 0 | Yes
2030-02-03 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 17:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 18:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 01:00 | 2030 100% ECP | -700 | 505 | 510 | 374.71 | 0 | 0 | Yes
2030-02-04 02:00 | 2030 100% ECP | -700 | 505 | 510 | 482.38 | 0 | 0 | Yes
2030-02-04 03:00 | 2030 100% ECP | -700 | 505 | 510 | 182.38 | 0 | 0 | Yes
2030-02-04 04:00 | 2030 100% ECP | -700 | 505 | 510 | 24.85 | 0 | 0 | Yes
2030-02-04 05:00 | 2030 100% ECP | -700 | 505 | 510 | 298 | 0 | 0 | Yes
2030-02-04 06:00 | 2030 100% ECP | -700 | 505 | 510 | 133.65 | 0 | 0 | Yes
2030-02-04 07:00 | 2030 100% ECP | -700 | 505 | 510 | 335.41 | 0 | 0 | Yes
2030-02-04 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 15:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 16:00 | 2030 100% ECP | 140 | 454.05 | 510 | 510 | 0 | 0 | No
2030-02-04 17:00 | 2030 100% ECP | 560 | 237.48 | 510 | 510 | 0 | 0 | No
2030-02-04 18:00 | 2030 100% ECP | 700 | 237.48 | 510 | 510 | 0 | 0 | No
2030-02-04 19:00 | 2030 100% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-02-04 20:00 | 2030 100% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-02-04 21:00 | 2030 100% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-02-04 22:00 | 2030 100% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-02-04 23:00 | 2030 100% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-02-05 | 2030 100% ECP | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-02-05 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 05:00 | 2030 100% ECP | 280 | 300 | 466.89 | 300 | 0 | 0 | No
2030-02-05 06:00 | 2030 100% ECP | -140 | 0 | 166.89 | 0 | 0 | 0 | No
2030-02-05 07:00 | 2030 100% ECP | -280 | 0 | 4.47 | 199.92 | 0 | 0 | No
2030-02-05 08:00 | 2030 100% ECP | -700 | 0 | -295.53 | -59.09 | 0 | 0 | No
2030-02-05 09:00 | 2030 100% ECP | -280 | -226 | -210 | 9.99 | 0 | 0 | No
2030-02-05 10:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-02-05 11:00 | 2030 100% ECP | -700 | -518.74 | -510 | 53.33 | 0 | 0 | No
2030-02-05 12:00 | 2030 100% ECP | -700 | -483.43 | -510 | 13 | 0 | 0 | No
2030-02-05 13:00 | 2030 100% ECP | -700 | -202.78 | -300 | 39.29 | 0 | 0 | No
2030-02-05 14:00 | 2030 100% ECP | -700 | 0 | 0 | 66.39 | 0 | 0 | No
2030-02-05 15:00 | 2030 100% ECP | -700 | 0 | -37.79 | 77.37 | 0 | 0 | No
2030-02-05 16:00 | 2030 100% ECP | -280 | 0 | 0 | 63.48 | 0 | 0 | No
2030-02-05 17:00 | 2030 100% ECP | -700 | -300 | -300 | -210 | 0 | 0 | No
2030-02-05 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-05 19:00 | 2030 100% ECP | -700 | -526 | -510 | -259.6 | 0 | 0 | No
2030-02-05 20:00 | 2030 100% ECP | -280 | -226 | -210 | 40.4 | 0 | 0 | No
2030-02-05 21:00 | 2030 100% ECP | 140 | 74 | 90 | 340.4 | 0 | 0 | No
2030-02-05 22:00 | 2030 100% ECP | -280 | 0 | 310.89 | 214.06 | 0 | 0 | No
2030-02-05 23:00 | 2030 100% ECP | 65.57 | 0 | 10.89 | 142.24 | 0 | 0 | No
2030-02-06 | 2030 100% ECP | 140 | 0 | 310.89 | 442.24 | 0 | 0 | No
2030-02-06 01:00 | 2030 100% ECP | 560 | 0 | 67 | 142.24 | 0 | 0 | No
2030-02-06 02:00 | 2030 100% ECP | 140 | 0 | 0 | 232.23 | 0 | 0 | No
2030-02-06 03:00 | 2030 100% ECP | -280 | 0 | 0 | 510 | 0 | 0 | No
2030-02-06 04:00 | 2030 100% ECP | -700 | 0 | 90 | 233.71 | 0 | 0 | No
2030-02-06 05:00 | 2030 100% ECP | -700 | -226 | -210 | -66.29 | 0 | 0 | No
2030-02-06 06:00 | 2030 100% ECP | -700 | -526 | -510 | -366.29 | 0 | 0 | No
2030-02-06 07:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-02-06 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 09:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-02-06 10:00 | 2030 100% ECP | -700 | -526 | -510 | -57 | 0 | 0 | No
2030-02-06 11:00 | 2030 100% ECP | -700 | -526 | -510 | -168.15 | 0 | 0 | No
2030-02-06 12:00 | 2030 100% ECP | -700 | -526 | -510 | -208.76 | 0 | 0 | No
2030-02-06 13:00 | 2030 100% ECP | -700 | -526 | -510 | -103.29 | 0 | 0 | No
2030-02-06 14:00 | 2030 100% ECP | -700 | -526 | -510 | -194.85 | 0 | 0 | No
2030-02-06 15:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-02-06 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 20:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 21:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 22:00 | 2030 100% ECP | -700 | -526 | -510 | -305.65 | 0 | 0 | No
2030-02-06 23:00 | 2030 100% ECP | -700 | -526 | -510 | -430.18 | 0 | 0 | No
2030-02-07 | 2030 100% ECP | -700 | -526 | -510 | -130.18 | 0 | 0 | No
2030-02-07 01:00 | 2030 100% ECP | -700 | -526 | -510 | -75.97 | 0 | 0 | No
2030-02-07 02:00 | 2030 100% ECP | -700 | -526 | -510 | -75.7 | 0 | 0 | Yes
2030-02-07 03:00 | 2030 100% ECP | -700 | -526 | -510 | -375.7 | 0 | 0 | Yes
2030-02-07 04:00 | 2030 100% ECP | -700 | -526 | -510 | -253.48 | 0 | 0 | Yes
2030-02-07 05:00 | 2030 100% ECP | -700 | -526 | -510 | -121.67 | 0 | 0 | Yes
2030-02-07 06:00 | 2030 100% ECP | -700 | -526 | -510 | 48.97 | 0 | 0 | Yes
2030-02-07 07:00 | 2030 100% ECP | -700 | -526 | -510 | -134.14 | 0 | 0 | Yes
2030-02-07 08:00 | 2030 100% ECP | -700 | -526 | -510 | -312.06 | 0 | 0 | Yes
2030-02-07 09:00 | 2030 100% ECP | -700 | -526 | -510 | -353.85 | 0 | 0 | Yes
2030-02-07 10:00 | 2030 100% ECP | -700 | -526 | -510 | -58.46 | 0 | 0 | Yes
2030-02-07 11:00 | 2030 100% ECP | -700 | -526 | -510 | -150.43 | 0 | 0 | Yes
2030-02-07 12:00 | 2030 100% ECP | -700 | -526 | -510 | -143.92 | 0 | 0 | Yes
2030-02-07 13:00 | 2030 100% ECP | -700 | -526 | -510 | 156.08 | 0 | 0 | Yes
2030-02-07 14:00 | 2030 100% ECP | -700 | -454.36 | -510 | 456.08 | 0 | 0 | Yes
2030-02-07 15:00 | 2030 100% ECP | -700 | -226 | -210 | 156.98 | 0 | 0 | Yes
2030-02-07 16:00 | 2030 100% ECP | -700 | -526 | -510 | -143.02 | 0 | 0 | Yes
2030-02-07 17:00 | 2030 100% ECP | -700 | -526 | -510 | -443.02 | 0 | 0 | Yes
2030-02-07 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-07 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-07 20:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-02-07 21:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-02-07 22:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-02-07 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 09:00 | 2030 100% ECP | -700 | 205 | 381.87 | 210 | 0 | 0 | Yes
2030-02-08 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 17:00 | 2030 100% ECP | -700 | 300 | 326.97 | 379.92 | 0 | 0 | Yes
2030-02-08 18:00 | 2030 100% ECP | -700 | 0 | 26.97 | 79.92 | 0 | 0 | Yes
2030-02-08 19:00 | 2030 100% ECP | -700 | 202.84 | 210 | 379.92 | 0 | 0 | Yes
2030-02-08 20:00 | 2030 100% ECP | -700 | 502.84 | 510 | 510 | 0 | 0 | Yes
2030-02-08 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 06:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-02-09 07:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-02-09 08:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-02-09 09:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 10:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 11:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 14:00 | 2030 100% ECP | -700 | -226 | -510 | -452.18 | 0 | 0 | Yes
2030-02-09 15:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-02-09 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 19:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-02-09 20:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-02-09 21:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-02-09 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 | 2030 100% ECP | -700 | 505 | 510 | 445.71 | 0 | 0 | Yes
2030-02-10 01:00 | 2030 100% ECP | -700 | 505 | 510 | 217.13 | 0 | 0 | Yes
2030-02-10 02:00 | 2030 100% ECP | -700 | 505 | 510 | 224.59 | 0 | 0 | Yes
2030-02-10 03:00 | 2030 100% ECP | -700 | 505 | 510 | 384.94 | 0 | 0 | Yes
2030-02-10 04:00 | 2030 100% ECP | -700 | 505 | 510 | 368.24 | 0 | 0 | Yes
2030-02-10 05:00 | 2030 100% ECP | -700 | 505 | 510 | 107.67 | 0 | 0 | Yes
2030-02-10 06:00 | 2030 100% ECP | -700 | 505 | 510 | 64.14 | 0 | 0 | Yes
2030-02-10 07:00 | 2030 100% ECP | -700 | 505 | 510 | 245.95 | 0 | 0 | Yes
2030-02-10 08:00 | 2030 100% ECP | -700 | 505 | 510 | 393.18 | 0 | 0 | Yes
2030-02-10 09:00 | 2030 100% ECP | -700 | 505 | 510 | 198.45 | 0 | 0 | Yes
2030-02-10 10:00 | 2030 100% ECP | -700 | 505 | 510 | 357.54 | 0 | 0 | Yes
2030-02-10 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 12:00 | 2030 100% ECP | -700 | 505 | 510 | 290.91 | 0 | 0 | Yes
2030-02-10 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 15:00 | 2030 100% ECP | -700 | 505 | 510 | 260.96 | 0 | 0 | Yes
2030-02-10 16:00 | 2030 100% ECP | -700 | 505 | 510 | 458.79 | 0 | 0 | Yes
2030-02-10 17:00 | 2030 100% ECP | -700 | 505 | 510 | 345.54 | 0 | 0 | Yes
2030-02-10 18:00 | 2030 100% ECP | -700 | 505 | 510 | 465.94 | 0 | 0 | Yes
2030-02-10 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 22:00 | 2030 100% ECP | -700 | 505 | 510 | 460.77 | 0 | 0 | Yes
2030-02-10 23:00 | 2030 100% ECP | -700 | 505 | 510 | 313.32 | 0 | 0 | Yes
2030-02-11 | 2030 100% ECP | -700 | 505 | 510 | 256.16 | 0 | 0 | Yes
2030-02-11 01:00 | 2030 100% ECP | -700 | 505 | 510 | 209.67 | 0 | 0 | Yes
2030-02-11 02:00 | 2030 100% ECP | -700 | 505 | 510 | 207.6 | 0 | 0 | Yes
2030-02-11 03:00 | 2030 100% ECP | -700 | 505 | 510 | 153.02 | 0 | 0 | Yes
2030-02-11 04:00 | 2030 100% ECP | -700 | 505 | 510 | 203.12 | 0 | 0 | Yes
2030-02-11 05:00 | 2030 100% ECP | -700 | 505 | 510 | 109.76 | 0 | 0 | Yes
2030-02-11 06:00 | 2030 100% ECP | -700 | 505 | 510 | 156.56 | 0 | 0 | Yes
2030-02-11 07:00 | 2030 100% ECP | -700 | 505 | 510 | 456.56 | 0 | 0 | Yes
2030-02-11 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 17:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 18:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 01:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 02:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 03:00 | 2030 100% ECP | 536.61 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 04:00 | 2030 100% ECP | 116.61 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 05:00 | 2030 100% ECP | -303.39 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 16:00 | 2030 100% ECP | -700 | 205 | 210 | 486.95 | 0 | 0 | No
2030-02-12 17:00 | 2030 100% ECP | -700 | -95 | -90 | 486.95 | 0 | 0 | No
2030-02-12 18:00 | 2030 100% ECP | -700 | -395 | -390 | 486.95 | 0 | 0 | No
2030-02-12 19:00 | 2030 100% ECP | -700 | -526 | -510 | 235.93 | 0 | 0 | No
2030-02-12 20:00 | 2030 100% ECP | -700 | -526 | -510 | 132.01 | 0 | 0 | No
2030-02-12 21:00 | 2030 100% ECP | -700 | -526 | -510 | -2.55 | 0 | 0 | No
2030-02-12 22:00 | 2030 100% ECP | -700 | -526 | -510 | -104.06 | 0 | 0 | No
2030-02-12 23:00 | 2030 100% ECP | -700 | -226 | -210 | 195.94 | 0 | 0 | Yes
2030-02-13 | 2030 100% ECP | -280 | 74 | 90 | 495.94 | 0 | 0 | Yes
2030-02-13 01:00 | 2030 100% ECP | 140 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-13 02:00 | 2030 100% ECP | 191.87 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 03:00 | 2030 100% ECP | 611.87 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 06:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 07:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 08:00 | 2030 100% ECP | 700 | 205 | 210 | 228.11 | 0 | 0 | No
2030-02-13 09:00 | 2030 100% ECP | 483.93 | -95 | -90 | 64.37 | 0 | 0 | No
2030-02-13 10:00 | 2030 100% ECP | 194.87 | -361.82 | -390 | 364.37 | 0 | 0 | No
2030-02-13 11:00 | 2030 100% ECP | 0 | -526 | -510 | 104.35 | 0 | 0 | No
2030-02-13 12:00 | 2030 100% ECP | -280 | -526 | -510 | -195.65 | 0 | 0 | No
2030-02-13 13:00 | 2030 100% ECP | -700 | -526 | -510 | -290.46 | 0 | 0 | No
2030-02-13 14:00 | 2030 100% ECP | -280 | -526 | -510 | 9.54 | 0 | 0 | No
2030-02-13 15:00 | 2030 100% ECP | 140 | -526 | -510 | 309.54 | 0 | 0 | No
2030-02-13 16:00 | 2030 100% ECP | 560 | -226 | -210 | 510 | 0 | 0 | No
2030-02-13 17:00 | 2030 100% ECP | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-02-13 18:00 | 2030 100% ECP | 700 | 0 | 0 | 390.1 | 0 | 0 | No
2030-02-13 19:00 | 2030 100% ECP | 700 | 56.11 | 300 | 510 | 0 | 0 | No
2030-02-13 20:00 | 2030 100% ECP | 700 | 213.63 | 390 | 510 | 0 | 0 | No
2030-02-13 21:00 | 2030 100% ECP | 560 | 74 | 90 | 510 | 0 | 0 | No
2030-02-13 22:00 | 2030 100% ECP | 140 | -226 | -210 | 510 | 0 | 0 | No
2030-02-13 23:00 | 2030 100% ECP | -280 | -526 | -510 | 442.14 | 0 | 0 | No
2030-02-14 | 2030 100% ECP | -700 | -526 | -510 | 197.98 | 0 | 0 | No
2030-02-14 01:00 | 2030 100% ECP | -700 | -526 | -510 | -31.98 | 0 | 0 | No
2030-02-14 02:00 | 2030 100% ECP | -700 | -526 | -510 | -142.84 | 0 | 0 | Yes
2030-02-14 03:00 | 2030 100% ECP | -700 | -526 | -510 | -194.32 | 0 | 0 | Yes
2030-02-14 04:00 | 2030 100% ECP | -700 | -526 | -510 | -152.12 | 0 | 0 | Yes
2030-02-14 05:00 | 2030 100% ECP | -700 | -526 | -510 | -400.03 | 0 | 0 | Yes
2030-02-14 06:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-14 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-14 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-14 09:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-02-14 10:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-02-14 11:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-02-14 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 14:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-14 15:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-02-14 16:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-02-14 17:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-02-14 18:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-02-14 19:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-02-14 20:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-02-14 21:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-02-14 22:00 | 2030 100% ECP | -700 | -226 | -328.32 | 280.16 | 0 | 0 | No
2030-02-14 23:00 | 2030 100% ECP | -700 | 74 | -28.32 | 510 | 0 | 0 | Yes
2030-02-15 | 2030 100% ECP | -700 | 374 | 271.68 | 510 | 0 | 0 | Yes
2030-02-15 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 12:00 | 2030 100% ECP | -700 | 302.34 | 210 | 510 | 0 | 0 | Yes
2030-02-15 13:00 | 2030 100% ECP | -700 | 2.34 | -90 | 510 | 0 | 0 | Yes
2030-02-15 14:00 | 2030 100% ECP | -700 | -297.66 | -390 | 312.49 | 0 | 0 | Yes
2030-02-15 15:00 | 2030 100% ECP | -700 | -226 | -210 | 130.86 | 0 | 0 | Yes
2030-02-15 16:00 | 2030 100% ECP | -700 | -526 | -510 | -169.14 | 0 | 0 | Yes
2030-02-15 17:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-02-15 18:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-02-15 19:00 | 2030 100% ECP | -700 | -526 | -510 | 190.17 | 0 | 0 | No
2030-02-15 20:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-02-15 21:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-02-15 22:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-02-15 23:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-16 | 2030 100% ECP | -700 | 505 | 510 | 346.54 | 0 | 0 | Yes
2030-02-16 01:00 | 2030 100% ECP | -700 | 505 | 510 | 105.07 | 0 | 0 | Yes
2030-02-16 02:00 | 2030 100% ECP | -700 | 505 | 510 | 405.07 | 0 | 0 | Yes
2030-02-16 03:00 | 2030 100% ECP | -700 | 505 | 510 | 341.59 | 0 | 0 | Yes
2030-02-16 04:00 | 2030 100% ECP | -700 | 505 | 510 | 96.8 | 0 | 0 | Yes
2030-02-16 05:00 | 2030 100% ECP | -700 | 505 | 510 | 291.42 | 0 | 0 | Yes
2030-02-16 06:00 | 2030 100% ECP | -700 | 505 | 510 | 488.14 | 0 | 0 | Yes
2030-02-16 07:00 | 2030 100% ECP | -700 | 505 | 510 | 483.82 | 0 | 0 | Yes
2030-02-16 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 09:00 | 2030 100% ECP | -700 | 505 | 510 | 469.55 | 0 | 0 | Yes
2030-02-16 10:00 | 2030 100% ECP | -700 | 505 | 510 | 413.35 | 0 | 0 | Yes
2030-02-16 11:00 | 2030 100% ECP | -700 | 505 | 510 | 408.94 | 0 | 0 | Yes
2030-02-16 12:00 | 2030 100% ECP | -700 | 505 | 510 | 390.8 | 0 | 0 | Yes
2030-02-16 13:00 | 2030 100% ECP | -700 | 505 | 510 | 397.47 | 0 | 0 | Yes
2030-02-16 14:00 | 2030 100% ECP | -700 | 505 | 510 | 404.57 | 0 | 0 | Yes
2030-02-16 15:00 | 2030 100% ECP | -700 | 505 | 429.98 | 305.99 | 0 | 0 | Yes
2030-02-16 16:00 | 2030 100% ECP | -700 | 205 | 129.98 | 90 | 0 | 0 | Yes
2030-02-16 17:00 | 2030 100% ECP | -700 | -95 | -170.02 | -210 | 0 | 0 | Yes
2030-02-16 18:00 | 2030 100% ECP | -700 | -395 | -470.02 | -510 | 0 | 0 | Yes
2030-02-16 19:00 | 2030 100% ECP | -700 | -95 | -170.02 | -210 | 0 | 0 | Yes
2030-02-16 20:00 | 2030 100% ECP | -700 | 205 | 129.98 | 90 | 0 | 0 | Yes
2030-02-16 21:00 | 2030 100% ECP | -700 | 505 | 429.98 | 390 | 0 | 0 | Yes
2030-02-16 22:00 | 2030 100% ECP | -700 | 505 | 510 | 322.21 | 0 | 0 | Yes
2030-02-16 23:00 | 2030 100% ECP | -700 | 505 | 510 | 236.04 | 0 | 0 | Yes
2030-02-17 | 2030 100% ECP | -700 | 505 | 510 | 106.78 | 0 | 0 | Yes
2030-02-17 01:00 | 2030 100% ECP | -700 | 505 | 510 | 100.61 | 0 | 0 | Yes
2030-02-17 02:00 | 2030 100% ECP | -700 | 505 | 510 | 82.56 | 0 | 0 | Yes
2030-02-17 03:00 | 2030 100% ECP | -700 | 505 | 510 | 55.35 | 0 | 0 | Yes
2030-02-17 04:00 | 2030 100% ECP | -700 | 505 | 510 | 141.3 | 0 | 0 | Yes
2030-02-17 05:00 | 2030 100% ECP | -700 | 505 | 510 | 441.3 | 0 | 0 | Yes
2030-02-17 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 12:00 | 2030 100% ECP | -700 | 505 | 510 | 434.13 | 0 | 0 | Yes
2030-02-17 13:00 | 2030 100% ECP | -700 | 505 | 510 | 447.63 | 0 | 0 | Yes
2030-02-17 14:00 | 2030 100% ECP | -700 | 505 | 510 | 498.07 | 0 | 0 | Yes
2030-02-17 15:00 | 2030 100% ECP | -700 | 505 | 510 | 458.03 | 0 | 0 | Yes
2030-02-17 16:00 | 2030 100% ECP | -700 | 505 | 510 | 401.07 | 0 | 0 | Yes
2030-02-17 17:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 18:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 23:00 | 2030 100% ECP | -700 | 505 | 510 | 355.36 | 0 | 0 | Yes
2030-02-18 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 17:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 18:00 | 2030 100% ECP | -700 | 205 | 436.64 | 510 | 0 | 0 | Yes
2030-02-18 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 01:00 | 2030 100% ECP | -624.66 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 02:00 | 2030 100% ECP | -431.69 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 03:00 | 2030 100% ECP | -110.91 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 04:00 | 2030 100% ECP | -530.91 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 05:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-02-19 06:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | No
2030-02-19 07:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-02-19 08:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-02-19 09:00 | 2030 100% ECP | -700 | -526 | -510 | 184.79 | 0 | 0 | No
2030-02-19 10:00 | 2030 100% ECP | -700 | -226 | -210 | 484.79 | 0 | 0 | Yes
2030-02-19 11:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-02-19 12:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-19 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-19 14:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-19 15:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-02-19 16:00 | 2030 100% ECP | -700 | -226 | -210 | 266.67 | 0 | 0 | Yes
2030-02-19 17:00 | 2030 100% ECP | -700 | -526 | -510 | -33.33 | 0 | 0 | Yes
2030-02-19 18:00 | 2030 100% ECP | -700 | -526 | -510 | -90 | 0 | 0 | No
2030-02-19 19:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-02-19 20:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-02-19 21:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-02-19 22:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | No
2030-02-19 23:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-20 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 08:00 | 2030 100% ECP | -700 | 266.33 | 210 | 307.32 | 0 | 0 | Yes
2030-02-20 09:00 | 2030 100% ECP | -700 | -33.67 | -90 | 7.32 | 0 | 0 | No
2030-02-20 10:00 | 2030 100% ECP | -700 | 266.33 | 210 | 307.32 | 0 | 0 | Yes
2030-02-20 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 15:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-20 16:00 | 2030 100% ECP | -700 | 74 | 90 | 251.7 | 0 | 0 | Yes
2030-02-20 17:00 | 2030 100% ECP | -700 | -226 | -210 | -48.3 | 0 | 0 | Yes
2030-02-20 18:00 | 2030 100% ECP | -700 | -526 | -510 | -348.3 | 0 | 0 | No
2030-02-20 19:00 | 2030 100% ECP | -700 | -526 | -510 | -48.3 | 0 | 0 | No
2030-02-20 20:00 | 2030 100% ECP | -700 | -231.39 | -390 | 251.7 | 0 | 0 | No
2030-02-20 21:00 | 2030 100% ECP | -700 | 68.61 | -90 | 510 | 0 | 0 | Yes
2030-02-20 22:00 | 2030 100% ECP | -700 | 368.61 | 210 | 510 | 0 | 0 | Yes
2030-02-20 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 15:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-02-21 16:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-02-21 17:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-02-21 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-21 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-21 20:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-02-21 21:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-02-21 22:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-02-21 23:00 | 2030 100% ECP | -700 | 505 | 510 | 369.67 | 0 | 0 | Yes
2030-02-22 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 02:00 | 2030 100% ECP | -700 | 505 | 510 | 410.64 | 0 | 0 | Yes
2030-02-22 03:00 | 2030 100% ECP | -700 | 505 | 510 | 382.26 | 0 | 0 | Yes
2030-02-22 04:00 | 2030 100% ECP | -700 | 505 | 510 | 170.49 | 0 | 0 | Yes
2030-02-22 05:00 | 2030 100% ECP | -700 | 505 | 510 | 368.47 | 0 | 0 | Yes
2030-02-22 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 15:00 | 2030 100% ECP | -700 | 374 | 390 | 482.62 | 0 | 0 | Yes
2030-02-22 16:00 | 2030 100% ECP | -700 | 74 | 90 | 182.62 | 0 | 0 | Yes
2030-02-22 17:00 | 2030 100% ECP | -700 | -226 | -210 | -117.38 | 0 | 0 | No
2030-02-22 18:00 | 2030 100% ECP | -700 | -526 | -510 | -417.38 | 0 | 0 | No
2030-02-22 19:00 | 2030 100% ECP | -700 | -526 | -510 | -117.38 | 0 | 0 | No
2030-02-22 20:00 | 2030 100% ECP | -700 | -526 | -510 | 182.62 | 0 | 0 | No
2030-02-22 21:00 | 2030 100% ECP | -700 | -226 | -210 | 482.62 | 0 | 0 | No
2030-02-22 22:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | No
2030-02-22 23:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-02-23 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 01:00 | 2030 100% ECP | -31.06 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 02:00 | 2030 100% ECP | -58.76 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 03:00 | 2030 100% ECP | -478.76 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 04:00 | 2030 100% ECP | -478.76 | 374 | 390 | 510 | 0 | 0 | No
2030-02-23 05:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | No
2030-02-23 06:00 | 2030 100% ECP | -700 | -226 | -210 | 404.3 | 0 | 0 | No
2030-02-23 07:00 | 2030 100% ECP | -700 | -526 | -510 | 177.6 | 0 | 0 | No
2030-02-23 08:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-02-23 09:00 | 2030 100% ECP | -489.56 | -526 | -510 | -143.31 | 0 | 0 | No
2030-02-23 10:00 | 2030 100% ECP | -700 | -226 | -210 | 156.69 | 0 | 0 | No
2030-02-23 11:00 | 2030 100% ECP | -700 | 74 | 90 | 456.69 | 0 | 0 | Yes
2030-02-23 12:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-23 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-23 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-23 15:00 | 2030 100% ECP | -420 | 300 | 510 | 510 | 0 | 0 | No
2030-02-23 16:00 | 2030 100% ECP | 0 | 0 | 231.81 | 210 | 0 | 0 | No
2030-02-23 17:00 | 2030 100% ECP | 420 | 0 | 0 | 210 | 0 | 0 | No
2030-02-23 18:00 | 2030 100% ECP | 0 | 0 | -132.4 | 510 | 0 | 0 | No
2030-02-23 19:00 | 2030 100% ECP | 0 | 0 | -215.08 | 510 | 0 | 0 | No
2030-02-23 20:00 | 2030 100% ECP | -140.38 | 0 | 0 | 510 | 0 | 0 | No
2030-02-23 21:00 | 2030 100% ECP | -560.38 | 0 | -284.99 | 510 | 0 | 0 | No
2030-02-23 22:00 | 2030 100% ECP | -464.14 | -226 | -510 | 510 | 0 | 0 | No
2030-02-23 23:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-02-24 | 2030 100% ECP | -700 | -526 | -510 | 390 | 0 | 0 | No
2030-02-24 01:00 | 2030 100% ECP | -700 | -526 | -510 | 90 | 0 | 0 | Yes
2030-02-24 02:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-02-24 03:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-24 04:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-24 05:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-24 06:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-02-24 07:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-02-24 08:00 | 2030 100% ECP | -700 | 300 | 98.77 | 390 | 0 | 0 | Yes
2030-02-24 09:00 | 2030 100% ECP | -700 | 0 | -201.23 | 399.08 | 0 | 0 | Yes
2030-02-24 10:00 | 2030 100% ECP | -700 | -300 | -501.23 | 510 | 0 | 0 | Yes
2030-02-24 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-02-24 12:00 | 2030 100% ECP | -700 | -526 | -510 | 413.91 | 0 | 0 | Yes
2030-02-24 13:00 | 2030 100% ECP | -700 | -526 | -510 | 312.3 | 0 | 0 | Yes
2030-02-24 14:00 | 2030 100% ECP | -700 | -526 | -510 | 12.3 | 0 | 0 | Yes
2030-02-24 15:00 | 2030 100% ECP | -700 | -526 | -510 | -287.7 | 0 | 0 | Yes
2030-02-24 16:00 | 2030 100% ECP | -700 | -526 | -510 | -459.18 | 0 | 0 | Yes
2030-02-24 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-24 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-24 19:00 | 2030 100% ECP | -700 | -526 | -510 | -300 | 0 | 0 | No
2030-02-24 20:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-02-24 21:00 | 2030 100% ECP | -700 | -526 | -510 | 228.7 | 0 | 0 | No
2030-02-24 22:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-02-24 23:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | No
2030-02-25 | 2030 100% ECP | -280 | 374 | 390 | 510 | 0 | 0 | No
2030-02-25 01:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 02:00 | 2030 100% ECP | 40.22 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 03:00 | 2030 100% ECP | 118.74 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 04:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 06:00 | 2030 100% ECP | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-02-25 07:00 | 2030 100% ECP | -700 | -95 | -90 | 210 | 0 | 0 | No
2030-02-25 08:00 | 2030 100% ECP | -700 | -395 | -390 | 226.06 | 0 | 0 | No
2030-02-25 09:00 | 2030 100% ECP | -700 | -526 | -510 | 457.88 | 0 | 0 | No
2030-02-25 10:00 | 2030 100% ECP | -700 | -526 | -510 | 216.55 | 0 | 0 | Yes
2030-02-25 11:00 | 2030 100% ECP | -700 | -526 | -510 | 342.85 | 0 | 0 | Yes
2030-02-25 12:00 | 2030 100% ECP | -700 | -526 | -510 | 331.8 | 0 | 0 | Yes
2030-02-25 13:00 | 2030 100% ECP | -700 | -526 | -510 | 176.7 | 0 | 0 | Yes
2030-02-25 14:00 | 2030 100% ECP | -700 | -526 | -510 | -10.66 | 0 | 0 | Yes
2030-02-25 15:00 | 2030 100% ECP | -700 | -526 | -510 | 289.34 | 0 | 0 | Yes
2030-02-25 16:00 | 2030 100% ECP | -700 | -526 | -510 | 289.34 | 0 | 0 | Yes
2030-02-25 17:00 | 2030 100% ECP | -700 | -526 | -510 | 93.97 | 0 | 0 | No
2030-02-25 18:00 | 2030 100% ECP | -700 | -526 | -510 | 217.56 | 0 | 0 | No
2030-02-25 19:00 | 2030 100% ECP | -700 | -526 | -510 | 440.24 | 0 | 0 | No
2030-02-25 20:00 | 2030 100% ECP | -700 | -526 | -510 | 440.24 | 0 | 0 | No
2030-02-25 21:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-02-25 22:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-02-25 23:00 | 2030 100% ECP | -700 | -526 | -510 | 419.49 | 0 | 0 | Yes
2030-02-26 | 2030 100% ECP | -280 | -226 | -210 | 510 | 0 | 0 | No
2030-02-26 01:00 | 2030 100% ECP | 140 | 74 | 90 | 510 | 0 | 0 | No
2030-02-26 02:00 | 2030 100% ECP | 560 | 374 | 390 | 510 | 0 | 0 | No
2030-02-26 03:00 | 2030 100% ECP | 529.86 | 505 | 445.03 | 510 | 0 | 0 | No
2030-02-26 04:00 | 2030 100% ECP | 109.86 | 205 | 145.03 | 264.75 | 0 | 0 | No
2030-02-26 05:00 | 2030 100% ECP | -310.14 | -95 | -154.97 | -35.25 | 0 | 0 | No
2030-02-26 06:00 | 2030 100% ECP | -700 | -395 | -454.97 | -335.25 | 0 | 0 | No
2030-02-26 07:00 | 2030 100% ECP | -700 | -526 | -510 | -401.49 | 0 | 0 | No
2030-02-26 08:00 | 2030 100% ECP | -700 | -526 | -510 | -101.49 | 0 | 0 | No
2030-02-26 09:00 | 2030 100% ECP | -700 | -526 | -510 | 198.51 | 0 | 0 | No
2030-02-26 10:00 | 2030 100% ECP | -700 | -526 | -510 | 24.99 | 0 | 0 | No
2030-02-26 11:00 | 2030 100% ECP | -700 | -526 | -510 | -24.27 | 0 | 0 | No
2030-02-26 12:00 | 2030 100% ECP | -700 | -526 | -510 | -24.27 | 0 | 0 | No
2030-02-26 13:00 | 2030 100% ECP | -700 | -526 | -510 | -107.25 | 0 | 0 | No
2030-02-26 14:00 | 2030 100% ECP | -700 | -526 | -510 | -260.92 | 0 | 0 | No
2030-02-26 15:00 | 2030 100% ECP | -606.35 | -300 | -510 | -70.24 | 0 | 0 | No
2030-02-26 16:00 | 2030 100% ECP | -186.35 | 0 | -210 | 229.76 | 0 | 0 | No
2030-02-26 17:00 | 2030 100% ECP | -606.35 | 193.75 | 90 | 160.26 | 0 | 0 | No
2030-02-26 18:00 | 2030 100% ECP | -700 | -106.25 | -210 | -139.74 | 0 | 0 | No
2030-02-26 19:00 | 2030 100% ECP | -700 | -406.25 | -510 | -439.74 | 0 | 0 | No
2030-02-26 20:00 | 2030 100% ECP | -560 | -106.25 | -210 | -139.74 | 0 | 0 | No
2030-02-26 21:00 | 2030 100% ECP | -140 | 193.75 | 90 | 160.26 | 0 | 0 | No
2030-02-26 22:00 | 2030 100% ECP | 280 | 493.75 | 390 | 460.26 | 0 | 0 | No
2030-02-26 23:00 | 2030 100% ECP | 700 | 334.08 | 510 | 510 | 0 | 0 | No
2030-02-27 | 2030 100% ECP | 700 | 336.2 | 510 | 489.44 | 0 | 0 | No
2030-02-27 01:00 | 2030 100% ECP | 700 | 133.41 | 464.41 | 300 | 0 | 0 | No
2030-02-27 02:00 | 2030 100% ECP | 700 | 0 | 164.41 | 0 | 0 | 0 | No
2030-02-27 03:00 | 2030 100% ECP | 700 | 0 | -41.82 | 0 | 0 | 0 | No
2030-02-27 04:00 | 2030 100% ECP | 700 | -42.63 | -341.82 | -300 | 0 | 0 | No
2030-02-27 05:00 | 2030 100% ECP | 420 | -112.27 | -510 | -245 | 0 | 0 | No
2030-02-27 06:00 | 2030 100% ECP | 0 | 0 | -417.12 | -175.25 | 0 | 0 | No
2030-02-27 07:00 | 2030 100% ECP | 0 | 0 | -117.12 | 92.68 | 0 | 0 | No
2030-02-27 08:00 | 2030 100% ECP | 140 | -169.99 | -210 | 392.68 | 0 | 0 | No
2030-02-27 09:00 | 2030 100% ECP | -280 | -469.99 | -510 | 92.68 | 0 | 0 | No
2030-02-27 10:00 | 2030 100% ECP | -700 | -526 | -510 | -97.11 | 0 | 0 | No
2030-02-27 11:00 | 2030 100% ECP | -700 | -526 | -510 | -62.79 | 0 | 0 | No
2030-02-27 12:00 | 2030 100% ECP | -700 | -368.2 | -510 | -63.1 | 0 | 0 | No
2030-02-27 13:00 | 2030 100% ECP | -700 | -68.2 | -210 | 210 | 0 | 0 | No
2030-02-27 14:00 | 2030 100% ECP | -700 | 231.8 | 90 | 510 | 0 | 0 | No
2030-02-27 15:00 | 2030 100% ECP | -700 | -43.36 | -210 | 510 | 0 | 0 | No
2030-02-27 16:00 | 2030 100% ECP | -280 | 0 | 0 | 210 | 0 | 0 | No
2030-02-27 17:00 | 2030 100% ECP | -280 | 0 | 0 | 510 | 0 | 0 | No
2030-02-27 18:00 | 2030 100% ECP | -700 | 0 | 0 | 275.95 | 0 | 0 | No
2030-02-27 19:00 | 2030 100% ECP | -700 | -49.1 | -300 | -24.05 | 0 | 0 | No
2030-02-27 20:00 | 2030 100% ECP | -657.63 | 0 | 0 | 275.95 | 0 | 0 | No
2030-02-27 21:00 | 2030 100% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-02-27 22:00 | 2030 100% ECP | -700 | 0 | -139.09 | 508.18 | 0 | 0 | No
2030-02-27 23:00 | 2030 100% ECP | -280 | -300 | -439.09 | 268.81 | 0 | 0 | No
2030-02-28 | 2030 100% ECP | -338.16 | -526 | -510 | 7.27 | 0 | 0 | No
2030-02-28 01:00 | 2030 100% ECP | -647.11 | -526 | -510 | 223.07 | 0 | 0 | No
2030-02-28 02:00 | 2030 100% ECP | -700 | -526 | -510 | 175.6 | 0 | 0 | No
2030-02-28 03:00 | 2030 100% ECP | -700 | -526 | -510 | 104.89 | 0 | 0 | No
2030-02-28 04:00 | 2030 100% ECP | -700 | -526 | -510 | 151.06 | 0 | 0 | No
2030-02-28 05:00 | 2030 100% ECP | -700 | -526 | -510 | 64.6 | 0 | 0 | No
2030-02-28 06:00 | 2030 100% ECP | -700 | -526 | -510 | -201.6 | 0 | 0 | No
2030-02-28 07:00 | 2030 100% ECP | -700 | -526 | -510 | -83.27 | 0 | 0 | No
2030-02-28 08:00 | 2030 100% ECP | -700 | -526 | -510 | -383.27 | 0 | 0 | No
2030-02-28 09:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-28 10:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-02-28 11:00 | 2030 100% ECP | -700 | -526 | -510 | 90 | 0 | 0 | No
2030-02-28 12:00 | 2030 100% ECP | -280 | -226 | -210 | 390 | 0 | 0 | No
2030-02-28 13:00 | 2030 100% ECP | 61.51 | 74 | 90 | 510 | 0 | 0 | No
2030-02-28 14:00 | 2030 100% ECP | 481.51 | 374 | 390 | 510 | 0 | 0 | No
2030-02-28 15:00 | 2030 100% ECP | 140 | 74 | 90 | 510 | 0 | 0 | No
2030-02-28 16:00 | 2030 100% ECP | -280 | -226 | -210 | 284.8 | 0 | 0 | No
2030-02-28 17:00 | 2030 100% ECP | -700 | -526 | -510 | 379.34 | 0 | 0 | No
2030-02-28 18:00 | 2030 100% ECP | -700 | -526 | -510 | 492.35 | 0 | 0 | No
2030-02-28 19:00 | 2030 100% ECP | -700 | -526 | -510 | 366.44 | 0 | 0 | No
2030-02-28 20:00 | 2030 100% ECP | -700 | -526 | -510 | 470.79 | 0 | 0 | No
2030-02-28 21:00 | 2030 100% ECP | -280 | -526 | -510 | 234.22 | 0 | 0 | No
2030-02-28 22:00 | 2030 100% ECP | -700 | -226 | -210 | 75.93 | 0 | 0 | No
2030-02-28 23:00 | 2030 100% ECP | -700 | 74 | 90 | 315.13 | 0 | 0 | Yes
2030-03-01 | 2030 100% ECP | -700 | 374 | 390 | 210 | 0 | 0 | Yes
2030-03-01 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 02:00 | 2030 100% ECP | -700 | 505 | 510 | 355.5 | 0 | 0 | Yes
2030-03-01 03:00 | 2030 100% ECP | -700 | 505 | 510 | 134.77 | 0 | 0 | Yes
2030-03-01 04:00 | 2030 100% ECP | -700 | 505 | 510 | 383.66 | 0 | 0 | Yes
2030-03-01 05:00 | 2030 100% ECP | -700 | 505 | 510 | 83.66 | 0 | 0 | Yes
2030-03-01 06:00 | 2030 100% ECP | -700 | 505 | 510 | 383.66 | 0 | 0 | Yes
2030-03-01 07:00 | 2030 100% ECP | -700 | 505 | 510 | 429.71 | 0 | 0 | Yes
2030-03-01 08:00 | 2030 100% ECP | -700 | 505 | 510 | 340.11 | 0 | 0 | Yes
2030-03-01 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 16:00 | 2030 100% ECP | -700 | 300 | 300 | 510 | 0 | 0 | Yes
2030-03-01 17:00 | 2030 100% ECP | -280 | 0 | 0 | 510 | 0 | 0 | No
2030-03-01 18:00 | 2030 100% ECP | -700 | 0 | 0 | 426.11 | 0 | 0 | No
2030-03-01 19:00 | 2030 100% ECP | -280 | 0 | 0 | 510 | 0 | 0 | No
2030-03-01 20:00 | 2030 100% ECP | 140 | 0 | 0 | 380.56 | 0 | 0 | No
2030-03-01 21:00 | 2030 100% ECP | 560 | 0 | -69.06 | 80.56 | 0 | 0 | No
2030-03-01 22:00 | 2030 100% ECP | 700 | 0 | -69.06 | 0 | 0 | 0 | No
2030-03-01 23:00 | 2030 100% ECP | 700 | 205 | 210 | 300 | 0 | 0 | No
2030-03-02 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-02 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-02 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-02 03:00 | 2030 100% ECP | 580.64 | 300 | 210 | 510 | 0 | 0 | No
2030-03-02 04:00 | 2030 100% ECP | 160.64 | 0 | -90 | 225.17 | 0 | 0 | No
2030-03-02 05:00 | 2030 100% ECP | -259.36 | -300 | -390 | 221.69 | 0 | 0 | No
2030-03-02 06:00 | 2030 100% ECP | -679.36 | -526 | -510 | -49.46 | 0 | 0 | No
2030-03-02 07:00 | 2030 100% ECP | -700 | -526 | -510 | -156.89 | 0 | 0 | No
2030-03-02 08:00 | 2030 100% ECP | -700 | -526 | -510 | -37.02 | 0 | 0 | No
2030-03-02 09:00 | 2030 100% ECP | -700 | -526 | -510 | 262.98 | 0 | 0 | Yes
2030-03-02 10:00 | 2030 100% ECP | -700 | -526 | -510 | 148.86 | 0 | 0 | Yes
2030-03-02 11:00 | 2030 100% ECP | -700 | -526 | -510 | -151.14 | 0 | 0 | Yes
2030-03-02 12:00 | 2030 100% ECP | -700 | -526 | -510 | -451.14 | 0 | 0 | Yes
2030-03-02 13:00 | 2030 100% ECP | -700 | -526 | -510 | -264.68 | 0 | 0 | Yes
2030-03-02 14:00 | 2030 100% ECP | -700 | -526 | -510 | -69.22 | 0 | 0 | Yes
2030-03-02 15:00 | 2030 100% ECP | -700 | -526 | -510 | -247.15 | 0 | 0 | Yes
2030-03-02 16:00 | 2030 100% ECP | -700 | -526 | -510 | -63.63 | 0 | 0 | Yes
2030-03-02 17:00 | 2030 100% ECP | -700 | -526 | -510 | 178.36 | 0 | 0 | No
2030-03-02 18:00 | 2030 100% ECP | -700 | -526 | -510 | -51.82 | 0 | 0 | No
2030-03-02 19:00 | 2030 100% ECP | -700 | -526 | -510 | 238.89 | 0 | 0 | No
2030-03-02 20:00 | 2030 100% ECP | -700 | -526 | -510 | 326.7 | 0 | 0 | No
2030-03-02 21:00 | 2030 100% ECP | -700 | -526 | -510 | 429.03 | 0 | 0 | No
2030-03-02 22:00 | 2030 100% ECP | -700 | -526 | -510 | 397.69 | 0 | 0 | No
2030-03-02 23:00 | 2030 100% ECP | -700 | -526 | -510 | 206.27 | 0 | 0 | No
2030-03-03 | 2030 100% ECP | -413.52 | -300 | -302.45 | 210 | 0 | 0 | No
2030-03-03 01:00 | 2030 100% ECP | 6.48 | 0 | -2.45 | 510 | 0 | 0 | No
2030-03-03 02:00 | 2030 100% ECP | 293.72 | 0 | 0 | 510 | 0 | 0 | No
2030-03-03 03:00 | 2030 100% ECP | 0 | 0 | -113.44 | 210 | 0 | 0 | No
2030-03-03 04:00 | 2030 100% ECP | 0 | -88.42 | -413.44 | -29.51 | 0 | 0 | No
2030-03-03 05:00 | 2030 100% ECP | 0 | -226 | -510 | -329.51 | 0 | 0 | No
2030-03-03 06:00 | 2030 100% ECP | -344.17 | -526 | -510 | -317.88 | 0 | 0 | No
2030-03-03 07:00 | 2030 100% ECP | -700 | -526 | -510 | -405.53 | 0 | 0 | No
2030-03-03 08:00 | 2030 100% ECP | -700 | -526 | -510 | -397.76 | 0 | 0 | No
2030-03-03 09:00 | 2030 100% ECP | -700 | -526 | -510 | -97.76 | 0 | 0 | No
2030-03-03 10:00 | 2030 100% ECP | -700 | -526 | -510 | -397.76 | 0 | 0 | No
2030-03-03 11:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-03 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-03 13:00 | 2030 100% ECP | -700 | -526 | -510 | -452.79 | 0 | 0 | Yes
2030-03-03 14:00 | 2030 100% ECP | -700 | -526 | -510 | -488.48 | 0 | 0 | Yes
2030-03-03 15:00 | 2030 100% ECP | -700 | -526 | -510 | -188.48 | 0 | 0 | No
2030-03-03 16:00 | 2030 100% ECP | -280 | -263.68 | -510 | -183.37 | 0 | 0 | No
2030-03-03 17:00 | 2030 100% ECP | -280 | -226 | -210 | 116.63 | 0 | 0 | No
2030-03-03 18:00 | 2030 100% ECP | -700 | -526 | -510 | -183.37 | 0 | 0 | No
2030-03-03 19:00 | 2030 100% ECP | -361.69 | -526 | -510 | 27.16 | 0 | 0 | No
2030-03-03 20:00 | 2030 100% ECP | 58.31 | -226 | -210 | 327.16 | 0 | 0 | No
2030-03-03 21:00 | 2030 100% ECP | 478.31 | 74 | 90 | 510 | 0 | 0 | No
2030-03-03 22:00 | 2030 100% ECP | 700 | 374 | 390 | 510 | 0 | 0 | No
2030-03-03 23:00 | 2030 100% ECP | 700 | 74 | 510 | 505.71 | 0 | 0 | No
2030-03-04 | 2030 100% ECP | 700 | 374 | 510 | 510 | 0 | 0 | No
2030-03-04 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-04 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-04 03:00 | 2030 100% ECP | 700 | 342.81 | 510 | 510 | 0 | 0 | No
2030-03-04 04:00 | 2030 100% ECP | 700 | 283 | 510 | 510 | 0 | 0 | No
2030-03-04 05:00 | 2030 100% ECP | 700 | 147.4 | 510 | 510 | 0 | 0 | No
2030-03-04 06:00 | 2030 100% ECP | 700 | 147.4 | 510 | 510 | 0 | 0 | No
2030-03-04 07:00 | 2030 100% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-04 08:00 | 2030 100% ECP | 700 | 179.99 | 510 | 510 | 0 | 0 | No
2030-03-04 09:00 | 2030 100% ECP | 700 | 0 | 230.23 | 419.36 | 0 | 0 | No
2030-03-04 10:00 | 2030 100% ECP | 700 | 0 | -69.77 | 460.91 | 0 | 0 | No
2030-03-04 11:00 | 2030 100% ECP | 700 | -300 | -369.77 | 160.91 | 0 | 0 | No
2030-03-04 12:00 | 2030 100% ECP | 700 | -526 | -510 | -139.09 | 0 | 0 | No
2030-03-04 13:00 | 2030 100% ECP | 700 | -526 | -510 | -127.72 | 0 | 0 | No
2030-03-04 14:00 | 2030 100% ECP | 700 | -526 | -510 | -130.94 | 0 | 0 | No
2030-03-04 15:00 | 2030 100% ECP | 700 | -526 | -510 | -122.85 | 0 | 0 | No
2030-03-04 16:00 | 2030 100% ECP | 700 | -226 | -210 | 0 | 0 | 0 | No
2030-03-04 17:00 | 2030 100% ECP | 700 | -226 | -482.22 | -210 | 0 | 0 | No
2030-03-04 18:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-04 19:00 | 2030 100% ECP | 700 | -492.15 | -510 | -510 | 0 | 0 | No
2030-03-04 20:00 | 2030 100% ECP | 700 | -192.15 | -210 | -284.8 | 0 | 0 | No
2030-03-04 21:00 | 2030 100% ECP | 700 | 107.85 | 90 | 15.2 | 0 | 0 | No
2030-03-04 22:00 | 2030 100% ECP | 700 | 407.85 | 390 | 315.2 | 0 | 0 | No
2030-03-04 23:00 | 2030 100% ECP | 700 | 174.51 | 510 | 176.92 | 0 | 0 | No
2030-03-05 | 2030 100% ECP | 700 | 243.82 | 510 | 58.59 | 0 | 0 | No
2030-03-05 01:00 | 2030 100% ECP | 700 | 97.19 | 210 | 207.54 | 0 | 0 | No
2030-03-05 02:00 | 2030 100% ECP | 700 | 397.19 | 510 | 507.54 | 0 | 0 | No
2030-03-05 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-05 04:00 | 2030 100% ECP | 700 | 407.03 | 510 | 510 | 0 | 0 | No
2030-03-05 05:00 | 2030 100% ECP | 280 | 107.03 | 210 | 210 | 0 | 0 | No
2030-03-05 06:00 | 2030 100% ECP | 700 | 0 | -78.34 | 0 | 0 | 0 | No
2030-03-05 07:00 | 2030 100% ECP | 604.3 | 0 | -78.34 | 0 | 0 | 0 | No
2030-03-05 08:00 | 2030 100% ECP | 184.3 | 0 | -378.34 | 0 | 0 | 0 | No
2030-03-05 09:00 | 2030 100% ECP | -235.7 | -300 | -510 | -61.7 | 0 | 0 | No
2030-03-05 10:00 | 2030 100% ECP | 0 | 0 | -210 | 238.3 | 0 | 0 | No
2030-03-05 11:00 | 2030 100% ECP | 0 | 0 | -262.23 | 358.45 | 0 | 0 | No
2030-03-05 12:00 | 2030 100% ECP | 0 | 0 | -510 | 510 | 0 | 0 | No
2030-03-05 13:00 | 2030 100% ECP | 280 | 0 | -510 | 419.15 | 0 | 0 | No
2030-03-05 14:00 | 2030 100% ECP | 700 | 0 | -300 | 119.15 | 0 | 0 | No
2030-03-05 15:00 | 2030 100% ECP | 700 | 0 | 0 | 390 | 0 | 0 | No
2030-03-05 16:00 | 2030 100% ECP | 700 | 39.04 | 0 | 90 | 0 | 0 | No
2030-03-05 17:00 | 2030 100% ECP | 700 | -260.96 | -300 | -210 | 0 | 0 | No
2030-03-05 18:00 | 2030 100% ECP | 280 | -526 | -510 | -510 | 0 | 0 | No
2030-03-05 19:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-05 20:00 | 2030 100% ECP | 700 | -526 | -510 | -210 | 0 | 0 | No
2030-03-05 21:00 | 2030 100% ECP | 700 | -526 | -510 | -23.5 | 0 | 0 | No
2030-03-05 22:00 | 2030 100% ECP | 700 | -526 | -510 | -175.88 | 0 | 0 | No
2030-03-05 23:00 | 2030 100% ECP | 700 | -226 | -213.47 | 0 | 0 | 0 | No
2030-03-06 | 2030 100% ECP | 700 | 0 | -488.8 | 300 | 0 | 0 | No
2030-03-06 01:00 | 2030 100% ECP | 656.21 | -259.19 | -510 | 0 | 0 | 0 | No
2030-03-06 02:00 | 2030 100% ECP | 236.21 | -526 | -510 | 0 | 0 | 0 | No
2030-03-06 03:00 | 2030 100% ECP | 105.17 | -526 | -510 | 77.19 | 0 | 0 | No
2030-03-06 04:00 | 2030 100% ECP | -280 | -526 | -510 | 204.35 | 0 | 0 | No
2030-03-06 05:00 | 2030 100% ECP | -700 | -429.91 | -510 | -95.65 | 0 | 0 | No
2030-03-06 06:00 | 2030 100% ECP | -700 | -526 | -510 | -299.07 | 0 | 0 | No
2030-03-06 07:00 | 2030 100% ECP | -700 | -526 | -510 | -157.01 | 0 | 0 | No
2030-03-06 08:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-03-06 09:00 | 2030 100% ECP | -700 | -526 | -510 | -149.86 | 0 | 0 | Yes
2030-03-06 10:00 | 2030 100% ECP | -700 | -526 | -510 | -149.86 | 0 | 0 | Yes
2030-03-06 11:00 | 2030 100% ECP | -700 | -526 | -510 | -327.47 | 0 | 0 | Yes
2030-03-06 12:00 | 2030 100% ECP | -700 | -526 | -510 | -55.48 | 0 | 0 | Yes
2030-03-06 13:00 | 2030 100% ECP | -700 | -526 | -510 | -54 | 0 | 0 | Yes
2030-03-06 14:00 | 2030 100% ECP | -700 | -526 | -510 | 246 | 0 | 0 | Yes
2030-03-06 15:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-03-06 16:00 | 2030 100% ECP | -700 | -526 | -510 | -300 | 0 | 0 | No
2030-03-06 17:00 | 2030 100% ECP | -637.77 | -526 | -510 | -101.4 | 0 | 0 | No
2030-03-06 18:00 | 2030 100% ECP | -217.77 | -526 | -510 | -401.4 | 0 | 0 | No
2030-03-06 19:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 20:00 | 2030 100% ECP | 0 | -526 | -510 | -298.95 | 0 | 0 | No
2030-03-06 21:00 | 2030 100% ECP | 0 | -526 | -510 | 1.05 | 0 | 0 | No
2030-03-06 22:00 | 2030 100% ECP | -342.72 | -526 | -510 | -110.78 | 0 | 0 | No
2030-03-06 23:00 | 2030 100% ECP | 77.28 | -257.26 | -510 | -95.32 | 0 | 0 | No
2030-03-07 | 2030 100% ECP | -342.72 | -526 | -510 | -282.99 | 0 | 0 | No
2030-03-07 01:00 | 2030 100% ECP | -475.64 | -526 | -510 | -108.38 | 0 | 0 | No
2030-03-07 02:00 | 2030 100% ECP | -700 | -526 | -510 | -4.15 | 0 | 0 | No
2030-03-07 03:00 | 2030 100% ECP | -700 | -526 | -510 | -41.61 | 0 | 0 | No
2030-03-07 04:00 | 2030 100% ECP | -700 | -526 | -510 | -210.72 | 0 | 0 | No
2030-03-07 05:00 | 2030 100% ECP | -700 | -526 | -510 | 89.28 | 0 | 0 | No
2030-03-07 06:00 | 2030 100% ECP | -700 | -526 | -510 | -3.29 | 0 | 0 | No
2030-03-07 07:00 | 2030 100% ECP | -700 | -526 | -510 | -37.61 | 0 | 0 | No
2030-03-07 08:00 | 2030 100% ECP | -700 | -526 | -510 | -24.63 | 0 | 0 | Yes
2030-03-07 09:00 | 2030 100% ECP | -700 | -526 | -510 | -173.58 | 0 | 0 | Yes
2030-03-07 10:00 | 2030 100% ECP | -700 | -526 | -510 | -473.58 | 0 | 0 | Yes
2030-03-07 11:00 | 2030 100% ECP | -700 | -226 | -210 | -173.58 | 0 | 0 | Yes
2030-03-07 12:00 | 2030 100% ECP | -700 | 74 | 90 | 126.42 | 0 | 0 | Yes
2030-03-07 13:00 | 2030 100% ECP | -700 | 374 | 390 | 426.42 | 0 | 0 | Yes
2030-03-07 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-07 15:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-03-07 16:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-03-07 17:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-03-07 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-07 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-07 20:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-07 21:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-03-07 22:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-03-07 23:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-03-08 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-08 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-08 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-08 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-08 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-08 05:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-08 06:00 | 2030 100% ECP | -700 | 74 | 90 | 479.38 | 0 | 0 | Yes
2030-03-08 07:00 | 2030 100% ECP | -700 | -226 | -210 | 179.38 | 0 | 0 | No
2030-03-08 08:00 | 2030 100% ECP | -700 | -526 | -510 | -120.62 | 0 | 0 | No
2030-03-08 09:00 | 2030 100% ECP | -700 | -526 | -510 | 2.36 | 0 | 0 | Yes
2030-03-08 10:00 | 2030 100% ECP | -700 | -226 | -210 | 302.36 | 0 | 0 | Yes
2030-03-08 11:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-08 12:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-08 13:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-08 14:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-08 15:00 | 2030 100% ECP | -700 | -226 | -210 | 487.51 | 0 | 0 | Yes
2030-03-08 16:00 | 2030 100% ECP | -700 | -526 | -510 | 187.51 | 0 | 0 | Yes
2030-03-08 17:00 | 2030 100% ECP | -700 | -526 | -510 | 197.06 | 0 | 0 | Yes
2030-03-08 18:00 | 2030 100% ECP | -700 | -526 | -510 | 497.06 | 0 | 0 | Yes
2030-03-08 19:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-03-08 20:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-03-08 21:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-03-08 22:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | Yes
2030-03-08 23:00 | 2030 100% ECP | -700 | -226 | -210 | 272.9 | 0 | 0 | Yes
2030-03-09 | 2030 100% ECP | -280 | 0 | 0 | 245.76 | 0 | 0 | No
2030-03-09 01:00 | 2030 100% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-03-09 02:00 | 2030 100% ECP | -534.88 | 205 | 261.6 | 510 | 0 | 0 | No
2030-03-09 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-09 04:00 | 2030 100% ECP | -619.78 | 205 | 210 | 487.96 | 0 | 0 | No
2030-03-09 05:00 | 2030 100% ECP | -700 | -95 | -90 | 187.96 | 0 | 0 | No
2030-03-09 06:00 | 2030 100% ECP | -700 | -395 | -390 | -112.04 | 0 | 0 | No
2030-03-09 07:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-03-09 08:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-03-09 09:00 | 2030 100% ECP | -700 | -526 | -510 | 159.92 | 0 | 0 | No
2030-03-09 10:00 | 2030 100% ECP | -700 | -526 | -510 | 5.39 | 0 | 0 | Yes
2030-03-09 11:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-03-09 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-09 13:00 | 2030 100% ECP | -700 | -526 | -510 | -258.74 | 0 | 0 | Yes
2030-03-09 14:00 | 2030 100% ECP | -700 | -493.7 | -510 | 41.26 | 0 | 0 | Yes
2030-03-09 15:00 | 2030 100% ECP | -700 | -526 | -510 | 341.26 | 0 | 0 | Yes
2030-03-09 16:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-03-09 17:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | Yes
2030-03-09 18:00 | 2030 100% ECP | -700 | -526 | -510 | -60.98 | 0 | 0 | Yes
2030-03-09 19:00 | 2030 100% ECP | -700 | -526 | -510 | -243.78 | 0 | 0 | Yes
2030-03-09 20:00 | 2030 100% ECP | -700 | -526 | -510 | -366.54 | 0 | 0 | Yes
2030-03-09 21:00 | 2030 100% ECP | -700 | -226 | -210 | -66.54 | 0 | 0 | Yes
2030-03-09 22:00 | 2030 100% ECP | -700 | 74 | 90 | 233.46 | 0 | 0 | Yes
2030-03-09 23:00 | 2030 100% ECP | -700 | 374 | 390 | 395.29 | 0 | 0 | Yes
2030-03-10 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 02:00 | 2030 100% ECP | -700 | 505 | 510 | 352.72 | 0 | 0 | Yes
2030-03-10 03:00 | 2030 100% ECP | -700 | 505 | 510 | 458.77 | 0 | 0 | Yes
2030-03-10 04:00 | 2030 100% ECP | -700 | 505 | 510 | 418.53 | 0 | 0 | Yes
2030-03-10 05:00 | 2030 100% ECP | -700 | 505 | 510 | 388.2 | 0 | 0 | Yes
2030-03-10 06:00 | 2030 100% ECP | -700 | 505 | 510 | 488.62 | 0 | 0 | Yes
2030-03-10 07:00 | 2030 100% ECP | -700 | 505 | 510 | 188.62 | 0 | 0 | Yes
2030-03-10 08:00 | 2030 100% ECP | -700 | 505 | 510 | 236.5 | 0 | 0 | Yes
2030-03-10 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 10:00 | 2030 100% ECP | -700 | 505 | 510 | 212.01 | 0 | 0 | Yes
2030-03-10 11:00 | 2030 100% ECP | -700 | 505 | 510 | 379.93 | 0 | 0 | Yes
2030-03-10 12:00 | 2030 100% ECP | -700 | 505 | 510 | 506.29 | 0 | 0 | Yes
2030-03-10 13:00 | 2030 100% ECP | -700 | 505 | 510 | 306.13 | 0 | 0 | Yes
2030-03-10 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 15:00 | 2030 100% ECP | -700 | 505 | 510 | 317.26 | 0 | 0 | Yes
2030-03-10 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 17:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 18:00 | 2030 100% ECP | -700 | 205 | 510 | 429.22 | 0 | 0 | No
2030-03-10 19:00 | 2030 100% ECP | -700 | 205 | 459.28 | 210 | 0 | 0 | No
2030-03-10 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 15:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-11 16:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-11 17:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-03-11 18:00 | 2030 100% ECP | -700 | -526 | -510 | 389.82 | 0 | 0 | No
2030-03-11 19:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-11 20:00 | 2030 100% ECP | -700 | -226 | -234.59 | 510 | 0 | 0 | No
2030-03-11 21:00 | 2030 100% ECP | -700 | 74 | 65.41 | 510 | 0 | 0 | Yes
2030-03-11 22:00 | 2030 100% ECP | -700 | 374 | 365.41 | 510 | 0 | 0 | Yes
2030-03-11 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 15:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-03-12 16:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-03-12 17:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-03-12 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-12 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-12 20:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-12 21:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-03-12 22:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-03-12 23:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-03-13 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 01:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 02:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 05:00 | 2030 100% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 06:00 | 2030 100% ECP | 0 | 205 | 210 | 227.6 | 0 | 0 | No
2030-03-13 07:00 | 2030 100% ECP | -420 | 0 | 0 | 0 | 0 | 0 | No
2030-03-13 08:00 | 2030 100% ECP | -534.47 | 0 | -88.06 | 201.24 | 0 | 0 | No
2030-03-13 09:00 | 2030 100% ECP | -280 | -226 | -388.06 | 501.24 | 0 | 0 | No
2030-03-13 10:00 | 2030 100% ECP | -700 | -526 | -510 | 201.24 | 0 | 0 | No
2030-03-13 11:00 | 2030 100% ECP | -700 | -526 | -510 | -98.76 | 0 | 0 | No
2030-03-13 12:00 | 2030 100% ECP | -700 | -526 | -510 | -343.28 | 0 | 0 | No
2030-03-13 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 14:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 15:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 16:00 | 2030 100% ECP | -316.28 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 20:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 21:00 | 2030 100% ECP | -280 | -226 | -222.14 | -210 | 0 | 0 | No
2030-03-13 22:00 | 2030 100% ECP | 140 | 0 | 0 | 0 | 0 | 0 | No
2030-03-13 23:00 | 2030 100% ECP | 560 | 0 | -90 | 0 | 0 | 0 | No
2030-03-14 | 2030 100% ECP | 700 | 0 | -70.63 | 0 | 0 | 0 | No
2030-03-14 01:00 | 2030 100% ECP | 280 | 167.41 | 210 | 210 | 0 | 0 | No
2030-03-14 02:00 | 2030 100% ECP | 700 | 467.41 | 510 | 510 | 0 | 0 | No
2030-03-14 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-14 04:00 | 2030 100% ECP | 540.28 | 505 | 510 | 510 | 0 | 0 | No
2030-03-14 05:00 | 2030 100% ECP | 120.28 | 418.66 | 390 | 510 | 0 | 0 | No
2030-03-14 06:00 | 2030 100% ECP | -299.72 | 118.66 | 90 | 210 | 0 | 0 | No
2030-03-14 07:00 | 2030 100% ECP | -700 | -181.34 | -210 | 0 | 0 | 0 | No
2030-03-14 08:00 | 2030 100% ECP | -700 | -481.34 | -510 | 0 | 0 | 0 | No
2030-03-14 09:00 | 2030 100% ECP | -700 | -526 | -510 | 64.25 | 0 | 0 | Yes
2030-03-14 10:00 | 2030 100% ECP | -700 | -526 | -510 | 364.25 | 0 | 0 | Yes
2030-03-14 11:00 | 2030 100% ECP | -700 | -226 | -488.26 | 324.45 | 0 | 0 | Yes
2030-03-14 12:00 | 2030 100% ECP | -700 | 74 | -188.26 | 510 | 0 | 0 | Yes
2030-03-14 13:00 | 2030 100% ECP | -700 | 374 | 111.74 | 510 | 0 | 0 | Yes
2030-03-14 14:00 | 2030 100% ECP | -700 | 374 | 390 | 429.55 | 0 | 0 | Yes
2030-03-14 15:00 | 2030 100% ECP | -700 | 74 | 90 | 129.55 | 0 | 0 | Yes
2030-03-14 16:00 | 2030 100% ECP | -700 | -226 | -210 | -170.45 | 0 | 0 | Yes
2030-03-14 17:00 | 2030 100% ECP | -700 | -526 | -510 | -470.45 | 0 | 0 | Yes
2030-03-14 18:00 | 2030 100% ECP | -700 | -526 | -510 | -359.94 | 0 | 0 | No
2030-03-14 19:00 | 2030 100% ECP | -700 | -526 | -510 | -59.94 | 0 | 0 | No
2030-03-14 20:00 | 2030 100% ECP | -700 | -526 | -510 | 240.06 | 0 | 0 | No
2030-03-14 21:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-03-14 22:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-14 23:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-15 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 13:00 | 2030 100% ECP | -700 | 374 | 390 | 402.32 | 0 | 0 | Yes
2030-03-15 14:00 | 2030 100% ECP | -700 | 74 | 90 | 102.32 | 0 | 0 | Yes
2030-03-15 15:00 | 2030 100% ECP | -700 | -226 | -210 | -197.68 | 0 | 0 | Yes
2030-03-15 16:00 | 2030 100% ECP | -700 | -526 | -510 | -497.68 | 0 | 0 | Yes
2030-03-15 17:00 | 2030 100% ECP | -700 | -526 | -510 | -197.68 | 0 | 0 | No
2030-03-15 18:00 | 2030 100% ECP | -700 | -226 | -210 | 102.32 | 0 | 0 | No
2030-03-15 19:00 | 2030 100% ECP | -700 | 0 | 0 | 262.91 | 0 | 0 | No
2030-03-15 20:00 | 2030 100% ECP | -280 | 0 | -119.56 | 497.84 | 0 | 0 | No
2030-03-15 21:00 | 2030 100% ECP | 0 | 0 | 0 | 497.84 | 0 | 0 | No
2030-03-15 22:00 | 2030 100% ECP | 280 | 0 | -140.1 | 497.84 | 0 | 0 | No
2030-03-15 23:00 | 2030 100% ECP | 700 | 0 | -140.1 | 412.11 | 0 | 0 | No
2030-03-16 | 2030 100% ECP | 700 | 0 | -440.1 | 229.83 | 0 | 0 | No
2030-03-16 01:00 | 2030 100% ECP | 700 | 0 | -510 | 214.51 | 0 | 0 | No
2030-03-16 02:00 | 2030 100% ECP | 560 | 0 | -510 | 510 | 0 | 0 | No
2030-03-16 03:00 | 2030 100% ECP | 140 | 0 | -510 | 316.16 | 0 | 0 | No
2030-03-16 04:00 | 2030 100% ECP | -280 | -198.35 | -510 | 16.16 | 0 | 0 | No
2030-03-16 05:00 | 2030 100% ECP | -700 | -498.35 | -510 | -73.31 | 0 | 0 | No
2030-03-16 06:00 | 2030 100% ECP | -700 | -526 | -510 | -373.31 | 0 | 0 | No
2030-03-16 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-16 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 09:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 10:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 11:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 12:00 | 2030 100% ECP | -700 | -526 | -510 | -273.3 | 0 | 0 | Yes
2030-03-16 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 14:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 15:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-03-16 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 18:00 | 2030 100% ECP | -700 | -526 | -510 | -375.82 | 0 | 0 | Yes
2030-03-16 19:00 | 2030 100% ECP | -700 | -526 | -510 | -75.82 | 0 | 0 | Yes
2030-03-16 20:00 | 2030 100% ECP | -700 | -526 | -510 | 224.18 | 0 | 0 | Yes
2030-03-16 21:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-03-16 22:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-16 23:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-17 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 17:00 | 2030 100% ECP | -700 | 300 | 249.24 | 510 | 0 | 0 | Yes
2030-03-17 18:00 | 2030 100% ECP | -700 | 0 | -50.76 | 210 | 0 | 0 | No
2030-03-17 19:00 | 2030 100% ECP | -700 | 300 | 249.24 | 510 | 0 | 0 | No
2030-03-17 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 21:00 | 2030 100% ECP | -536.02 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 22:00 | 2030 100% ECP | -116.02 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 23:00 | 2030 100% ECP | 303.98 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 06:00 | 2030 100% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 07:00 | 2030 100% ECP | 263.77 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 08:00 | 2030 100% ECP | 683.77 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 09:00 | 2030 100% ECP | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-03-18 10:00 | 2030 100% ECP | 700 | -95 | -90 | 510 | 0 | 0 | No
2030-03-18 11:00 | 2030 100% ECP | 480.36 | -395 | -390 | 475.22 | 0 | 0 | No
2030-03-18 12:00 | 2030 100% ECP | 700 | -526 | -510 | 240.97 | 0 | 0 | No
2030-03-18 13:00 | 2030 100% ECP | 700 | -526 | -510 | 314.15 | 0 | 0 | No
2030-03-18 14:00 | 2030 100% ECP | 700 | -526 | -510 | 149.74 | 0 | 0 | No
2030-03-18 15:00 | 2030 100% ECP | 700 | -526 | -510 | -150.26 | 0 | 0 | No
2030-03-18 16:00 | 2030 100% ECP | 700 | -226 | -210 | 132.81 | 0 | 0 | No
2030-03-18 17:00 | 2030 100% ECP | 700 | 0 | 0 | 432.81 | 0 | 0 | No
2030-03-18 18:00 | 2030 100% ECP | 314.82 | 0 | 0 | 418.92 | 0 | 0 | No
2030-03-18 19:00 | 2030 100% ECP | 346.2 | 0 | 0 | 510 | 0 | 0 | No
2030-03-18 20:00 | 2030 100% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-03-18 21:00 | 2030 100% ECP | 700 | 0 | 0 | 468.54 | 0 | 0 | No
2030-03-18 22:00 | 2030 100% ECP | 700 | 0 | 0 | 431.3 | 0 | 0 | No
2030-03-18 23:00 | 2030 100% ECP | 700 | 0 | 0 | 503.05 | 0 | 0 | No
2030-03-19 | 2030 100% ECP | 700 | 0 | 300 | 395.72 | 0 | 0 | No
2030-03-19 01:00 | 2030 100% ECP | 700 | 0 | 510 | 95.72 | 0 | 0 | No
2030-03-19 02:00 | 2030 100% ECP | 700 | 0 | 453.05 | 0 | 0 | 0 | No
2030-03-19 03:00 | 2030 100% ECP | 700 | 0 | 166.29 | 300 | 0 | 0 | No
2030-03-19 04:00 | 2030 100% ECP | 700 | 0 | 416.13 | 0 | 0 | 0 | No
2030-03-19 05:00 | 2030 100% ECP | 420 | 0 | 188.67 | 300 | 0 | 0 | No
2030-03-19 06:00 | 2030 100% ECP | 0 | 0 | -111.33 | 221.16 | 0 | 0 | No
2030-03-19 07:00 | 2030 100% ECP | -420 | -300 | -411.33 | -78.84 | 0 | 0 | No
2030-03-19 08:00 | 2030 100% ECP | -700 | -526 | -510 | -378.84 | 0 | 0 | No
2030-03-19 09:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-19 10:00 | 2030 100% ECP | -700 | -526 | -510 | -249.17 | 0 | 0 | No
2030-03-19 11:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-19 12:00 | 2030 100% ECP | -700 | -526 | -510 | -364.38 | 0 | 0 | No
2030-03-19 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-19 14:00 | 2030 100% ECP | -700 | -526 | -510 | -476.1 | 0 | 0 | No
2030-03-19 15:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-19 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-19 17:00 | 2030 100% ECP | -280 | -526 | -510 | -437.73 | 0 | 0 | No
2030-03-19 18:00 | 2030 100% ECP | -700 | -526 | -510 | -137.73 | 0 | 0 | No
2030-03-19 19:00 | 2030 100% ECP | -280 | -526 | -510 | -98.95 | 0 | 0 | No
2030-03-19 20:00 | 2030 100% ECP | 0 | -526 | -510 | -194.79 | 0 | 0 | No
2030-03-19 21:00 | 2030 100% ECP | 45.57 | -526 | -510 | 105.21 | 0 | 0 | No
2030-03-19 22:00 | 2030 100% ECP | 465.57 | -526 | -510 | -100 | 0 | 0 | No
2030-03-19 23:00 | 2030 100% ECP | 658.07 | -526 | -510 | 200 | 0 | 0 | No
2030-03-20 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-03-20 01:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-03-20 02:00 | 2030 100% ECP | 700 | -526 | -510 | 11.34 | 0 | 0 | No
2030-03-20 03:00 | 2030 100% ECP | 700 | -526 | -510 | 160.38 | 0 | 0 | No
2030-03-20 04:00 | 2030 100% ECP | 592.85 | -526 | -510 | 160.38 | 0 | 0 | No
2030-03-20 05:00 | 2030 100% ECP | 172.85 | -526 | -510 | 78.29 | 0 | 0 | No
2030-03-20 06:00 | 2030 100% ECP | 0 | -526 | -510 | 170.54 | 0 | 0 | No
2030-03-20 07:00 | 2030 100% ECP | -280 | -526 | -510 | 278.58 | 0 | 0 | No
2030-03-20 08:00 | 2030 100% ECP | -700 | -526 | -510 | 358.48 | 0 | 0 | No
2030-03-20 09:00 | 2030 100% ECP | -700 | -526 | -510 | 270.88 | 0 | 0 | Yes
2030-03-20 10:00 | 2030 100% ECP | -700 | -526 | -510 | 245.27 | 0 | 0 | Yes
2030-03-20 11:00 | 2030 100% ECP | -700 | -526 | -510 | 122.72 | 0 | 0 | Yes
2030-03-20 12:00 | 2030 100% ECP | -700 | -526 | -510 | 171.91 | 0 | 0 | Yes
2030-03-20 13:00 | 2030 100% ECP | -700 | -526 | -510 | 93.72 | 0 | 0 | Yes
2030-03-20 14:00 | 2030 100% ECP | -700 | -526 | -510 | 101.63 | 0 | 0 | Yes
2030-03-20 15:00 | 2030 100% ECP | -700 | -526 | -510 | 169.89 | 0 | 0 | Yes
2030-03-20 16:00 | 2030 100% ECP | -700 | -526 | -510 | 414.92 | 0 | 0 | Yes
2030-03-20 17:00 | 2030 100% ECP | -700 | -526 | -510 | 474.98 | 0 | 0 | No
2030-03-20 18:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-20 19:00 | 2030 100% ECP | -280 | -526 | -510 | 489.42 | 0 | 0 | No
2030-03-20 20:00 | 2030 100% ECP | 140 | -526 | -510 | 281.67 | 0 | 0 | No
2030-03-20 21:00 | 2030 100% ECP | 560 | -526 | -510 | -18.33 | 0 | 0 | No
2030-03-20 22:00 | 2030 100% ECP | 140 | -526 | -510 | 0 | 0 | 0 | No
2030-03-20 23:00 | 2030 100% ECP | -280 | -226 | -356.52 | -48.44 | 0 | 0 | No
2030-03-21 | 2030 100% ECP | -700 | 0 | -510 | -175.1 | 0 | 0 | No
2030-03-21 01:00 | 2030 100% ECP | -700 | -95 | -315.98 | -300 | 0 | 0 | No
2030-03-21 02:00 | 2030 100% ECP | -700 | 205 | -15.98 | 0 | 0 | 0 | Yes
2030-03-21 03:00 | 2030 100% ECP | -700 | 505 | 284.02 | 300 | 0 | 0 | No
2030-03-21 04:00 | 2030 100% ECP | -700 | 374 | 90 | 252.07 | 0 | 0 | No
2030-03-21 05:00 | 2030 100% ECP | -700 | 74 | -210 | -47.93 | 0 | 0 | No
2030-03-21 06:00 | 2030 100% ECP | -700 | -226 | -510 | -347.93 | 0 | 0 | No
2030-03-21 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-21 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-21 09:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-03-21 10:00 | 2030 100% ECP | -700 | 0 | 21.12 | 0 | 0 | 0 | Yes
2030-03-21 11:00 | 2030 100% ECP | -700 | 300 | 321.12 | 300 | 0 | 0 | Yes
2030-03-21 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 15:00 | 2030 100% ECP | -700 | 300 | 300 | 442.37 | 0 | 0 | Yes
2030-03-21 16:00 | 2030 100% ECP | -280 | 0 | 0 | 142.37 | 0 | 0 | No
2030-03-21 17:00 | 2030 100% ECP | 140 | 0 | -300 | -14.04 | 0 | 0 | No
2030-03-21 18:00 | 2030 100% ECP | 560 | 0 | -510 | 49.07 | 0 | 0 | No
2030-03-21 19:00 | 2030 100% ECP | 700 | 0 | -510 | 349.07 | 0 | 0 | No
2030-03-21 20:00 | 2030 100% ECP | 700 | -97.03 | -300 | 229.6 | 0 | 0 | No
2030-03-21 21:00 | 2030 100% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-03-21 22:00 | 2030 100% ECP | 700 | 300 | 300 | 510 | 0 | 0 | No
2030-03-21 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 04:00 | 2030 100% ECP | 700 | 300 | 312.79 | 510 | 0 | 0 | No
2030-03-22 05:00 | 2030 100% ECP | 280 | 0 | 12.79 | 438.91 | 0 | 0 | No
2030-03-22 06:00 | 2030 100% ECP | 0 | -300 | -287.21 | 420.77 | 0 | 0 | No
2030-03-22 07:00 | 2030 100% ECP | -280 | -526 | -510 | 452.43 | 0 | 0 | No
2030-03-22 08:00 | 2030 100% ECP | -700 | -526 | -510 | 443.58 | 0 | 0 | No
2030-03-22 09:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-03-22 10:00 | 2030 100% ECP | -700 | -526 | -510 | 326.71 | 0 | 0 | Yes
2030-03-22 11:00 | 2030 100% ECP | -700 | -526 | -510 | 213.59 | 0 | 0 | Yes
2030-03-22 12:00 | 2030 100% ECP | -700 | -526 | -510 | 39.51 | 0 | 0 | Yes
2030-03-22 13:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-03-22 14:00 | 2030 100% ECP | -700 | -526 | -510 | 85.75 | 0 | 0 | Yes
2030-03-22 15:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-03-22 16:00 | 2030 100% ECP | -700 | -526 | -510 | 95.39 | 0 | 0 | Yes
2030-03-22 17:00 | 2030 100% ECP | -700 | -526 | -510 | 121.68 | 0 | 0 | No
2030-03-22 18:00 | 2030 100% ECP | -695.55 | -526 | -510 | 421.68 | 0 | 0 | No
2030-03-22 19:00 | 2030 100% ECP | -275.55 | -526 | -510 | 510 | 0 | 0 | No
2030-03-22 20:00 | 2030 100% ECP | 144.45 | -226 | -210 | 510 | 0 | 0 | No
2030-03-22 21:00 | 2030 100% ECP | 564.45 | 74 | 90 | 335.4 | 0 | 0 | No
2030-03-22 22:00 | 2030 100% ECP | 434.76 | 374 | 390 | 510 | 0 | 0 | No
2030-03-22 23:00 | 2030 100% ECP | 14.76 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 | 2030 100% ECP | -405.24 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 01:00 | 2030 100% ECP | -177.61 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 02:00 | 2030 100% ECP | -187.5 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 03:00 | 2030 100% ECP | -607.5 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 05:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-03-23 06:00 | 2030 100% ECP | -700 | 74 | 90 | 404.12 | 0 | 0 | No
2030-03-23 07:00 | 2030 100% ECP | -700 | -226 | -210 | 104.12 | 0 | 0 | No
2030-03-23 08:00 | 2030 100% ECP | -700 | -526 | -510 | -195.88 | 0 | 0 | No
2030-03-23 09:00 | 2030 100% ECP | -700 | -526 | -510 | -130.65 | 0 | 0 | Yes
2030-03-23 10:00 | 2030 100% ECP | -700 | -226 | -210 | 169.35 | 0 | 0 | Yes
2030-03-23 11:00 | 2030 100% ECP | -700 | 74 | 90 | 469.35 | 0 | 0 | Yes
2030-03-23 12:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-23 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-23 14:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-23 15:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-23 16:00 | 2030 100% ECP | -700 | -226 | -210 | 368.24 | 0 | 0 | Yes
2030-03-23 17:00 | 2030 100% ECP | -700 | -526 | -510 | 195.39 | 0 | 0 | No
2030-03-23 18:00 | 2030 100% ECP | -700 | -526 | -510 | -104.61 | 0 | 0 | No
2030-03-23 19:00 | 2030 100% ECP | -700 | -526 | -510 | -404.61 | 0 | 0 | No
2030-03-23 20:00 | 2030 100% ECP | -700 | -526 | -510 | -106.57 | 0 | 0 | No
2030-03-23 21:00 | 2030 100% ECP | -700 | -526 | -510 | 193.43 | 0 | 0 | No
2030-03-23 22:00 | 2030 100% ECP | -700 | -226 | -210 | 493.43 | 0 | 0 | No
2030-03-23 23:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-24 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-24 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 17:00 | 2030 100% ECP | -700 | 300 | 297.83 | 300 | 0 | 0 | Yes
2030-03-24 18:00 | 2030 100% ECP | -700 | 0 | -2.17 | 0 | 0 | 0 | Yes
2030-03-24 19:00 | 2030 100% ECP | -700 | -95 | -300.45 | -287.86 | 0 | 0 | No
2030-03-24 20:00 | 2030 100% ECP | -700 | 205 | -0.45 | 12.14 | 0 | 0 | Yes
2030-03-24 21:00 | 2030 100% ECP | -700 | 505 | 299.55 | 312.14 | 0 | 0 | Yes
2030-03-24 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-25 | 2030 100% ECP | -699.71 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 01:00 | 2030 100% ECP | -699.71 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 02:00 | 2030 100% ECP | -699.71 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 03:00 | 2030 100% ECP | -279.71 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 04:00 | 2030 100% ECP | -45.05 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 05:00 | 2030 100% ECP | -45.05 | 205 | 210 | 510 | 0 | 0 | No
2030-03-25 06:00 | 2030 100% ECP | -280 | -95 | -90 | 244.51 | 0 | 0 | No
2030-03-25 07:00 | 2030 100% ECP | -700 | -395 | -390 | -55.49 | 0 | 0 | No
2030-03-25 08:00 | 2030 100% ECP | -700 | -526 | -510 | -60.58 | 0 | 0 | No
2030-03-25 09:00 | 2030 100% ECP | -700 | -526 | -510 | -193.98 | 0 | 0 | Yes
2030-03-25 10:00 | 2030 100% ECP | -700 | -526 | -510 | -290.19 | 0 | 0 | Yes
2030-03-25 11:00 | 2030 100% ECP | -700 | -526 | -510 | -167.44 | 0 | 0 | Yes
2030-03-25 12:00 | 2030 100% ECP | -700 | -526 | -510 | -212.38 | 0 | 0 | Yes
2030-03-25 13:00 | 2030 100% ECP | -700 | -526 | -510 | -119.46 | 0 | 0 | Yes
2030-03-25 14:00 | 2030 100% ECP | -700 | -526 | -510 | -6.11 | 0 | 0 | Yes
2030-03-25 15:00 | 2030 100% ECP | -280 | -526 | -510 | 57.27 | 0 | 0 | No
2030-03-25 16:00 | 2030 100% ECP | 140 | -526 | -510 | 145.94 | 0 | 0 | No
2030-03-25 17:00 | 2030 100% ECP | 560 | -526 | -510 | -39.09 | 0 | 0 | No
2030-03-25 18:00 | 2030 100% ECP | 700 | -526 | -510 | -339.09 | 0 | 0 | No
2030-03-25 19:00 | 2030 100% ECP | 700 | -526 | -510 | -417.35 | 0 | 0 | No
2030-03-25 20:00 | 2030 100% ECP | 700 | -526 | -510 | -117.35 | 0 | 0 | No
2030-03-25 21:00 | 2030 100% ECP | 700 | -226 | -210 | 182.65 | 0 | 0 | No
2030-03-25 22:00 | 2030 100% ECP | 700 | 0 | 90 | 68.95 | 0 | 0 | No
2030-03-25 23:00 | 2030 100% ECP | 700 | 0 | 390 | 0 | 0 | 0 | No
2030-03-26 | 2030 100% ECP | 700 | 0 | 510 | 32.97 | 0 | 0 | No
2030-03-26 01:00 | 2030 100% ECP | 700 | 0 | 462.92 | 0 | 0 | 0 | No
2030-03-26 02:00 | 2030 100% ECP | 700 | 0 | 302.85 | 0 | 0 | 0 | No
2030-03-26 03:00 | 2030 100% ECP | 700 | 0 | 302.85 | 0 | 0 | 0 | No
2030-03-26 04:00 | 2030 100% ECP | 700 | 0 | 2.85 | 0 | 0 | 0 | No
2030-03-26 05:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-03-26 06:00 | 2030 100% ECP | 560 | 0 | -33.08 | 0 | 0 | 0 | No
2030-03-26 07:00 | 2030 100% ECP | 140 | -300 | -333.08 | -300 | 0 | 0 | No
2030-03-26 08:00 | 2030 100% ECP | -280 | -526 | -510 | -324.04 | 0 | 0 | No
2030-03-26 09:00 | 2030 100% ECP | -700 | -526 | -510 | -24.04 | 0 | 0 | Yes
2030-03-26 10:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-03-26 11:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-03-26 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-03-26 13:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-03-26 14:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-03-26 15:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-03-26 16:00 | 2030 100% ECP | -280 | -526 | -510 | 58.17 | 0 | 0 | No
2030-03-26 17:00 | 2030 100% ECP | 140 | -526 | -510 | -241.83 | 0 | 0 | No
2030-03-26 18:00 | 2030 100% ECP | 560 | -526 | -510 | -62.45 | 0 | 0 | No
2030-03-26 19:00 | 2030 100% ECP | 700 | -526 | -510 | -88.22 | 0 | 0 | No
2030-03-26 20:00 | 2030 100% ECP | 700 | -526 | -510 | -388.22 | 0 | 0 | No
2030-03-26 21:00 | 2030 100% ECP | 700 | -526 | -510 | -227.37 | 0 | 0 | No
2030-03-26 22:00 | 2030 100% ECP | 700 | -226 | -510 | 72.63 | 0 | 0 | No
2030-03-26 23:00 | 2030 100% ECP | 700 | -526 | -510 | -142.27 | 0 | 0 | No
2030-03-27 | 2030 100% ECP | 700 | -226 | -510 | -175.36 | 0 | 0 | No
2030-03-27 01:00 | 2030 100% ECP | 700 | -60.91 | -510 | -186.29 | 0 | 0 | No
2030-03-27 02:00 | 2030 100% ECP | 700 | -50.53 | -510 | -186.14 | 0 | 0 | No
2030-03-27 03:00 | 2030 100% ECP | 700 | -106.33 | -510 | -234.75 | 0 | 0 | No
2030-03-27 04:00 | 2030 100% ECP | 700 | -220.56 | -510 | -263.75 | 0 | 0 | No
2030-03-27 05:00 | 2030 100% ECP | 344.64 | 0 | -510 | -506.56 | 0 | 0 | No
2030-03-27 06:00 | 2030 100% ECP | -75.36 | 0 | -510 | -494.68 | 0 | 0 | No
2030-03-27 07:00 | 2030 100% ECP | -495.36 | -226 | -510 | -456.89 | 0 | 0 | No
2030-03-27 08:00 | 2030 100% ECP | -700 | -526 | -510 | -156.89 | 0 | 0 | No
2030-03-27 09:00 | 2030 100% ECP | -700 | -526 | -510 | -28.39 | 0 | 0 | Yes
2030-03-27 10:00 | 2030 100% ECP | -700 | -526 | -510 | -74.12 | 0 | 0 | Yes
2030-03-27 11:00 | 2030 100% ECP | -700 | -526 | -510 | -99.01 | 0 | 0 | Yes
2030-03-27 12:00 | 2030 100% ECP | -700 | -526 | -510 | -235.52 | 0 | 0 | Yes
2030-03-27 13:00 | 2030 100% ECP | -700 | -526 | -510 | -213.05 | 0 | 0 | Yes
2030-03-27 14:00 | 2030 100% ECP | -700 | -526 | -510 | -239.26 | 0 | 0 | Yes
2030-03-27 15:00 | 2030 100% ECP | -700 | -526 | -510 | 60.74 | 0 | 0 | Yes
2030-03-27 16:00 | 2030 100% ECP | -700 | -526 | -510 | 360.74 | 0 | 0 | Yes
2030-03-27 17:00 | 2030 100% ECP | -700 | -526 | -510 | 464.17 | 0 | 0 | No
2030-03-27 18:00 | 2030 100% ECP | -700 | -526 | -510 | 372.07 | 0 | 0 | No
2030-03-27 19:00 | 2030 100% ECP | -700 | -526 | -510 | 263.23 | 0 | 0 | No
2030-03-27 20:00 | 2030 100% ECP | -700 | -526 | -510 | -36.77 | 0 | 0 | No
2030-03-27 21:00 | 2030 100% ECP | -700 | -526 | -510 | -336.77 | 0 | 0 | No
2030-03-27 22:00 | 2030 100% ECP | -348.99 | -300 | -300 | -510 | 0 | 0 | No
2030-03-27 23:00 | 2030 100% ECP | 71.01 | 0 | 0 | -390.58 | 0 | 0 | No
2030-03-28 | 2030 100% ECP | 411.21 | 300 | 300 | -90.58 | 0 | 0 | No
2030-03-28 01:00 | 2030 100% ECP | 0 | 298.19 | 510 | 209.42 | 0 | 0 | No
2030-03-28 02:00 | 2030 100% ECP | -409.23 | 505 | 510 | 509.42 | 0 | 0 | No
2030-03-28 03:00 | 2030 100% ECP | -480.81 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 06:00 | 2030 100% ECP | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-03-28 07:00 | 2030 100% ECP | -700 | -95 | -90 | 210 | 0 | 0 | No
2030-03-28 08:00 | 2030 100% ECP | -700 | -95 | -343.67 | 510 | 0 | 0 | Yes
2030-03-28 09:00 | 2030 100% ECP | -700 | 205 | -43.67 | 510 | 0 | 0 | Yes
2030-03-28 10:00 | 2030 100% ECP | -700 | 505 | 256.33 | 510 | 0 | 0 | Yes
2030-03-28 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 15:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-28 16:00 | 2030 100% ECP | -700 | 74 | 90 | 462.7 | 0 | 0 | Yes
2030-03-28 17:00 | 2030 100% ECP | -700 | -226 | -210 | 162.7 | 0 | 0 | Yes
2030-03-28 18:00 | 2030 100% ECP | -700 | -526 | -510 | -137.3 | 0 | 0 | No
2030-03-28 19:00 | 2030 100% ECP | -700 | -526 | -510 | -437.3 | 0 | 0 | No
2030-03-28 20:00 | 2030 100% ECP | -700 | -526 | -510 | -137.3 | 0 | 0 | No
2030-03-28 21:00 | 2030 100% ECP | -700 | -226 | -210 | 162.7 | 0 | 0 | No
2030-03-28 22:00 | 2030 100% ECP | -700 | 74 | 90 | 462.7 | 0 | 0 | No
2030-03-28 23:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-29 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 08:00 | 2030 100% ECP | -700 | 205 | 320.84 | 510 | 0 | 0 | Yes
2030-03-29 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 14:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-29 15:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-29 16:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-03-29 17:00 | 2030 100% ECP | -280 | -526 | -510 | 241.99 | 0 | 0 | Yes
2030-03-29 18:00 | 2030 100% ECP | 140 | -526 | -510 | 279.33 | 0 | 0 | No
2030-03-29 19:00 | 2030 100% ECP | 560 | -526 | -510 | 510 | 0 | 0 | No
2030-03-29 20:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-29 21:00 | 2030 100% ECP | 700 | -226 | -210 | 510 | 0 | 0 | No
2030-03-29 22:00 | 2030 100% ECP | 700 | 0 | 44.9 | 297.11 | 0 | 0 | No
2030-03-29 23:00 | 2030 100% ECP | 700 | 300 | 344.9 | 510 | 0 | 0 | No
2030-03-30 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 04:00 | 2030 100% ECP | 700 | 505 | 510 | 478.22 | 0 | 0 | No
2030-03-30 05:00 | 2030 100% ECP | 700 | 505 | 510 | 178.22 | 0 | 0 | No
2030-03-30 06:00 | 2030 100% ECP | 420.14 | 505 | 510 | -121.78 | 0 | 0 | No
2030-03-30 07:00 | 2030 100% ECP | 0.14 | 205 | 210 | -421.78 | 0 | 0 | No
2030-03-30 08:00 | 2030 100% ECP | -419.86 | -95 | -90 | -510 | 0 | 0 | Yes
2030-03-30 09:00 | 2030 100% ECP | -700 | 0 | -233.72 | -210 | 0 | 0 | Yes
2030-03-30 10:00 | 2030 100% ECP | -700 | -201.6 | -385.54 | 90 | 0 | 0 | Yes
2030-03-30 11:00 | 2030 100% ECP | -700 | -501.6 | -510 | -210 | 0 | 0 | Yes
2030-03-30 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-30 13:00 | 2030 100% ECP | -700 | -526 | -510 | -500.17 | 0 | 0 | Yes
2030-03-30 14:00 | 2030 100% ECP | -700 | -526 | -510 | -200.17 | 0 | 0 | Yes
2030-03-30 15:00 | 2030 100% ECP | -700 | -526 | -510 | 99.83 | 0 | 0 | Yes
2030-03-30 16:00 | 2030 100% ECP | -674.72 | -526 | -510 | 113.98 | 0 | 0 | Yes
2030-03-30 17:00 | 2030 100% ECP | -254.72 | -526 | -510 | 134.2 | 0 | 0 | No
2030-03-30 18:00 | 2030 100% ECP | 165.28 | -526 | -510 | 0 | 0 | 0 | No
2030-03-30 19:00 | 2030 100% ECP | 585.28 | -526 | -510 | 289.83 | 0 | 0 | No
2030-03-30 20:00 | 2030 100% ECP | 700 | -300 | -300 | 211.64 | 0 | 0 | No
2030-03-30 21:00 | 2030 100% ECP | 700 | 0 | 0 | 350.82 | 0 | 0 | No
2030-03-30 22:00 | 2030 100% ECP | 700 | 300 | 300 | 510 | 0 | 0 | No
2030-03-30 23:00 | 2030 100% ECP | 700 | 300 | 358.87 | 432.18 | 0 | 0 | No
2030-03-31 | 2030 100% ECP | 700 | 0 | 58.87 | 132.18 | 0 | 0 | No
2030-03-31 01:00 | 2030 100% ECP | 700 | -300 | -241.13 | -167.82 | 0 | 0 | No
2030-03-31 02:00 | 2030 100% ECP | 700 | -437.76 | -510 | -90.68 | 0 | 0 | No
2030-03-31 03:00 | 2030 100% ECP | 700 | -526 | -510 | -101.41 | 0 | 0 | No
2030-03-31 04:00 | 2030 100% ECP | 700 | -460.45 | -510 | 8.03 | 0 | 0 | No
2030-03-31 05:00 | 2030 100% ECP | 700 | -526 | -510 | -32.07 | 0 | 0 | No
2030-03-31 06:00 | 2030 100% ECP | 700 | -526 | -510 | -224.91 | 0 | 0 | No
2030-03-31 07:00 | 2030 100% ECP | 560 | -526 | -510 | -96.7 | 0 | 0 | No
2030-03-31 08:00 | 2030 100% ECP | 140 | -526 | -510 | -30.11 | 0 | 0 | No
2030-03-31 09:00 | 2030 100% ECP | -280 | -526 | -510 | 0 | 0 | 0 | Yes
2030-03-31 10:00 | 2030 100% ECP | -700 | -526 | -510 | 108.38 | 0 | 0 | Yes
2030-03-31 11:00 | 2030 100% ECP | -700 | -526 | -510 | 321.03 | 0 | 0 | Yes
2030-03-31 12:00 | 2030 100% ECP | -700 | -526 | -510 | 267.77 | 0 | 0 | Yes
2030-03-31 13:00 | 2030 100% ECP | -700 | -526 | -510 | 245.27 | 0 | 0 | Yes
2030-03-31 14:00 | 2030 100% ECP | -700 | -526 | -510 | 197.33 | 0 | 0 | Yes
2030-03-31 15:00 | 2030 100% ECP | -573.92 | -526 | -510 | -6.69 | 0 | 0 | Yes
2030-03-31 16:00 | 2030 100% ECP | -153.92 | -526 | -510 | 67.4 | 0 | 0 | No
2030-03-31 17:00 | 2030 100% ECP | 266.08 | -526 | -510 | 67.4 | 0 | 0 | No
2030-03-31 18:00 | 2030 100% ECP | 686.08 | -289.18 | -510 | 367.4 | 0 | 0 | No
2030-03-31 19:00 | 2030 100% ECP | 700 | 0 | -510 | 426.81 | 0 | 0 | No
2030-03-31 20:00 | 2030 100% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-03-31 21:00 | 2030 100% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-03-31 22:00 | 2030 100% ECP | 700 | 0 | -510 | 427.56 | 0 | 0 | No
2030-03-31 23:00 | 2030 100% ECP | 700 | 0 | -510 | 359.51 | 0 | 0 | No
2030-04-01 | 2030 100% ECP | 700 | -300 | -510 | 303.72 | 0 | 0 | No
2030-04-01 01:00 | 2030 100% ECP | 700 | -86.85 | -510 | 207.26 | 0 | 0 | No
2030-04-01 02:00 | 2030 100% ECP | 700 | -386.85 | -510 | 122.76 | 0 | 0 | No
2030-04-01 03:00 | 2030 100% ECP | 700 | -526 | -510 | 2.79 | 0 | 0 | No
2030-04-01 04:00 | 2030 100% ECP | 700 | -292.7 | -510 | 226.99 | 0 | 0 | No
2030-04-01 05:00 | 2030 100% ECP | 700 | 0 | -319.22 | 163.38 | 0 | 0 | No
2030-04-01 06:00 | 2030 100% ECP | 674.15 | 0 | -172.58 | 220 | 0 | 0 | No
2030-04-01 07:00 | 2030 100% ECP | 254.15 | 0 | 54.76 | 456.85 | 0 | 0 | No
2030-04-01 08:00 | 2030 100% ECP | -165.85 | -226 | -210 | 510 | 0 | 0 | No
2030-04-01 09:00 | 2030 100% ECP | -585.85 | -526 | -510 | 448.5 | 0 | 0 | Yes
2030-04-01 10:00 | 2030 100% ECP | -700 | -526 | -510 | 430.57 | 0 | 0 | Yes
2030-04-01 11:00 | 2030 100% ECP | -700 | -526 | -510 | 163.82 | 0 | 0 | Yes
2030-04-01 12:00 | 2030 100% ECP | -700 | -526 | -510 | 150.52 | 0 | 0 | Yes
2030-04-01 13:00 | 2030 100% ECP | -700 | -526 | -510 | 450.52 | 0 | 0 | Yes
2030-04-01 14:00 | 2030 100% ECP | -700 | -287.74 | -510 | 510 | 0 | 0 | Yes
2030-04-01 15:00 | 2030 100% ECP | -413.86 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-01 16:00 | 2030 100% ECP | 6.14 | -526 | -510 | 228.5 | 0 | 0 | No
2030-04-01 17:00 | 2030 100% ECP | 426.14 | -526 | -510 | 172.26 | 0 | 0 | No
2030-04-01 18:00 | 2030 100% ECP | 6.14 | -526 | -510 | 280.82 | 0 | 0 | No
2030-04-01 19:00 | 2030 100% ECP | -413.86 | -526 | -510 | 227.86 | 0 | 0 | No
2030-04-01 20:00 | 2030 100% ECP | -140 | -395 | -390 | 0 | 0 | 0 | No
2030-04-01 21:00 | 2030 100% ECP | 280 | -95 | -90 | 0 | 0 | 0 | No
2030-04-01 22:00 | 2030 100% ECP | 700 | 205 | 210 | 217.56 | 0 | 0 | No
2030-04-01 23:00 | 2030 100% ECP | 682.21 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 | 2030 100% ECP | 314.47 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 01:00 | 2030 100% ECP | -105.53 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 02:00 | 2030 100% ECP | -525.53 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 15:00 | 2030 100% ECP | -700 | 505 | 464.99 | 510 | 0 | 0 | Yes
2030-04-02 16:00 | 2030 100% ECP | -700 | 374 | 164.99 | 510 | 0 | 0 | Yes
2030-04-02 17:00 | 2030 100% ECP | -700 | 74 | -135.01 | 501.19 | 0 | 0 | No
2030-04-02 18:00 | 2030 100% ECP | -280 | -226 | -435.01 | 201.19 | 0 | 0 | No
2030-04-02 19:00 | 2030 100% ECP | 0 | -526 | -510 | 428.57 | 0 | 0 | No
2030-04-02 20:00 | 2030 100% ECP | -411.27 | -526 | -510 | 510 | 0 | 0 | No
2030-04-02 21:00 | 2030 100% ECP | 0 | -464.61 | -510 | 510 | 0 | 0 | No
2030-04-02 22:00 | 2030 100% ECP | 280 | -164.61 | -211.26 | 498.21 | 0 | 0 | No
2030-04-02 23:00 | 2030 100% ECP | 700 | 135.39 | 88.74 | 510 | 0 | 0 | No
2030-04-03 | 2030 100% ECP | 280 | 0 | -44.99 | 210 | 0 | 0 | No
2030-04-03 01:00 | 2030 100% ECP | 616.8 | 0 | 0 | 0 | 0 | 0 | No
2030-04-03 02:00 | 2030 100% ECP | 196.8 | 0 | -53.76 | 138.17 | 0 | 0 | No
2030-04-03 03:00 | 2030 100% ECP | 0 | 0 | -210 | 0 | 0 | 0 | No
2030-04-03 04:00 | 2030 100% ECP | 0 | -300 | -510 | 0 | 0 | 0 | No
2030-04-03 05:00 | 2030 100% ECP | -280 | -526 | -510 | 64.2 | 0 | 0 | No
2030-04-03 06:00 | 2030 100% ECP | -700 | -526 | -510 | 132.41 | 0 | 0 | No
2030-04-03 07:00 | 2030 100% ECP | -700 | -526 | -510 | 285.07 | 0 | 0 | No
2030-04-03 08:00 | 2030 100% ECP | -493.7 | -526 | -510 | 349.43 | 0 | 0 | No
2030-04-03 09:00 | 2030 100% ECP | -700 | -526 | -510 | 315.53 | 0 | 0 | No
2030-04-03 10:00 | 2030 100% ECP | -700 | -526 | -510 | 288.43 | 0 | 0 | No
2030-04-03 11:00 | 2030 100% ECP | -700 | -526 | -510 | 264.63 | 0 | 0 | No
2030-04-03 12:00 | 2030 100% ECP | -700 | -526 | -510 | 85.09 | 0 | 0 | No
2030-04-03 13:00 | 2030 100% ECP | -700 | -526 | -510 | 98.11 | 0 | 0 | No
2030-04-03 14:00 | 2030 100% ECP | -700 | -526 | -510 | -147.52 | 0 | 0 | No
2030-04-03 15:00 | 2030 100% ECP | -700 | -526 | -510 | -110.18 | 0 | 0 | No
2030-04-03 16:00 | 2030 100% ECP | -700 | -526 | -510 | 149.18 | 0 | 0 | No
2030-04-03 17:00 | 2030 100% ECP | -280 | -226 | -510 | 224.24 | 0 | 0 | No
2030-04-03 18:00 | 2030 100% ECP | -700 | -526 | -510 | -75.76 | 0 | 0 | No
2030-04-03 19:00 | 2030 100% ECP | -700 | -526 | -510 | -211.29 | 0 | 0 | No
2030-04-03 20:00 | 2030 100% ECP | -280 | -300 | -510 | 88.71 | 0 | 0 | No
2030-04-03 21:00 | 2030 100% ECP | 140 | 0 | -510 | 346.79 | 0 | 0 | No
2030-04-03 22:00 | 2030 100% ECP | 560 | 0 | -433.61 | 222.37 | 0 | 0 | No
2030-04-03 23:00 | 2030 100% ECP | 700 | 0 | -510 | 190.79 | 0 | 0 | No
2030-04-04 | 2030 100% ECP | 700 | 0 | -473.8 | 13.93 | 0 | 0 | No
2030-04-04 01:00 | 2030 100% ECP | 700 | 0 | -510 | 103.73 | 0 | 0 | No
2030-04-04 02:00 | 2030 100% ECP | 700 | 0 | -510 | 81.81 | 0 | 0 | No
2030-04-04 03:00 | 2030 100% ECP | 700 | 0 | -510 | 65.15 | 0 | 0 | No
2030-04-04 04:00 | 2030 100% ECP | 354.03 | 0 | -510 | 0 | 0 | 0 | No
2030-04-04 05:00 | 2030 100% ECP | -65.97 | 0 | -483.95 | 40.19 | 0 | 0 | No
2030-04-04 06:00 | 2030 100% ECP | -485.97 | 0 | -510 | 165.98 | 0 | 0 | No
2030-04-04 07:00 | 2030 100% ECP | -280 | -226 | -510 | 347.11 | 0 | 0 | No
2030-04-04 08:00 | 2030 100% ECP | -700 | -526 | -510 | 461.13 | 0 | 0 | No
2030-04-04 09:00 | 2030 100% ECP | -700 | -526 | -510 | 211.44 | 0 | 0 | Yes
2030-04-04 10:00 | 2030 100% ECP | -700 | -526 | -510 | -88.56 | 0 | 0 | Yes
2030-04-04 11:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | Yes
2030-04-04 12:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-04-04 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-04 14:00 | 2030 100% ECP | -700 | -226 | -258.36 | 510 | 0 | 0 | Yes
2030-04-04 15:00 | 2030 100% ECP | -700 | -526 | -510 | 330.01 | 0 | 0 | Yes
2030-04-04 16:00 | 2030 100% ECP | -700 | -526 | -510 | 30.01 | 0 | 0 | Yes
2030-04-04 17:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-04-04 18:00 | 2030 100% ECP | -700 | -526 | -510 | 274.91 | 0 | 0 | Yes
2030-04-04 19:00 | 2030 100% ECP | -700 | -526 | -510 | 318.85 | 0 | 0 | No
2030-04-04 20:00 | 2030 100% ECP | -700 | -526 | -510 | 318.85 | 0 | 0 | No
2030-04-04 21:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-04-04 22:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-04-04 23:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-04-05 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 03:00 | 2030 100% ECP | -700 | 505 | 510 | 484.94 | 0 | 0 | Yes
2030-04-05 04:00 | 2030 100% ECP | -700 | 505 | 510 | 184.94 | 0 | 0 | Yes
2030-04-05 05:00 | 2030 100% ECP | -700 | 505 | 510 | 169.79 | 0 | 0 | Yes
2030-04-05 06:00 | 2030 100% ECP | -700 | 505 | 510 | 236.02 | 0 | 0 | Yes
2030-04-05 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 10:00 | 2030 100% ECP | -700 | 505 | 510 | 500.96 | 0 | 0 | Yes
2030-04-05 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 12:00 | 2030 100% ECP | -700 | 505 | 510 | 471.35 | 0 | 0 | Yes
2030-04-05 13:00 | 2030 100% ECP | -700 | 505 | 510 | 252.5 | 0 | 0 | Yes
2030-04-05 14:00 | 2030 100% ECP | -700 | 505 | 510 | 198.41 | 0 | 0 | Yes
2030-04-05 15:00 | 2030 100% ECP | -700 | 505 | 510 | 213.22 | 0 | 0 | Yes
2030-04-05 16:00 | 2030 100% ECP | -700 | 505 | 510 | 310.32 | 0 | 0 | Yes
2030-04-05 17:00 | 2030 100% ECP | -700 | 505 | 510 | 359.8 | 0 | 0 | Yes
2030-04-05 18:00 | 2030 100% ECP | -700 | 505 | 510 | 334.95 | 0 | 0 | Yes
2030-04-05 19:00 | 2030 100% ECP | -700 | 505 | 510 | 298.28 | 0 | 0 | Yes
2030-04-05 20:00 | 2030 100% ECP | -700 | 505 | 510 | 309.97 | 0 | 0 | Yes
2030-04-05 21:00 | 2030 100% ECP | -700 | 505 | 510 | 298.22 | 0 | 0 | Yes
2030-04-05 22:00 | 2030 100% ECP | -700 | 505 | 510 | 220.77 | 0 | 0 | Yes
2030-04-05 23:00 | 2030 100% ECP | -700 | 505 | 510 | 165.77 | 0 | 0 | Yes
2030-04-06 | 2030 100% ECP | -700 | 505 | 510 | 465.77 | 0 | 0 | Yes
2030-04-06 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 13:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-04-06 14:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-04-06 15:00 | 2030 100% ECP | -700 | -226 | -210 | 502.77 | 0 | 0 | Yes
2030-04-06 16:00 | 2030 100% ECP | -700 | -526 | -510 | 202.77 | 0 | 0 | Yes
2030-04-06 17:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-04-06 18:00 | 2030 100% ECP | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-04-06 19:00 | 2030 100% ECP | 0 | -526 | -510 | 510 | 0 | 0 | No
2030-04-06 20:00 | 2030 100% ECP | 420 | -526 | -510 | 320.65 | 0 | 0 | No
2030-04-06 21:00 | 2030 100% ECP | 700 | -474.44 | -510 | 510 | 0 | 0 | No
2030-04-06 22:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-06 23:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-07 | 2030 100% ECP | 700 | -435.99 | -510 | 413.59 | 0 | 0 | No
2030-04-07 01:00 | 2030 100% ECP | 700 | -409.99 | -510 | 510 | 0 | 0 | No
2030-04-07 02:00 | 2030 100% ECP | 700 | -109.99 | -510 | 510 | 0 | 0 | No
2030-04-07 03:00 | 2030 100% ECP | 700 | -313.05 | -510 | 441.15 | 0 | 0 | No
2030-04-07 04:00 | 2030 100% ECP | 560 | -442.33 | -510 | 387.75 | 0 | 0 | No
2030-04-07 05:00 | 2030 100% ECP | 140 | -142.33 | -510 | 398.23 | 0 | 0 | No
2030-04-07 06:00 | 2030 100% ECP | -280 | -442.33 | -510 | 387.82 | 0 | 0 | No
2030-04-07 07:00 | 2030 100% ECP | -700 | -526 | -510 | 466.6 | 0 | 0 | No
2030-04-07 08:00 | 2030 100% ECP | -700 | -526 | -510 | 407 | 0 | 0 | Yes
2030-04-07 09:00 | 2030 100% ECP | -700 | -526 | -510 | 173.91 | 0 | 0 | Yes
2030-04-07 10:00 | 2030 100% ECP | -700 | -526 | -510 | -126.09 | 0 | 0 | Yes
2030-04-07 11:00 | 2030 100% ECP | -700 | -526 | -510 | -268.81 | 0 | 0 | Yes
2030-04-07 12:00 | 2030 100% ECP | -700 | -226 | -210 | 31.19 | 0 | 0 | Yes
2030-04-07 13:00 | 2030 100% ECP | -700 | -526 | -510 | 267.6 | 0 | 0 | Yes
2030-04-07 14:00 | 2030 100% ECP | -700 | -526 | -510 | 396.18 | 0 | 0 | Yes
2030-04-07 15:00 | 2030 100% ECP | -700 | -255.91 | -510 | 196.13 | 0 | 0 | Yes
2030-04-07 16:00 | 2030 100% ECP | -700 | -526 | -510 | -103.87 | 0 | 0 | Yes
2030-04-07 17:00 | 2030 100% ECP | -700 | -526 | -510 | 181.31 | 0 | 0 | No
2030-04-07 18:00 | 2030 100% ECP | -280 | -526 | -510 | 481.31 | 0 | 0 | No
2030-04-07 19:00 | 2030 100% ECP | 140 | -526 | -510 | 510 | 0 | 0 | No
2030-04-07 20:00 | 2030 100% ECP | 560 | -526 | -510 | 510 | 0 | 0 | No
2030-04-07 21:00 | 2030 100% ECP | 700 | -526 | -510 | 469.82 | 0 | 0 | No
2030-04-07 22:00 | 2030 100% ECP | 280 | -526 | -510 | 300 | 0 | 0 | No
2030-04-07 23:00 | 2030 100% ECP | 469.79 | -526 | -510 | 0 | 0 | 0 | No
2030-04-08 | 2030 100% ECP | 700 | -526 | -510 | -300 | 0 | 0 | No
2030-04-08 01:00 | 2030 100% ECP | 700 | -524.06 | -510 | -472.54 | 0 | 0 | No
2030-04-08 02:00 | 2030 100% ECP | 700 | -233.98 | -510 | -378.44 | 0 | 0 | No
2030-04-08 03:00 | 2030 100% ECP | 700 | -233.98 | -510 | -381.45 | 0 | 0 | No
2030-04-08 04:00 | 2030 100% ECP | 700 | -526 | -510 | -363.19 | 0 | 0 | No
2030-04-08 05:00 | 2030 100% ECP | 560 | -372.32 | -510 | -290.73 | 0 | 0 | No
2030-04-08 06:00 | 2030 100% ECP | 140 | -72.32 | -510 | -131.06 | 0 | 0 | No
2030-04-08 07:00 | 2030 100% ECP | -280 | -226 | -510 | 168.94 | 0 | 0 | No
2030-04-08 08:00 | 2030 100% ECP | -700 | -526 | -510 | 468.94 | 0 | 0 | No
2030-04-08 09:00 | 2030 100% ECP | -700 | -526 | -510 | 502.47 | 0 | 0 | Yes
2030-04-08 10:00 | 2030 100% ECP | -700 | -526 | -510 | 471.85 | 0 | 0 | Yes
2030-04-08 11:00 | 2030 100% ECP | -700 | -526 | -510 | 447.88 | 0 | 0 | Yes
2030-04-08 12:00 | 2030 100% ECP | -700 | -526 | -510 | 147.88 | 0 | 0 | Yes
2030-04-08 13:00 | 2030 100% ECP | -700 | -526 | -510 | 10.34 | 0 | 0 | Yes
2030-04-08 14:00 | 2030 100% ECP | -700 | -526 | -510 | 0.66 | 0 | 0 | Yes
2030-04-08 15:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | Yes
2030-04-08 16:00 | 2030 100% ECP | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-04-08 17:00 | 2030 100% ECP | 140 | -504.92 | -510 | 414.44 | 0 | 0 | No
2030-04-08 18:00 | 2030 100% ECP | -140 | -526 | -510 | 114.44 | 0 | 0 | No
2030-04-08 19:00 | 2030 100% ECP | -560 | -526 | -510 | -185.56 | 0 | 0 | No
2030-04-08 20:00 | 2030 100% ECP | -140 | -526 | -510 | -87.95 | 0 | 0 | No
2030-04-08 21:00 | 2030 100% ECP | 280 | -226 | -210 | 212.05 | 0 | 0 | No
2030-04-08 22:00 | 2030 100% ECP | 700 | 0 | 90 | 74.32 | 0 | 0 | No
2030-04-08 23:00 | 2030 100% ECP | 700 | 0 | 108.95 | 0 | 0 | 0 | No
2030-04-09 | 2030 100% ECP | 700 | 0 | 408.95 | 20.16 | 0 | 0 | No
2030-04-09 01:00 | 2030 100% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-04-09 02:00 | 2030 100% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-04-09 03:00 | 2030 100% ECP | 700 | 0 | 390 | 0 | 0 | 0 | No
2030-04-09 04:00 | 2030 100% ECP | 700 | 0 | 90 | 0 | 0 | 0 | No
2030-04-09 05:00 | 2030 100% ECP | 280 | 0 | -210 | -53.86 | 0 | 0 | No
2030-04-09 06:00 | 2030 100% ECP | -140 | -300 | -510 | -353.86 | 0 | 0 | No
2030-04-09 07:00 | 2030 100% ECP | -560 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 08:00 | 2030 100% ECP | -700 | -526 | -510 | -407.15 | 0 | 0 | No
2030-04-09 09:00 | 2030 100% ECP | -700 | -526 | -510 | -407.55 | 0 | 0 | Yes
2030-04-09 10:00 | 2030 100% ECP | -700 | -526 | -510 | -431.01 | 0 | 0 | Yes
2030-04-09 11:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-04-09 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-04-09 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-04-09 14:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-04-09 15:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-04-09 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 17:00 | 2030 100% ECP | -280 | -415.81 | -510 | -417.18 | 0 | 0 | No
2030-04-09 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 20:00 | 2030 100% ECP | -280 | -226 | -510 | -300 | 0 | 0 | No
2030-04-09 21:00 | 2030 100% ECP | 140 | 0 | -510 | 0 | 0 | 0 | No
2030-04-09 22:00 | 2030 100% ECP | 560 | 0 | -510 | -262.76 | 0 | 0 | No
2030-04-09 23:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-10 | 2030 100% ECP | 700 | 0 | -210 | 0 | 0 | 0 | No
2030-04-10 01:00 | 2030 100% ECP | 700 | 0 | -501.69 | 0 | 0 | 0 | No
2030-04-10 02:00 | 2030 100% ECP | 700 | 0 | -201.69 | 0 | 0 | 0 | No
2030-04-10 03:00 | 2030 100% ECP | 700 | 0 | -9.1 | 0 | 0 | 0 | No
2030-04-10 04:00 | 2030 100% ECP | 420 | 0 | 0 | 0 | 0 | 0 | No
2030-04-10 05:00 | 2030 100% ECP | 0 | 0 | 0 | 0 | 0 | 0 | No
2030-04-10 06:00 | 2030 100% ECP | -420 | 0 | -210 | 0 | 0 | 0 | No
2030-04-10 07:00 | 2030 100% ECP | -370.47 | -226 | -510 | -60.6 | 0 | 0 | No
2030-04-10 08:00 | 2030 100% ECP | -496.94 | -526 | -510 | 66.36 | 0 | 0 | No
2030-04-10 09:00 | 2030 100% ECP | -700 | -526 | -510 | 65.58 | 0 | 0 | No
2030-04-10 10:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 11:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 13:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 14:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 15:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 16:00 | 2030 100% ECP | -280 | -269.54 | -510 | 35.22 | 0 | 0 | No
2030-04-10 17:00 | 2030 100% ECP | 140 | -526 | -510 | -264.78 | 0 | 0 | No
2030-04-10 18:00 | 2030 100% ECP | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-04-10 19:00 | 2030 100% ECP | -422.48 | -526 | -510 | -499.07 | 0 | 0 | No
2030-04-10 20:00 | 2030 100% ECP | -2.48 | -300 | -300 | -199.07 | 0 | 0 | No
2030-04-10 21:00 | 2030 100% ECP | 417.52 | 0 | 0 | 100.93 | 0 | 0 | No
2030-04-10 22:00 | 2030 100% ECP | 700 | 202.81 | 300 | 301.49 | 0 | 0 | No
2030-04-10 23:00 | 2030 100% ECP | 700 | 0 | 0 | 1.49 | 0 | 0 | No
2030-04-11 | 2030 100% ECP | 700 | 0 | 31.95 | 0 | 0 | 0 | No
2030-04-11 01:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 02:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 03:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 04:00 | 2030 100% ECP | 280 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 05:00 | 2030 100% ECP | -140 | 0 | 40.55 | 0 | 0 | 0 | No
2030-04-11 06:00 | 2030 100% ECP | -560 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 07:00 | 2030 100% ECP | -700 | -226 | -210 | 233.71 | 0 | 0 | No
2030-04-11 08:00 | 2030 100% ECP | -700 | -526 | -510 | -66.29 | 0 | 0 | No
2030-04-11 09:00 | 2030 100% ECP | -700 | -526 | -510 | -366.29 | 0 | 0 | Yes
2030-04-11 10:00 | 2030 100% ECP | -700 | -526 | -510 | -102.2 | 0 | 0 | Yes
2030-04-11 11:00 | 2030 100% ECP | -700 | -526 | -510 | -158.19 | 0 | 0 | Yes
2030-04-11 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-04-11 13:00 | 2030 100% ECP | -700 | -526 | -510 | -199.32 | 0 | 0 | Yes
2030-04-11 14:00 | 2030 100% ECP | -700 | -526 | -510 | -132.47 | 0 | 0 | Yes
2030-04-11 15:00 | 2030 100% ECP | -700 | -526 | -510 | -346.88 | 0 | 0 | Yes
2030-04-11 16:00 | 2030 100% ECP | -700 | -526 | -510 | -46.88 | 0 | 0 | Yes
2030-04-11 17:00 | 2030 100% ECP | -700 | -526 | -510 | -208.05 | 0 | 0 | No
2030-04-11 18:00 | 2030 100% ECP | -700 | -526 | -510 | -508.05 | 0 | 0 | No
2030-04-11 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-11 20:00 | 2030 100% ECP | -280 | -446.56 | -510 | -210 | 0 | 0 | No
2030-04-11 21:00 | 2030 100% ECP | 140 | -146.56 | -210 | 90 | 0 | 0 | No
2030-04-11 22:00 | 2030 100% ECP | 560 | 153.44 | 90 | 390 | 0 | 0 | No
2030-04-11 23:00 | 2030 100% ECP | 700 | 0 | 390 | 106.44 | 0 | 0 | No
2030-04-12 | 2030 100% ECP | 700 | 300 | 510 | 406.44 | 0 | 0 | No
2030-04-12 01:00 | 2030 100% ECP | 700 | 173.4 | 510 | 510 | 0 | 0 | No
2030-04-12 02:00 | 2030 100% ECP | 700 | 473.4 | 510 | 510 | 0 | 0 | No
2030-04-12 03:00 | 2030 100% ECP | 700 | 302.73 | 390 | 390 | 0 | 0 | No
2030-04-12 04:00 | 2030 100% ECP | 700 | 2.73 | 90 | 90 | 0 | 0 | No
2030-04-12 05:00 | 2030 100% ECP | 280 | -297.27 | -210 | -210 | 0 | 0 | No
2030-04-12 06:00 | 2030 100% ECP | -140 | -526 | -510 | -510 | 0 | 0 | No
2030-04-12 07:00 | 2030 100% ECP | -560 | -526 | -510 | -510 | 0 | 0 | No
2030-04-12 08:00 | 2030 100% ECP | -474.94 | -526 | -510 | -510 | 0 | 0 | No
2030-04-12 09:00 | 2030 100% ECP | -229.44 | -526 | -510 | -510 | 0 | 0 | No
2030-04-12 10:00 | 2030 100% ECP | -649.44 | -526 | -510 | -336.54 | 0 | 0 | No
2030-04-12 11:00 | 2030 100% ECP | -700 | -526 | -510 | -36.54 | 0 | 0 | No
2030-04-12 12:00 | 2030 100% ECP | -700 | -526 | -510 | -278.23 | 0 | 0 | No
2030-04-12 13:00 | 2030 100% ECP | -700 | -526 | -510 | -184.14 | 0 | 0 | No
2030-04-12 14:00 | 2030 100% ECP | -700 | -526 | -510 | -371.43 | 0 | 0 | No
2030-04-12 15:00 | 2030 100% ECP | -700 | -526 | -510 | -228.95 | 0 | 0 | No
2030-04-12 16:00 | 2030 100% ECP | -700 | -526 | -510 | -82.34 | 0 | 0 | Yes
2030-04-12 17:00 | 2030 100% ECP | -700 | -526 | -510 | 68.02 | 0 | 0 | No
2030-04-12 18:00 | 2030 100% ECP | -700 | -526 | -510 | -34.63 | 0 | 0 | No
2030-04-12 19:00 | 2030 100% ECP | -700 | -526 | -510 | 62.72 | 0 | 0 | No
2030-04-12 20:00 | 2030 100% ECP | -700 | -526 | -510 | 57.85 | 0 | 0 | No
2030-04-12 21:00 | 2030 100% ECP | -700 | -226 | -210 | 251.65 | 0 | 0 | Yes
2030-04-12 22:00 | 2030 100% ECP | -700 | 74 | 90 | 63.96 | 0 | 0 | Yes
2030-04-12 23:00 | 2030 100% ECP | -700 | 374 | 390 | 0 | 0 | 0 | Yes
2030-04-13 | 2030 100% ECP | -700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-04-13 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-13 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-13 03:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-04-13 04:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-04-13 05:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-04-13 06:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-13 07:00 | 2030 100% ECP | -700 | -526 | -510 | -351.77 | 0 | 0 | No
2030-04-13 08:00 | 2030 100% ECP | -700 | -526 | -510 | -51.77 | 0 | 0 | Yes
2030-04-13 09:00 | 2030 100% ECP | -700 | -526 | -510 | 248.23 | 0 | 0 | Yes
2030-04-13 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 14:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 15:00 | 2030 100% ECP | -700 | -526 | -510 | 483.35 | 0 | 0 | Yes
2030-04-13 16:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 17:00 | 2030 100% ECP | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-04-13 18:00 | 2030 100% ECP | 140 | -526 | -510 | 510 | 0 | 0 | No
2030-04-13 19:00 | 2030 100% ECP | 560 | -526 | -510 | 510 | 0 | 0 | No
2030-04-13 20:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-13 21:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-13 22:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-13 23:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-14 | 2030 100% ECP | 700 | -231.31 | -510 | 210 | 0 | 0 | No
2030-04-14 01:00 | 2030 100% ECP | 700 | -377.83 | -510 | 167.77 | 0 | 0 | No
2030-04-14 02:00 | 2030 100% ECP | 700 | -377.83 | -510 | 179.6 | 0 | 0 | No
2030-04-14 03:00 | 2030 100% ECP | 700 | -377.83 | -510 | 86.82 | 0 | 0 | No
2030-04-14 04:00 | 2030 100% ECP | 700 | -377.83 | -510 | 82.11 | 0 | 0 | No
2030-04-14 05:00 | 2030 100% ECP | 700 | -77.83 | -510 | 87.04 | 0 | 0 | No
2030-04-14 06:00 | 2030 100% ECP | 560 | -377.83 | -510 | 164.04 | 0 | 0 | No
2030-04-14 07:00 | 2030 100% ECP | 140 | -526 | -510 | 189.74 | 0 | 0 | No
2030-04-14 08:00 | 2030 100% ECP | -280 | -526 | -510 | 123.68 | 0 | 0 | Yes
2030-04-14 09:00 | 2030 100% ECP | -700 | -526 | -510 | 55.73 | 0 | 0 | Yes
2030-04-14 10:00 | 2030 100% ECP | -700 | -526 | -510 | 69.87 | 0 | 0 | Yes
2030-04-14 11:00 | 2030 100% ECP | -700 | -526 | -510 | 32.71 | 0 | 0 | Yes
2030-04-14 12:00 | 2030 100% ECP | -700 | -526 | -510 | 84.93 | 0 | 0 | Yes
2030-04-14 13:00 | 2030 100% ECP | -700 | -526 | -510 | 8.01 | 0 | 0 | Yes
2030-04-14 14:00 | 2030 100% ECP | -700 | -526 | -510 | 62.01 | 0 | 0 | Yes
2030-04-14 15:00 | 2030 100% ECP | -700 | -526 | -510 | 70.19 | 0 | 0 | Yes
2030-04-14 16:00 | 2030 100% ECP | -700 | -526 | -510 | 169.33 | 0 | 0 | Yes
2030-04-14 17:00 | 2030 100% ECP | -280 | -526 | -510 | 258.6 | 0 | 0 | No
2030-04-14 18:00 | 2030 100% ECP | 140 | -526 | -510 | 326.89 | 0 | 0 | No
2030-04-14 19:00 | 2030 100% ECP | 560 | -226 | -510 | 369.52 | 0 | 0 | No
2030-04-14 20:00 | 2030 100% ECP | 700 | 0 | -510 | 366.07 | 0 | 0 | No
2030-04-14 21:00 | 2030 100% ECP | 700 | 0 | -510 | 359.39 | 0 | 0 | No
2030-04-14 22:00 | 2030 100% ECP | 700 | 0 | -510 | 252.32 | 0 | 0 | No
2030-04-14 23:00 | 2030 100% ECP | 700 | -196.04 | -510 | 147.65 | 0 | 0 | No
2030-04-15 | 2030 100% ECP | 700 | 0 | -510 | 88.91 | 0 | 0 | No
2030-04-15 01:00 | 2030 100% ECP | 700 | 0 | -510 | 83.85 | 0 | 0 | No
2030-04-15 02:00 | 2030 100% ECP | 700 | 0 | -510 | 89.36 | 0 | 0 | No
2030-04-15 03:00 | 2030 100% ECP | 700 | 0 | -510 | 79.52 | 0 | 0 | No
2030-04-15 04:00 | 2030 100% ECP | 700 | 0 | -510 | 52.36 | 0 | 0 | No
2030-04-15 05:00 | 2030 100% ECP | 700 | 0 | -510 | 69.19 | 0 | 0 | No
2030-04-15 06:00 | 2030 100% ECP | 687.76 | -232.67 | -510 | 154.15 | 0 | 0 | No
2030-04-15 07:00 | 2030 100% ECP | 267.76 | -526 | -510 | 243.43 | 0 | 0 | No
2030-04-15 08:00 | 2030 100% ECP | -152.24 | -526 | -510 | 256.06 | 0 | 0 | Yes
2030-04-15 09:00 | 2030 100% ECP | -572.24 | -526 | -510 | 215.77 | 0 | 0 | Yes
2030-04-15 10:00 | 2030 100% ECP | -700 | -526 | -510 | 178.22 | 0 | 0 | Yes
2030-04-15 11:00 | 2030 100% ECP | -700 | -526 | -510 | 173.14 | 0 | 0 | Yes
2030-04-15 12:00 | 2030 100% ECP | -700 | -526 | -510 | 178.61 | 0 | 0 | Yes
2030-04-15 13:00 | 2030 100% ECP | -700 | -526 | -510 | 147.89 | 0 | 0 | Yes
2030-04-15 14:00 | 2030 100% ECP | -700 | -526 | -510 | 126.5 | 0 | 0 | Yes
2030-04-15 15:00 | 2030 100% ECP | -700 | -526 | -510 | 157.27 | 0 | 0 | Yes
2030-04-15 16:00 | 2030 100% ECP | -700 | -526 | -510 | 263.99 | 0 | 0 | Yes
2030-04-15 17:00 | 2030 100% ECP | -280 | -526 | -510 | 417.54 | 0 | 0 | No
2030-04-15 18:00 | 2030 100% ECP | 140 | -526 | -510 | 399.19 | 0 | 0 | No
2030-04-15 19:00 | 2030 100% ECP | 560 | -431.25 | -510 | 350.12 | 0 | 0 | No
2030-04-15 20:00 | 2030 100% ECP | 700 | -131.25 | -510 | 306.42 | 0 | 0 | No
2030-04-15 21:00 | 2030 100% ECP | 700 | -129.59 | -510 | 372.62 | 0 | 0 | No
2030-04-15 22:00 | 2030 100% ECP | 700 | -429.59 | -510 | 265.98 | 0 | 0 | No
2030-04-15 23:00 | 2030 100% ECP | 700 | -526 | -510 | 36.75 | 0 | 0 | No
2030-04-16 | 2030 100% ECP | 700 | -226 | -510 | -55.57 | 0 | 0 | No
2030-04-16 01:00 | 2030 100% ECP | 700 | 0 | -510 | -120.31 | 0 | 0 | No
2030-04-16 02:00 | 2030 100% ECP | 700 | 0 | -510 | -135.76 | 0 | 0 | No
2030-04-16 03:00 | 2030 100% ECP | 700 | 0 | -510 | -59.28 | 0 | 0 | No
2030-04-16 04:00 | 2030 100% ECP | 560 | -101 | -510 | -42.07 | 0 | 0 | No
2030-04-16 05:00 | 2030 100% ECP | 140 | -152.97 | -510 | -80.27 | 0 | 0 | No
2030-04-16 06:00 | 2030 100% ECP | -280 | -395.94 | -510 | -81.23 | 0 | 0 | No
2030-04-16 07:00 | 2030 100% ECP | -700 | -526 | -510 | 134.39 | 0 | 0 | No
2030-04-16 08:00 | 2030 100% ECP | -700 | -526 | -510 | 213.33 | 0 | 0 | Yes
2030-04-16 09:00 | 2030 100% ECP | -700 | -526 | -510 | 163.97 | 0 | 0 | Yes
2030-04-16 10:00 | 2030 100% ECP | -700 | -526 | -510 | 67.59 | 0 | 0 | Yes
2030-04-16 11:00 | 2030 100% ECP | -700 | -526 | -510 | -75.64 | 0 | 0 | Yes
2030-04-16 12:00 | 2030 100% ECP | -700 | -526 | -510 | -295.25 | 0 | 0 | Yes
2030-04-16 13:00 | 2030 100% ECP | -700 | -526 | -510 | -415.7 | 0 | 0 | Yes
2030-04-16 14:00 | 2030 100% ECP | -700 | -526 | -510 | -414.08 | 0 | 0 | Yes
2030-04-16 15:00 | 2030 100% ECP | -700 | -526 | -510 | -385.72 | 0 | 0 | Yes
2030-04-16 16:00 | 2030 100% ECP | -700 | -526 | -510 | -85.72 | 0 | 0 | Yes
2030-04-16 17:00 | 2030 100% ECP | -700 | -526 | -510 | 214.28 | 0 | 0 | No
2030-04-16 18:00 | 2030 100% ECP | -280 | -526 | -510 | 299.57 | 0 | 0 | No
2030-04-16 19:00 | 2030 100% ECP | -378.71 | -526 | -510 | 168.69 | 0 | 0 | No
2030-04-16 20:00 | 2030 100% ECP | 0 | -526 | -510 | -131.31 | 0 | 0 | No
2030-04-16 21:00 | 2030 100% ECP | 420 | -412.27 | -510 | -431.31 | 0 | 0 | No
2030-04-16 22:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-16 23:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-17 | 2030 100% ECP | 700 | -526 | -510 | -214.65 | 0 | 0 | No
2030-04-17 01:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-17 02:00 | 2030 100% ECP | 700 | -226 | -510 | -302.86 | 0 | 0 | No
2030-04-17 03:00 | 2030 100% ECP | 700 | -329.07 | -510 | -373.67 | 0 | 0 | No
2030-04-17 04:00 | 2030 100% ECP | 700 | -104.26 | -510 | -510 | 0 | 0 | No
2030-04-17 05:00 | 2030 100% ECP | 420 | -49.59 | -510 | -510 | 0 | 0 | No
2030-04-17 06:00 | 2030 100% ECP | 0 | -349.59 | -510 | -433.73 | 0 | 0 | No
2030-04-17 07:00 | 2030 100% ECP | -280 | -526 | -510 | -450.05 | 0 | 0 | No
2030-04-17 08:00 | 2030 100% ECP | -700 | -526 | -510 | -401.29 | 0 | 0 | Yes
2030-04-17 09:00 | 2030 100% ECP | -700 | -526 | -510 | -224.28 | 0 | 0 | Yes
2030-04-17 10:00 | 2030 100% ECP | -700 | -526 | -510 | 35.55 | 0 | 0 | Yes
2030-04-17 11:00 | 2030 100% ECP | -700 | -526 | -510 | -264.45 | 0 | 0 | Yes
2030-04-17 12:00 | 2030 100% ECP | -700 | -526 | -510 | -319.59 | 0 | 0 | Yes
2030-04-17 13:00 | 2030 100% ECP | -700 | -526 | -510 | -435.12 | 0 | 0 | Yes
2030-04-17 14:00 | 2030 100% ECP | -700 | -526 | -510 | -282.17 | 0 | 0 | Yes
2030-04-17 15:00 | 2030 100% ECP | -700 | -526 | -510 | -12.09 | 0 | 0 | Yes
2030-04-17 16:00 | 2030 100% ECP | -700 | -526 | -510 | 43.63 | 0 | 0 | Yes
2030-04-17 17:00 | 2030 100% ECP | -700 | -526 | -510 | 281.77 | 0 | 0 | No
2030-04-17 18:00 | 2030 100% ECP | -700 | -526 | -510 | 75.94 | 0 | 0 | Yes
2030-04-17 19:00 | 2030 100% ECP | -700 | -526 | -510 | 375.94 | 0 | 0 | No
2030-04-17 20:00 | 2030 100% ECP | -577.36 | -526 | -510 | 382.06 | 0 | 0 | No
2030-04-17 21:00 | 2030 100% ECP | -157.36 | -526 | -510 | 82.06 | 0 | 0 | No
2030-04-17 22:00 | 2030 100% ECP | -326.74 | -526 | -510 | -217.94 | 0 | 0 | No
2030-04-17 23:00 | 2030 100% ECP | 0 | -526 | -510 | -256.27 | 0 | 0 | No
2030-04-18 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-04-18 01:00 | 2030 100% ECP | 0 | -526 | -510 | -293.76 | 0 | 0 | No
2030-04-18 02:00 | 2030 100% ECP | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-04-18 03:00 | 2030 100% ECP | 0 | -526 | -510 | -134.25 | 0 | 0 | No
2030-04-18 04:00 | 2030 100% ECP | 0 | -526 | -510 | -242.75 | 0 | 0 | No
2030-04-18 05:00 | 2030 100% ECP | 0 | -526 | -510 | -359.9 | 0 | 0 | No
2030-04-18 06:00 | 2030 100% ECP | 0 | -526 | -510 | -120.43 | 0 | 0 | Yes
2030-04-18 07:00 | 2030 100% ECP | -280 | -526 | -510 | -86.05 | 0 | 0 | No
2030-04-18 08:00 | 2030 100% ECP | -700 | -526 | -510 | -20.55 | 0 | 0 | No
2030-04-18 09:00 | 2030 100% ECP | -700 | -526 | -510 | -20.55 | 0 | 0 | No
2030-04-18 10:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-18 11:00 | 2030 100% ECP | -700 | -526 | -510 | 54.34 | 0 | 0 | No
2030-04-18 12:00 | 2030 100% ECP | -700 | -526 | -510 | -92.69 | 0 | 0 | No
2030-04-18 13:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-18 14:00 | 2030 100% ECP | -700 | -526 | -510 | 63.95 | 0 | 0 | No
2030-04-18 15:00 | 2030 100% ECP | -700 | -526 | -510 | -8.49 | 0 | 0 | No
2030-04-18 16:00 | 2030 100% ECP | -700 | -526 | -510 | 160.74 | 0 | 0 | No
2030-04-18 17:00 | 2030 100% ECP | -280 | -526 | -510 | -139.26 | 0 | 0 | No
2030-04-18 18:00 | 2030 100% ECP | -700 | -526 | -510 | -439.26 | 0 | 0 | No
2030-04-18 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-18 20:00 | 2030 100% ECP | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-04-18 21:00 | 2030 100% ECP | 140 | -526 | -510 | -457.97 | 0 | 0 | No
2030-04-18 22:00 | 2030 100% ECP | 354.93 | -526 | -510 | -157.97 | 0 | 0 | No
2030-04-18 23:00 | 2030 100% ECP | 700 | -526 | -510 | -73.16 | 0 | 0 | No
2030-04-19 | 2030 100% ECP | 280 | -526 | -510 | -276.09 | 0 | 0 | No
2030-04-19 01:00 | 2030 100% ECP | 0 | -526 | -510 | -351.33 | 0 | 0 | No
2030-04-19 02:00 | 2030 100% ECP | 192.46 | -526 | -510 | -357.85 | 0 | 0 | No
2030-04-19 03:00 | 2030 100% ECP | 405.32 | -526 | -510 | -145.64 | 0 | 0 | No
2030-04-19 04:00 | 2030 100% ECP | 236.78 | -526 | -510 | -412.09 | 0 | 0 | No
2030-04-19 05:00 | 2030 100% ECP | 140 | -526 | -510 | -112.09 | 0 | 0 | No
2030-04-19 06:00 | 2030 100% ECP | 140 | -526 | -510 | 2.13 | 0 | 0 | Yes
2030-04-19 07:00 | 2030 100% ECP | -280 | -526 | -510 | -297.87 | 0 | 0 | No
2030-04-19 08:00 | 2030 100% ECP | -700 | -526 | -510 | -12.02 | 0 | 0 | No
2030-04-19 09:00 | 2030 100% ECP | -700 | -526 | -510 | -312.02 | 0 | 0 | Yes
2030-04-19 10:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-04-19 11:00 | 2030 100% ECP | -700 | -526 | -510 | -476.15 | 0 | 0 | Yes
2030-04-19 12:00 | 2030 100% ECP | -700 | -526 | -510 | -237.48 | 0 | 0 | Yes
2030-04-19 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-04-19 14:00 | 2030 100% ECP | -700 | -526 | -510 | -400.35 | 0 | 0 | Yes
2030-04-19 15:00 | 2030 100% ECP | -700 | -526 | -510 | -141.18 | 0 | 0 | Yes
2030-04-19 16:00 | 2030 100% ECP | -700 | -526 | -510 | -84.35 | 0 | 0 | Yes
2030-04-19 17:00 | 2030 100% ECP | -700 | -526 | -510 | 58.63 | 0 | 0 | Yes
2030-04-19 18:00 | 2030 100% ECP | -700 | -526 | -510 | 220.06 | 0 | 0 | No
2030-04-19 19:00 | 2030 100% ECP | -700 | -526 | -510 | 89.64 | 0 | 0 | No
2030-04-19 20:00 | 2030 100% ECP | -700 | -526 | -510 | 41.58 | 0 | 0 | No
2030-04-19 21:00 | 2030 100% ECP | -280 | -300 | -390 | 120.49 | 0 | 0 | No
2030-04-19 22:00 | 2030 100% ECP | 140 | 0 | -90 | 118.93 | 0 | 0 | No
2030-04-19 23:00 | 2030 100% ECP | 560 | 300 | 210 | 418.93 | 0 | 0 | No
2030-04-20 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 01:00 | 2030 100% ECP | 300.63 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 02:00 | 2030 100% ECP | 446.36 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 03:00 | 2030 100% ECP | 293.91 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 04:00 | 2030 100% ECP | 0 | 374 | 390 | 390 | 0 | 0 | No
2030-04-20 05:00 | 2030 100% ECP | -280 | 74 | 90 | 90 | 0 | 0 | No
2030-04-20 06:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-04-20 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-20 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-04-20 09:00 | 2030 100% ECP | -700 | -526 | -510 | -382.89 | 0 | 0 | Yes
2030-04-20 10:00 | 2030 100% ECP | -700 | -226 | -210 | -82.89 | 0 | 0 | Yes
2030-04-20 11:00 | 2030 100% ECP | -700 | 74 | 90 | 217.11 | 0 | 0 | Yes
2030-04-20 12:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-04-20 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-20 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-20 15:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-04-20 16:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-04-20 17:00 | 2030 100% ECP | -700 | -226 | -210 | 439.24 | 0 | 0 | Yes
2030-04-20 18:00 | 2030 100% ECP | -700 | -526 | -510 | 139.24 | 0 | 0 | No
2030-04-20 19:00 | 2030 100% ECP | -700 | -526 | -510 | -160.76 | 0 | 0 | No
2030-04-20 20:00 | 2030 100% ECP | -700 | -226 | -210 | 139.24 | 0 | 0 | No
2030-04-20 21:00 | 2030 100% ECP | -700 | 74 | 90 | 439.24 | 0 | 0 | No
2030-04-20 22:00 | 2030 100% ECP | -383.49 | 374 | 390 | 510 | 0 | 0 | No
2030-04-20 23:00 | 2030 100% ECP | -127.89 | 505 | 510 | 510 | 0 | 0 | No
2030-04-21 | 2030 100% ECP | -547.89 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 01:00 | 2030 100% ECP | -421.6 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 02:00 | 2030 100% ECP | -700 | 505 | 510 | 431.24 | 0 | 0 | Yes
2030-04-21 03:00 | 2030 100% ECP | -280 | 505 | 510 | 131.24 | 0 | 0 | Yes
2030-04-21 04:00 | 2030 100% ECP | -700 | 505 | 510 | 258.81 | 0 | 0 | Yes
2030-04-21 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 07:00 | 2030 100% ECP | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-04-21 08:00 | 2030 100% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-04-21 09:00 | 2030 100% ECP | -700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-04-21 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 17:00 | 2030 100% ECP | -700 | 300 | 510 | 367.79 | 0 | 0 | Yes
2030-04-21 18:00 | 2030 100% ECP | -280 | 0 | 210 | 67.79 | 0 | 0 | No
2030-04-21 19:00 | 2030 100% ECP | -700 | -235.55 | -90 | -232.21 | 0 | 0 | No
2030-04-21 20:00 | 2030 100% ECP | -280 | 64.45 | 210 | 67.79 | 0 | 0 | No
2030-04-21 21:00 | 2030 100% ECP | 0 | 364.45 | 510 | 367.79 | 0 | 0 | Yes
2030-04-21 22:00 | 2030 100% ECP | 0 | 505 | 510 | 356.52 | 0 | 0 | Yes
2030-04-21 23:00 | 2030 100% ECP | 0 | 505 | 510 | 238.06 | 0 | 0 | Yes
2030-04-22 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-22 01:00 | 2030 100% ECP | 311.86 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-22 02:00 | 2030 100% ECP | 0 | 505 | 510 | 494.51 | 0 | 0 | Yes
2030-04-22 03:00 | 2030 100% ECP | 0 | 505 | 510 | 194.51 | 0 | 0 | Yes
2030-04-22 04:00 | 2030 100% ECP | 0 | 505 | 510 | -105.49 | 0 | 0 | No
2030-04-22 05:00 | 2030 100% ECP | 47.21 | 374 | 456.33 | -405.49 | 0 | 0 | No
2030-04-22 06:00 | 2030 100% ECP | -280 | 74 | 156.33 | -311.32 | 0 | 0 | No
2030-04-22 07:00 | 2030 100% ECP | -700 | -226 | -143.67 | -11.32 | 0 | 0 | No
2030-04-22 08:00 | 2030 100% ECP | -700 | -526 | -443.67 | -311.32 | 0 | 0 | Yes
2030-04-22 09:00 | 2030 100% ECP | -700 | -226 | -510 | -267.5 | 0 | 0 | Yes
2030-04-22 10:00 | 2030 100% ECP | -700 | 0 | -332.9 | 0 | 0 | 0 | Yes
2030-04-22 11:00 | 2030 100% ECP | -700 | 0 | -41.2 | 0 | 0 | 0 | Yes
2030-04-22 12:00 | 2030 100% ECP | -700 | 300 | 258.8 | 300 | 0 | 0 | Yes
2030-04-22 13:00 | 2030 100% ECP | -700 | 84.37 | 114.51 | 510 | 0 | 0 | Yes
2030-04-22 14:00 | 2030 100% ECP | -700 | 0 | -185.49 | 468.8 | 0 | 0 | Yes
2030-04-22 15:00 | 2030 100% ECP | -700 | -300 | -485.49 | 168.8 | 0 | 0 | Yes
2030-04-22 16:00 | 2030 100% ECP | -280 | -526 | -510 | 168.8 | 0 | 0 | No
2030-04-22 17:00 | 2030 100% ECP | -426.78 | -526 | -510 | 0 | 0 | 0 | No
2030-04-22 18:00 | 2030 100% ECP | -6.78 | -526 | -510 | 0 | 0 | 0 | No
2030-04-22 19:00 | 2030 100% ECP | 413.22 | -526 | -510 | -300 | 0 | 0 | No
2030-04-22 20:00 | 2030 100% ECP | 700 | -526 | -510 | -100.48 | 0 | 0 | No
2030-04-22 21:00 | 2030 100% ECP | 423.93 | -526 | -510 | 183.07 | 0 | 0 | No
2030-04-22 22:00 | 2030 100% ECP | 3.93 | -526 | -510 | 183.07 | 0 | 0 | No
2030-04-22 23:00 | 2030 100% ECP | 0 | -526 | -510 | -3.9 | 0 | 0 | No
2030-04-23 | 2030 100% ECP | 308.69 | -526 | -510 | -228.29 | 0 | 0 | No
2030-04-23 01:00 | 2030 100% ECP | 308.69 | -526 | -510 | -297.66 | 0 | 0 | No
2030-04-23 02:00 | 2030 100% ECP | 700 | -526 | -510 | -143.31 | 0 | 0 | No
2030-04-23 03:00 | 2030 100% ECP | 700 | -526 | -510 | -27.59 | 0 | 0 | No
2030-04-23 04:00 | 2030 100% ECP | 700 | -526 | -510 | -27.59 | 0 | 0 | No
2030-04-23 05:00 | 2030 100% ECP | 420 | -526 | -510 | -38.03 | 0 | 0 | No
2030-04-23 06:00 | 2030 100% ECP | 0 | -526 | -510 | -35.84 | 0 | 0 | No
2030-04-23 07:00 | 2030 100% ECP | -280 | -526 | -510 | -332.82 | 0 | 0 | No
2030-04-23 08:00 | 2030 100% ECP | -700 | -526 | -510 | -286.67 | 0 | 0 | No
2030-04-23 09:00 | 2030 100% ECP | -700 | -526 | -510 | -339.94 | 0 | 0 | Yes
2030-04-23 10:00 | 2030 100% ECP | -700 | -526 | -510 | -351.46 | 0 | 0 | Yes
2030-04-23 11:00 | 2030 100% ECP | -700 | -526 | -510 | -215.26 | 0 | 0 | Yes
2030-04-23 12:00 | 2030 100% ECP | -700 | -526 | -510 | -248.68 | 0 | 0 | Yes
2030-04-23 13:00 | 2030 100% ECP | -700 | -526 | -510 | -252.16 | 0 | 0 | Yes
2030-04-23 14:00 | 2030 100% ECP | -700 | -526 | -510 | -201.5 | 0 | 0 | Yes
2030-04-23 15:00 | 2030 100% ECP | -700 | -526 | -510 | -168.35 | 0 | 0 | Yes
2030-04-23 16:00 | 2030 100% ECP | -700 | -526 | -510 | -69.1 | 0 | 0 | No
2030-04-23 17:00 | 2030 100% ECP | -465.66 | -526 | -510 | -369.1 | 0 | 0 | No
2030-04-23 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-23 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-23 20:00 | 2030 100% ECP | -412.33 | -526 | -510 | -510 | 0 | 0 | No
2030-04-23 21:00 | 2030 100% ECP | 7.67 | -526 | -510 | -282.88 | 0 | 0 | No
2030-04-23 22:00 | 2030 100% ECP | 427.67 | -226 | -210 | 17.12 | 0 | 0 | No
2030-04-23 23:00 | 2030 100% ECP | 700 | 0 | -494.3 | -7.31 | 0 | 0 | No
2030-04-24 | 2030 100% ECP | 700 | 0 | -194.3 | 292.69 | 0 | 0 | No
2030-04-24 01:00 | 2030 100% ECP | 700 | 0 | 105.7 | 510 | 0 | 0 | No
2030-04-24 02:00 | 2030 100% ECP | 700 | 0 | 405.7 | 510 | 0 | 0 | No
2030-04-24 03:00 | 2030 100% ECP | 700 | 0 | 300 | 300 | 0 | 0 | No
2030-04-24 04:00 | 2030 100% ECP | 402.62 | 0 | 0 | 0 | 0 | 0 | No
2030-04-24 05:00 | 2030 100% ECP | -17.38 | -300 | -300 | -300 | 0 | 0 | No
2030-04-24 06:00 | 2030 100% ECP | -437.38 | -526 | -510 | -360.21 | 0 | 0 | No
2030-04-24 07:00 | 2030 100% ECP | -700 | -526 | -510 | -308.31 | 0 | 0 | No
2030-04-24 08:00 | 2030 100% ECP | -700 | -526 | -510 | -8.31 | 0 | 0 | No
2030-04-24 09:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-04-24 10:00 | 2030 100% ECP | -700 | -526 | -510 | 87.53 | 0 | 0 | Yes
2030-04-24 11:00 | 2030 100% ECP | -700 | -526 | -510 | 387.53 | 0 | 0 | Yes
2030-04-24 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-24 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-24 14:00 | 2030 100% ECP | -700 | -526 | -510 | 298.94 | 0 | 0 | Yes
2030-04-24 15:00 | 2030 100% ECP | -700 | -526 | -510 | -1.06 | 0 | 0 | No
2030-04-24 16:00 | 2030 100% ECP | -700 | -526 | -510 | 89.29 | 0 | 0 | No
2030-04-24 17:00 | 2030 100% ECP | -582.94 | -526 | -510 | 142.64 | 0 | 0 | No
2030-04-24 18:00 | 2030 100% ECP | -700 | -526 | -510 | -157.36 | 0 | 0 | No
2030-04-24 19:00 | 2030 100% ECP | -338.03 | -526 | -510 | -457.36 | 0 | 0 | No
2030-04-24 20:00 | 2030 100% ECP | 81.97 | -526 | -510 | -157.36 | 0 | 0 | No
2030-04-24 21:00 | 2030 100% ECP | 501.97 | -526 | -510 | 142.64 | 0 | 0 | No
2030-04-24 22:00 | 2030 100% ECP | 700 | -476.98 | -510 | 139.87 | 0 | 0 | No
2030-04-24 23:00 | 2030 100% ECP | 700 | -176.98 | -210 | 439.87 | 0 | 0 | No
2030-04-25 | 2030 100% ECP | 700 | 123.02 | 90 | 510 | 0 | 0 | No
2030-04-25 01:00 | 2030 100% ECP | 700 | 423.02 | 390 | 510 | 0 | 0 | No
2030-04-25 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-25 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-25 04:00 | 2030 100% ECP | 560 | 300 | 210 | 300 | 0 | 0 | No
2030-04-25 05:00 | 2030 100% ECP | 140 | 0 | -90 | 0 | 0 | 0 | No
2030-04-25 06:00 | 2030 100% ECP | -280 | -300 | -390 | -166.34 | 0 | 0 | No
2030-04-25 07:00 | 2030 100% ECP | -700 | -526 | -510 | -346.78 | 0 | 0 | No
2030-04-25 08:00 | 2030 100% ECP | -700 | -526 | -510 | -346.78 | 0 | 0 | No
2030-04-25 09:00 | 2030 100% ECP | -700 | -526 | -510 | -176.01 | 0 | 0 | Yes
2030-04-25 10:00 | 2030 100% ECP | -700 | -526 | -510 | 123.99 | 0 | 0 | Yes
2030-04-25 11:00 | 2030 100% ECP | -700 | -526 | -510 | 423.99 | 0 | 0 | Yes
2030-04-25 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-25 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-25 14:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-25 15:00 | 2030 100% ECP | -700 | -526 | -510 | 379.16 | 0 | 0 | Yes
2030-04-25 16:00 | 2030 100% ECP | -700 | -526 | -510 | 79.16 | 0 | 0 | No
2030-04-25 17:00 | 2030 100% ECP | -700 | -526 | -510 | 195.24 | 0 | 0 | No
2030-04-25 18:00 | 2030 100% ECP | -700 | -526 | -510 | -10.29 | 0 | 0 | No
2030-04-25 19:00 | 2030 100% ECP | -675.71 | -526 | -510 | -310.29 | 0 | 0 | No
2030-04-25 20:00 | 2030 100% ECP | -255.71 | -526 | -510 | -353.51 | 0 | 0 | No
2030-04-25 21:00 | 2030 100% ECP | 164.29 | -526 | -510 | -53.51 | 0 | 0 | No
2030-04-25 22:00 | 2030 100% ECP | 584.29 | -344.5 | -510 | -134.25 | 0 | 0 | No
2030-04-25 23:00 | 2030 100% ECP | 700 | -44.5 | -210 | 165.75 | 0 | 0 | No
2030-04-26 | 2030 100% ECP | 700 | 0 | 90 | 328.16 | 0 | 0 | No
2030-04-26 01:00 | 2030 100% ECP | 700 | 0 | 390 | 510 | 0 | 0 | No
2030-04-26 02:00 | 2030 100% ECP | 700 | 0 | 510 | 422.84 | 0 | 0 | No
2030-04-26 03:00 | 2030 100% ECP | 700 | 0 | 234.85 | 295.39 | 0 | 0 | No
2030-04-26 04:00 | 2030 100% ECP | 420 | 0 | -65.15 | 0 | 0 | 0 | No
2030-04-26 05:00 | 2030 100% ECP | 0 | -300 | -365.15 | -300 | 0 | 0 | No
2030-04-26 06:00 | 2030 100% ECP | -420 | -526 | -510 | -510 | 0 | 0 | No
2030-04-26 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-26 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-26 09:00 | 2030 100% ECP | -700 | -526 | -510 | -356.43 | 0 | 0 | No
2030-04-26 10:00 | 2030 100% ECP | -700 | -526 | -510 | -264.99 | 0 | 0 | No
2030-04-26 11:00 | 2030 100% ECP | -700 | -526 | -510 | -264.99 | 0 | 0 | No
2030-04-26 12:00 | 2030 100% ECP | -700 | -526 | -510 | -267.72 | 0 | 0 | No
2030-04-26 13:00 | 2030 100% ECP | -700 | -526 | -510 | -434.43 | 0 | 0 | No
2030-04-26 14:00 | 2030 100% ECP | -700 | -526 | -510 | -379.74 | 0 | 0 | No
2030-04-26 15:00 | 2030 100% ECP | -468.36 | -526 | -510 | -379.74 | 0 | 0 | No
2030-04-26 16:00 | 2030 100% ECP | -48.36 | -226 | -510 | -312.9 | 0 | 0 | No
2030-04-26 17:00 | 2030 100% ECP | 371.64 | -226 | -210 | -210 | 0 | 0 | No
2030-04-26 18:00 | 2030 100% ECP | -48.36 | -526 | -510 | -510 | 0 | 0 | No
2030-04-26 19:00 | 2030 100% ECP | -468.36 | -526 | -510 | -510 | 0 | 0 | Yes
2030-04-26 20:00 | 2030 100% ECP | -689.93 | -526 | -510 | -510 | 0 | 0 | No
2030-04-26 21:00 | 2030 100% ECP | -269.93 | -526 | -510 | -510 | 0 | 0 | No
2030-04-26 22:00 | 2030 100% ECP | 150.07 | -226 | -210 | -210 | 0 | 0 | No
2030-04-26 23:00 | 2030 100% ECP | 570.07 | 0 | -134.87 | 0 | 0 | 0 | No
2030-04-27 | 2030 100% ECP | 700 | 0 | -434.87 | 0 | 0 | 0 | No
2030-04-27 01:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-27 02:00 | 2030 100% ECP | 700 | 0 | -510 | -52.36 | 0 | 0 | No
2030-04-27 03:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-27 04:00 | 2030 100% ECP | 420 | 0 | -510 | -29.57 | 0 | 0 | No
2030-04-27 05:00 | 2030 100% ECP | 0 | -180.21 | -210 | -210 | 0 | 0 | No
2030-04-27 06:00 | 2030 100% ECP | -420 | -480.21 | -510 | -510 | 0 | 0 | No
2030-04-27 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-27 08:00 | 2030 100% ECP | -700 | -526 | -510 | -263.84 | 0 | 0 | No
2030-04-27 09:00 | 2030 100% ECP | -700 | -526 | -510 | -326.15 | 0 | 0 | Yes
2030-04-27 10:00 | 2030 100% ECP | -700 | -526 | -510 | -438.72 | 0 | 0 | Yes
2030-04-27 11:00 | 2030 100% ECP | -700 | -526 | -510 | -138.72 | 0 | 0 | Yes
2030-04-27 12:00 | 2030 100% ECP | -700 | -526 | -510 | -204 | 0 | 0 | Yes
2030-04-27 13:00 | 2030 100% ECP | -700 | -526 | -510 | -307.44 | 0 | 0 | Yes
2030-04-27 14:00 | 2030 100% ECP | -700 | -526 | -510 | -307.44 | 0 | 0 | Yes
2030-04-27 15:00 | 2030 100% ECP | -700 | -526 | -510 | -149.42 | 0 | 0 | Yes
2030-04-27 16:00 | 2030 100% ECP | -700 | -526 | -510 | -288.55 | 0 | 0 | No
2030-04-27 17:00 | 2030 100% ECP | -700 | -526 | -510 | -227.2 | 0 | 0 | No
2030-04-27 18:00 | 2030 100% ECP | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-04-27 19:00 | 2030 100% ECP | 140 | -526 | -510 | -510 | 0 | 0 | No
2030-04-27 20:00 | 2030 100% ECP | 560 | -526 | -510 | -510 | 0 | 0 | No
2030-04-27 21:00 | 2030 100% ECP | 700 | -280.48 | -510 | -305.07 | 0 | 0 | No
2030-04-27 22:00 | 2030 100% ECP | 700 | 0 | -510 | -5.07 | 0 | 0 | No
2030-04-27 23:00 | 2030 100% ECP | 700 | 0 | -510 | -36.47 | 0 | 0 | No
2030-04-28 | 2030 100% ECP | 700 | 0 | -510 | -172.65 | 0 | 0 | No
2030-04-28 01:00 | 2030 100% ECP | 700 | 0 | -510 | -113.56 | 0 | 0 | No
2030-04-28 02:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-28 03:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-04-28 04:00 | 2030 100% ECP | 700 | 0 | -510 | -271.05 | 0 | 0 | No
2030-04-28 05:00 | 2030 100% ECP | 700 | 0 | -510 | -132.2 | 0 | 0 | No
2030-04-28 06:00 | 2030 100% ECP | 524.51 | -226 | -510 | -60.94 | 0 | 0 | No
2030-04-28 07:00 | 2030 100% ECP | 104.51 | -526 | -510 | -122.58 | 0 | 0 | No
2030-04-28 08:00 | 2030 100% ECP | -315.49 | -526 | -510 | -177.14 | 0 | 0 | Yes
2030-04-28 09:00 | 2030 100% ECP | -700 | -526 | -510 | -245.69 | 0 | 0 | Yes
2030-04-28 10:00 | 2030 100% ECP | -700 | -526 | -510 | -304.6 | 0 | 0 | Yes
2030-04-28 11:00 | 2030 100% ECP | -700 | -526 | -510 | -257.14 | 0 | 0 | Yes
2030-04-28 12:00 | 2030 100% ECP | -700 | -526 | -510 | -270.98 | 0 | 0 | Yes
2030-04-28 13:00 | 2030 100% ECP | -700 | -526 | -510 | -233.72 | 0 | 0 | Yes
2030-04-28 14:00 | 2030 100% ECP | -700 | -526 | -510 | -328.79 | 0 | 0 | Yes
2030-04-28 15:00 | 2030 100% ECP | -700 | -526 | -510 | -171.78 | 0 | 0 | Yes
2030-04-28 16:00 | 2030 100% ECP | -431.34 | -526 | -510 | -156.69 | 0 | 0 | Yes
2030-04-28 17:00 | 2030 100% ECP | -11.34 | -526 | -510 | -21.07 | 0 | 0 | No
2030-04-28 18:00 | 2030 100% ECP | 408.66 | -526 | -510 | 27.17 | 0 | 0 | No
2030-04-28 19:00 | 2030 100% ECP | 700 | -526 | -510 | 57.44 | 0 | 0 | No
2030-04-28 20:00 | 2030 100% ECP | 700 | -526 | -510 | 148.84 | 0 | 0 | No
2030-04-28 21:00 | 2030 100% ECP | 700 | -526 | -510 | 131.97 | 0 | 0 | No
2030-04-28 22:00 | 2030 100% ECP | 700 | -526 | -510 | 55.38 | 0 | 0 | No
2030-04-28 23:00 | 2030 100% ECP | 700 | -526 | -510 | 77.48 | 0 | 0 | No
2030-04-29 | 2030 100% ECP | 700 | -526 | -510 | -114.71 | 0 | 0 | No
2030-04-29 01:00 | 2030 100% ECP | 700 | -526 | -510 | -158.68 | 0 | 0 | No
2030-04-29 02:00 | 2030 100% ECP | 700 | -526 | -510 | -135.25 | 0 | 0 | No
2030-04-29 03:00 | 2030 100% ECP | 700 | -526 | -510 | 41.65 | 0 | 0 | No
2030-04-29 04:00 | 2030 100% ECP | 700 | -526 | -510 | -203.68 | 0 | 0 | No
2030-04-29 05:00 | 2030 100% ECP | 700 | -526 | -510 | -120.1 | 0 | 0 | No
2030-04-29 06:00 | 2030 100% ECP | 700 | -526 | -510 | -79 | 0 | 0 | No
2030-04-29 07:00 | 2030 100% ECP | 280 | -526 | -510 | -6.83 | 0 | 0 | No
2030-04-29 08:00 | 2030 100% ECP | -140 | -526 | -510 | -185.96 | 0 | 0 | No
2030-04-29 09:00 | 2030 100% ECP | -560 | -526 | -510 | -88.89 | 0 | 0 | No
2030-04-29 10:00 | 2030 100% ECP | -700 | -526 | -510 | -388.89 | 0 | 0 | Yes
2030-04-29 11:00 | 2030 100% ECP | -700 | -526 | -510 | -90 | 0 | 0 | Yes
2030-04-29 12:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | Yes
2030-04-29 13:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-04-29 14:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-04-29 15:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-04-29 16:00 | 2030 100% ECP | -560 | 74 | 338.79 | 510 | 0 | 0 | No
2030-04-29 17:00 | 2030 100% ECP | -140 | 0 | 127.51 | 510 | 0 | 0 | No
2030-04-29 18:00 | 2030 100% ECP | 280 | 74.23 | 412.75 | 510 | 0 | 0 | No
2030-04-29 19:00 | 2030 100% ECP | 700 | 0 | 112.75 | 510 | 0 | 0 | Yes
2030-04-29 20:00 | 2030 100% ECP | 700 | -300 | -187.25 | 510 | 0 | 0 | No
2030-04-29 21:00 | 2030 100% ECP | 700 | 0 | 112.75 | 396.64 | 0 | 0 | No
2030-04-29 22:00 | 2030 100% ECP | 700 | 300 | 412.75 | 510 | 0 | 0 | No
2030-04-29 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 05:00 | 2030 100% ECP | 700 | 300 | 320.9 | 510 | 0 | 0 | No
2030-04-30 06:00 | 2030 100% ECP | 700 | 0 | 20.9 | 210 | 0 | 0 | No
2030-04-30 07:00 | 2030 100% ECP | 700 | -300 | -279.1 | 0 | 0 | 0 | No
2030-04-30 08:00 | 2030 100% ECP | 700 | 0 | 20.9 | 300 | 0 | 0 | No
2030-04-30 09:00 | 2030 100% ECP | 280 | -212.03 | -279.1 | 510 | 0 | 0 | No
2030-04-30 10:00 | 2030 100% ECP | 0 | -319.89 | -510 | 510 | 0 | 0 | No
2030-04-30 11:00 | 2030 100% ECP | 0 | -483.23 | -510 | 510 | 0 | 0 | No
2030-04-30 12:00 | 2030 100% ECP | 0 | -183.23 | -510 | 510 | 0 | 0 | No
2030-04-30 13:00 | 2030 100% ECP | 0 | 0 | -210 | 510 | 0 | 0 | No
2030-04-30 14:00 | 2030 100% ECP | 0 | -75.62 | -510 | 510 | 0 | 0 | No
2030-04-30 15:00 | 2030 100% ECP | 0 | -226 | -502 | 380.19 | 0 | 0 | No
2030-04-30 16:00 | 2030 100% ECP | 280 | -526 | -510 | 80.19 | 0 | 0 | No
2030-04-30 17:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-30 18:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-30 19:00 | 2030 100% ECP | 700 | -526 | -510 | 4.31 | 0 | 0 | No
2030-04-30 20:00 | 2030 100% ECP | 700 | -526 | -510 | 304.31 | 0 | 0 | No
2030-04-30 21:00 | 2030 100% ECP | 700 | -526 | -510 | 373.7 | 0 | 0 | No
2030-04-30 22:00 | 2030 100% ECP | 700 | -526 | -510 | 401.83 | 0 | 0 | No
2030-04-30 23:00 | 2030 100% ECP | 700 | -226 | -210 | 492.44 | 0 | 0 | No
2030-05-01 | 2030 100% ECP | 700 | 74 | 90 | 510 | 0 | 0 | No
2030-05-01 01:00 | 2030 100% ECP | 700 | 374 | 390 | 510 | 0 | 0 | No
2030-05-01 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-01 03:00 | 2030 100% ECP | 700 | 505 | 404.81 | 510 | 0 | 0 | No
2030-05-01 04:00 | 2030 100% ECP | 700 | 205 | 104.81 | 510 | 0 | 0 | No
2030-05-01 05:00 | 2030 100% ECP | 700 | -95 | -195.19 | 510 | 0 | 0 | No
2030-05-01 06:00 | 2030 100% ECP | 560 | -395 | -495.19 | 510 | 0 | 0 | No
2030-05-01 07:00 | 2030 100% ECP | 140 | -526 | -510 | 510 | 0 | 0 | No
2030-05-01 08:00 | 2030 100% ECP | -280 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 09:00 | 2030 100% ECP | -700 | -526 | -510 | 452.63 | 0 | 0 | Yes
2030-05-01 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 14:00 | 2030 100% ECP | -700 | -526 | -510 | 434.24 | 0 | 0 | Yes
2030-05-01 15:00 | 2030 100% ECP | -700 | -526 | -510 | 134.24 | 0 | 0 | Yes
2030-05-01 16:00 | 2030 100% ECP | -700 | -526 | -510 | -165.76 | 0 | 0 | Yes
2030-05-01 17:00 | 2030 100% ECP | -280 | -526 | -510 | -169.89 | 0 | 0 | Yes
2030-05-01 18:00 | 2030 100% ECP | 140 | -526 | -510 | 60.84 | 0 | 0 | No
2030-05-01 19:00 | 2030 100% ECP | 560 | -526 | -510 | 360.84 | 0 | 0 | No
2030-05-01 20:00 | 2030 100% ECP | 700 | -526 | -510 | 360.84 | 0 | 0 | No
2030-05-01 21:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-01 22:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-01 23:00 | 2030 100% ECP | 700 | -526 | -510 | 425.52 | 0 | 0 | No
2030-05-02 | 2030 100% ECP | 700 | -300 | -369.3 | 262.71 | 0 | 0 | No
2030-05-02 01:00 | 2030 100% ECP | 700 | 0 | -69.3 | 210 | 0 | 0 | No
2030-05-02 02:00 | 2030 100% ECP | 700 | 300 | 230.7 | 510 | 0 | 0 | No
2030-05-02 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-02 04:00 | 2030 100% ECP | 700 | 300 | 323.69 | 510 | 0 | 0 | No
2030-05-02 05:00 | 2030 100% ECP | 560 | 0 | 23.69 | 339.4 | 0 | 0 | No
2030-05-02 06:00 | 2030 100% ECP | 140 | -300 | -276.31 | 380.99 | 0 | 0 | No
2030-05-02 07:00 | 2030 100% ECP | -280 | -526 | -510 | 500.18 | 0 | 0 | No
2030-05-02 08:00 | 2030 100% ECP | -700 | -526 | -510 | 200.18 | 0 | 0 | Yes
2030-05-02 09:00 | 2030 100% ECP | -700 | -526 | -510 | 149.96 | 0 | 0 | Yes
2030-05-02 10:00 | 2030 100% ECP | -700 | -526 | -510 | 176.64 | 0 | 0 | Yes
2030-05-02 11:00 | 2030 100% ECP | -700 | -526 | -510 | 255.51 | 0 | 0 | Yes
2030-05-02 12:00 | 2030 100% ECP | -700 | -526 | -510 | 194.78 | 0 | 0 | Yes
2030-05-02 13:00 | 2030 100% ECP | -700 | -526 | -510 | 153.2 | 0 | 0 | Yes
2030-05-02 14:00 | 2030 100% ECP | -700 | -526 | -510 | 190.05 | 0 | 0 | Yes
2030-05-02 15:00 | 2030 100% ECP | -700 | -526 | -510 | 316.04 | 0 | 0 | Yes
2030-05-02 16:00 | 2030 100% ECP | -700 | -526 | -510 | 407.57 | 0 | 0 | No
2030-05-02 17:00 | 2030 100% ECP | -459.35 | -526 | -510 | 510 | 0 | 0 | No
2030-05-02 18:00 | 2030 100% ECP | -39.35 | -526 | -510 | 365.98 | 0 | 0 | No
2030-05-02 19:00 | 2030 100% ECP | 0 | -526 | -510 | 65.98 | 0 | 0 | No
2030-05-02 20:00 | 2030 100% ECP | 0 | -526 | -510 | 210 | 0 | 0 | No
2030-05-02 21:00 | 2030 100% ECP | 317.37 | -526 | -510 | 510 | 0 | 0 | No
2030-05-02 22:00 | 2030 100% ECP | 280 | -526 | -510 | 510 | 0 | 0 | No
2030-05-02 23:00 | 2030 100% ECP | 700 | -526 | -510 | 422.08 | 0 | 0 | No
2030-05-03 | 2030 100% ECP | 700 | -388.81 | -510 | 122.08 | 0 | 0 | No
2030-05-03 01:00 | 2030 100% ECP | 700 | -388.81 | -510 | 300.88 | 0 | 0 | No
2030-05-03 02:00 | 2030 100% ECP | 700 | -388.81 | -510 | 365.44 | 0 | 0 | No
2030-05-03 03:00 | 2030 100% ECP | 700 | -526 | -510 | 65.44 | 0 | 0 | No
2030-05-03 04:00 | 2030 100% ECP | 700 | -526 | -510 | 65.44 | 0 | 0 | No
2030-05-03 05:00 | 2030 100% ECP | 280 | -526 | -510 | 365.44 | 0 | 0 | No
2030-05-03 06:00 | 2030 100% ECP | -140 | -526 | -510 | 339.61 | 0 | 0 | No
2030-05-03 07:00 | 2030 100% ECP | -560 | -526 | -510 | 446.44 | 0 | 0 | No
2030-05-03 08:00 | 2030 100% ECP | -700 | -526 | -510 | 493.04 | 0 | 0 | No
2030-05-03 09:00 | 2030 100% ECP | -700 | -526 | -510 | 193.04 | 0 | 0 | Yes
2030-05-03 10:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-03 11:00 | 2030 100% ECP | -700 | -526 | -510 | 35.58 | 0 | 0 | Yes
2030-05-03 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-03 13:00 | 2030 100% ECP | -700 | -526 | -510 | 28.79 | 0 | 0 | Yes
2030-05-03 14:00 | 2030 100% ECP | -700 | -526 | -510 | 328.79 | 0 | 0 | Yes
2030-05-03 15:00 | 2030 100% ECP | -700 | -526 | -510 | 284.78 | 0 | 0 | Yes
2030-05-03 16:00 | 2030 100% ECP | -700 | -526 | -510 | 300 | 0 | 0 | Yes
2030-05-03 17:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-03 18:00 | 2030 100% ECP | -280 | -526 | -510 | -300 | 0 | 0 | No
2030-05-03 19:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-05-03 20:00 | 2030 100% ECP | 0 | -526 | -510 | -337.1 | 0 | 0 | No
2030-05-03 21:00 | 2030 100% ECP | 420 | -526 | -510 | -37.1 | 0 | 0 | No
2030-05-03 22:00 | 2030 100% ECP | 344.44 | -526 | -510 | -18.38 | 0 | 0 | No
2030-05-03 23:00 | 2030 100% ECP | 0 | -526 | -510 | -160.32 | 0 | 0 | No
2030-05-04 | 2030 100% ECP | 0 | -526 | -510 | -310.28 | 0 | 0 | No
2030-05-04 01:00 | 2030 100% ECP | 0 | -526 | -510 | -442.22 | 0 | 0 | No
2030-05-04 02:00 | 2030 100% ECP | 0 | -526 | -510 | -305.04 | 0 | 0 | No
2030-05-04 03:00 | 2030 100% ECP | 0 | -526 | -510 | -251.45 | 0 | 0 | No
2030-05-04 04:00 | 2030 100% ECP | -263.91 | -526 | -510 | -237.01 | 0 | 0 | No
2030-05-04 05:00 | 2030 100% ECP | -683.91 | -526 | -510 | -218.05 | 0 | 0 | No
2030-05-04 06:00 | 2030 100% ECP | -700 | -526 | -510 | 81.95 | 0 | 0 | No
2030-05-04 07:00 | 2030 100% ECP | -700 | -526 | -510 | 130.66 | 0 | 0 | No
2030-05-04 08:00 | 2030 100% ECP | -700 | -526 | -510 | 13.85 | 0 | 0 | Yes
2030-05-04 09:00 | 2030 100% ECP | -700 | -526 | -510 | -112.75 | 0 | 0 | Yes
2030-05-04 10:00 | 2030 100% ECP | -700 | -526 | -510 | -257.72 | 0 | 0 | Yes
2030-05-04 11:00 | 2030 100% ECP | -700 | -526 | -510 | -237.1 | 0 | 0 | Yes
2030-05-04 12:00 | 2030 100% ECP | -700 | -526 | -510 | -15.72 | 0 | 0 | Yes
2030-05-04 13:00 | 2030 100% ECP | -700 | -526 | -510 | -67.99 | 0 | 0 | Yes
2030-05-04 14:00 | 2030 100% ECP | -700 | -526 | -510 | -315.06 | 0 | 0 | Yes
2030-05-04 15:00 | 2030 100% ECP | -700 | -526 | -510 | -337.9 | 0 | 0 | Yes
2030-05-04 16:00 | 2030 100% ECP | -700 | -526 | -510 | -294.56 | 0 | 0 | Yes
2030-05-04 17:00 | 2030 100% ECP | -700 | -526 | -510 | -342.9 | 0 | 0 | Yes
2030-05-04 18:00 | 2030 100% ECP | -700 | -526 | -510 | -275.35 | 0 | 0 | Yes
2030-05-04 19:00 | 2030 100% ECP | -700 | -526 | -510 | -244.68 | 0 | 0 | No
2030-05-04 20:00 | 2030 100% ECP | -700 | -526 | -510 | -218.47 | 0 | 0 | No
2030-05-04 21:00 | 2030 100% ECP | -700 | -526 | -510 | -194.39 | 0 | 0 | No
2030-05-04 22:00 | 2030 100% ECP | -700 | -526 | -510 | -444.95 | 0 | 0 | No
2030-05-04 23:00 | 2030 100% ECP | -700 | -526 | -510 | -340.09 | 0 | 0 | No
2030-05-05 | 2030 100% ECP | -700 | -526 | -510 | -40.09 | 0 | 0 | No
2030-05-05 01:00 | 2030 100% ECP | -700 | -526 | -510 | 212.83 | 0 | 0 | No
2030-05-05 02:00 | 2030 100% ECP | -700 | -526 | -510 | 4.08 | 0 | 0 | No
2030-05-05 03:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-05 04:00 | 2030 100% ECP | -700 | -526 | -510 | -40.98 | 0 | 0 | Yes
2030-05-05 05:00 | 2030 100% ECP | -700 | -526 | -510 | -1.87 | 0 | 0 | Yes
2030-05-05 06:00 | 2030 100% ECP | -700 | -526 | -510 | -301.87 | 0 | 0 | Yes
2030-05-05 07:00 | 2030 100% ECP | -700 | -526 | -510 | -417.57 | 0 | 0 | Yes
2030-05-05 08:00 | 2030 100% ECP | -700 | -526 | -510 | -491.56 | 0 | 0 | Yes
2030-05-05 09:00 | 2030 100% ECP | -700 | -526 | -510 | -191.56 | 0 | 0 | Yes
2030-05-05 10:00 | 2030 100% ECP | -700 | -526 | -510 | -8.74 | 0 | 0 | Yes
2030-05-05 11:00 | 2030 100% ECP | -700 | -526 | -510 | -8.74 | 0 | 0 | Yes
2030-05-05 12:00 | 2030 100% ECP | -700 | -526 | -510 | -308.74 | 0 | 0 | Yes
2030-05-05 13:00 | 2030 100% ECP | -700 | -526 | -510 | -402.08 | 0 | 0 | Yes
2030-05-05 14:00 | 2030 100% ECP | -700 | -526 | -510 | -455.7 | 0 | 0 | Yes
2030-05-05 15:00 | 2030 100% ECP | -700 | -526 | -510 | -468.31 | 0 | 0 | Yes
2030-05-05 16:00 | 2030 100% ECP | -700 | -526 | -510 | -231.25 | 0 | 0 | Yes
2030-05-05 17:00 | 2030 100% ECP | -700 | -526 | -510 | -39.61 | 0 | 0 | Yes
2030-05-05 18:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-05 19:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-05 20:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-05 21:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-05 22:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-05 23:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-06 | 2030 100% ECP | -700 | -526 | -510 | 47.97 | 0 | 0 | No
2030-05-06 01:00 | 2030 100% ECP | -700 | -526 | -510 | -83 | 0 | 0 | No
2030-05-06 02:00 | 2030 100% ECP | -502.32 | -526 | -510 | -40.23 | 0 | 0 | No
2030-05-06 03:00 | 2030 100% ECP | -82.32 | -526 | -510 | -27.31 | 0 | 0 | No
2030-05-06 04:00 | 2030 100% ECP | 337.68 | -526 | -510 | 78.5 | 0 | 0 | No
2030-05-06 05:00 | 2030 100% ECP | 560 | -526 | -510 | 0 | 0 | 0 | No
2030-05-06 06:00 | 2030 100% ECP | 140 | -526 | -510 | 27.99 | 0 | 0 | No
2030-05-06 07:00 | 2030 100% ECP | -280 | -526 | -510 | -45.56 | 0 | 0 | Yes
2030-05-06 08:00 | 2030 100% ECP | -700 | -526 | -510 | 50.52 | 0 | 0 | Yes
2030-05-06 09:00 | 2030 100% ECP | -700 | -526 | -510 | 4.56 | 0 | 0 | Yes
2030-05-06 10:00 | 2030 100% ECP | -700 | -526 | -510 | 77.23 | 0 | 0 | Yes
2030-05-06 11:00 | 2030 100% ECP | -700 | -526 | -510 | 77.23 | 0 | 0 | Yes
2030-05-06 12:00 | 2030 100% ECP | -700 | -526 | -510 | 100.92 | 0 | 0 | Yes
2030-05-06 13:00 | 2030 100% ECP | -700 | -526 | -510 | 118.14 | 0 | 0 | Yes
2030-05-06 14:00 | 2030 100% ECP | -700 | -526 | -510 | 118.14 | 0 | 0 | Yes
2030-05-06 15:00 | 2030 100% ECP | -700 | -526 | -510 | 91.51 | 0 | 0 | Yes
2030-05-06 16:00 | 2030 100% ECP | -700 | -526 | -510 | 252.27 | 0 | 0 | Yes
2030-05-06 17:00 | 2030 100% ECP | -700 | -526 | -510 | 377.07 | 0 | 0 | Yes
2030-05-06 18:00 | 2030 100% ECP | -280 | -526 | -510 | 457.52 | 0 | 0 | No
2030-05-06 19:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-06 20:00 | 2030 100% ECP | -700 | -526 | -510 | 469.29 | 0 | 0 | No
2030-05-06 21:00 | 2030 100% ECP | -522.06 | -526 | -510 | 510 | 0 | 0 | No
2030-05-06 22:00 | 2030 100% ECP | -102.06 | -526 | -510 | 479.13 | 0 | 0 | No
2030-05-06 23:00 | 2030 100% ECP | 317.94 | -526 | -510 | 429.01 | 0 | 0 | No
2030-05-07 | 2030 100% ECP | 291.54 | -526 | -510 | 226.33 | 0 | 0 | No
2030-05-07 01:00 | 2030 100% ECP | 532.78 | -526 | -510 | 231.82 | 0 | 0 | No
2030-05-07 02:00 | 2030 100% ECP | 112.78 | -526 | -510 | 171.24 | 0 | 0 | No
2030-05-07 03:00 | 2030 100% ECP | -307.22 | -526 | -510 | 158.15 | 0 | 0 | No
2030-05-07 04:00 | 2030 100% ECP | -700 | -526 | -510 | 170.22 | 0 | 0 | No
2030-05-07 05:00 | 2030 100% ECP | -700 | -526 | -510 | 179.68 | 0 | 0 | No
2030-05-07 06:00 | 2030 100% ECP | -700 | -526 | -510 | 203.99 | 0 | 0 | No
2030-05-07 07:00 | 2030 100% ECP | -700 | -526 | -510 | 329.45 | 0 | 0 | No
2030-05-07 08:00 | 2030 100% ECP | -700 | -526 | -510 | 397.14 | 0 | 0 | Yes
2030-05-07 09:00 | 2030 100% ECP | -700 | -526 | -510 | 291.92 | 0 | 0 | Yes
2030-05-07 10:00 | 2030 100% ECP | -700 | -526 | -510 | 268.52 | 0 | 0 | Yes
2030-05-07 11:00 | 2030 100% ECP | -700 | -526 | -510 | 206.6 | 0 | 0 | Yes
2030-05-07 12:00 | 2030 100% ECP | -700 | -526 | -510 | 77.16 | 0 | 0 | Yes
2030-05-07 13:00 | 2030 100% ECP | -700 | -526 | -510 | 35.72 | 0 | 0 | Yes
2030-05-07 14:00 | 2030 100% ECP | -700 | -526 | -510 | -33.41 | 0 | 0 | Yes
2030-05-07 15:00 | 2030 100% ECP | -700 | -526 | -510 | -57.9 | 0 | 0 | Yes
2030-05-07 16:00 | 2030 100% ECP | -700 | -526 | -510 | 171.02 | 0 | 0 | Yes
2030-05-07 17:00 | 2030 100% ECP | -280 | -526 | -510 | 346.09 | 0 | 0 | No
2030-05-07 18:00 | 2030 100% ECP | -2.81 | -526 | -510 | 310.78 | 0 | 0 | No
2030-05-07 19:00 | 2030 100% ECP | 417.19 | -526 | -510 | 396.99 | 0 | 0 | No
2030-05-07 20:00 | 2030 100% ECP | 700 | -526 | -510 | 429.31 | 0 | 0 | No
2030-05-07 21:00 | 2030 100% ECP | 700 | -526 | -510 | 485.65 | 0 | 0 | No
2030-05-07 22:00 | 2030 100% ECP | 700 | -228.86 | -510 | 499.29 | 0 | 0 | No
2030-05-07 23:00 | 2030 100% ECP | 700 | -526 | -510 | 288.63 | 0 | 0 | No
2030-05-08 | 2030 100% ECP | 700 | -226 | -510 | 0 | 0 | 0 | No
2030-05-08 01:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 02:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 03:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 04:00 | 2030 100% ECP | 700 | -226 | -510 | 0 | 0 | 0 | No
2030-05-08 05:00 | 2030 100% ECP | 700 | -87.43 | -510 | 0 | 0 | 0 | No
2030-05-08 06:00 | 2030 100% ECP | 560 | -387.43 | -510 | 0 | 0 | 0 | No
2030-05-08 07:00 | 2030 100% ECP | 140 | -526 | -510 | 127.32 | 0 | 0 | No
2030-05-08 08:00 | 2030 100% ECP | -280 | -526 | -510 | 240.31 | 0 | 0 | Yes
2030-05-08 09:00 | 2030 100% ECP | -700 | -526 | -510 | 334.5 | 0 | 0 | Yes
2030-05-08 10:00 | 2030 100% ECP | -700 | -526 | -510 | 34.5 | 0 | 0 | Yes
2030-05-08 11:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-08 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-08 13:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-08 14:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-08 15:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-08 16:00 | 2030 100% ECP | -700 | -526 | -510 | 107.93 | 0 | 0 | Yes
2030-05-08 17:00 | 2030 100% ECP | -280 | -526 | -510 | -149.15 | 0 | 0 | No
2030-05-08 18:00 | 2030 100% ECP | 140 | -526 | -510 | -210 | 0 | 0 | No
2030-05-08 19:00 | 2030 100% ECP | 560 | -526 | -510 | -510 | 0 | 0 | No
2030-05-08 20:00 | 2030 100% ECP | 700 | -526 | -510 | -210 | 0 | 0 | No
2030-05-08 21:00 | 2030 100% ECP | 700 | -526 | -510 | -6.51 | 0 | 0 | No
2030-05-08 22:00 | 2030 100% ECP | 700 | -226 | -510 | 90.74 | 0 | 0 | No
2030-05-08 23:00 | 2030 100% ECP | 700 | 0 | -510 | 1.27 | 0 | 0 | No
2030-05-09 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-05-09 01:00 | 2030 100% ECP | 700 | 0 | -487.73 | 0 | 0 | 0 | No
2030-05-09 02:00 | 2030 100% ECP | 700 | 0 | -298.12 | 0 | 0 | 0 | No
2030-05-09 03:00 | 2030 100% ECP | 700 | 0 | -489.44 | 0 | 0 | 0 | No
2030-05-09 04:00 | 2030 100% ECP | 660.22 | 0 | -189.44 | 0 | 0 | 0 | No
2030-05-09 05:00 | 2030 100% ECP | 240.22 | 0 | -489.44 | 0 | 0 | 0 | No
2030-05-09 06:00 | 2030 100% ECP | -179.78 | -226 | -510 | 0 | 0 | 0 | No
2030-05-09 07:00 | 2030 100% ECP | -599.78 | -526 | 0 | -186.89 | 0 | 0 | No
2030-05-09 08:00 | 2030 100% ECP | -700 | -526 | 0 | 91.55 | 0 | 0 | Yes
2030-05-09 09:00 | 2030 100% ECP | -700 | -526 | 0 | 67.78 | 0 | 0 | Yes
2030-05-09 10:00 | 2030 100% ECP | -700 | -526 | 0 | 30.87 | 0 | 0 | Yes
2030-05-09 11:00 | 2030 100% ECP | -700 | -526 | 0 | 49.7 | 0 | 0 | Yes
2030-05-09 12:00 | 2030 100% ECP | -700 | -526 | 0 | 64.27 | 0 | 0 | Yes
2030-05-09 13:00 | 2030 100% ECP | -700 | -526 | 0 | 36.46 | 0 | 0 | Yes
2030-05-09 14:00 | 2030 100% ECP | -700 | -526 | 0 | 26.58 | 0 | 0 | Yes
2030-05-09 15:00 | 2030 100% ECP | -700 | -526 | 0 | 84.49 | 0 | 0 | Yes
2030-05-09 16:00 | 2030 100% ECP | -700 | -526 | 0 | 200.2 | 0 | 0 | Yes
2030-05-09 17:00 | 2030 100% ECP | -700 | -526 | 0 | 155.34 | 0 | 0 | No
2030-05-09 18:00 | 2030 100% ECP | -456.48 | -526 | 0 | -86.95 | 0 | 0 | No
2030-05-09 19:00 | 2030 100% ECP | -36.48 | -526 | 0 | 2.64 | 0 | 0 | No
2030-05-09 20:00 | 2030 100% ECP | 0 | -526 | 0 | 123.66 | 0 | 0 | No
2030-05-09 21:00 | 2030 100% ECP | -257.19 | -526 | 0 | 26.68 | 0 | 0 | No
2030-05-09 22:00 | 2030 100% ECP | 0 | -526 | 0 | -120.08 | 0 | 0 | No
2030-05-09 23:00 | 2030 100% ECP | 0 | -526 | 0 | -217.84 | 0 | 0 | No
2030-05-10 | 2030 100% ECP | -235.22 | -395 | 0 | -318.28 | 0 | 0 | No
2030-05-10 01:00 | 2030 100% ECP | -641.25 | -95 | 0 | -18.28 | 0 | 0 | No
2030-05-10 02:00 | 2030 100% ECP | -221.25 | 205 | 0 | 210 | 0 | 0 | No
2030-05-10 03:00 | 2030 100% ECP | -186.45 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 04:00 | 2030 100% ECP | -606.45 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 05:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 06:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 07:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 08:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 09:00 | 2030 100% ECP | -700 | 505 | 0 | 431.15 | 0 | 0 | Yes
2030-05-10 10:00 | 2030 100% ECP | -700 | 505 | 0 | 279.38 | 0 | 0 | Yes
2030-05-10 11:00 | 2030 100% ECP | -700 | 505 | 0 | 463.61 | 0 | 0 | Yes
2030-05-10 12:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 13:00 | 2030 100% ECP | -700 | 505 | 0 | 384.19 | 0 | 0 | Yes
2030-05-10 14:00 | 2030 100% ECP | -700 | 505 | 0 | 287.53 | 0 | 0 | Yes
2030-05-10 15:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 16:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 17:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 18:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 19:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 20:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 21:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 22:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 23:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 01:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 02:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 03:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-11 04:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 05:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 06:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-11 07:00 | 2030 100% ECP | -700 | 505 | 300 | 510 | 0 | 0 | Yes
2030-05-11 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 14:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-05-11 15:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-05-11 16:00 | 2030 100% ECP | -700 | -226 | -210 | 294.75 | 0 | 0 | Yes
2030-05-11 17:00 | 2030 100% ECP | -560 | -526 | -510 | -5.25 | 0 | 0 | Yes
2030-05-11 18:00 | 2030 100% ECP | -140 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-11 19:00 | 2030 100% ECP | 280 | -526 | -510 | 0 | 0 | 0 | No
2030-05-11 20:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-11 21:00 | 2030 100% ECP | 700 | -395 | -393.99 | 0 | 0 | 0 | No
2030-05-11 22:00 | 2030 100% ECP | 700 | -95 | -93.99 | 46 | 0 | 0 | No
2030-05-11 23:00 | 2030 100% ECP | 700 | 205 | 206.01 | 210 | 0 | 0 | No
2030-05-12 | 2030 100% ECP | 700 | 505 | 506.01 | 510 | 0 | 0 | No
2030-05-12 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 05:00 | 2030 100% ECP | 700 | 389.99 | 510 | 510 | 0 | 0 | No
2030-05-12 06:00 | 2030 100% ECP | 280 | 89.99 | 210 | 510 | 0 | 0 | No
2030-05-12 07:00 | 2030 100% ECP | -140 | -210.01 | -90 | 338.89 | 0 | 0 | Yes
2030-05-12 08:00 | 2030 100% ECP | -560 | -510.01 | -390 | 204.2 | 0 | 0 | Yes
2030-05-12 09:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-12 10:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-12 11:00 | 2030 100% ECP | -700 | -526 | -510 | -130.11 | 0 | 0 | Yes
2030-05-12 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-12 13:00 | 2030 100% ECP | -700 | -526 | -510 | -296.58 | 0 | 0 | Yes
2030-05-12 14:00 | 2030 100% ECP | -700 | -526 | -510 | -202.47 | 0 | 0 | Yes
2030-05-12 15:00 | 2030 100% ECP | -700 | -526 | -510 | -502.47 | 0 | 0 | Yes
2030-05-12 16:00 | 2030 100% ECP | -700 | -526 | -510 | -495.8 | 0 | 0 | No
2030-05-12 17:00 | 2030 100% ECP | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-05-12 18:00 | 2030 100% ECP | -150.52 | -526 | -510 | -316.61 | 0 | 0 | No
2030-05-12 19:00 | 2030 100% ECP | 0 | -526 | -510 | -133.88 | 0 | 0 | No
2030-05-12 20:00 | 2030 100% ECP | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-05-12 21:00 | 2030 100% ECP | 0 | -526 | -510 | -300 | 0 | 0 | No
2030-05-12 22:00 | 2030 100% ECP | 280 | -300 | -210 | -90 | 0 | 0 | No
2030-05-12 23:00 | 2030 100% ECP | 700 | 0 | 90 | 210 | 0 | 0 | No
2030-05-13 | 2030 100% ECP | 700 | 300 | 390 | 510 | 0 | 0 | No
2030-05-13 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 05:00 | 2030 100% ECP | 560 | 374 | 508.6 | 510 | 0 | 0 | No
2030-05-13 06:00 | 2030 100% ECP | 140 | 74 | 208.6 | 510 | 0 | 0 | No
2030-05-13 07:00 | 2030 100% ECP | -280 | -226 | -91.4 | 510 | 0 | 0 | Yes
2030-05-13 08:00 | 2030 100% ECP | -700 | -526 | -391.4 | 510 | 0 | 0 | Yes
2030-05-13 09:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 10:00 | 2030 100% ECP | -700 | -446.58 | -510 | 510 | 0 | 0 | Yes
2030-05-13 11:00 | 2030 100% ECP | -700 | -526 | -510 | 495.89 | 0 | 0 | Yes
2030-05-13 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 14:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 15:00 | 2030 100% ECP | -700 | -322.41 | -510 | 510 | 0 | 0 | Yes
2030-05-13 16:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 17:00 | 2030 100% ECP | -280 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 18:00 | 2030 100% ECP | 140 | -526 | -510 | 510 | 0 | 0 | No
2030-05-13 19:00 | 2030 100% ECP | 560 | -526 | -510 | 236.17 | 0 | 0 | No
2030-05-13 20:00 | 2030 100% ECP | 700 | -526 | -510 | 402.71 | 0 | 0 | No
2030-05-13 21:00 | 2030 100% ECP | 700 | -526 | -510 | 402.71 | 0 | 0 | No
2030-05-13 22:00 | 2030 100% ECP | 700 | -526 | -510 | 402.71 | 0 | 0 | No
2030-05-13 23:00 | 2030 100% ECP | 700 | -526 | -510 | 466.8 | 0 | 0 | No
2030-05-14 | 2030 100% ECP | 700 | -526 | -510 | 166.8 | 0 | 0 | No
2030-05-14 01:00 | 2030 100% ECP | 700 | -526 | -510 | 113.71 | 0 | 0 | No
2030-05-14 02:00 | 2030 100% ECP | 700 | -526 | -510 | 91.48 | 0 | 0 | No
2030-05-14 03:00 | 2030 100% ECP | 700 | -324.82 | -510 | 101.1 | 0 | 0 | No
2030-05-14 04:00 | 2030 100% ECP | 700 | -391.94 | -510 | 101.24 | 0 | 0 | No
2030-05-14 05:00 | 2030 100% ECP | 700 | -526 | -510 | 98.16 | 0 | 0 | No
2030-05-14 06:00 | 2030 100% ECP | 280 | -526 | -510 | 139.46 | 0 | 0 | No
2030-05-14 07:00 | 2030 100% ECP | -140 | -526 | -510 | 190.95 | 0 | 0 | No
2030-05-14 08:00 | 2030 100% ECP | -560 | -526 | -510 | 94.55 | 0 | 0 | Yes
2030-05-14 09:00 | 2030 100% ECP | -700 | -526 | -510 | 97.23 | 0 | 0 | Yes
2030-05-14 10:00 | 2030 100% ECP | -700 | -526 | -510 | 34.01 | 0 | 0 | Yes
2030-05-14 11:00 | 2030 100% ECP | -700 | -526 | -510 | 28.78 | 0 | 0 | Yes
2030-05-14 12:00 | 2030 100% ECP | -700 | -526 | -510 | -100 | 0 | 0 | Yes
2030-05-14 13:00 | 2030 100% ECP | -700 | -526 | -510 | -165.97 | 0 | 0 | Yes
2030-05-14 14:00 | 2030 100% ECP | -700 | -526 | -510 | 36.35 | 0 | 0 | Yes
2030-05-14 15:00 | 2030 100% ECP | -700 | -526 | -510 | -87.21 | 0 | 0 | Yes
2030-05-14 16:00 | 2030 100% ECP | -700 | -526 | -510 | -259.02 | 0 | 0 | Yes
2030-05-14 17:00 | 2030 100% ECP | -280 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-14 18:00 | 2030 100% ECP | 140 | -526 | -510 | 117.46 | 0 | 0 | No
2030-05-14 19:00 | 2030 100% ECP | 560 | -526 | -510 | 52.83 | 0 | 0 | No
2030-05-14 20:00 | 2030 100% ECP | 700 | -300 | -510 | 303.19 | 0 | 0 | No
2030-05-14 21:00 | 2030 100% ECP | 700 | 0 | -510 | 434.22 | 0 | 0 | No
2030-05-14 22:00 | 2030 100% ECP | 700 | -300 | -510 | 459.72 | 0 | 0 | No
2030-05-14 23:00 | 2030 100% ECP | 700 | -526 | -510 | 328.42 | 0 | 0 | No
2030-05-15 | 2030 100% ECP | 700 | -479.07 | -510 | 261.42 | 0 | 0 | No
2030-05-15 01:00 | 2030 100% ECP | 700 | -300 | -510 | 164.57 | 0 | 0 | No
2030-05-15 02:00 | 2030 100% ECP | 700 | 0 | -510 | 305.74 | 0 | 0 | No
2030-05-15 03:00 | 2030 100% ECP | 700 | -144.33 | -510 | 294.43 | 0 | 0 | No
2030-05-15 04:00 | 2030 100% ECP | 700 | -226 | -510 | 260.93 | 0 | 0 | No
2030-05-15 05:00 | 2030 100% ECP | 700 | -526 | -510 | 268.72 | 0 | 0 | No
2030-05-15 06:00 | 2030 100% ECP | 372.05 | -526 | -510 | 11.08 | 0 | 0 | No
2030-05-15 07:00 | 2030 100% ECP | -47.95 | -526 | -510 | 311.08 | 0 | 0 | No
2030-05-15 08:00 | 2030 100% ECP | -467.95 | -526 | -510 | 336.29 | 0 | 0 | Yes
2030-05-15 09:00 | 2030 100% ECP | -700 | -526 | -510 | 48.88 | 0 | 0 | Yes
2030-05-15 10:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-15 11:00 | 2030 100% ECP | -700 | -526 | -510 | -75.56 | 0 | 0 | Yes
2030-05-15 12:00 | 2030 100% ECP | -700 | -526 | -510 | -165.68 | 0 | 0 | Yes
2030-05-15 13:00 | 2030 100% ECP | -700 | -526 | -510 | -65.6 | 0 | 0 | Yes
2030-05-15 14:00 | 2030 100% ECP | -700 | -526 | -510 | -149.98 | 0 | 0 | Yes
2030-05-15 15:00 | 2030 100% ECP | -700 | -526 | -510 | 71.22 | 0 | 0 | Yes
2030-05-15 16:00 | 2030 100% ECP | -700 | -526 | -510 | 212.97 | 0 | 0 | Yes
2030-05-15 17:00 | 2030 100% ECP | -280 | -526 | -510 | 336.49 | 0 | 0 | No
2030-05-15 18:00 | 2030 100% ECP | 140 | -526 | -510 | 510 | 0 | 0 | No
2030-05-15 19:00 | 2030 100% ECP | 560 | -526 | -510 | 510 | 0 | 0 | No
2030-05-15 20:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-15 21:00 | 2030 100% ECP | 700 | -335.85 | -510 | 510 | 0 | 0 | No
2030-05-15 22:00 | 2030 100% ECP | 700 | -35.85 | -510 | 437.08 | 0 | 0 | No
2030-05-15 23:00 | 2030 100% ECP | 700 | -335.85 | -510 | 345.56 | 0 | 0 | No
2030-05-16 | 2030 100% ECP | 700 | -35.85 | -414.15 | 207.54 | 0 | 0 | No
2030-05-16 01:00 | 2030 100% ECP | 700 | 0 | -114.15 | 190.91 | 0 | 0 | No
2030-05-16 02:00 | 2030 100% ECP | 700 | 0 | 0 | 233.94 | 0 | 0 | No
2030-05-16 03:00 | 2030 100% ECP | 700 | 0 | 300 | 468.97 | 0 | 0 | No
2030-05-16 04:00 | 2030 100% ECP | 639.76 | 0 | 137.13 | 387.01 | 0 | 0 | No
2030-05-16 05:00 | 2030 100% ECP | 219.76 | 0 | -162.87 | 170.55 | 0 | 0 | No
2030-05-16 06:00 | 2030 100% ECP | -200.24 | -226 | -462.87 | 144.45 | 0 | 0 | No
2030-05-16 07:00 | 2030 100% ECP | -620.24 | -526 | -510 | 311.29 | 0 | 0 | No
2030-05-16 08:00 | 2030 100% ECP | -700 | -526 | -510 | 461.61 | 0 | 0 | Yes
2030-05-16 09:00 | 2030 100% ECP | -700 | -526 | -510 | 404.86 | 0 | 0 | Yes
2030-05-16 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-16 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-16 12:00 | 2030 100% ECP | -700 | -526 | -510 | 340.62 | 0 | 0 | Yes
2030-05-16 13:00 | 2030 100% ECP | -700 | -526 | -510 | 366.53 | 0 | 0 | Yes
2030-05-16 14:00 | 2030 100% ECP | -280 | -526 | -510 | 334.3 | 0 | 0 | Yes
2030-05-16 15:00 | 2030 100% ECP | 140 | -526 | -510 | 474.07 | 0 | 0 | No
2030-05-16 16:00 | 2030 100% ECP | 560 | -526 | -510 | 510 | 0 | 0 | No
2030-05-16 17:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-16 18:00 | 2030 100% ECP | 669.68 | -526 | -510 | 510 | 0 | 0 | No
2030-05-16 19:00 | 2030 100% ECP | 669.68 | -526 | -510 | 508.48 | 0 | 0 | No
2030-05-16 20:00 | 2030 100% ECP | 669.68 | -526 | -510 | 508.48 | 0 | 0 | No
2030-05-16 21:00 | 2030 100% ECP | 669.68 | -526 | -510 | 510 | 0 | 0 | No
2030-05-16 22:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-16 23:00 | 2030 100% ECP | 420 | -526 | -510 | 401.82 | 0 | 0 | No
2030-05-17 | 2030 100% ECP | 0 | -526 | -510 | 153.72 | 0 | 0 | No
2030-05-17 01:00 | 2030 100% ECP | 0 | -526 | -510 | 150.68 | 0 | 0 | No
2030-05-17 02:00 | 2030 100% ECP | 0 | -511.51 | -510 | 145.62 | 0 | 0 | No
2030-05-17 03:00 | 2030 100% ECP | 0 | -238.81 | -510 | 130.43 | 0 | 0 | No
2030-05-17 04:00 | 2030 100% ECP | -167.57 | -526 | -510 | 118.28 | 0 | 0 | No
2030-05-17 05:00 | 2030 100% ECP | -215.55 | -526 | -510 | 99.04 | 0 | 0 | No
2030-05-17 06:00 | 2030 100% ECP | -225.06 | -526 | -510 | 180.56 | 0 | 0 | No
2030-05-17 07:00 | 2030 100% ECP | -102.34 | -526 | -510 | 335.48 | 0 | 0 | No
2030-05-17 08:00 | 2030 100% ECP | 317.66 | -526 | -510 | 421.31 | 0 | 0 | No
2030-05-17 09:00 | 2030 100% ECP | -102.34 | -526 | -510 | 410.71 | 0 | 0 | No
2030-05-17 10:00 | 2030 100% ECP | -522.34 | -526 | -510 | 510 | 0 | 0 | No
2030-05-17 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-17 12:00 | 2030 100% ECP | -700 | -252.96 | -510 | 510 | 0 | 0 | No
2030-05-17 13:00 | 2030 100% ECP | -700 | 0 | -210 | 510 | 0 | 0 | No
2030-05-17 14:00 | 2030 100% ECP | -700 | 300 | 90 | 510 | 0 | 0 | No
2030-05-17 15:00 | 2030 100% ECP | -305.43 | 0 | -210 | 510 | 0 | 0 | No
2030-05-17 16:00 | 2030 100% ECP | 114.57 | -300 | -510 | 302.74 | 0 | 0 | No
2030-05-17 17:00 | 2030 100% ECP | 140 | -526 | -510 | 355.08 | 0 | 0 | No
2030-05-17 18:00 | 2030 100% ECP | -280 | -526 | -510 | 137.54 | 0 | 0 | No
2030-05-17 19:00 | 2030 100% ECP | -700 | -526 | -510 | 421.31 | 0 | 0 | No
2030-05-17 20:00 | 2030 100% ECP | -700 | -526 | -510 | 273.85 | 0 | 0 | No
2030-05-17 21:00 | 2030 100% ECP | -700 | -526 | -510 | 313.08 | 0 | 0 | No
2030-05-17 22:00 | 2030 100% ECP | -700 | -526 | -510 | 13.08 | 0 | 0 | No
2030-05-17 23:00 | 2030 100% ECP | -280 | -300 | -210.12 | 274.06 | 0 | 0 | No
2030-05-18 | 2030 100% ECP | 140 | 0 | 89.88 | 510 | 0 | 0 | No
2030-05-18 01:00 | 2030 100% ECP | 560 | 300 | 389.88 | 510 | 0 | 0 | No
2030-05-18 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 05:00 | 2030 100% ECP | 509.07 | 205 | 210 | 242.24 | 0 | 0 | No
2030-05-18 06:00 | 2030 100% ECP | 89.07 | -95 | -90 | -57.76 | 0 | 0 | No
2030-05-18 07:00 | 2030 100% ECP | 509.07 | 205 | 210 | 242.24 | 0 | 0 | No
2030-05-18 08:00 | 2030 100% ECP | 472.96 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 09:00 | 2030 100% ECP | 52.96 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 10:00 | 2030 100% ECP | 52.96 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 11:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 12:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 13:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 14:00 | 2030 100% ECP | 198.8 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 15:00 | 2030 100% ECP | 485.48 | 205 | 210 | 510 | 0 | 0 | No
2030-05-18 16:00 | 2030 100% ECP | 700 | -95 | -90 | 210 | 0 | 0 | No
2030-05-18 17:00 | 2030 100% ECP | 695.86 | -395 | -390 | 147.52 | 0 | 0 | No
2030-05-18 18:00 | 2030 100% ECP | 275.86 | -526 | -510 | 147.52 | 0 | 0 | No
2030-05-18 19:00 | 2030 100% ECP | -144.14 | -526 | -510 | 149.87 | 0 | 0 | No
2030-05-18 20:00 | 2030 100% ECP | -564.14 | -526 | -510 | 449.87 | 0 | 0 | No
2030-05-18 21:00 | 2030 100% ECP | -443.57 | -526 | -510 | 337.11 | 0 | 0 | No
2030-05-18 22:00 | 2030 100% ECP | -23.57 | -526 | -510 | 245.19 | 0 | 0 | No
2030-05-18 23:00 | 2030 100% ECP | 396.43 | -526 | -510 | 101.83 | 0 | 0 | No
2030-05-19 | 2030 100% ECP | 584.37 | -300 | -357.22 | 103.37 | 0 | 0 | No
2030-05-19 01:00 | 2030 100% ECP | 700 | 0 | -57.22 | 403.37 | 0 | 0 | No
2030-05-19 02:00 | 2030 100% ECP | 700 | 300 | 242.78 | 510 | 0 | 0 | No
2030-05-19 03:00 | 2030 100% ECP | 700 | 293.64 | 90 | 510 | 0 | 0 | No
2030-05-19 04:00 | 2030 100% ECP | 700 | -6.36 | -210 | 484.35 | 0 | 0 | No
2030-05-19 05:00 | 2030 100% ECP | 700 | -306.36 | -510 | 184.35 | 0 | 0 | No
2030-05-19 06:00 | 2030 100% ECP | 560 | -526 | -510 | -23.16 | 0 | 0 | No
2030-05-19 07:00 | 2030 100% ECP | 140 | -526 | -510 | 0.92 | 0 | 0 | No
2030-05-19 08:00 | 2030 100% ECP | -280 | -526 | -510 | -89.05 | 0 | 0 | Yes
2030-05-19 09:00 | 2030 100% ECP | -700 | -526 | -510 | -54.89 | 0 | 0 | Yes
2030-05-19 10:00 | 2030 100% ECP | -700 | -526 | -510 | -144.12 | 0 | 0 | Yes
2030-05-19 11:00 | 2030 100% ECP | -700 | -526 | -510 | -8.14 | 0 | 0 | Yes
2030-05-19 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-19 13:00 | 2030 100% ECP | -700 | -526 | -510 | 82.79 | 0 | 0 | Yes
2030-05-19 14:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-19 15:00 | 2030 100% ECP | -700 | -526 | -510 | 61.71 | 0 | 0 | Yes
2030-05-19 16:00 | 2030 100% ECP | -700 | -526 | -510 | 119.14 | 0 | 0 | Yes
2030-05-19 17:00 | 2030 100% ECP | -280 | -526 | -510 | 256.2 | 0 | 0 | No
2030-05-19 18:00 | 2030 100% ECP | 140 | -526 | -510 | 76.71 | 0 | 0 | No
2030-05-19 19:00 | 2030 100% ECP | 560 | -526 | -510 | 376.71 | 0 | 0 | No
2030-05-19 20:00 | 2030 100% ECP | 700 | -526 | -510 | 403.3 | 0 | 0 | No
2030-05-19 21:00 | 2030 100% ECP | 280 | -526 | -510 | 323.84 | 0 | 0 | No
2030-05-19 22:00 | 2030 100% ECP | 280 | -526 | -510 | 124.97 | 0 | 0 | No
2030-05-19 23:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-20 | 2030 100% ECP | 700 | -526 | -510 | 150.46 | 0 | 0 | No
2030-05-20 01:00 | 2030 100% ECP | 700 | -526 | -510 | 164.37 | 0 | 0 | No
2030-05-20 02:00 | 2030 100% ECP | 700 | -526 | -510 | 203.43 | 0 | 0 | No
2030-05-20 03:00 | 2030 100% ECP | 700 | -526 | -510 | 179.44 | 0 | 0 | No
2030-05-20 04:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-20 05:00 | 2030 100% ECP | 556.7 | -526 | -510 | 129.69 | 0 | 0 | Yes
2030-05-20 06:00 | 2030 100% ECP | 136.7 | -526 | -510 | 102.66 | 0 | 0 | No
2030-05-20 07:00 | 2030 100% ECP | -283.3 | -526 | -510 | 302.76 | 0 | 0 | Yes
2030-05-20 08:00 | 2030 100% ECP | -700 | -526 | -510 | 164.44 | 0 | 0 | Yes
2030-05-20 09:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-20 10:00 | 2030 100% ECP | -700 | -526 | -510 | 240.88 | 0 | 0 | Yes
2030-05-20 11:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-20 12:00 | 2030 100% ECP | -700 | -526 | -510 | 283.14 | 0 | 0 | Yes
2030-05-20 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-20 14:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-20 15:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-20 16:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-20 17:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-20 18:00 | 2030 100% ECP | -280 | -226 | -472.43 | 510 | 0 | 0 | No
2030-05-20 19:00 | 2030 100% ECP | -318.89 | -526 | -510 | 510 | 0 | 0 | No
2030-05-20 20:00 | 2030 100% ECP | -440.81 | -395 | -390 | 240.56 | 0 | 0 | No
2030-05-20 21:00 | 2030 100% ECP | -20.81 | -95 | -90 | 401.73 | 0 | 0 | No
2030-05-20 22:00 | 2030 100% ECP | 399.19 | 205 | 210 | 510 | 0 | 0 | No
2030-05-20 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-21 | 2030 100% ECP | 700 | 317.98 | 510 | 510 | 0 | 0 | No
2030-05-21 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-21 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-21 03:00 | 2030 100% ECP | 700 | 377.04 | 390 | 510 | 0 | 0 | No
2030-05-21 04:00 | 2030 100% ECP | 700 | 77.04 | 90 | 499.27 | 0 | 0 | No
2030-05-21 05:00 | 2030 100% ECP | 700 | -222.96 | -210 | 391.78 | 0 | 0 | No
2030-05-21 06:00 | 2030 100% ECP | 560 | -522.96 | -510 | 476.83 | 0 | 0 | No
2030-05-21 07:00 | 2030 100% ECP | 140 | -526 | -510 | 510 | 0 | 0 | No
2030-05-21 08:00 | 2030 100% ECP | -280 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-21 09:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-21 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-21 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-21 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-21 13:00 | 2030 100% ECP | -700 | -526 | -510 | 504.1 | 0 | 0 | Yes
2030-05-21 14:00 | 2030 100% ECP | -700 | -526 | -510 | 310.19 | 0 | 0 | Yes
2030-05-21 15:00 | 2030 100% ECP | -700 | -526 | -510 | 10.19 | 0 | 0 | Yes
2030-05-21 16:00 | 2030 100% ECP | -700 | -526 | -510 | 47.76 | 0 | 0 | Yes
2030-05-21 17:00 | 2030 100% ECP | -700 | -526 | -510 | 52.25 | 0 | 0 | Yes
2030-05-21 18:00 | 2030 100% ECP | -700 | -526 | -510 | -247.75 | 0 | 0 | Yes
2030-05-21 19:00 | 2030 100% ECP | -700 | -526 | -510 | 52.25 | 0 | 0 | Yes
2030-05-21 20:00 | 2030 100% ECP | -700 | -526 | -510 | 187.91 | 0 | 0 | Yes
2030-05-21 21:00 | 2030 100% ECP | -700 | -526 | -510 | -112.09 | 0 | 0 | Yes
2030-05-21 22:00 | 2030 100% ECP | -700 | -395 | -489.5 | -412.09 | 0 | 0 | Yes
2030-05-21 23:00 | 2030 100% ECP | -700 | -95 | -189.5 | -112.09 | 0 | 0 | Yes
2030-05-22 | 2030 100% ECP | -700 | 205 | 110.5 | 187.91 | 0 | 0 | Yes
2030-05-22 01:00 | 2030 100% ECP | -700 | 505 | 410.5 | 34.86 | 0 | 0 | Yes
2030-05-22 02:00 | 2030 100% ECP | -700 | 505 | 510 | 5.39 | 0 | 0 | Yes
2030-05-22 03:00 | 2030 100% ECP | -700 | 505 | 510 | 164.58 | 0 | 0 | Yes
2030-05-22 04:00 | 2030 100% ECP | -700 | 505 | 510 | 334.14 | 0 | 0 | Yes
2030-05-22 05:00 | 2030 100% ECP | -700 | 505 | 510 | 215.86 | 0 | 0 | Yes
2030-05-22 06:00 | 2030 100% ECP | -700 | 505 | 510 | 122.65 | 0 | 0 | Yes
2030-05-22 07:00 | 2030 100% ECP | -700 | 505 | 510 | 223.56 | 0 | 0 | Yes
2030-05-22 08:00 | 2030 100% ECP | -700 | 505 | 510 | 298.64 | 0 | 0 | Yes
2030-05-22 09:00 | 2030 100% ECP | -700 | 505 | 510 | 280.17 | 0 | 0 | Yes
2030-05-22 10:00 | 2030 100% ECP | -700 | 505 | 510 | 196.25 | 0 | 0 | Yes
2030-05-22 11:00 | 2030 100% ECP | -700 | 505 | 510 | 141.9 | 0 | 0 | Yes
2030-05-22 12:00 | 2030 100% ECP | -700 | 505 | 510 | 145.07 | 0 | 0 | Yes
2030-05-22 13:00 | 2030 100% ECP | -700 | 505 | 510 | 112.26 | 0 | 0 | Yes
2030-05-22 14:00 | 2030 100% ECP | -700 | 505 | 510 | 90.17 | 0 | 0 | Yes
2030-05-22 15:00 | 2030 100% ECP | -700 | 505 | 510 | 99.88 | 0 | 0 | Yes
2030-05-22 16:00 | 2030 100% ECP | -700 | 505 | 510 | 203.96 | 0 | 0 | Yes
2030-05-22 17:00 | 2030 100% ECP | -700 | 505 | 510 | 295.14 | 0 | 0 | Yes
2030-05-22 18:00 | 2030 100% ECP | -700 | 505 | 510 | 327.03 | 0 | 0 | Yes
2030-05-22 19:00 | 2030 100% ECP | -700 | 505 | 510 | 322.77 | 0 | 0 | Yes
2030-05-22 20:00 | 2030 100% ECP | -700 | 505 | 510 | 286.84 | 0 | 0 | Yes
2030-05-22 21:00 | 2030 100% ECP | -700 | 505 | 510 | 504.4 | 0 | 0 | Yes
2030-05-22 22:00 | 2030 100% ECP | -700 | 505 | 510 | 456.27 | 0 | 0 | Yes
2030-05-22 23:00 | 2030 100% ECP | -700 | 505 | 510 | 245.6 | 0 | 0 | Yes
2030-05-23 | 2030 100% ECP | -700 | 505 | 510 | 239.82 | 0 | 0 | Yes
2030-05-23 01:00 | 2030 100% ECP | -700 | 505 | 510 | 267.9 | 0 | 0 | Yes
2030-05-23 02:00 | 2030 100% ECP | -700 | 505 | 510 | 29.45 | 0 | 0 | Yes
2030-05-23 03:00 | 2030 100% ECP | -700 | 505 | 510 | -49.07 | 0 | 0 | Yes
2030-05-23 04:00 | 2030 100% ECP | -700 | 505 | 510 | 21.55 | 0 | 0 | Yes
2030-05-23 05:00 | 2030 100% ECP | -700 | 505 | 510 | -94.08 | 0 | 0 | Yes
2030-05-23 06:00 | 2030 100% ECP | -700 | 505 | 510 | -25.08 | 0 | 0 | Yes
2030-05-23 07:00 | 2030 100% ECP | -700 | 505 | 510 | 137.36 | 0 | 0 | Yes
2030-05-23 08:00 | 2030 100% ECP | -700 | 505 | 510 | 260.09 | 0 | 0 | Yes
2030-05-23 09:00 | 2030 100% ECP | -700 | 505 | 510 | 302.56 | 0 | 0 | Yes
2030-05-23 10:00 | 2030 100% ECP | -700 | 505 | 510 | 271.24 | 0 | 0 | Yes
2030-05-23 11:00 | 2030 100% ECP | -700 | 505 | 510 | 277.96 | 0 | 0 | Yes
2030-05-23 12:00 | 2030 100% ECP | -700 | 505 | 510 | 282.82 | 0 | 0 | Yes
2030-05-23 13:00 | 2030 100% ECP | -700 | 505 | 510 | 240.18 | 0 | 0 | Yes
2030-05-23 14:00 | 2030 100% ECP | -700 | 505 | 510 | 190.78 | 0 | 0 | Yes
2030-05-23 15:00 | 2030 100% ECP | -700 | 505 | 510 | 261.64 | 0 | 0 | Yes
2030-05-23 16:00 | 2030 100% ECP | -700 | 505 | 510 | 306.12 | 0 | 0 | Yes
2030-05-23 17:00 | 2030 100% ECP | -700 | 505 | 510 | 456.21 | 0 | 0 | Yes
2030-05-23 18:00 | 2030 100% ECP | -700 | 505 | 510 | 483.68 | 0 | 0 | Yes
2030-05-23 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-23 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-23 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-23 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-23 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 14:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-05-24 15:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-05-24 16:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-05-24 17:00 | 2030 100% ECP | -700 | -526 | -510 | 465.18 | 0 | 0 | Yes
2030-05-24 18:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-24 19:00 | 2030 100% ECP | -700 | -526 | -510 | 484.8 | 0 | 0 | No
2030-05-24 20:00 | 2030 100% ECP | -580.58 | -526 | -510 | 475.98 | 0 | 0 | No
2030-05-24 21:00 | 2030 100% ECP | -160.58 | -526 | -510 | 510 | 0 | 0 | No
2030-05-24 22:00 | 2030 100% ECP | 259.42 | -526 | -510 | 510 | 0 | 0 | No
2030-05-24 23:00 | 2030 100% ECP | 679.42 | -526 | -510 | 510 | 0 | 0 | No
2030-05-25 | 2030 100% ECP | 259.42 | -526 | -510 | 210 | 0 | 0 | No
2030-05-25 01:00 | 2030 100% ECP | -26.49 | -526 | -510 | 400.49 | 0 | 0 | No
2030-05-25 02:00 | 2030 100% ECP | -446.49 | -526 | 0 | 391.95 | 0 | 0 | No
2030-05-25 03:00 | 2030 100% ECP | -549.48 | -526 | 0 | 131.27 | 0 | 0 | No
2030-05-25 04:00 | 2030 100% ECP | -129.48 | -526 | 0 | 300 | 0 | 0 | No
2030-05-25 05:00 | 2030 100% ECP | -549.48 | -526 | 0 | 0 | 0 | 0 | No
2030-05-25 06:00 | 2030 100% ECP | -700 | -526 | 0 | 300 | 0 | 0 | No
2030-05-25 07:00 | 2030 100% ECP | -700 | -526 | 0 | 230.1 | 0 | 0 | Yes
2030-05-25 08:00 | 2030 100% ECP | -700 | -526 | 0 | -69.9 | 0 | 0 | Yes
2030-05-25 09:00 | 2030 100% ECP | -700 | -526 | 0 | 0 | 0 | 0 | Yes
2030-05-25 10:00 | 2030 100% ECP | -700 | -526 | 0 | -179.29 | 0 | 0 | Yes
2030-05-25 11:00 | 2030 100% ECP | -700 | -526 | 0 | -414.38 | 0 | 0 | Yes
2030-05-25 12:00 | 2030 100% ECP | -700 | -526 | 0 | -114.38 | 0 | 0 | Yes
2030-05-25 13:00 | 2030 100% ECP | -700 | -526 | 0 | 144.74 | 0 | 0 | Yes
2030-05-25 14:00 | 2030 100% ECP | -700 | -526 | 0 | 87.84 | 0 | 0 | Yes
2030-05-25 15:00 | 2030 100% ECP | -700 | -526 | 0 | 151.05 | 0 | 0 | Yes
2030-05-25 16:00 | 2030 100% ECP | -537.3 | -526 | 0 | 300 | 0 | 0 | Yes
2030-05-25 17:00 | 2030 100% ECP | -117.3 | -526 | 0 | 0 | 0 | 0 | No
2030-05-25 18:00 | 2030 100% ECP | 302.7 | -526 | 0 | 9.92 | 0 | 0 | No
2030-05-25 19:00 | 2030 100% ECP | 450.35 | -526 | 0 | 309.92 | 0 | 0 | No
2030-05-25 20:00 | 2030 100% ECP | 700 | -526 | 0 | 267.39 | 0 | 0 | No
2030-05-25 21:00 | 2030 100% ECP | 280 | -526 | 0 | -32.61 | 0 | 0 | No
2030-05-25 22:00 | 2030 100% ECP | 700 | -526 | 0 | 267.39 | 0 | 0 | No
2030-05-25 23:00 | 2030 100% ECP | 700 | -526 | 0 | 315.65 | 0 | 0 | No
2030-05-26 | 2030 100% ECP | 700 | -526 | 0 | 159.58 | 0 | 0 | No
2030-05-26 01:00 | 2030 100% ECP | 700 | -500.08 | 0 | 130.22 | 0 | 0 | No
2030-05-26 02:00 | 2030 100% ECP | 700 | -200.08 | 0 | 105.78 | 0 | 0 | No
2030-05-26 03:00 | 2030 100% ECP | 700 | -500.08 | 0 | 0 | 0 | 0 | No
2030-05-26 04:00 | 2030 100% ECP | 700 | -526 | 0 | -22.41 | 0 | 0 | No
2030-05-26 05:00 | 2030 100% ECP | 700 | -526 | 0 | 0 | 0 | 0 | Yes
2030-05-26 06:00 | 2030 100% ECP | 287.98 | -526 | 0 | -1.13 | 0 | 0 | No
2030-05-26 07:00 | 2030 100% ECP | -132.02 | -526 | 0 | 0 | 0 | 0 | No
2030-05-26 08:00 | 2030 100% ECP | -552.02 | -526 | 0 | -0.52 | 0 | 0 | Yes
2030-05-26 09:00 | 2030 100% ECP | -700 | -526 | 0 | -28.1 | 0 | 0 | Yes
2030-05-26 10:00 | 2030 100% ECP | -700 | -526 | 0 | -0.58 | 0 | 0 | Yes
2030-05-26 11:00 | 2030 100% ECP | -700 | -526 | 0 | 0 | 0 | 0 | Yes
2030-05-26 12:00 | 2030 100% ECP | -700 | -526 | 0 | 0 | 0 | 0 | Yes
2030-05-26 13:00 | 2030 100% ECP | -700 | -526 | 0 | 0 | 0 | 0 | Yes
2030-05-26 14:00 | 2030 100% ECP | -700 | -526 | 0 | 24.47 | 0 | 0 | Yes
2030-05-26 15:00 | 2030 100% ECP | -700 | -526 | 0 | 67.16 | 0 | 0 | Yes
2030-05-26 16:00 | 2030 100% ECP | -700 | -526 | 0 | 69.55 | 0 | 0 | Yes
2030-05-26 17:00 | 2030 100% ECP | -280 | -526 | 0 | 278.9 | 0 | 0 | Yes
2030-05-26 18:00 | 2030 100% ECP | 140 | -526 | 0 | 278.9 | 0 | 0 | No
2030-05-26 19:00 | 2030 100% ECP | 560 | -411.11 | 0 | 309.29 | 0 | 0 | No
2030-05-26 20:00 | 2030 100% ECP | 700 | -526 | 0 | 342.55 | 0 | 0 | No
2030-05-26 21:00 | 2030 100% ECP | 700 | -300 | 0 | 386.89 | 0 | 0 | No
2030-05-26 22:00 | 2030 100% ECP | 700 | 0 | 0 | 383.31 | 0 | 0 | No
2030-05-26 23:00 | 2030 100% ECP | 700 | -226 | 0 | 312.71 | 0 | 0 | No
2030-05-27 | 2030 100% ECP | 700 | -526 | 0 | 60.56 | 0 | 0 | No
2030-05-27 01:00 | 2030 100% ECP | 700 | -526 | 0 | 50.43 | 0 | 0 | No
2030-05-27 02:00 | 2030 100% ECP | 700 | -526 | -510 | 48.41 | 0 | 0 | No
2030-05-27 03:00 | 2030 100% ECP | 700 | -245.99 | -510 | 33.22 | 0 | 0 | No
2030-05-27 04:00 | 2030 100% ECP | 700 | -348.86 | -510 | 19.04 | 0 | 0 | No
2030-05-27 05:00 | 2030 100% ECP | 700 | -526 | -510 | -4.4 | 0 | 0 | No
2030-05-27 06:00 | 2030 100% ECP | 577.14 | -526 | -510 | 43.41 | 0 | 0 | No
2030-05-27 07:00 | 2030 100% ECP | 157.14 | -526 | -510 | 119.93 | 0 | 0 | No
2030-05-27 08:00 | 2030 100% ECP | -262.86 | -526 | -510 | 154.89 | 0 | 0 | Yes
2030-05-27 09:00 | 2030 100% ECP | -682.86 | -526 | -510 | 128.86 | 0 | 0 | Yes
2030-05-27 10:00 | 2030 100% ECP | -700 | -526 | -510 | 0.25 | 0 | 0 | Yes
2030-05-27 11:00 | 2030 100% ECP | -700 | -526 | -510 | -28.19 | 0 | 0 | Yes
2030-05-27 12:00 | 2030 100% ECP | -700 | -526 | -510 | -132.08 | 0 | 0 | Yes
2030-05-27 13:00 | 2030 100% ECP | -700 | -526 | -510 | -177.89 | 0 | 0 | Yes
2030-05-27 14:00 | 2030 100% ECP | -700 | -526 | -510 | -164.07 | 0 | 0 | Yes
2030-05-27 15:00 | 2030 100% ECP | -700 | -526 | -510 | -149.13 | 0 | 0 | Yes
2030-05-27 16:00 | 2030 100% ECP | -671.05 | -526 | -510 | 3.14 | 0 | 0 | Yes
2030-05-27 17:00 | 2030 100% ECP | -251.05 | -526 | -510 | 120.73 | 0 | 0 | No
2030-05-27 18:00 | 2030 100% ECP | 168.95 | -526 | -510 | 112.98 | 0 | 0 | No
2030-05-27 19:00 | 2030 100% ECP | 588.95 | -526 | -510 | 81.74 | 0 | 0 | No
2030-05-27 20:00 | 2030 100% ECP | 700 | -526 | -510 | 10.81 | 0 | 0 | No
2030-05-27 21:00 | 2030 100% ECP | 700 | -526 | -510 | 200.82 | 0 | 0 | No
2030-05-27 22:00 | 2030 100% ECP | 700 | -526 | -510 | 176.42 | 0 | 0 | No
2030-05-27 23:00 | 2030 100% ECP | 700 | -526 | -510 | 100.4 | 0 | 0 | No
2030-05-28 | 2030 100% ECP | 700 | -526 | -510 | 107.4 | 0 | 0 | No
2030-05-28 01:00 | 2030 100% ECP | 700 | -526 | -510 | 124.88 | 0 | 0 | No
2030-05-28 02:00 | 2030 100% ECP | 700 | -526 | -510 | 125.7 | 0 | 0 | No
2030-05-28 03:00 | 2030 100% ECP | 700 | -526 | -510 | 110.11 | 0 | 0 | No
2030-05-28 04:00 | 2030 100% ECP | 700 | -526 | -510 | 83.88 | 0 | 0 | No
2030-05-28 05:00 | 2030 100% ECP | 560 | -526 | -510 | 58.82 | 0 | 0 | No
2030-05-28 06:00 | 2030 100% ECP | 140 | -526 | -510 | 114.86 | 0 | 0 | No
2030-05-28 07:00 | 2030 100% ECP | -280 | -526 | -510 | 158.93 | 0 | 0 | Yes
2030-05-28 08:00 | 2030 100% ECP | -700 | -526 | -510 | 234.73 | 0 | 0 | Yes
2030-05-28 09:00 | 2030 100% ECP | -700 | -526 | -510 | 166.58 | 0 | 0 | Yes
2030-05-28 10:00 | 2030 100% ECP | -700 | -526 | -510 | 117.61 | 0 | 0 | Yes
2030-05-28 11:00 | 2030 100% ECP | -700 | -526 | -510 | 100.52 | 0 | 0 | Yes
2030-05-28 12:00 | 2030 100% ECP | -700 | -526 | -510 | 37.3 | 0 | 0 | Yes
2030-05-28 13:00 | 2030 100% ECP | -700 | -526 | -510 | -60.5 | 0 | 0 | Yes
2030-05-28 14:00 | 2030 100% ECP | -700 | -526 | -510 | -102.13 | 0 | 0 | Yes
2030-05-28 15:00 | 2030 100% ECP | -700 | -526 | -510 | 7.39 | 0 | 0 | Yes
2030-05-28 16:00 | 2030 100% ECP | -700 | -526 | -510 | 57.14 | 0 | 0 | Yes
2030-05-28 17:00 | 2030 100% ECP | -700 | -526 | -510 | 159.5 | 0 | 0 | Yes
2030-05-28 18:00 | 2030 100% ECP | -700 | -526 | -510 | 154.44 | 0 | 0 | Yes
2030-05-28 19:00 | 2030 100% ECP | -700 | -526 | -510 | 150.87 | 0 | 0 | No
2030-05-28 20:00 | 2030 100% ECP | -280 | -526 | -510 | 191.31 | 0 | 0 | Yes
2030-05-28 21:00 | 2030 100% ECP | 0 | -526 | -510 | 228.38 | 0 | 0 | No
2030-05-28 22:00 | 2030 100% ECP | -382.16 | -526 | -510 | 164.86 | 0 | 0 | No
2030-05-28 23:00 | 2030 100% ECP | -166.91 | -526 | -510 | 51.04 | 0 | 0 | No
2030-05-29 | 2030 100% ECP | -175.45 | -526 | -510 | -58.34 | 0 | 0 | No
2030-05-29 01:00 | 2030 100% ECP | -595.45 | -526 | -510 | 27.49 | 0 | 0 | No
2030-05-29 02:00 | 2030 100% ECP | -700 | -526 | -510 | -43.06 | 0 | 0 | No
2030-05-29 03:00 | 2030 100% ECP | -700 | -526 | -510 | -0.15 | 0 | 0 | No
2030-05-29 04:00 | 2030 100% ECP | -700 | -526 | -510 | -82.55 | 0 | 0 | No
2030-05-29 05:00 | 2030 100% ECP | -700 | -526 | -510 | -103.01 | 0 | 0 | No
2030-05-29 06:00 | 2030 100% ECP | -700 | -526 | -510 | -152.43 | 0 | 0 | Yes
2030-05-29 07:00 | 2030 100% ECP | -700 | -526 | -510 | -54.42 | 0 | 0 | Yes
2030-05-29 08:00 | 2030 100% ECP | -700 | -526 | -510 | -169.23 | 0 | 0 | Yes
2030-05-29 09:00 | 2030 100% ECP | -700 | -526 | -510 | -411.39 | 0 | 0 | Yes
2030-05-29 10:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 11:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 13:00 | 2030 100% ECP | -700 | -526 | -510 | -460.81 | 0 | 0 | Yes
2030-05-29 14:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 15:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 16:00 | 2030 100% ECP | -700 | -526 | -510 | -350.71 | 0 | 0 | Yes
2030-05-29 17:00 | 2030 100% ECP | -700 | -526 | -510 | -149.9 | 0 | 0 | Yes
2030-05-29 18:00 | 2030 100% ECP | -700 | -526 | -510 | -19.73 | 0 | 0 | Yes
2030-05-29 19:00 | 2030 100% ECP | -280 | -526 | -510 | 113.16 | 0 | 0 | No
2030-05-29 20:00 | 2030 100% ECP | 90.77 | -526 | -510 | 330.54 | 0 | 0 | No
2030-05-29 21:00 | 2030 100% ECP | 510.77 | -526 | -510 | 319.36 | 0 | 0 | No
2030-05-29 22:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-29 23:00 | 2030 100% ECP | 280 | -526 | -510 | 471.06 | 0 | 0 | No
2030-05-30 | 2030 100% ECP | 700 | -526 | -510 | 311.41 | 0 | 0 | No
2030-05-30 01:00 | 2030 100% ECP | 700 | -526 | -510 | 356.06 | 0 | 0 | No
2030-05-30 02:00 | 2030 100% ECP | 700 | -526 | -510 | 320.76 | 0 | 0 | No
2030-05-30 03:00 | 2030 100% ECP | 700 | -226 | -250.23 | 510 | 0 | 0 | No
2030-05-30 04:00 | 2030 100% ECP | 280 | -526 | -510 | 478.9 | 0 | 0 | No
2030-05-30 05:00 | 2030 100% ECP | -140 | -526 | -510 | 229.35 | 0 | 0 | No
2030-05-30 06:00 | 2030 100% ECP | -560 | -526 | -510 | 49.82 | 0 | 0 | Yes
2030-05-30 07:00 | 2030 100% ECP | -700 | -526 | -510 | 349.82 | 0 | 0 | Yes
2030-05-30 08:00 | 2030 100% ECP | -700 | -526 | -510 | 116.16 | 0 | 0 | Yes
2030-05-30 09:00 | 2030 100% ECP | -700 | -526 | -510 | 235.58 | 0 | 0 | Yes
2030-05-30 10:00 | 2030 100% ECP | -700 | -526 | -510 | 225.61 | 0 | 0 | Yes
2030-05-30 11:00 | 2030 100% ECP | -700 | -234.48 | -510 | 510 | 0 | 0 | Yes
2030-05-30 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-30 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-30 14:00 | 2030 100% ECP | -700 | -526 | -510 | 425.34 | 0 | 0 | Yes
2030-05-30 15:00 | 2030 100% ECP | -700 | -526 | -510 | 125.34 | 0 | 0 | Yes
2030-05-30 16:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-30 17:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-30 18:00 | 2030 100% ECP | -535.35 | -526 | -510 | 0 | 0 | 0 | No
2030-05-30 19:00 | 2030 100% ECP | -115.35 | -526 | -510 | 37.93 | 0 | 0 | No
2030-05-30 20:00 | 2030 100% ECP | 280 | -526 | -510 | 337.93 | 0 | 0 | Yes
2030-05-30 21:00 | 2030 100% ECP | -140 | -395 | -424.07 | 306.83 | 0 | 0 | No
2030-05-30 22:00 | 2030 100% ECP | 280 | -95 | -124.07 | 510 | 0 | 0 | No
2030-05-30 23:00 | 2030 100% ECP | 700 | 205 | 175.93 | 248.58 | 0 | 0 | No
2030-05-31 | 2030 100% ECP | 700 | 505 | 475.93 | 510 | 0 | 0 | No
2030-05-31 01:00 | 2030 100% ECP | 700 | 505 | 510 | 368.77 | 0 | 0 | No
2030-05-31 02:00 | 2030 100% ECP | 700 | 505 | 510 | 68.77 | 0 | 0 | No
2030-05-31 03:00 | 2030 100% ECP | 700 | 505 | 510 | 350.93 | 0 | 0 | No
2030-05-31 04:00 | 2030 100% ECP | 700 | 300 | 271.21 | 459.58 | 0 | 0 | No
2030-05-31 05:00 | 2030 100% ECP | 560 | 0 | -28.79 | 159.58 | 0 | 0 | No
2030-05-31 06:00 | 2030 100% ECP | 140 | -300 | -328.79 | -140.42 | 0 | 0 | No
2030-05-31 07:00 | 2030 100% ECP | -280 | -526 | -510 | -440.42 | 0 | 0 | Yes
2030-05-31 08:00 | 2030 100% ECP | -700 | -526 | -510 | -290.49 | 0 | 0 | Yes
2030-05-31 09:00 | 2030 100% ECP | -700 | -526 | -510 | -110.99 | 0 | 0 | Yes
2030-05-31 10:00 | 2030 100% ECP | -700 | -526 | -510 | -311.86 | 0 | 0 | Yes
2030-05-31 11:00 | 2030 100% ECP | -700 | -526 | -510 | -198.83 | 0 | 0 | Yes
2030-05-31 12:00 | 2030 100% ECP | -700 | -526 | -510 | 77.97 | 0 | 0 | Yes
2030-05-31 13:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-31 14:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-31 15:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-31 16:00 | 2030 100% ECP | -700 | -526 | -510 | 170.81 | 0 | 0 | Yes
2030-05-31 17:00 | 2030 100% ECP | -440.36 | -526 | -510 | 306.45 | 0 | 0 | Yes
2030-05-31 18:00 | 2030 100% ECP | -20.36 | -526 | -510 | 367.03 | 0 | 0 | No
2030-05-31 19:00 | 2030 100% ECP | 399.64 | -526 | -510 | 405.43 | 0 | 0 | No
2030-05-31 20:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-31 21:00 | 2030 100% ECP | 700 | -526 | -510 | 425.05 | 0 | 0 | No
2030-05-31 22:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-31 23:00 | 2030 100% ECP | 700 | -526 | -510 | 287.11 | 0 | 0 | No
2030-06-01 | 2030 100% ECP | 700 | -226 | -210 | 389.15 | 0 | 0 | No
2030-06-01 01:00 | 2030 100% ECP | 700 | 0 | -96.63 | 176.71 | 0 | 0 | No
2030-06-01 02:00 | 2030 100% ECP | 700 | -269.53 | -396.63 | 16.31 | 0 | 0 | No
2030-06-01 03:00 | 2030 100% ECP | 700 | -526 | -510 | -1.67 | 0 | 0 | No
2030-06-01 04:00 | 2030 100% ECP | 700 | -526 | -510 | -77.27 | 0 | 0 | No
2030-06-01 05:00 | 2030 100% ECP | 560 | -526 | -510 | -77.08 | 0 | 0 | No
2030-06-01 06:00 | 2030 100% ECP | 140 | -526 | -510 | -96.63 | 0 | 0 | No
2030-06-01 07:00 | 2030 100% ECP | -280 | -526 | -510 | -45.12 | 0 | 0 | Yes
2030-06-01 08:00 | 2030 100% ECP | -700 | -526 | -510 | -65.36 | 0 | 0 | Yes
2030-06-01 09:00 | 2030 100% ECP | -700 | -526 | -510 | -71.68 | 0 | 0 | Yes
2030-06-01 10:00 | 2030 100% ECP | -700 | -526 | -510 | -91.75 | 0 | 0 | Yes
2030-06-01 11:00 | 2030 100% ECP | -700 | -526 | -510 | -54.59 | 0 | 0 | Yes
2030-06-01 12:00 | 2030 100% ECP | -700 | -526 | -510 | -51.1 | 0 | 0 | Yes
2030-06-01 13:00 | 2030 100% ECP | -700 | -526 | -510 | -96.77 | 0 | 0 | Yes
2030-06-01 14:00 | 2030 100% ECP | -700 | -526 | -510 | -92.58 | 0 | 0 | Yes
2030-06-01 15:00 | 2030 100% ECP | -700 | -526 | -510 | -71.38 | 0 | 0 | Yes
2030-06-01 16:00 | 2030 100% ECP | -650.58 | -526 | -510 | 26.93 | 0 | 0 | Yes
2030-06-01 17:00 | 2030 100% ECP | -230.58 | -526 | -510 | 298.56 | 0 | 0 | Yes
2030-06-01 18:00 | 2030 100% ECP | 189.42 | -526 | -510 | 334.68 | 0 | 0 | No
2030-06-01 19:00 | 2030 100% ECP | 609.42 | -526 | -510 | 330.92 | 0 | 0 | No
2030-06-01 20:00 | 2030 100% ECP | 700 | -477.16 | -510 | 443.34 | 0 | 0 | Yes
2030-06-01 21:00 | 2030 100% ECP | 700 | -177.16 | -510 | 270.18 | 0 | 0 | No
2030-06-01 22:00 | 2030 100% ECP | 700 | 0 | -510 | 200.51 | 0 | 0 | No
2030-06-01 23:00 | 2030 100% ECP | 700 | 0 | -510 | 200.51 | 0 | 0 | No
2030-06-02 | 2030 100% ECP | 700 | -300 | -510 | 127.5 | 0 | 0 | No
2030-06-02 01:00 | 2030 100% ECP | 700 | -324.78 | -510 | 163.7 | 0 | 0 | No
2030-06-02 02:00 | 2030 100% ECP | 700 | -321.74 | -510 | 150.68 | 0 | 0 | No
2030-06-02 03:00 | 2030 100% ECP | 700 | -21.74 | -510 | 122.72 | 0 | 0 | No
2030-06-02 04:00 | 2030 100% ECP | 700 | -321.74 | -510 | 92.58 | 0 | 0 | No
2030-06-02 05:00 | 2030 100% ECP | 560.04 | -226 | -510 | 55.48 | 0 | 0 | No
2030-06-02 06:00 | 2030 100% ECP | 140.04 | -526 | -510 | 50.02 | 0 | 0 | No
2030-06-02 07:00 | 2030 100% ECP | -279.96 | -526 | -510 | 19.94 | 0 | 0 | Yes
2030-06-02 08:00 | 2030 100% ECP | -699.96 | -526 | -510 | -55.55 | 0 | 0 | Yes
2030-06-02 09:00 | 2030 100% ECP | -700 | -526 | -510 | -112.78 | 0 | 0 | Yes
2030-06-02 10:00 | 2030 100% ECP | -700 | -526 | -510 | -90.77 | 0 | 0 | Yes
2030-06-02 11:00 | 2030 100% ECP | -700 | -526 | -510 | -60.3 | 0 | 0 | Yes
2030-06-02 12:00 | 2030 100% ECP | -700 | -526 | -510 | -51.53 | 0 | 0 | Yes
2030-06-02 13:00 | 2030 100% ECP | -700 | -526 | -510 | -41.83 | 0 | 0 | Yes
2030-06-02 14:00 | 2030 100% ECP | -700 | -526 | -510 | -45.25 | 0 | 0 | Yes
2030-06-02 15:00 | 2030 100% ECP | -700 | -526 | -510 | -93.91 | 0 | 0 | Yes
2030-06-02 16:00 | 2030 100% ECP | -700 | -526 | -510 | -28.01 | 0 | 0 | Yes
2030-06-02 17:00 | 2030 100% ECP | -280 | -526 | -510 | -48.27 | 0 | 0 | Yes
2030-06-02 18:00 | 2030 100% ECP | 140 | -526 | -510 | -348.27 | 0 | 0 | No
2030-06-02 19:00 | 2030 100% ECP | 560 | -526 | -510 | -215.63 | 0 | 0 | No
2030-06-02 20:00 | 2030 100% ECP | 700 | -526 | -510 | -89.91 | 0 | 0 | No
2030-06-02 21:00 | 2030 100% ECP | 280 | -526 | -510 | 210.09 | 0 | 0 | No
2030-06-02 22:00 | 2030 100% ECP | 700 | -526 | -510 | 340.43 | 0 | 0 | No
2030-06-02 23:00 | 2030 100% ECP | 700 | -526 | -510 | 220.62 | 0 | 0 | No
2030-06-03 | 2030 100% ECP | 700 | -526 | -510 | 6.55 | 0 | 0 | No
2030-06-03 01:00 | 2030 100% ECP | 695.23 | -526 | -510 | -48.07 | 0 | 0 | No
2030-06-03 02:00 | 2030 100% ECP | 275.23 | -228.74 | -399.46 | 1.19 | 0 | 0 | No
2030-06-03 03:00 | 2030 100% ECP | -144.77 | 71.26 | -99.46 | 204.36 | 0 | 0 | No
2030-06-03 04:00 | 2030 100% ECP | -564.77 | 205 | 200.54 | 210 | 0 | 0 | Yes
2030-06-03 05:00 | 2030 100% ECP | -700 | 505 | 500.54 | 510 | 0 | 0 | Yes
2030-06-03 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 14:00 | 2030 100% ECP | -700 | 374 | 224.45 | 300 | 0 | 0 | Yes
2030-06-03 15:00 | 2030 100% ECP | -700 | 74 | -75.55 | 0 | 0 | 0 | Yes
2030-06-03 16:00 | 2030 100% ECP | -700 | -226 | -375.55 | -300 | 0 | 0 | Yes
2030-06-03 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-03 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-03 19:00 | 2030 100% ECP | -700 | -226 | -255.17 | -210 | 0 | 0 | No
2030-06-03 20:00 | 2030 100% ECP | -280 | 0 | 14.98 | 0 | 0 | 0 | No
2030-06-03 21:00 | 2030 100% ECP | 0 | 0 | 314.98 | 0 | 0 | 0 | No
2030-06-03 22:00 | 2030 100% ECP | 0 | 0 | 510 | 0 | 0 | 0 | No
2030-06-03 23:00 | 2030 100% ECP | 0 | 0 | 510 | 0 | 0 | 0 | No
2030-06-04 | 2030 100% ECP | 0 | 0 | 510 | 300 | 0 | 0 | No
2030-06-04 01:00 | 2030 100% ECP | 0 | 0 | 510 | 510 | 0 | 0 | No
2030-06-04 02:00 | 2030 100% ECP | 0 | 0 | 510 | 510 | 0 | 0 | No
2030-06-04 03:00 | 2030 100% ECP | 0 | 74 | 510 | 510 | 0 | 0 | No
2030-06-04 04:00 | 2030 100% ECP | 0 | 374 | 311.59 | 510 | 0 | 0 | No
2030-06-04 05:00 | 2030 100% ECP | 0 | 74 | 11.59 | 510 | 0 | 0 | No
2030-06-04 06:00 | 2030 100% ECP | 0 | -226 | -288.41 | 267.7 | 0 | 0 | No
2030-06-04 07:00 | 2030 100% ECP | -280 | -526 | -510 | 8.79 | 0 | 0 | No
2030-06-04 08:00 | 2030 100% ECP | -700 | -526 | -510 | 308.79 | 0 | 0 | No
2030-06-04 09:00 | 2030 100% ECP | -700 | -526 | -510 | 8.79 | 0 | 0 | No
2030-06-04 10:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-04 11:00 | 2030 100% ECP | -700 | -526 | -510 | 140.44 | 0 | 0 | Yes
2030-06-04 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-04 13:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-06-04 14:00 | 2030 100% ECP | -700 | -526 | -510 | -208.05 | 0 | 0 | Yes
2030-06-04 15:00 | 2030 100% ECP | -700 | -526 | -510 | -334.61 | 0 | 0 | Yes
2030-06-04 16:00 | 2030 100% ECP | -700 | -526 | -510 | -146.25 | 0 | 0 | No
2030-06-04 17:00 | 2030 100% ECP | -700 | -526 | -510 | -129.95 | 0 | 0 | Yes
2030-06-04 18:00 | 2030 100% ECP | -700 | -526 | -510 | -101.35 | 0 | 0 | No
2030-06-04 19:00 | 2030 100% ECP | -445.28 | -526 | -510 | -401.35 | 0 | 0 | No
2030-06-04 20:00 | 2030 100% ECP | -617.75 | -526 | -510 | -153.08 | 0 | 0 | No
2030-06-04 21:00 | 2030 100% ECP | -700 | -526 | -510 | -222.82 | 0 | 0 | No
2030-06-04 22:00 | 2030 100% ECP | -280 | -526 | -510 | -176.46 | 0 | 0 | No
2030-06-04 23:00 | 2030 100% ECP | 0 | -526 | -510 | -32.38 | 0 | 0 | No
2030-06-05 | 2030 100% ECP | -351.4 | -395 | -390 | 11.96 | 0 | 0 | No
2030-06-05 01:00 | 2030 100% ECP | -700 | -95 | -90 | 311.96 | 0 | 0 | No
2030-06-05 02:00 | 2030 100% ECP | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-06-05 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-05 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-05 05:00 | 2030 100% ECP | -700 | 300 | 501.56 | 300 | 0 | 0 | No
2030-06-05 06:00 | 2030 100% ECP | -700 | 0 | 201.56 | 0 | 0 | 0 | No
2030-06-05 07:00 | 2030 100% ECP | -700 | -114.86 | -98.44 | -300 | 0 | 0 | Yes
2030-06-05 08:00 | 2030 100% ECP | -700 | 185.14 | 201.56 | 0 | 0 | 0 | Yes
2030-06-05 09:00 | 2030 100% ECP | -700 | 485.14 | 501.56 | 228.27 | 0 | 0 | Yes
2030-06-05 10:00 | 2030 100% ECP | -700 | 505 | 510 | 136.96 | 0 | 0 | Yes
2030-06-05 11:00 | 2030 100% ECP | -700 | 505 | 510 | 46.61 | 0 | 0 | Yes
2030-06-05 12:00 | 2030 100% ECP | -700 | 505 | 510 | 178.94 | 0 | 0 | Yes
2030-06-05 13:00 | 2030 100% ECP | -700 | 505 | 510 | 81.31 | 0 | 0 | Yes
2030-06-05 14:00 | 2030 100% ECP | -700 | 505 | 510 | 40.71 | 0 | 0 | Yes
2030-06-05 15:00 | 2030 100% ECP | -700 | 505 | 510 | 38.05 | 0 | 0 | Yes
2030-06-05 16:00 | 2030 100% ECP | -700 | 505 | 510 | 152.93 | 0 | 0 | Yes
2030-06-05 17:00 | 2030 100% ECP | -700 | 505 | 510 | 297.69 | 0 | 0 | Yes
2030-06-05 18:00 | 2030 100% ECP | -700 | 505 | 510 | 228.56 | 0 | 0 | Yes
2030-06-05 19:00 | 2030 100% ECP | -700 | 505 | 510 | 199.61 | 0 | 0 | Yes
2030-06-05 20:00 | 2030 100% ECP | -700 | 505 | 510 | 208.69 | 0 | 0 | Yes
2030-06-05 21:00 | 2030 100% ECP | -700 | 505 | 510 | 196.5 | 0 | 0 | Yes
2030-06-05 22:00 | 2030 100% ECP | -700 | 505 | 510 | 59.1 | 0 | 0 | Yes
2030-06-05 23:00 | 2030 100% ECP | -700 | 505 | 510 | -14.56 | 0 | 0 | Yes
2030-06-06 | 2030 100% ECP | -700 | 505 | 510 | 285.44 | 0 | 0 | Yes
2030-06-06 01:00 | 2030 100% ECP | -700 | 505 | 510 | 39.29 | 0 | 0 | Yes
2030-06-06 02:00 | 2030 100% ECP | -700 | 505 | 510 | 339.29 | 0 | 0 | Yes
2030-06-06 03:00 | 2030 100% ECP | -700 | 505 | 510 | 84.8 | 0 | 0 | Yes
2030-06-06 04:00 | 2030 100% ECP | -700 | 505 | 510 | 45.7 | 0 | 0 | Yes
2030-06-06 05:00 | 2030 100% ECP | -700 | 505 | 510 | -36.77 | 0 | 0 | Yes
2030-06-06 06:00 | 2030 100% ECP | -700 | 505 | 510 | 34.37 | 0 | 0 | Yes
2030-06-06 07:00 | 2030 100% ECP | -700 | 505 | 510 | 143.78 | 0 | 0 | Yes
2030-06-06 08:00 | 2030 100% ECP | -700 | 505 | 510 | 206.68 | 0 | 0 | Yes
2030-06-06 09:00 | 2030 100% ECP | -700 | 505 | 510 | 388.07 | 0 | 0 | Yes
2030-06-06 10:00 | 2030 100% ECP | -700 | 505 | 510 | 395.25 | 0 | 0 | Yes
2030-06-06 11:00 | 2030 100% ECP | -700 | 505 | 510 | 470.41 | 0 | 0 | Yes
2030-06-06 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-06 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-06 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-06 15:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-06-06 16:00 | 2030 100% ECP | -700 | 74 | 90 | 379.19 | 0 | 0 | Yes
2030-06-06 17:00 | 2030 100% ECP | -700 | -226 | -210 | 79.19 | 0 | 0 | Yes
2030-06-06 18:00 | 2030 100% ECP | -700 | -526 | -510 | -220.81 | 0 | 0 | No
2030-06-06 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-06 20:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-06 21:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-06 22:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-06 23:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-06-07 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-06-07 01:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-06-07 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-07 03:00 | 2030 100% ECP | -700 | 505 | 458.47 | 390 | 0 | 0 | Yes
2030-06-07 04:00 | 2030 100% ECP | -700 | 205 | 158.47 | 90 | 0 | 0 | Yes
2030-06-07 05:00 | 2030 100% ECP | -700 | -95 | -141.53 | -210 | 0 | 0 | No
2030-06-07 06:00 | 2030 100% ECP | -700 | -395 | -441.53 | -510 | 0 | 0 | No
2030-06-07 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-07 09:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-07 10:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-07 11:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-07 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-07 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-07 14:00 | 2030 100% ECP | -700 | -322.78 | -510 | -510 | 0 | 0 | Yes
2030-06-07 15:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-07 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-07 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-07 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 19:00 | 2030 100% ECP | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 20:00 | 2030 100% ECP | 140 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 21:00 | 2030 100% ECP | 560 | -526 | -510 | -467.21 | 0 | 0 | No
2030-06-07 22:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 23:00 | 2030 100% ECP | 473.53 | -300 | -510 | -244.96 | 0 | 0 | No
2030-06-08 | 2030 100% ECP | 503.81 | -151.23 | -510 | 0 | 0 | 0 | No
2030-06-08 01:00 | 2030 100% ECP | 83.81 | -71.27 | -510 | -46.4 | 0 | 0 | No
2030-06-08 02:00 | 2030 100% ECP | 503.81 | -71.27 | -510 | -3.74 | 0 | 0 | No
2030-06-08 03:00 | 2030 100% ECP | 656.97 | 0 | -241.94 | 0 | 0 | 0 | No
2030-06-08 04:00 | 2030 100% ECP | 236.97 | -300 | -510 | -146.02 | 0 | 0 | No
2030-06-08 05:00 | 2030 100% ECP | -152.5 | -526 | -510 | -159.39 | 0 | 0 | No
2030-06-08 06:00 | 2030 100% ECP | -572.5 | -526 | -510 | 52.76 | 0 | 0 | No
2030-06-08 07:00 | 2030 100% ECP | -700 | -526 | -510 | 110.64 | 0 | 0 | Yes
2030-06-08 08:00 | 2030 100% ECP | -700 | -526 | -510 | 87.89 | 0 | 0 | Yes
2030-06-08 09:00 | 2030 100% ECP | -700 | -526 | -510 | 92.6 | 0 | 0 | Yes
2030-06-08 10:00 | 2030 100% ECP | -700 | -526 | -510 | -40.85 | 0 | 0 | Yes
2030-06-08 11:00 | 2030 100% ECP | -700 | -526 | -510 | -23.38 | 0 | 0 | Yes
2030-06-08 12:00 | 2030 100% ECP | -700 | -526 | -510 | -43.16 | 0 | 0 | Yes
2030-06-08 13:00 | 2030 100% ECP | -700 | -526 | -510 | -46.26 | 0 | 0 | Yes
2030-06-08 14:00 | 2030 100% ECP | -700 | -526 | -510 | -103.51 | 0 | 0 | Yes
2030-06-08 15:00 | 2030 100% ECP | -700 | -526 | -510 | -118.26 | 0 | 0 | Yes
2030-06-08 16:00 | 2030 100% ECP | -700 | -526 | -510 | -46.38 | 0 | 0 | Yes
2030-06-08 17:00 | 2030 100% ECP | -280 | -526 | -510 | 58.48 | 0 | 0 | Yes
2030-06-08 18:00 | 2030 100% ECP | 140 | -526 | -510 | -241.52 | 0 | 0 | No
2030-06-08 19:00 | 2030 100% ECP | 560 | -526 | -510 | -510 | 0 | 0 | No
2030-06-08 20:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-08 21:00 | 2030 100% ECP | 700 | -526 | -510 | -214.17 | 0 | 0 | No
2030-06-08 22:00 | 2030 100% ECP | 700 | -526 | -510 | 85.83 | 0 | 0 | No
2030-06-08 23:00 | 2030 100% ECP | 700 | -526 | -510 | 0.4 | 0 | 0 | No
2030-06-09 | 2030 100% ECP | 700 | -526 | -510 | -12.64 | 0 | 0 | No
2030-06-09 01:00 | 2030 100% ECP | 700 | -447.65 | -510 | 18.6 | 0 | 0 | No
2030-06-09 02:00 | 2030 100% ECP | 700 | -526 | -510 | 41.35 | 0 | 0 | No
2030-06-09 03:00 | 2030 100% ECP | 700 | -481.87 | -510 | 18.97 | 0 | 0 | No
2030-06-09 04:00 | 2030 100% ECP | 700 | -526 | -510 | -9.09 | 0 | 0 | No
2030-06-09 05:00 | 2030 100% ECP | 700 | -526 | -510 | -45.14 | 0 | 0 | No
2030-06-09 06:00 | 2030 100% ECP | 700 | -526 | -510 | -21.46 | 0 | 0 | No
2030-06-09 07:00 | 2030 100% ECP | 700 | -526 | -510 | -6.47 | 0 | 0 | No
2030-06-09 08:00 | 2030 100% ECP | 560 | -526 | -510 | -38.91 | 0 | 0 | No
2030-06-09 09:00 | 2030 100% ECP | 140 | -526 | -510 | -23.41 | 0 | 0 | No
2030-06-09 10:00 | 2030 100% ECP | -280 | -526 | -510 | -12.66 | 0 | 0 | No
2030-06-09 11:00 | 2030 100% ECP | -700 | -526 | -510 | 28.3 | 0 | 0 | No
2030-06-09 12:00 | 2030 100% ECP | -700 | -526 | -510 | 55.97 | 0 | 0 | No
2030-06-09 13:00 | 2030 100% ECP | -700 | -526 | -510 | 62.41 | 0 | 0 | No
2030-06-09 14:00 | 2030 100% ECP | -389.52 | -526 | -510 | 35.67 | 0 | 0 | No
2030-06-09 15:00 | 2030 100% ECP | 30.48 | -526 | -510 | 93.64 | 0 | 0 | No
2030-06-09 16:00 | 2030 100% ECP | 450.48 | -526 | -510 | 157.15 | 0 | 0 | No
2030-06-09 17:00 | 2030 100% ECP | 700 | -526 | -510 | 184.41 | 0 | 0 | No
2030-06-09 18:00 | 2030 100% ECP | 700 | -526 | -510 | 117.19 | 0 | 0 | No
2030-06-09 19:00 | 2030 100% ECP | 700 | -526 | -510 | 64.06 | 0 | 0 | No
2030-06-09 20:00 | 2030 100% ECP | 337.58 | -526 | -510 | 8.58 | 0 | 0 | No
2030-06-09 21:00 | 2030 100% ECP | 700 | -526 | -510 | 58.78 | 0 | 0 | No
2030-06-09 22:00 | 2030 100% ECP | 700 | -526 | -510 | 15.05 | 0 | 0 | No
2030-06-09 23:00 | 2030 100% ECP | 280 | -526 | -510 | -36.17 | 0 | 0 | No
2030-06-10 | 2030 100% ECP | 0 | -526 | -510 | 20.13 | 0 | 0 | No
2030-06-10 01:00 | 2030 100% ECP | -125.19 | -526 | -510 | 16.61 | 0 | 0 | No
2030-06-10 02:00 | 2030 100% ECP | 0 | -526 | -510 | -146.91 | 0 | 0 | No
2030-06-10 03:00 | 2030 100% ECP | 280 | -526 | -510 | -203.77 | 0 | 0 | No
2030-06-10 04:00 | 2030 100% ECP | 700 | -526 | -510 | -226.34 | 0 | 0 | No
2030-06-10 05:00 | 2030 100% ECP | 700 | -526 | -510 | -20.03 | 0 | 0 | No
2030-06-10 06:00 | 2030 100% ECP | 560 | -526 | -510 | 69.91 | 0 | 0 | No
2030-06-10 07:00 | 2030 100% ECP | 140 | -526 | -510 | 187.51 | 0 | 0 | No
2030-06-10 08:00 | 2030 100% ECP | -280 | -526 | -510 | 258.07 | 0 | 0 | No
2030-06-10 09:00 | 2030 100% ECP | -700 | -526 | -510 | 163.16 | 0 | 0 | Yes
2030-06-10 10:00 | 2030 100% ECP | -700 | -526 | -510 | 231.21 | 0 | 0 | Yes
2030-06-10 11:00 | 2030 100% ECP | -700 | -526 | -510 | 238.05 | 0 | 0 | Yes
2030-06-10 12:00 | 2030 100% ECP | -700 | -526 | -510 | 133.53 | 0 | 0 | Yes
2030-06-10 13:00 | 2030 100% ECP | -700 | -526 | -510 | 150.34 | 0 | 0 | Yes
2030-06-10 14:00 | 2030 100% ECP | -700 | -526 | -510 | 195.04 | 0 | 0 | Yes
2030-06-10 15:00 | 2030 100% ECP | -700 | -526 | -510 | 216.51 | 0 | 0 | Yes
2030-06-10 16:00 | 2030 100% ECP | -700 | -526 | -510 | 290.75 | 0 | 0 | Yes
2030-06-10 17:00 | 2030 100% ECP | -280 | -526 | -510 | 241.38 | 0 | 0 | No
2030-06-10 18:00 | 2030 100% ECP | 0 | -526 | -510 | 81.68 | 0 | 0 | No
2030-06-10 19:00 | 2030 100% ECP | -420 | -526 | -510 | -26.18 | 0 | 0 | No
2030-06-10 20:00 | 2030 100% ECP | -700 | -526 | -510 | -55.51 | 0 | 0 | No
2030-06-10 21:00 | 2030 100% ECP | -633.01 | -300 | -300 | -170.79 | 0 | 0 | No
2030-06-10 22:00 | 2030 100% ECP | -213.01 | 0 | 0 | -470.79 | 0 | 0 | No
2030-06-10 23:00 | 2030 100% ECP | -470.16 | 300 | 300 | -170.79 | 0 | 0 | Yes
2030-06-11 | 2030 100% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-11 01:00 | 2030 100% ECP | -700 | 505 | 510 | 150.36 | 0 | 0 | Yes
2030-06-11 02:00 | 2030 100% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-11 03:00 | 2030 100% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-11 04:00 | 2030 100% ECP | -700 | 505 | 510 | -41.94 | 0 | 0 | Yes
2030-06-11 05:00 | 2030 100% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-11 06:00 | 2030 100% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-11 07:00 | 2030 100% ECP | -700 | 505 | 510 | 102.55 | 0 | 0 | Yes
2030-06-11 08:00 | 2030 100% ECP | -700 | 505 | 510 | 95.31 | 0 | 0 | Yes
2030-06-11 09:00 | 2030 100% ECP | -700 | 505 | 510 | 52.82 | 0 | 0 | Yes
2030-06-11 10:00 | 2030 100% ECP | -700 | 505 | 510 | 15.37 | 0 | 0 | Yes
2030-06-11 11:00 | 2030 100% ECP | -700 | 505 | 510 | 51.54 | 0 | 0 | Yes
2030-06-11 12:00 | 2030 100% ECP | -700 | 505 | 510 | 331 | 0 | 0 | Yes
2030-06-11 13:00 | 2030 100% ECP | -700 | 505 | 510 | 280.24 | 0 | 0 | Yes
2030-06-11 14:00 | 2030 100% ECP | -700 | 505 | 510 | 394.76 | 0 | 0 | Yes
2030-06-11 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 17:00 | 2030 100% ECP | -700 | 300 | 351.26 | 510 | 0 | 0 | Yes
2030-06-11 18:00 | 2030 100% ECP | -700 | 0 | 51.26 | 422.1 | 0 | 0 | Yes
2030-06-11 19:00 | 2030 100% ECP | -700 | 300 | 351.26 | 510 | 0 | 0 | Yes
2030-06-11 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 21:00 | 2030 100% ECP | -700 | 505 | 510 | 414.52 | 0 | 0 | Yes
2030-06-11 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 23:00 | 2030 100% ECP | -700 | 505 | 510 | 436.96 | 0 | 0 | Yes
2030-06-12 | 2030 100% ECP | -571.29 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-12 01:00 | 2030 100% ECP | -696.24 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-12 02:00 | 2030 100% ECP | -700 | 505 | 510 | 409.77 | 0 | 0 | Yes
2030-06-12 03:00 | 2030 100% ECP | -700 | 505 | 510 | 216.13 | 0 | 0 | Yes
2030-06-12 04:00 | 2030 100% ECP | -700 | 505 | 510 | 33.14 | 0 | 0 | Yes
2030-06-12 05:00 | 2030 100% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-12 06:00 | 2030 100% ECP | -700 | 505 | 510 | 257 | 0 | 0 | Yes
2030-06-12 07:00 | 2030 100% ECP | -700 | 505 | 510 | 372.23 | 0 | 0 | Yes
2030-06-12 08:00 | 2030 100% ECP | -700 | 205 | 510 | 166 | 0 | 0 | Yes
2030-06-12 09:00 | 2030 100% ECP | -700 | 505 | 510 | 466 | 0 | 0 | Yes
2030-06-12 10:00 | 2030 100% ECP | -700 | 505 | 510 | 413.45 | 0 | 0 | Yes
2030-06-12 11:00 | 2030 100% ECP | -700 | 505 | 510 | 267.97 | 0 | 0 | Yes
2030-06-12 12:00 | 2030 100% ECP | -700 | 505 | 510 | 200.59 | 0 | 0 | Yes
2030-06-12 13:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-06-12 14:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-06-12 15:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-06-12 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-12 17:00 | 2030 100% ECP | -327.65 | -278.85 | -510 | -457.46 | 0 | 0 | Yes
2030-06-12 18:00 | 2030 100% ECP | 92.35 | -526 | -510 | -510 | 0 | 0 | No
2030-06-12 19:00 | 2030 100% ECP | 512.35 | -526 | -510 | -510 | 0 | 0 | No
2030-06-12 20:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-12 21:00 | 2030 100% ECP | 280 | -526 | -510 | -510 | 0 | 0 | No
2030-06-12 22:00 | 2030 100% ECP | 700 | -300 | -397.73 | -459.95 | 0 | 0 | No
2030-06-12 23:00 | 2030 100% ECP | 700 | 0 | -97.73 | -159.95 | 0 | 0 | No
2030-06-13 | 2030 100% ECP | 700 | 300 | 202.27 | 140.05 | 0 | 0 | No
2030-06-13 01:00 | 2030 100% ECP | 700 | 0 | -13.17 | 401.57 | 0 | 0 | No
2030-06-13 02:00 | 2030 100% ECP | 700 | -300 | -313.17 | 101.57 | 0 | 0 | No
2030-06-13 03:00 | 2030 100% ECP | 700 | -226 | -422.87 | 310.42 | 0 | 0 | No
2030-06-13 04:00 | 2030 100% ECP | 700 | -526 | -510 | 62.26 | 0 | 0 | No
2030-06-13 05:00 | 2030 100% ECP | 700 | -526 | -510 | -82.89 | 0 | 0 | No
2030-06-13 06:00 | 2030 100% ECP | 700 | -526 | -510 | -62.73 | 0 | 0 | No
2030-06-13 07:00 | 2030 100% ECP | 318.03 | -526 | -510 | -222.49 | 0 | 0 | No
2030-06-13 08:00 | 2030 100% ECP | -101.97 | -526 | -510 | -40.27 | 0 | 0 | No
2030-06-13 09:00 | 2030 100% ECP | -521.97 | -526 | -510 | 56.45 | 0 | 0 | Yes
2030-06-13 10:00 | 2030 100% ECP | -700 | -526 | -510 | 342.87 | 0 | 0 | Yes
2030-06-13 11:00 | 2030 100% ECP | -700 | -526 | -510 | 81.13 | 0 | 0 | Yes
2030-06-13 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-06-13 13:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-06-13 14:00 | 2030 100% ECP | -700 | -526 | -510 | -159.98 | 0 | 0 | Yes
2030-06-13 15:00 | 2030 100% ECP | -700 | -526 | -510 | -34.2 | 0 | 0 | Yes
2030-06-13 16:00 | 2030 100% ECP | -700 | -526 | -510 | -99.99 | 0 | 0 | Yes
2030-06-13 17:00 | 2030 100% ECP | -280 | -526 | -510 | 128.44 | 0 | 0 | No
2030-06-13 18:00 | 2030 100% ECP | -700 | -526 | -510 | 128.44 | 0 | 0 | No
2030-06-13 19:00 | 2030 100% ECP | -630.59 | -526 | -510 | 0 | 0 | 0 | No
2030-06-13 20:00 | 2030 100% ECP | -210.59 | -526 | -510 | -300 | 0 | 0 | Yes
2030-06-13 21:00 | 2030 100% ECP | -140 | -526 | -510 | 0 | 0 | 0 | No
2030-06-13 22:00 | 2030 100% ECP | 280 | -526 | -510 | 115.7 | 0 | 0 | No
2030-06-13 23:00 | 2030 100% ECP | 700 | -526 | -510 | -91.15 | 0 | 0 | No
2030-06-14 | 2030 100% ECP | 700 | -226 | -510 | -13.75 | 0 | 0 | No
2030-06-14 01:00 | 2030 100% ECP | 700 | -526 | -510 | -313.75 | 0 | 0 | No
2030-06-14 02:00 | 2030 100% ECP | 700 | -370.03 | -510 | -141.93 | 0 | 0 | No
2030-06-14 03:00 | 2030 100% ECP | 700 | -221.72 | -510 | -38.61 | 0 | 0 | No
2030-06-14 04:00 | 2030 100% ECP | 700 | -521.72 | -510 | -210 | 0 | 0 | No
2030-06-14 05:00 | 2030 100% ECP | 700 | -521.72 | -510 | -510 | 0 | 0 | No
2030-06-14 06:00 | 2030 100% ECP | 560 | -526 | -510 | -493.69 | 0 | 0 | No
2030-06-14 07:00 | 2030 100% ECP | 140 | -526 | -510 | -193.69 | 0 | 0 | No
2030-06-14 08:00 | 2030 100% ECP | -280 | -526 | -510 | 0 | 0 | 0 | Yes
2030-06-14 09:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-06-14 10:00 | 2030 100% ECP | -700 | -526 | -510 | -294.17 | 0 | 0 | Yes
2030-06-14 11:00 | 2030 100% ECP | -700 | -526 | -510 | -354.39 | 0 | 0 | Yes
2030-06-14 12:00 | 2030 100% ECP | -700 | -526 | -510 | -372.07 | 0 | 0 | Yes
2030-06-14 13:00 | 2030 100% ECP | -700 | -526 | -510 | -72.7 | 0 | 0 | Yes
2030-06-14 14:00 | 2030 100% ECP | -700 | -526 | -510 | -372.7 | 0 | 0 | Yes
2030-06-14 15:00 | 2030 100% ECP | -700 | -526 | -510 | -372.7 | 0 | 0 | Yes
2030-06-14 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-14 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-14 18:00 | 2030 100% ECP | -283.98 | -526 | -510 | -510 | 0 | 0 | No
2030-06-14 19:00 | 2030 100% ECP | 136.02 | -526 | -510 | -510 | 0 | 0 | No
2030-06-14 20:00 | 2030 100% ECP | 556.02 | -526 | -510 | -510 | 0 | 0 | No
2030-06-14 21:00 | 2030 100% ECP | 700 | -526 | -510 | -491.56 | 0 | 0 | No
2030-06-14 22:00 | 2030 100% ECP | 700 | -226 | -510 | -191.56 | 0 | 0 | No
2030-06-14 23:00 | 2030 100% ECP | 700 | 0 | -510 | -236.3 | 0 | 0 | No
2030-06-15 | 2030 100% ECP | 700 | -104.15 | -510 | 0 | 0 | 0 | No
2030-06-15 01:00 | 2030 100% ECP | 700 | 0 | -510 | -246.03 | 0 | 0 | No
2030-06-15 02:00 | 2030 100% ECP | 700 | 0 | -510 | -317.66 | 0 | 0 | No
2030-06-15 03:00 | 2030 100% ECP | 700 | -34.9 | -510 | -102.83 | 0 | 0 | No
2030-06-15 04:00 | 2030 100% ECP | 700 | 0 | -510 | -291.43 | 0 | 0 | No
2030-06-15 05:00 | 2030 100% ECP | 280 | 0 | -510 | 0 | 0 | 0 | No
2030-06-15 06:00 | 2030 100% ECP | -140 | -300 | -510 | -210 | 0 | 0 | No
2030-06-15 07:00 | 2030 100% ECP | -560 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-15 09:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-15 10:00 | 2030 100% ECP | -700 | -526 | -510 | -399.1 | 0 | 0 | Yes
2030-06-15 11:00 | 2030 100% ECP | -700 | -526 | -510 | -363.49 | 0 | 0 | Yes
2030-06-15 12:00 | 2030 100% ECP | -700 | -526 | -510 | -257.08 | 0 | 0 | Yes
2030-06-15 13:00 | 2030 100% ECP | -700 | -526 | -510 | -419.72 | 0 | 0 | Yes
2030-06-15 14:00 | 2030 100% ECP | -700 | -526 | -510 | -451.73 | 0 | 0 | Yes
2030-06-15 15:00 | 2030 100% ECP | -700 | -526 | -510 | -151.73 | 0 | 0 | Yes
2030-06-15 16:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-06-15 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 19:00 | 2030 100% ECP | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 20:00 | 2030 100% ECP | 140 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-15 21:00 | 2030 100% ECP | 560 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 22:00 | 2030 100% ECP | 700 | -526 | -510 | -232.7 | 0 | 0 | No
2030-06-15 23:00 | 2030 100% ECP | 700 | -526 | -510 | -257.47 | 0 | 0 | No
2030-06-16 | 2030 100% ECP | 700 | -526 | -510 | -364.56 | 0 | 0 | No
2030-06-16 01:00 | 2030 100% ECP | 700 | -262.15 | -510 | -321.94 | 0 | 0 | No
2030-06-16 02:00 | 2030 100% ECP | 700 | -526 | -510 | -332.02 | 0 | 0 | No
2030-06-16 03:00 | 2030 100% ECP | 700 | -526 | -510 | -355.22 | 0 | 0 | No
2030-06-16 04:00 | 2030 100% ECP | 700 | -526 | -510 | -323.3 | 0 | 0 | No
2030-06-16 05:00 | 2030 100% ECP | 700 | -393.44 | -510 | -23.3 | 0 | 0 | No
2030-06-16 06:00 | 2030 100% ECP | 560 | -526 | -510 | -4.2 | 0 | 0 | No
2030-06-16 07:00 | 2030 100% ECP | 140 | -526 | -510 | 4.71 | 0 | 0 | No
2030-06-16 08:00 | 2030 100% ECP | -280 | -526 | -510 | -24.46 | 0 | 0 | Yes
2030-06-16 09:00 | 2030 100% ECP | -700 | -526 | -510 | -56.09 | 0 | 0 | Yes
2030-06-16 10:00 | 2030 100% ECP | -700 | -526 | -510 | -61.33 | 0 | 0 | Yes
2030-06-16 11:00 | 2030 100% ECP | -700 | -526 | -510 | -45.35 | 0 | 0 | Yes
2030-06-16 12:00 | 2030 100% ECP | -700 | -526 | -510 | -22.58 | 0 | 0 | Yes
2030-06-16 13:00 | 2030 100% ECP | -700 | -526 | -510 | -8.24 | 0 | 0 | Yes
2030-06-16 14:00 | 2030 100% ECP | -700 | -526 | -510 | -57.39 | 0 | 0 | Yes
2030-06-16 15:00 | 2030 100% ECP | -700 | -526 | -510 | -103.21 | 0 | 0 | Yes
2030-06-16 16:00 | 2030 100% ECP | -700 | -526 | -510 | -58.78 | 0 | 0 | Yes
2030-06-16 17:00 | 2030 100% ECP | -280 | -526 | -510 | -90.64 | 0 | 0 | No
2030-06-16 18:00 | 2030 100% ECP | 0 | -526 | -510 | 38.14 | 0 | 0 | No
2030-06-16 19:00 | 2030 100% ECP | 420 | -526 | -510 | 16.1 | 0 | 0 | No
2030-06-16 20:00 | 2030 100% ECP | 576.86 | -526 | -510 | -197.81 | 0 | 0 | Yes
2030-06-16 21:00 | 2030 100% ECP | 488.46 | -526 | -510 | -245.3 | 0 | 0 | No
2030-06-16 22:00 | 2030 100% ECP | 68.46 | -526 | -510 | -152.58 | 0 | 0 | No
2030-06-16 23:00 | 2030 100% ECP | 488.46 | -526 | -510 | -97.39 | 0 | 0 | No
2030-06-17 | 2030 100% ECP | 682.77 | -526 | -510 | -155.7 | 0 | 0 | No
2030-06-17 01:00 | 2030 100% ECP | 682.77 | -526 | -510 | -192.97 | 0 | 0 | No
2030-06-17 02:00 | 2030 100% ECP | 682.77 | -526 | -510 | -130.25 | 0 | 0 | No
2030-06-17 03:00 | 2030 100% ECP | 682.77 | -526 | -510 | -191.02 | 0 | 0 | No
2030-06-17 04:00 | 2030 100% ECP | 700 | -526 | -510 | -213.34 | 0 | 0 | No
2030-06-17 05:00 | 2030 100% ECP | 700 | -526 | -510 | -209.66 | 0 | 0 | No
2030-06-17 06:00 | 2030 100% ECP | 700 | -526 | -510 | -99.38 | 0 | 0 | No
2030-06-17 07:00 | 2030 100% ECP | 560 | -526 | -510 | 93.46 | 0 | 0 | No
2030-06-17 08:00 | 2030 100% ECP | 140 | -526 | -510 | 251.69 | 0 | 0 | No
2030-06-17 09:00 | 2030 100% ECP | -280 | -526 | -510 | 293.8 | 0 | 0 | Yes
2030-06-17 10:00 | 2030 100% ECP | -700 | -526 | -510 | 277.48 | 0 | 0 | Yes
2030-06-17 11:00 | 2030 100% ECP | -700 | -526 | -510 | 316.22 | 0 | 0 | Yes
2030-06-17 12:00 | 2030 100% ECP | -700 | -526 | -510 | 279.14 | 0 | 0 | Yes
2030-06-17 13:00 | 2030 100% ECP | -700 | -526 | -510 | 199.69 | 0 | 0 | Yes
2030-06-17 14:00 | 2030 100% ECP | -700 | -526 | -510 | 233.3 | 0 | 0 | Yes
2030-06-17 15:00 | 2030 100% ECP | -700 | -526 | -510 | 242.27 | 0 | 0 | Yes
2030-06-17 16:00 | 2030 100% ECP | -414.16 | -526 | -510 | 303.7 | 0 | 0 | No
2030-06-17 17:00 | 2030 100% ECP | -700 | -526 | -510 | 395.18 | 0 | 0 | No
2030-06-17 18:00 | 2030 100% ECP | -280 | -226 | -510 | 424.74 | 0 | 0 | No
2030-06-17 19:00 | 2030 100% ECP | 140 | 0 | -510 | 310.78 | 0 | 0 | No
2030-06-17 20:00 | 2030 100% ECP | 560 | 0 | -510 | 311.42 | 0 | 0 | Yes
2030-06-17 21:00 | 2030 100% ECP | 700 | 0 | -510 | 294.36 | 0 | 0 | No
2030-06-17 22:00 | 2030 100% ECP | 700 | 0 | -510 | 239.53 | 0 | 0 | No
2030-06-17 23:00 | 2030 100% ECP | 700 | 0 | -510 | 117.7 | 0 | 0 | No
2030-06-18 | 2030 100% ECP | 700 | -130.51 | -510 | 85.1 | 0 | 0 | No
2030-06-18 01:00 | 2030 100% ECP | 700 | 0 | -510 | 90.44 | 0 | 0 | No
2030-06-18 02:00 | 2030 100% ECP | 700 | 0 | -510 | 98.26 | 0 | 0 | No
2030-06-18 03:00 | 2030 100% ECP | 700 | 0 | -510 | 88.33 | 0 | 0 | No
2030-06-18 04:00 | 2030 100% ECP | 700 | 0 | -510 | 55.24 | 0 | 0 | No
2030-06-18 05:00 | 2030 100% ECP | 560 | 0 | -510 | 31.04 | 0 | 0 | No
2030-06-18 06:00 | 2030 100% ECP | 140 | -241.54 | -510 | 89.73 | 0 | 0 | No
2030-06-18 07:00 | 2030 100% ECP | -280 | -526 | -510 | 214.52 | 0 | 0 | No
2030-06-18 08:00 | 2030 100% ECP | -700 | -526 | -510 | 232.04 | 0 | 0 | No
2030-06-18 09:00 | 2030 100% ECP | -700 | -526 | -510 | 227.83 | 0 | 0 | No
2030-06-18 10:00 | 2030 100% ECP | -700 | -526 | -510 | 188.65 | 0 | 0 | No
2030-06-18 11:00 | 2030 100% ECP | -700 | -526 | -510 | 215.38 | 0 | 0 | No
2030-06-18 12:00 | 2030 100% ECP | -700 | -526 | -510 | 219.62 | 0 | 0 | No
2030-06-18 13:00 | 2030 100% ECP | -700 | -526 | -510 | 169.69 | 0 | 0 | No
2030-06-18 14:00 | 2030 100% ECP | -700 | -526 | -510 | 177.73 | 0 | 0 | No
2030-06-18 15:00 | 2030 100% ECP | -700 | -526 | -510 | 173.08 | 0 | 0 | No
2030-06-18 16:00 | 2030 100% ECP | -280 | -526 | -510 | 217.51 | 0 | 0 | No
2030-06-18 17:00 | 2030 100% ECP | 140 | -526 | -510 | 172.33 | 0 | 0 | No
2030-06-18 18:00 | 2030 100% ECP | 560 | -526 | -510 | 229.34 | 0 | 0 | No
2030-06-18 19:00 | 2030 100% ECP | 700 | -526 | -510 | -61.04 | 0 | 0 | No
2030-06-18 20:00 | 2030 100% ECP | 700 | -526 | -510 | -352.72 | 0 | 0 | No
2030-06-18 21:00 | 2030 100% ECP | 686.93 | -526 | -510 | -362.85 | 0 | 0 | No
2030-06-18 22:00 | 2030 100% ECP | 686.93 | -526 | -510 | -223.2 | 0 | 0 | No
2030-06-18 23:00 | 2030 100% ECP | 686.93 | -526 | -510 | -16.33 | 0 | 0 | No
2030-06-19 | 2030 100% ECP | 700 | -526 | -510 | -88.53 | 0 | 0 | No
2030-06-19 01:00 | 2030 100% ECP | 700 | -526 | -510 | -163.72 | 0 | 0 | No
2030-06-19 02:00 | 2030 100% ECP | 700 | -526 | -510 | -10.31 | 0 | 0 | No
2030-06-19 03:00 | 2030 100% ECP | 700 | -526 | -510 | -142.16 | 0 | 0 | No
2030-06-19 04:00 | 2030 100% ECP | 700 | -526 | -510 | -98.43 | 0 | 0 | No
2030-06-19 05:00 | 2030 100% ECP | 700 | -526 | -510 | -17.01 | 0 | 0 | No
2030-06-19 06:00 | 2030 100% ECP | 560 | -526 | -510 | -14.91 | 0 | 0 | No
2030-06-19 07:00 | 2030 100% ECP | 140 | -526 | -510 | 108.39 | 0 | 0 | No
2030-06-19 08:00 | 2030 100% ECP | -280 | -526 | -510 | 114.06 | 0 | 0 | No
2030-06-19 09:00 | 2030 100% ECP | -700 | -526 | -510 | 240.47 | 0 | 0 | No
2030-06-19 10:00 | 2030 100% ECP | -700 | -526 | -510 | 104.48 | 0 | 0 | No
2030-06-19 11:00 | 2030 100% ECP | -700 | -526 | -510 | 280.35 | 0 | 0 | No
2030-06-19 12:00 | 2030 100% ECP | -700 | -526 | -510 | 232.06 | 0 | 0 | No
2030-06-19 13:00 | 2030 100% ECP | -700 | -526 | -510 | 204.84 | 0 | 0 | No
2030-06-19 14:00 | 2030 100% ECP | -700 | -526 | -510 | 207.82 | 0 | 0 | No
2030-06-19 15:00 | 2030 100% ECP | -700 | -526 | -510 | 220.5 | 0 | 0 | No
2030-06-19 16:00 | 2030 100% ECP | -700 | -526 | -510 | 37.73 | 0 | 0 | No
2030-06-19 17:00 | 2030 100% ECP | -700 | -526 | -510 | -15.39 | 0 | 0 | No
2030-06-19 18:00 | 2030 100% ECP | -329 | -526 | -510 | 79.7 | 0 | 0 | No
2030-06-19 19:00 | 2030 100% ECP | 0 | -526 | -510 | 205.88 | 0 | 0 | No
2030-06-19 20:00 | 2030 100% ECP | 178.93 | -526 | -510 | 255.27 | 0 | 0 | No
2030-06-19 21:00 | 2030 100% ECP | 510.32 | -526 | -510 | 291.45 | 0 | 0 | No
2030-06-19 22:00 | 2030 100% ECP | 197.79 | -526 | -510 | 157.04 | 0 | 0 | No
2030-06-19 23:00 | 2030 100% ECP | 0 | -526 | -510 | 137.61 | 0 | 0 | No
2030-06-20 | 2030 100% ECP | 0 | -526 | -510 | 64.88 | 0 | 0 | No
2030-06-20 01:00 | 2030 100% ECP | 0 | -526 | -510 | 137.52 | 0 | 0 | No
2030-06-20 02:00 | 2030 100% ECP | 0 | -526 | -510 | 127.39 | 0 | 0 | No
2030-06-20 03:00 | 2030 100% ECP | 0 | -526 | -510 | 77.49 | 0 | 0 | No
2030-06-20 04:00 | 2030 100% ECP | -135.22 | -526 | -510 | 61.59 | 0 | 0 | No
2030-06-20 05:00 | 2030 100% ECP | -555.22 | -526 | -510 | -18.69 | 0 | 0 | No
2030-06-20 06:00 | 2030 100% ECP | -700 | -526 | -510 | 30.4 | 0 | 0 | No
2030-06-20 07:00 | 2030 100% ECP | -700 | -526 | -510 | 104.51 | 0 | 0 | Yes
2030-06-20 08:00 | 2030 100% ECP | -700 | -526 | -510 | 11.04 | 0 | 0 | Yes
2030-06-20 09:00 | 2030 100% ECP | -700 | -526 | -510 | -161.47 | 0 | 0 | Yes
2030-06-20 10:00 | 2030 100% ECP | -700 | -526 | -510 | -132.95 | 0 | 0 | Yes
2030-06-20 11:00 | 2030 100% ECP | -700 | -526 | -510 | -346.06 | 0 | 0 | Yes
2030-06-20 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 14:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 15:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 20:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 21:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-20 22:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-06-20 23:00 | 2030 100% ECP | -700 | 74 | 90 | 43.19 | 0 | 0 | Yes
2030-06-21 | 2030 100% ECP | -700 | 374 | 390 | 343.19 | 0 | 0 | Yes
2030-06-21 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 15:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-06-21 16:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-06-21 17:00 | 2030 100% ECP | -700 | -226 | -210 | 405.26 | 0 | 0 | Yes
2030-06-21 18:00 | 2030 100% ECP | -700 | -526 | -510 | 105.26 | 0 | 0 | Yes
2030-06-21 19:00 | 2030 100% ECP | -280 | -526 | -510 | 219.09 | 0 | 0 | No
2030-06-21 20:00 | 2030 100% ECP | -627.5 | -526 | -510 | 0 | 0 | 0 | No
2030-06-21 21:00 | 2030 100% ECP | -397.92 | -526 | -510 | 210 | 0 | 0 | No
2030-06-21 22:00 | 2030 100% ECP | 22.08 | -526 | -510 | 510 | 0 | 0 | No
2030-06-21 23:00 | 2030 100% ECP | 442.08 | -526 | -510 | 379.41 | 0 | 0 | No
2030-06-22 | 2030 100% ECP | 22.08 | -357.83 | -510 | 284.57 | 0 | 0 | No
2030-06-22 01:00 | 2030 100% ECP | -167.48 | -526 | -510 | 510 | 0 | 0 | No
2030-06-22 02:00 | 2030 100% ECP | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-06-22 03:00 | 2030 100% ECP | -700 | -526 | -510 | 234.7 | 0 | 0 | Yes
2030-06-22 04:00 | 2030 100% ECP | -700 | -526 | -510 | -65.3 | 0 | 0 | Yes
2030-06-22 05:00 | 2030 100% ECP | -700 | -526 | -510 | -365.3 | 0 | 0 | Yes
2030-06-22 06:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-22 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-22 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-22 09:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-06-22 10:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-06-22 11:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-06-22 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 17:00 | 2030 100% ECP | -700 | 300 | 210 | 211.62 | 0 | 0 | Yes
2030-06-22 18:00 | 2030 100% ECP | -700 | 0 | -90 | -88.38 | 0 | 0 | Yes
2030-06-22 19:00 | 2030 100% ECP | -700 | 300 | 210 | 211.62 | 0 | 0 | Yes
2030-06-22 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-22 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 01:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 02:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-23 06:00 | 2030 100% ECP | 700 | 205 | 210 | 245.97 | 0 | 0 | No
2030-06-23 07:00 | 2030 100% ECP | 700 | 166.24 | 90 | 510 | 0 | 0 | No
2030-06-23 08:00 | 2030 100% ECP | 280 | -133.76 | -210 | 368.54 | 0 | 0 | No
2030-06-23 09:00 | 2030 100% ECP | 0 | -433.76 | -510 | 510 | 0 | 0 | No
2030-06-23 10:00 | 2030 100% ECP | 0 | -526 | -510 | 365.13 | 0 | 0 | No
2030-06-23 11:00 | 2030 100% ECP | -92.58 | -526 | -510 | 473.6 | 0 | 0 | No
2030-06-23 12:00 | 2030 100% ECP | -512.58 | -526 | -510 | 437.02 | 0 | 0 | No
2030-06-23 13:00 | 2030 100% ECP | -321.78 | -526 | -510 | 481.82 | 0 | 0 | No
2030-06-23 14:00 | 2030 100% ECP | 0 | -526 | -510 | 236.79 | 0 | 0 | No
2030-06-23 15:00 | 2030 100% ECP | -195.25 | -526 | -510 | 381.23 | 0 | 0 | No
2030-06-23 16:00 | 2030 100% ECP | 208.9 | -526 | -510 | 300 | 0 | 0 | No
2030-06-23 17:00 | 2030 100% ECP | 628.9 | -526 | -510 | 0 | 0 | 0 | No
2030-06-23 18:00 | 2030 100% ECP | 700 | -526 | -510 | 220.23 | 0 | 0 | No
2030-06-23 19:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-23 20:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-23 21:00 | 2030 100% ECP | 700 | -526 | -510 | 233.65 | 0 | 0 | No
2030-06-23 22:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-23 23:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-24 | 2030 100% ECP | 700 | -395 | -415.77 | 275.93 | 0 | 0 | No
2030-06-24 01:00 | 2030 100% ECP | 700 | -95 | -115.77 | 354.06 | 0 | 0 | No
2030-06-24 02:00 | 2030 100% ECP | 700 | 205 | 184.23 | 449.95 | 0 | 0 | No
2030-06-24 03:00 | 2030 100% ECP | 700 | 505 | 484.23 | 510 | 0 | 0 | No
2030-06-24 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-24 05:00 | 2030 100% ECP | 700 | 205 | 210 | 312.89 | 0 | 0 | No
2030-06-24 06:00 | 2030 100% ECP | 560 | 137.69 | 90 | 510 | 0 | 0 | No
2030-06-24 07:00 | 2030 100% ECP | 140 | -162.31 | -210 | 510 | 0 | 0 | No
2030-06-24 08:00 | 2030 100% ECP | -280 | -462.31 | -510 | 510 | 0 | 0 | Yes
2030-06-24 09:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-06-24 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-06-24 11:00 | 2030 100% ECP | -700 | -526 | -510 | 425.75 | 0 | 0 | Yes
2030-06-24 12:00 | 2030 100% ECP | -700 | -526 | -510 | 396.57 | 0 | 0 | Yes
2030-06-24 13:00 | 2030 100% ECP | -700 | -526 | -510 | 374.89 | 0 | 0 | Yes
2030-06-24 14:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-06-24 15:00 | 2030 100% ECP | -700 | -526 | -510 | 483.65 | 0 | 0 | Yes
2030-06-24 16:00 | 2030 100% ECP | -364.55 | -526 | -510 | 510 | 0 | 0 | Yes
2030-06-24 17:00 | 2030 100% ECP | 55.45 | -526 | -510 | 510 | 0 | 0 | No
2030-06-24 18:00 | 2030 100% ECP | 475.45 | -526 | -510 | 510 | 0 | 0 | No
2030-06-24 19:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-06-24 20:00 | 2030 100% ECP | 669.6 | -526 | -510 | 510 | 0 | 0 | No
2030-06-24 21:00 | 2030 100% ECP | 249.6 | -300 | -450.04 | 510 | 0 | 0 | No
2030-06-24 22:00 | 2030 100% ECP | 636.84 | 0 | -150.04 | 457.85 | 0 | 0 | No
2030-06-24 23:00 | 2030 100% ECP | 700 | 300 | 149.96 | 510 | 0 | 0 | No
2030-06-25 | 2030 100% ECP | 700 | 0 | 21.2 | 210 | 0 | 0 | No
2030-06-25 01:00 | 2030 100% ECP | 700 | 0 | -108.31 | 349.32 | 0 | 0 | No
2030-06-25 02:00 | 2030 100% ECP | 700 | -300 | -408.31 | 318.87 | 0 | 0 | No
2030-06-25 03:00 | 2030 100% ECP | 700 | -342.63 | -510 | 429.01 | 0 | 0 | No
2030-06-25 04:00 | 2030 100% ECP | 700 | -526 | -510 | 459.89 | 0 | 0 | No
2030-06-25 05:00 | 2030 100% ECP | 700 | -526 | -510 | 459.89 | 0 | 0 | No
2030-06-25 06:00 | 2030 100% ECP | 309.52 | -526 | -510 | 459.89 | 0 | 0 | No
2030-06-25 07:00 | 2030 100% ECP | -110.48 | -526 | -510 | 395.22 | 0 | 0 | No
2030-06-25 08:00 | 2030 100% ECP | -530.48 | -526 | -510 | 428.61 | 0 | 0 | Yes
2030-06-25 09:00 | 2030 100% ECP | -700 | -526 | -510 | 386.84 | 0 | 0 | Yes
2030-06-25 10:00 | 2030 100% ECP | -700 | -526 | -510 | 309.96 | 0 | 0 | Yes
2030-06-25 11:00 | 2030 100% ECP | -700 | -526 | -510 | 208.51 | 0 | 0 | Yes
2030-06-25 12:00 | 2030 100% ECP | -700 | -526 | -510 | 508.51 | 0 | 0 | Yes
2030-06-25 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-06-25 14:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-06-25 15:00 | 2030 100% ECP | -700 | -226 | -422.98 | 510 | 0 | 0 | Yes
2030-06-25 16:00 | 2030 100% ECP | -280 | -526 | -510 | 380.05 | 0 | 0 | No
2030-06-25 17:00 | 2030 100% ECP | 140 | -226 | -510 | 416.94 | 0 | 0 | No
2030-06-25 18:00 | 2030 100% ECP | 560 | 0 | -510 | 510 | 0 | 0 | No
2030-06-25 19:00 | 2030 100% ECP | 700 | 0 | -510 | 418.4 | 0 | 0 | No
2030-06-25 20:00 | 2030 100% ECP | 700 | -300 | -510 | 409.37 | 0 | 0 | No
2030-06-25 21:00 | 2030 100% ECP | 700 | -69.02 | -510 | 394.88 | 0 | 0 | No
2030-06-25 22:00 | 2030 100% ECP | 700 | -69.02 | -510 | 409.04 | 0 | 0 | No
2030-06-25 23:00 | 2030 100% ECP | 700 | 0 | -510 | 368.6 | 0 | 0 | No
2030-06-26 | 2030 100% ECP | 700 | 0 | -338.51 | 247.05 | 0 | 0 | No
2030-06-26 01:00 | 2030 100% ECP | 700 | 0 | -38.51 | 273.15 | 0 | 0 | No
2030-06-26 02:00 | 2030 100% ECP | 700 | 0 | 229.53 | 305.41 | 0 | 0 | No
2030-06-26 03:00 | 2030 100% ECP | 700 | 0 | -70.47 | 290.43 | 0 | 0 | No
2030-06-26 04:00 | 2030 100% ECP | 657.84 | 0 | -370.47 | 93.6 | 0 | 0 | No
2030-06-26 05:00 | 2030 100% ECP | 237.84 | 0 | -510 | 0 | 0 | 0 | No
2030-06-26 06:00 | 2030 100% ECP | -182.16 | -226 | -510 | 0 | 0 | 0 | No
2030-06-26 07:00 | 2030 100% ECP | -602.16 | -526 | -510 | 283.86 | 0 | 0 | No
2030-06-26 08:00 | 2030 100% ECP | -700 | -526 | -510 | 299.69 | 0 | 0 | Yes
2030-06-26 09:00 | 2030 100% ECP | -700 | -526 | -510 | 226.61 | 0 | 0 | Yes
2030-06-26 10:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | Yes
2030-06-26 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-06-26 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-06-26 13:00 | 2030 100% ECP | -700 | -526 | -510 | 305.39 | 0 | 0 | Yes
2030-06-26 14:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-06-26 15:00 | 2030 100% ECP | -490.56 | -526 | -510 | 510 | 0 | 0 | No
2030-06-26 16:00 | 2030 100% ECP | -78.71 | -453.05 | -510 | 510 | 0 | 0 | No
2030-06-26 17:00 | 2030 100% ECP | -498.71 | -526 | -510 | 510 | 0 | 0 | No
2030-06-26 18:00 | 2030 100% ECP | -699.83 | -526 | -510 | 510 | 0 | 0 | No
2030-06-26 19:00 | 2030 100% ECP | -699.83 | -526 | -510 | 510 | 0 | 0 | No
2030-06-26 20:00 | 2030 100% ECP | -279.83 | -526 | -510 | 510 | 0 | 0 | No
2030-06-26 21:00 | 2030 100% ECP | -279.83 | -526 | -510 | 348.42 | 0 | 0 | No
2030-06-26 22:00 | 2030 100% ECP | -560 | -395 | -502.55 | 443.74 | 0 | 0 | No
2030-06-26 23:00 | 2030 100% ECP | -140 | -95 | -202.55 | 293.71 | 0 | 0 | No
2030-06-27 | 2030 100% ECP | 280 | 205 | 97.45 | 324.66 | 0 | 0 | No
2030-06-27 01:00 | 2030 100% ECP | 700 | 505 | 397.45 | 510 | 0 | 0 | No
2030-06-27 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 05:00 | 2030 100% ECP | 700 | 300 | 284.25 | 396.77 | 0 | 0 | No
2030-06-27 06:00 | 2030 100% ECP | 700 | 0 | -15.75 | 96.77 | 0 | 0 | No
2030-06-27 07:00 | 2030 100% ECP | 560 | 0 | -315.75 | 120.73 | 0 | 0 | No
2030-06-27 08:00 | 2030 100% ECP | 140 | -156.14 | -510 | 210 | 0 | 0 | No
2030-06-27 09:00 | 2030 100% ECP | -280 | 143.86 | -210 | 510 | 0 | 0 | Yes
2030-06-27 10:00 | 2030 100% ECP | -700 | 443.86 | 90 | 510 | 0 | 0 | Yes
2030-06-27 11:00 | 2030 100% ECP | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-06-27 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 17:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 18:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 20:00 | 2030 100% ECP | -700 | 505 | 510 | 472.07 | 0 | 0 | Yes
2030-06-27 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 02:00 | 2030 100% ECP | -700 | 505 | 510 | 455.88 | 0 | 0 | Yes
2030-06-28 03:00 | 2030 100% ECP | -700 | 505 | 510 | 434 | 0 | 0 | Yes
2030-06-28 04:00 | 2030 100% ECP | -700 | 505 | 510 | 191.52 | 0 | 0 | Yes
2030-06-28 05:00 | 2030 100% ECP | -700 | 505 | 510 | 159.33 | 0 | 0 | Yes
2030-06-28 06:00 | 2030 100% ECP | -700 | 505 | 510 | 248.55 | 0 | 0 | Yes
2030-06-28 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 13:00 | 2030 100% ECP | -700 | 505 | 510 | 426.96 | 0 | 0 | Yes
2030-06-28 14:00 | 2030 100% ECP | -700 | 505 | 510 | 412.13 | 0 | 0 | Yes
2030-06-28 15:00 | 2030 100% ECP | -700 | 505 | 510 | 337.02 | 0 | 0 | Yes
2030-06-28 16:00 | 2030 100% ECP | -700 | 505 | 510 | 384.22 | 0 | 0 | Yes
2030-06-28 17:00 | 2030 100% ECP | -700 | 505 | 510 | 410.71 | 0 | 0 | Yes
2030-06-28 18:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 19:00 | 2030 100% ECP | -700 | 505 | 510 | 420.12 | 0 | 0 | Yes
2030-06-28 20:00 | 2030 100% ECP | -700 | 505 | 510 | 464.42 | 0 | 0 | Yes
2030-06-28 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 23:00 | 2030 100% ECP | -700 | 505 | 510 | 487.98 | 0 | 0 | Yes
2030-06-29 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 17:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 18:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 20:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 22:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 23:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 06:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 07:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 08:00 | 2030 100% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 09:00 | 2030 100% ECP | -140 | 205 | 270.51 | 510 | 0 | 0 | No
2030-06-30 10:00 | 2030 100% ECP | -560 | 0 | 0 | 510 | 0 | 0 | No
2030-06-30 11:00 | 2030 100% ECP | -700 | -150.33 | -210 | 510 | 0 | 0 | No
2030-06-30 12:00 | 2030 100% ECP | -700 | -450.33 | -510 | 510 | 0 | 0 | No
2030-06-30 13:00 | 2030 100% ECP | -560 | -526 | -510 | 510 | 0 | 0 | No
2030-06-30 14:00 | 2030 100% ECP | -140 | -526 | -510 | 510 | 0 | 0 | No
2030-06-30 15:00 | 2030 100% ECP | 280 | -526 | -510 | 449.36 | 0 | 0 | No
2030-06-30 16:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-06-30 17:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-06-30 18:00 | 2030 100% ECP | 700 | -334.95 | -510 | 510 | 0 | 0 | No
2030-06-30 19:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-06-30 20:00 | 2030 100% ECP | 700 | -526 | -510 | 435.56 | 0 | 0 | Yes
2030-06-30 21:00 | 2030 100% ECP | 700 | -309.37 | -510 | 510 | 0 | 0 | No
2030-06-30 22:00 | 2030 100% ECP | 700 | -354.93 | -510 | 510 | 0 | 0 | No
2030-06-30 23:00 | 2030 100% ECP | 700 | -64.22 | -510 | 440.08 | 0 | 0 | No
2030-07-01 | 2030 100% ECP | 700 | -300 | -510 | 140.08 | 0 | 0 | No
2030-07-01 01:00 | 2030 100% ECP | 700 | 0 | -510 | 61.16 | 0 | 0 | No
2030-07-01 02:00 | 2030 100% ECP | 700 | -148.75 | -510 | 51.73 | 0 | 0 | No
2030-07-01 03:00 | 2030 100% ECP | 700 | -448.75 | -510 | 30.56 | 0 | 0 | No
2030-07-01 04:00 | 2030 100% ECP | 700 | -300 | -510 | 0 | 0 | 0 | No
2030-07-01 05:00 | 2030 100% ECP | 700 | 0 | -510 | -21.58 | 0 | 0 | No
2030-07-01 06:00 | 2030 100% ECP | 700 | -300 | -510 | 0 | 0 | 0 | No
2030-07-01 07:00 | 2030 100% ECP | 700 | -526 | -510 | 58.02 | 0 | 0 | No
2030-07-01 08:00 | 2030 100% ECP | 700 | -526 | -510 | 25.99 | 0 | 0 | No
2030-07-01 09:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-01 10:00 | 2030 100% ECP | 700 | -526 | -510 | 239.7 | 0 | 0 | No
2030-07-01 11:00 | 2030 100% ECP | 700 | -526 | -510 | 277.14 | 0 | 0 | No
2030-07-01 12:00 | 2030 100% ECP | 700 | -526 | -510 | 225.85 | 0 | 0 | No
2030-07-01 13:00 | 2030 100% ECP | 700 | -526 | -510 | 163.87 | 0 | 0 | No
2030-07-01 14:00 | 2030 100% ECP | 700 | -526 | -510 | 147.71 | 0 | 0 | No
2030-07-01 15:00 | 2030 100% ECP | 700 | -526 | -510 | 125.44 | 0 | 0 | No
2030-07-01 16:00 | 2030 100% ECP | 700 | -526 | -510 | 99.34 | 0 | 0 | No
2030-07-01 17:00 | 2030 100% ECP | 700 | -526 | -510 | 123.89 | 0 | 0 | No
2030-07-01 18:00 | 2030 100% ECP | 280 | -526 | -510 | 182.67 | 0 | 0 | No
2030-07-01 19:00 | 2030 100% ECP | -140 | -526 | -510 | 174.33 | 0 | 0 | No
2030-07-01 20:00 | 2030 100% ECP | -560 | -526 | -510 | 151.86 | 0 | 0 | No
2030-07-01 21:00 | 2030 100% ECP | -140 | -526 | -510 | 179.33 | 0 | 0 | No
2030-07-01 22:00 | 2030 100% ECP | 280 | -526 | -510 | 217.02 | 0 | 0 | No
2030-07-01 23:00 | 2030 100% ECP | 700 | -526 | -510 | 172.11 | 0 | 0 | No
2030-07-02 | 2030 100% ECP | 700 | -526 | -510 | 112.13 | 0 | 0 | No
2030-07-02 01:00 | 2030 100% ECP | 700 | -526 | -510 | 111.19 | 0 | 0 | No
2030-07-02 02:00 | 2030 100% ECP | 700 | -526 | -510 | 94.89 | 0 | 0 | No
2030-07-02 03:00 | 2030 100% ECP | 700 | -526 | -510 | 85.87 | 0 | 0 | No
2030-07-02 04:00 | 2030 100% ECP | 700 | -526 | -510 | 72.71 | 0 | 0 | No
2030-07-02 05:00 | 2030 100% ECP | 354.95 | -526 | -510 | 40.29 | 0 | 0 | No
2030-07-02 06:00 | 2030 100% ECP | -65.05 | -526 | -510 | 61.99 | 0 | 0 | No
2030-07-02 07:00 | 2030 100% ECP | -485.05 | -526 | -510 | 127.67 | 0 | 0 | No
2030-07-02 08:00 | 2030 100% ECP | -700 | -526 | -510 | 125.53 | 0 | 0 | Yes
2030-07-02 09:00 | 2030 100% ECP | -700 | -526 | -510 | -47.63 | 0 | 0 | Yes
2030-07-02 10:00 | 2030 100% ECP | -700 | -526 | -510 | -233.51 | 0 | 0 | Yes
2030-07-02 11:00 | 2030 100% ECP | -700 | -526 | -510 | -182.12 | 0 | 0 | Yes
2030-07-02 12:00 | 2030 100% ECP | -700 | -526 | -510 | 49.96 | 0 | 0 | Yes
2030-07-02 13:00 | 2030 100% ECP | -700 | -526 | -510 | -26.96 | 0 | 0 | Yes
2030-07-02 14:00 | 2030 100% ECP | -700 | -526 | -510 | 25.14 | 0 | 0 | Yes
2030-07-02 15:00 | 2030 100% ECP | -700 | -526 | -510 | 50.49 | 0 | 0 | Yes
2030-07-02 16:00 | 2030 100% ECP | -700 | -526 | -510 | 192.06 | 0 | 0 | Yes
2030-07-02 17:00 | 2030 100% ECP | -280 | -526 | -510 | 345 | 0 | 0 | No
2030-07-02 18:00 | 2030 100% ECP | 19.22 | -526 | -510 | 378.91 | 0 | 0 | No
2030-07-02 19:00 | 2030 100% ECP | 439.22 | -526 | -510 | 329.03 | 0 | 0 | No
2030-07-02 20:00 | 2030 100% ECP | 658.36 | -526 | -510 | 238.74 | 0 | 0 | No
2030-07-02 21:00 | 2030 100% ECP | 238.36 | -526 | -510 | 217.51 | 0 | 0 | No
2030-07-02 22:00 | 2030 100% ECP | 0 | -526 | -510 | 273.52 | 0 | 0 | No
2030-07-02 23:00 | 2030 100% ECP | -237.44 | -526 | -510 | 135.48 | 0 | 0 | No
2030-07-03 | 2030 100% ECP | -293.27 | -526 | -510 | -40.34 | 0 | 0 | No
2030-07-03 01:00 | 2030 100% ECP | -700 | -526 | -510 | 7.42 | 0 | 0 | No
2030-07-03 02:00 | 2030 100% ECP | -700 | -526 | -510 | -193.42 | 0 | 0 | Yes
2030-07-03 03:00 | 2030 100% ECP | -700 | -463.9 | -510 | 106.58 | 0 | 0 | Yes
2030-07-03 04:00 | 2030 100% ECP | -700 | -526 | -510 | 154.72 | 0 | 0 | Yes
2030-07-03 05:00 | 2030 100% ECP | -700 | -526 | -510 | -145.28 | 0 | 0 | Yes
2030-07-03 06:00 | 2030 100% ECP | -700 | -526 | -510 | -90 | 0 | 0 | Yes
2030-07-03 07:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | Yes
2030-07-03 08:00 | 2030 100% ECP | -700 | -226 | -273.33 | 510 | 0 | 0 | Yes
2030-07-03 09:00 | 2030 100% ECP | -700 | 74 | 26.67 | 510 | 0 | 0 | Yes
2030-07-03 10:00 | 2030 100% ECP | -700 | 374 | 326.67 | 510 | 0 | 0 | Yes
2030-07-03 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-03 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-03 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-03 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-03 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-03 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 17:00 | 2030 100% ECP | -481.53 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 18:00 | 2030 100% ECP | -61.53 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 19:00 | 2030 100% ECP | 358.47 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 20:00 | 2030 100% ECP | 280 | 300 | 499.25 | 510 | 0 | 0 | No
2030-07-03 21:00 | 2030 100% ECP | -140 | 0 | 199.25 | 510 | 0 | 0 | No
2030-07-03 22:00 | 2030 100% ECP | 280 | 300 | 499.25 | 510 | 0 | 0 | No
2030-07-03 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 05:00 | 2030 100% ECP | 700 | 300 | 384.8 | 510 | 0 | 0 | No
2030-07-04 06:00 | 2030 100% ECP | 700 | 0 | 84.8 | 510 | 0 | 0 | No
2030-07-04 07:00 | 2030 100% ECP | 700 | -300 | -215.2 | 510 | 0 | 0 | No
2030-07-04 08:00 | 2030 100% ECP | 280 | -526 | -510 | 510 | 0 | 0 | No
2030-07-04 09:00 | 2030 100% ECP | -140 | -526 | -510 | 510 | 0 | 0 | No
2030-07-04 10:00 | 2030 100% ECP | -560 | -499.06 | -510 | 510 | 0 | 0 | No
2030-07-04 11:00 | 2030 100% ECP | -700 | -404.56 | -510 | 510 | 0 | 0 | Yes
2030-07-04 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-07-04 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-07-04 14:00 | 2030 100% ECP | -700 | -226 | -310.07 | 510 | 0 | 0 | Yes
2030-07-04 15:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-07-04 16:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-07-04 17:00 | 2030 100% ECP | -700 | -526 | -510 | 356.92 | 0 | 0 | Yes
2030-07-04 18:00 | 2030 100% ECP | -700 | -526 | -510 | 56.92 | 0 | 0 | Yes
2030-07-04 19:00 | 2030 100% ECP | -700 | -526 | -510 | -243.08 | 0 | 0 | Yes
2030-07-04 20:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-07-04 21:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-07-04 22:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-07-04 23:00 | 2030 100% ECP | -700 | 374 | 390 | 200.66 | 0 | 0 | Yes
2030-07-05 | 2030 100% ECP | -700 | 505 | 510 | 66.58 | 0 | 0 | Yes
2030-07-05 01:00 | 2030 100% ECP | -700 | 505 | 510 | 72.69 | 0 | 0 | Yes
2030-07-05 02:00 | 2030 100% ECP | -700 | 505 | 510 | -24.2 | 0 | 0 | Yes
2030-07-05 03:00 | 2030 100% ECP | -700 | 505 | 510 | 226.19 | 0 | 0 | Yes
2030-07-05 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 05:00 | 2030 100% ECP | -700 | 505 | 510 | 271.21 | 0 | 0 | Yes
2030-07-05 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 10:00 | 2030 100% ECP | -700 | 505 | 510 | 456.21 | 0 | 0 | Yes
2030-07-05 11:00 | 2030 100% ECP | -700 | 499.16 | 510 | 156.21 | 0 | 0 | Yes
2030-07-05 12:00 | 2030 100% ECP | -700 | 444.41 | 510 | -143.79 | 0 | 0 | Yes
2030-07-05 13:00 | 2030 100% ECP | -700 | 484.55 | 510 | 0 | 0 | 0 | Yes
2030-07-05 14:00 | 2030 100% ECP | -700 | 505 | 358.34 | 0 | 0 | 0 | Yes
2030-07-05 15:00 | 2030 100% ECP | -700 | 469.29 | 510 | 0 | 0 | 0 | Yes
2030-07-05 16:00 | 2030 100% ECP | -700 | 505 | 510 | 84.08 | 0 | 0 | Yes
2030-07-05 17:00 | 2030 100% ECP | -700 | 505 | 510 | 257.99 | 0 | 0 | Yes
2030-07-05 18:00 | 2030 100% ECP | -700 | 505 | 510 | 195.74 | 0 | 0 | Yes
2030-07-05 19:00 | 2030 100% ECP | -700 | 505 | 510 | 272.98 | 0 | 0 | Yes
2030-07-05 20:00 | 2030 100% ECP | -700 | 505 | 510 | 444.33 | 0 | 0 | Yes
2030-07-05 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 22:00 | 2030 100% ECP | -700 | 505 | 510 | 362.66 | 0 | 0 | Yes
2030-07-05 23:00 | 2030 100% ECP | -700 | 505 | 510 | 498.66 | 0 | 0 | Yes
2030-07-06 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 03:00 | 2030 100% ECP | -700 | 505 | 510 | 457.31 | 0 | 0 | Yes
2030-07-06 04:00 | 2030 100% ECP | -700 | 505 | 510 | 157.31 | 0 | 0 | Yes
2030-07-06 05:00 | 2030 100% ECP | -700 | 505 | 510 | 426.93 | 0 | 0 | Yes
2030-07-06 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 07:00 | 2030 100% ECP | -700 | 505 | 510 | 420.76 | 0 | 0 | Yes
2030-07-06 08:00 | 2030 100% ECP | -700 | 505 | 510 | 395.08 | 0 | 0 | Yes
2030-07-06 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 12:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-07-06 13:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-07-06 14:00 | 2030 100% ECP | -700 | -226 | -210 | 250.66 | 0 | 0 | Yes
2030-07-06 15:00 | 2030 100% ECP | -700 | -526 | -510 | -49.34 | 0 | 0 | Yes
2030-07-06 16:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-07-06 17:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-07-06 18:00 | 2030 100% ECP | -280 | -526 | -510 | 0 | 0 | 0 | No
2030-07-06 19:00 | 2030 100% ECP | -700 | -526 | -510 | 74 | 0 | 0 | No
2030-07-06 20:00 | 2030 100% ECP | -700 | -526 | -510 | 374 | 0 | 0 | No
2030-07-06 21:00 | 2030 100% ECP | -327.29 | -526 | -510 | 275.18 | 0 | 0 | No
2030-07-06 22:00 | 2030 100% ECP | 92.71 | -395 | -390 | 39.86 | 0 | 0 | No
2030-07-06 23:00 | 2030 100% ECP | 512.71 | -95 | -90 | 85.67 | 0 | 0 | No
2030-07-07 | 2030 100% ECP | 280 | 205 | 210 | 342.94 | 0 | 0 | No
2030-07-07 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-07 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-07 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-07 04:00 | 2030 100% ECP | 700 | 300 | 249.15 | 510 | 0 | 0 | No
2030-07-07 05:00 | 2030 100% ECP | 700 | 0 | -50.85 | 267.56 | 0 | 0 | No
2030-07-07 06:00 | 2030 100% ECP | 700 | -300 | -350.85 | 53.36 | 0 | 0 | No
2030-07-07 07:00 | 2030 100% ECP | 700 | -526 | -510 | 9.01 | 0 | 0 | No
2030-07-07 08:00 | 2030 100% ECP | 700 | -526 | -510 | 90.19 | 0 | 0 | No
2030-07-07 09:00 | 2030 100% ECP | 700 | -526 | -510 | 175.31 | 0 | 0 | No
2030-07-07 10:00 | 2030 100% ECP | 700 | -526 | -510 | 289.69 | 0 | 0 | No
2030-07-07 11:00 | 2030 100% ECP | 700 | -526 | -510 | 364.07 | 0 | 0 | No
2030-07-07 12:00 | 2030 100% ECP | 700 | -526 | -510 | 439.52 | 0 | 0 | No
2030-07-07 13:00 | 2030 100% ECP | 700 | -526 | -510 | 475.76 | 0 | 0 | No
2030-07-07 14:00 | 2030 100% ECP | 700 | -526 | -510 | 435.45 | 0 | 0 | No
2030-07-07 15:00 | 2030 100% ECP | 700 | -526 | -510 | 318.29 | 0 | 0 | No
2030-07-07 16:00 | 2030 100% ECP | 700 | -526 | -510 | 18.29 | 0 | 0 | No
2030-07-07 17:00 | 2030 100% ECP | 700 | -526 | -510 | 160.26 | 0 | 0 | No
2030-07-07 18:00 | 2030 100% ECP | 700 | -526 | -510 | 397.04 | 0 | 0 | No
2030-07-07 19:00 | 2030 100% ECP | 280 | -526 | -510 | 355.65 | 0 | 0 | No
2030-07-07 20:00 | 2030 100% ECP | 0 | -526 | -510 | 272.77 | 0 | 0 | Yes
2030-07-07 21:00 | 2030 100% ECP | -82.83 | -526 | -510 | 108.06 | 0 | 0 | No
2030-07-07 22:00 | 2030 100% ECP | 66.2 | -526 | -510 | 180.37 | 0 | 0 | No
2030-07-07 23:00 | 2030 100% ECP | 486.2 | -526 | -510 | 236.02 | 0 | 0 | No
2030-07-08 | 2030 100% ECP | 66.2 | -526 | -510 | 28.29 | 0 | 0 | No
2030-07-08 01:00 | 2030 100% ECP | 89.61 | -526 | -510 | 17.5 | 0 | 0 | No
2030-07-08 02:00 | 2030 100% ECP | 280 | -526 | -510 | 13.44 | 0 | 0 | No
2030-07-08 03:00 | 2030 100% ECP | 700 | -526 | -510 | -22.26 | 0 | 0 | No
2030-07-08 04:00 | 2030 100% ECP | 700 | -526 | -510 | 3.69 | 0 | 0 | No
2030-07-08 05:00 | 2030 100% ECP | 700 | -526 | -510 | -7.57 | 0 | 0 | No
2030-07-08 06:00 | 2030 100% ECP | 700 | -526 | -510 | 6.76 | 0 | 0 | No
2030-07-08 07:00 | 2030 100% ECP | 700 | -526 | -510 | 300.46 | 0 | 0 | No
2030-07-08 08:00 | 2030 100% ECP | 700 | -526 | -510 | 330.77 | 0 | 0 | No
2030-07-08 09:00 | 2030 100% ECP | 700 | -526 | -510 | 342.13 | 0 | 0 | No
2030-07-08 10:00 | 2030 100% ECP | 700 | -526 | -510 | 335.74 | 0 | 0 | No
2030-07-08 11:00 | 2030 100% ECP | 700 | -526 | -510 | 362.5 | 0 | 0 | No
2030-07-08 12:00 | 2030 100% ECP | 700 | -526 | -510 | 394.07 | 0 | 0 | No
2030-07-08 13:00 | 2030 100% ECP | 700 | -526 | -510 | 374.08 | 0 | 0 | No
2030-07-08 14:00 | 2030 100% ECP | 700 | -526 | -510 | 397.94 | 0 | 0 | No
2030-07-08 15:00 | 2030 100% ECP | 700 | -526 | -510 | 419.53 | 0 | 0 | No
2030-07-08 16:00 | 2030 100% ECP | 700 | -526 | -510 | 479.19 | 0 | 0 | No
2030-07-08 17:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-08 18:00 | 2030 100% ECP | 700 | -526 | -510 | 494.46 | 0 | 0 | No
2030-07-08 19:00 | 2030 100% ECP | 280 | -526 | -510 | 442.11 | 0 | 0 | No
2030-07-08 20:00 | 2030 100% ECP | -140 | -526 | -510 | 327.84 | 0 | 0 | No
2030-07-08 21:00 | 2030 100% ECP | -140 | -526 | -510 | 48.2 | 0 | 0 | No
2030-07-08 22:00 | 2030 100% ECP | 280 | -526 | -510 | 164.37 | 0 | 0 | No
2030-07-08 23:00 | 2030 100% ECP | 700 | -226 | -210 | 42.39 | 0 | 0 | No
2030-07-09 | 2030 100% ECP | 700 | 74 | 90 | 247.11 | 0 | 0 | No
2030-07-09 01:00 | 2030 100% ECP | 700 | 374 | 390 | 510 | 0 | 0 | No
2030-07-09 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-09 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-09 04:00 | 2030 100% ECP | 700 | 300 | 374.14 | 510 | 0 | 0 | No
2030-07-09 05:00 | 2030 100% ECP | 280 | 0 | 74.14 | 210 | 0 | 0 | No
2030-07-09 06:00 | 2030 100% ECP | -140 | -300 | -225.86 | 284.45 | 0 | 0 | No
2030-07-09 07:00 | 2030 100% ECP | -280 | -526 | -510 | 346.07 | 0 | 0 | No
2030-07-09 08:00 | 2030 100% ECP | -700 | -526 | -510 | 409.58 | 0 | 0 | Yes
2030-07-09 09:00 | 2030 100% ECP | -700 | -526 | -510 | 167.77 | 0 | 0 | Yes
2030-07-09 10:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-07-09 11:00 | 2030 100% ECP | -700 | -526 | -510 | -258.8 | 0 | 0 | Yes
2030-07-09 12:00 | 2030 100% ECP | -700 | -526 | -510 | -401.78 | 0 | 0 | Yes
2030-07-09 13:00 | 2030 100% ECP | -700 | -526 | -510 | -314.51 | 0 | 0 | Yes
2030-07-09 14:00 | 2030 100% ECP | -700 | -526 | -510 | -319.85 | 0 | 0 | Yes
2030-07-09 15:00 | 2030 100% ECP | -700 | -526 | -510 | -203.29 | 0 | 0 | Yes
2030-07-09 16:00 | 2030 100% ECP | -700 | -526 | -510 | -311.31 | 0 | 0 | Yes
2030-07-09 17:00 | 2030 100% ECP | -700 | -526 | -510 | -179.18 | 0 | 0 | Yes
2030-07-09 18:00 | 2030 100% ECP | -280 | -526 | -510 | -153.98 | 0 | 0 | No
2030-07-09 19:00 | 2030 100% ECP | -286.51 | -526 | -510 | 0 | 0 | 0 | No
2030-07-09 20:00 | 2030 100% ECP | -383.58 | -526 | -510 | 300 | 0 | 0 | No
2030-07-09 21:00 | 2030 100% ECP | -140 | -526 | -510 | 359.58 | 0 | 0 | No
2030-07-09 22:00 | 2030 100% ECP | 280 | -526 | -510 | 505.78 | 0 | 0 | No
2030-07-09 23:00 | 2030 100% ECP | 700 | -526 | -510 | 351.1 | 0 | 0 | No
2030-07-10 | 2030 100% ECP | 700 | -356.74 | -510 | 240.52 | 0 | 0 | No
2030-07-10 01:00 | 2030 100% ECP | 700 | -513.55 | -510 | 341.52 | 0 | 0 | No
2030-07-10 02:00 | 2030 100% ECP | 700 | -213.55 | -510 | 303.54 | 0 | 0 | No
2030-07-10 03:00 | 2030 100% ECP | 700 | -213.55 | -510 | 332.08 | 0 | 0 | No
2030-07-10 04:00 | 2030 100% ECP | 700 | -513.55 | -510 | 95.78 | 0 | 0 | No
2030-07-10 05:00 | 2030 100% ECP | 700 | -526 | -510 | 244.08 | 0 | 0 | No
2030-07-10 06:00 | 2030 100% ECP | 280 | -526 | -510 | 345.14 | 0 | 0 | No
2030-07-10 07:00 | 2030 100% ECP | -140 | -526 | -510 | 321.77 | 0 | 0 | Yes
2030-07-10 08:00 | 2030 100% ECP | -560 | -526 | -510 | 260.74 | 0 | 0 | Yes
2030-07-10 09:00 | 2030 100% ECP | -700 | -526 | -510 | -6.69 | 0 | 0 | Yes
2030-07-10 10:00 | 2030 100% ECP | -700 | -526 | -510 | -35.64 | 0 | 0 | Yes
2030-07-10 11:00 | 2030 100% ECP | -700 | -526 | -510 | -335.64 | 0 | 0 | Yes
2030-07-10 12:00 | 2030 100% ECP | -700 | -526 | -510 | -239.54 | 0 | 0 | Yes
2030-07-10 13:00 | 2030 100% ECP | -700 | -526 | -510 | -221.36 | 0 | 0 | Yes
2030-07-10 14:00 | 2030 100% ECP | -700 | -526 | -510 | -429.07 | 0 | 0 | Yes
2030-07-10 15:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-07-10 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-07-10 17:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-07-10 18:00 | 2030 100% ECP | -581.96 | -526 | -510 | -80.5 | 0 | 0 | No
2030-07-10 19:00 | 2030 100% ECP | -161.96 | -226 | -510 | 109.29 | 0 | 0 | No
2030-07-10 20:00 | 2030 100% ECP | 258.04 | 0 | -510 | 112.74 | 0 | 0 | Yes
2030-07-10 21:00 | 2030 100% ECP | 678.04 | 0 | -510 | 412.74 | 0 | 0 | No
2030-07-10 22:00 | 2030 100% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-07-10 23:00 | 2030 100% ECP | 700 | 0 | -510 | 342.88 | 0 | 0 | No
2030-07-11 | 2030 100% ECP | 700 | 0 | -510 | 42.88 | 0 | 0 | No
2030-07-11 01:00 | 2030 100% ECP | 700 | 0 | -510 | 25.57 | 0 | 0 | No
2030-07-11 02:00 | 2030 100% ECP | 700 | 0 | -510 | -29.79 | 0 | 0 | No
2030-07-11 03:00 | 2030 100% ECP | 700 | 0 | -210 | 0 | 0 | 0 | No
2030-07-11 04:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-07-11 05:00 | 2030 100% ECP | 560 | 0 | -510 | -97.35 | 0 | 0 | No
2030-07-11 06:00 | 2030 100% ECP | 140 | -297.5 | -510 | -29.85 | 0 | 0 | No
2030-07-11 07:00 | 2030 100% ECP | -280 | -526 | -510 | -21.69 | 0 | 0 | No
2030-07-11 08:00 | 2030 100% ECP | -700 | -526 | -510 | -1.17 | 0 | 0 | Yes
2030-07-11 09:00 | 2030 100% ECP | -700 | -526 | -510 | -21.51 | 0 | 0 | Yes
2030-07-11 10:00 | 2030 100% ECP | -700 | -526 | -510 | -66.17 | 0 | 0 | Yes
2030-07-11 11:00 | 2030 100% ECP | -700 | -526 | -510 | -38.67 | 0 | 0 | Yes
2030-07-11 12:00 | 2030 100% ECP | -700 | -526 | -510 | 70.91 | 0 | 0 | Yes
2030-07-11 13:00 | 2030 100% ECP | -700 | -526 | -510 | 45.89 | 0 | 0 | Yes
2030-07-11 14:00 | 2030 100% ECP | -700 | -526 | -510 | 31.11 | 0 | 0 | Yes
2030-07-11 15:00 | 2030 100% ECP | -700 | -526 | -510 | 121.84 | 0 | 0 | Yes
2030-07-11 16:00 | 2030 100% ECP | -280 | -526 | -510 | 147.09 | 0 | 0 | Yes
2030-07-11 17:00 | 2030 100% ECP | 140 | -526 | -510 | 242.64 | 0 | 0 | No
2030-07-11 18:00 | 2030 100% ECP | 560 | -526 | -510 | 301.95 | 0 | 0 | No
2030-07-11 19:00 | 2030 100% ECP | 700 | -304.27 | -510 | 328.49 | 0 | 0 | No
2030-07-11 20:00 | 2030 100% ECP | 700 | -4.27 | -510 | 319.04 | 0 | 0 | No
2030-07-11 21:00 | 2030 100% ECP | 700 | 0 | -510 | 187.69 | 0 | 0 | No
2030-07-11 22:00 | 2030 100% ECP | 700 | -300 | -510 | 243.57 | 0 | 0 | No
2030-07-11 23:00 | 2030 100% ECP | 700 | -417.01 | -510 | 154.67 | 0 | 0 | No
2030-07-12 | 2030 100% ECP | 700 | -421.61 | -510 | 0 | 0 | 0 | No
2030-07-12 01:00 | 2030 100% ECP | 700 | -526 | -510 | 67.76 | 0 | 0 | No
2030-07-12 02:00 | 2030 100% ECP | 700 | -526 | -510 | 23.22 | 0 | 0 | No
2030-07-12 03:00 | 2030 100% ECP | 700 | -437.27 | -510 | 23.22 | 0 | 0 | No
2030-07-12 04:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-12 05:00 | 2030 100% ECP | 560 | -526 | -510 | -29.51 | 0 | 0 | No
2030-07-12 06:00 | 2030 100% ECP | 140 | -526 | -510 | -26.38 | 0 | 0 | No
2030-07-12 07:00 | 2030 100% ECP | -280 | -526 | -510 | -32.63 | 0 | 0 | No
2030-07-12 08:00 | 2030 100% ECP | -700 | -526 | -510 | -122.59 | 0 | 0 | Yes
2030-07-12 09:00 | 2030 100% ECP | -700 | -526 | -510 | -25.81 | 0 | 0 | Yes
2030-07-12 10:00 | 2030 100% ECP | -700 | -526 | -510 | -182.15 | 0 | 0 | Yes
2030-07-12 11:00 | 2030 100% ECP | -700 | -526 | -510 | -249.36 | 0 | 0 | Yes
2030-07-12 12:00 | 2030 100% ECP | -700 | -526 | -510 | -197.63 | 0 | 0 | Yes
2030-07-12 13:00 | 2030 100% ECP | -700 | -526 | -510 | -408.83 | 0 | 0 | Yes
2030-07-12 14:00 | 2030 100% ECP | -700 | -526 | -510 | -363.29 | 0 | 0 | Yes
2030-07-12 15:00 | 2030 100% ECP | -700 | -526 | -510 | -414.95 | 0 | 0 | Yes
2030-07-12 16:00 | 2030 100% ECP | -700 | -526 | -510 | -343.4 | 0 | 0 | Yes
2030-07-12 17:00 | 2030 100% ECP | -280 | -526 | -510 | -194.38 | 0 | 0 | No
2030-07-12 18:00 | 2030 100% ECP | -700 | -526 | -510 | 5.78 | 0 | 0 | No
2030-07-12 19:00 | 2030 100% ECP | -700 | -526 | -510 | 51.66 | 0 | 0 | No
2030-07-12 20:00 | 2030 100% ECP | -700 | -526 | -510 | -87.73 | 0 | 0 | No
2030-07-12 21:00 | 2030 100% ECP | -700 | -526 | -510 | -14.39 | 0 | 0 | No
2030-07-12 22:00 | 2030 100% ECP | -280 | -526 | -510 | -20.18 | 0 | 0 | No
2030-07-12 23:00 | 2030 100% ECP | 140 | -526 | -510 | 58.65 | 0 | 0 | No
2030-07-13 | 2030 100% ECP | 368.77 | -226 | -210 | 210 | 0 | 0 | No
2030-07-13 01:00 | 2030 100% ECP | 700 | 74 | 90 | 510 | 0 | 0 | No
2030-07-13 02:00 | 2030 100% ECP | 700 | 374 | 390 | 510 | 0 | 0 | No
2030-07-13 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-13 04:00 | 2030 100% ECP | 700 | 300 | 353.15 | 485.47 | 0 | 0 | No
2030-07-13 05:00 | 2030 100% ECP | 700 | 0 | 53.15 | 185.47 | 0 | 0 | No
2030-07-13 06:00 | 2030 100% ECP | 700 | -300 | -246.85 | -114.53 | 0 | 0 | No
2030-07-13 07:00 | 2030 100% ECP | 560 | -526 | -510 | -414.53 | 0 | 0 | No
2030-07-13 08:00 | 2030 100% ECP | 140 | -526 | -510 | -480.84 | 0 | 0 | No
2030-07-13 09:00 | 2030 100% ECP | -280 | -526 | -510 | -180.84 | 0 | 0 | Yes
2030-07-13 10:00 | 2030 100% ECP | -700 | -526 | -510 | 119.16 | 0 | 0 | Yes
2030-07-13 11:00 | 2030 100% ECP | -700 | -526 | -510 | 125.78 | 0 | 0 | Yes
2030-07-13 12:00 | 2030 100% ECP | -700 | -526 | -510 | 376.1 | 0 | 0 | Yes
2030-07-13 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-07-13 14:00 | 2030 100% ECP | -700 | -526 | -510 | 502.82 | 0 | 0 | Yes
2030-07-13 15:00 | 2030 100% ECP | -700 | -226 | -360.59 | 202.82 | 0 | 0 | Yes
2030-07-13 16:00 | 2030 100% ECP | -499.75 | -526 | -510 | -97.18 | 0 | 0 | No
2030-07-13 17:00 | 2030 100% ECP | -79.75 | -526 | -510 | 0 | 0 | 0 | No
2030-07-13 18:00 | 2030 100% ECP | -79.75 | -526 | -510 | 0 | 0 | 0 | No
2030-07-13 19:00 | 2030 100% ECP | -421.8 | -526 | -510 | 0 | 0 | 0 | No
2030-07-13 20:00 | 2030 100% ECP | -421.8 | -526 | -510 | 0 | 0 | 0 | No
2030-07-13 21:00 | 2030 100% ECP | -421.8 | -526 | -510 | 0 | 0 | 0 | No
2030-07-13 22:00 | 2030 100% ECP | -26.24 | -526 | -510 | 0 | 0 | 0 | No
2030-07-13 23:00 | 2030 100% ECP | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 | 2030 100% ECP | -140 | -273.85 | -210 | 209.71 | 0 | 0 | No
2030-07-14 01:00 | 2030 100% ECP | 280 | 26.15 | 90 | 268.67 | 0 | 0 | No
2030-07-14 02:00 | 2030 100% ECP | 700 | 326.15 | 390 | 510 | 0 | 0 | No
2030-07-14 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-14 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-14 05:00 | 2030 100% ECP | 700 | 374 | 390 | 510 | 0 | 0 | No
2030-07-14 06:00 | 2030 100% ECP | 700 | 74 | 90 | 279.82 | 0 | 0 | No
2030-07-14 07:00 | 2030 100% ECP | 366.61 | -226 | -210 | 388.47 | 0 | 0 | No
2030-07-14 08:00 | 2030 100% ECP | -53.39 | -526 | -510 | 88.47 | 0 | 0 | No
2030-07-14 09:00 | 2030 100% ECP | -473.39 | -526 | -510 | -13.44 | 0 | 0 | No
2030-07-14 10:00 | 2030 100% ECP | -700 | -526 | -510 | 262.4 | 0 | 0 | No
2030-07-14 11:00 | 2030 100% ECP | -700 | -526 | -510 | 269.18 | 0 | 0 | No
2030-07-14 12:00 | 2030 100% ECP | -700 | -526 | -510 | 104.06 | 0 | 0 | No
2030-07-14 13:00 | 2030 100% ECP | -700 | -526 | -510 | -16.26 | 0 | 0 | No
2030-07-14 14:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 15:00 | 2030 100% ECP | -700 | -526 | -510 | 0.36 | 0 | 0 | No
2030-07-14 16:00 | 2030 100% ECP | -282.3 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 17:00 | 2030 100% ECP | -280 | -526 | -510 | 253.48 | 0 | 0 | No
2030-07-14 18:00 | 2030 100% ECP | -700 | -526 | -510 | 139.38 | 0 | 0 | No
2030-07-14 19:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 20:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 21:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 22:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 23:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-15 | 2030 100% ECP | -700 | -526 | -510 | 20.1 | 0 | 0 | No
2030-07-15 01:00 | 2030 100% ECP | -700 | -526 | -510 | 150.71 | 0 | 0 | No
2030-07-15 02:00 | 2030 100% ECP | -624.29 | -526 | -510 | 49.64 | 0 | 0 | No
2030-07-15 03:00 | 2030 100% ECP | -204.29 | -526 | -510 | 43.08 | 0 | 0 | No
2030-07-15 04:00 | 2030 100% ECP | 215.71 | -526 | -510 | -79.03 | 0 | 0 | No
2030-07-15 05:00 | 2030 100% ECP | 560 | -526 | -510 | 0 | 0 | 0 | Yes
2030-07-15 06:00 | 2030 100% ECP | 140 | -526 | -510 | -71.26 | 0 | 0 | No
2030-07-15 07:00 | 2030 100% ECP | -280 | -526 | -510 | 17.82 | 0 | 0 | No
2030-07-15 08:00 | 2030 100% ECP | -700 | -526 | -510 | -46.31 | 0 | 0 | Yes
2030-07-15 09:00 | 2030 100% ECP | -700 | -526 | -510 | -123.85 | 0 | 0 | Yes
2030-07-15 10:00 | 2030 100% ECP | -700 | -526 | -510 | -244.78 | 0 | 0 | Yes
2030-07-15 11:00 | 2030 100% ECP | -700 | -526 | -510 | -170.38 | 0 | 0 | Yes
2030-07-15 12:00 | 2030 100% ECP | -700 | -526 | -510 | -206.9 | 0 | 0 | Yes
2030-07-15 13:00 | 2030 100% ECP | -700 | -526 | -510 | -396.33 | 0 | 0 | Yes
2030-07-15 14:00 | 2030 100% ECP | -700 | -526 | -510 | -225.05 | 0 | 0 | Yes
2030-07-15 15:00 | 2030 100% ECP | -700 | -526 | -510 | 24.91 | 0 | 0 | Yes
2030-07-15 16:00 | 2030 100% ECP | -700 | -526 | -510 | -88.17 | 0 | 0 | Yes
2030-07-15 17:00 | 2030 100% ECP | -700 | -526 | -510 | -4.77 | 0 | 0 | Yes
2030-07-15 18:00 | 2030 100% ECP | -700 | -526 | -510 | -153.42 | 0 | 0 | No
2030-07-15 19:00 | 2030 100% ECP | -280 | -526 | -510 | -119.6 | 0 | 0 | No
2030-07-15 20:00 | 2030 100% ECP | -173.69 | -526 | -510 | 171.43 | 0 | 0 | No
2030-07-15 21:00 | 2030 100% ECP | -173.69 | -526 | -510 | 155.53 | 0 | 0 | No
2030-07-15 22:00 | 2030 100% ECP | -173.69 | -526 | -510 | 22.3 | 0 | 0 | No
2030-07-15 23:00 | 2030 100% ECP | -140 | -300 | -397.6 | 28.54 | 0 | 0 | No
2030-07-16 | 2030 100% ECP | 280 | 0 | -97.6 | 210 | 0 | 0 | No
2030-07-16 01:00 | 2030 100% ECP | 700 | 300 | 202.4 | 510 | 0 | 0 | No
2030-07-16 02:00 | 2030 100% ECP | 700 | 0 | 125.91 | 510 | 0 | 0 | No
2030-07-16 03:00 | 2030 100% ECP | 280 | 0 | 0 | 210 | 0 | 0 | No
2030-07-16 04:00 | 2030 100% ECP | 0 | 0 | -210 | 259.25 | 0 | 0 | No
2030-07-16 05:00 | 2030 100% ECP | 91.54 | -300 | -510 | 286.09 | 0 | 0 | No
2030-07-16 06:00 | 2030 100% ECP | 22.03 | -526 | -510 | 376.6 | 0 | 0 | No
2030-07-16 07:00 | 2030 100% ECP | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-07-16 08:00 | 2030 100% ECP | -700 | -526 | -510 | 444.51 | 0 | 0 | No
2030-07-16 09:00 | 2030 100% ECP | -700 | -526 | -510 | 500.15 | 0 | 0 | Yes
2030-07-16 10:00 | 2030 100% ECP | -700 | -526 | -510 | 457.87 | 0 | 0 | Yes
2030-07-16 11:00 | 2030 100% ECP | -700 | -526 | -510 | 352.33 | 0 | 0 | Yes
2030-07-16 12:00 | 2030 100% ECP | -700 | -526 | -510 | 122.09 | 0 | 0 | Yes
2030-07-16 13:00 | 2030 100% ECP | -700 | -526 | -510 | -33.47 | 0 | 0 | Yes
2030-07-16 14:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-07-16 15:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-07-16 16:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-07-16 17:00 | 2030 100% ECP | -700 | -526 | -510 | 90 | 0 | 0 | Yes
2030-07-16 18:00 | 2030 100% ECP | -700 | -526 | -510 | -17.48 | 0 | 0 | No
2030-07-16 19:00 | 2030 100% ECP | -280 | -526 | -510 | 282.52 | 0 | 0 | No
2030-07-16 20:00 | 2030 100% ECP | -7.02 | -526 | -510 | 366.85 | 0 | 0 | No
2030-07-16 21:00 | 2030 100% ECP | -82.1 | -526 | -510 | 310.77 | 0 | 0 | No
2030-07-16 22:00 | 2030 100% ECP | 0 | -526 | -510 | 393.34 | 0 | 0 | No
2030-07-16 23:00 | 2030 100% ECP | 0 | -526 | -510 | 224.66 | 0 | 0 | No
2030-07-17 | 2030 100% ECP | 0 | -454.06 | -510 | 257.75 | 0 | 0 | No
2030-07-17 01:00 | 2030 100% ECP | 0 | -154.06 | -510 | 52.18 | 0 | 0 | No
2030-07-17 02:00 | 2030 100% ECP | 0 | 0 | -368.23 | 236.48 | 0 | 0 | No
2030-07-17 03:00 | 2030 100% ECP | 0 | 0 | -510 | 125.5 | 0 | 0 | No
2030-07-17 04:00 | 2030 100% ECP | 0 | 0 | -510 | -65.2 | 0 | 0 | No
2030-07-17 05:00 | 2030 100% ECP | 0 | -300 | -510 | -78.7 | 0 | 0 | Yes
2030-07-17 06:00 | 2030 100% ECP | -280 | -526 | -510 | -36.39 | 0 | 0 | No
2030-07-17 07:00 | 2030 100% ECP | -700 | -526 | -510 | 174.01 | 0 | 0 | No
2030-07-17 08:00 | 2030 100% ECP | -700 | -526 | -510 | 465.9 | 0 | 0 | Yes
2030-07-17 09:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-07-17 10:00 | 2030 100% ECP | -700 | -526 | -510 | 503.42 | 0 | 0 | Yes
2030-07-17 11:00 | 2030 100% ECP | -700 | -526 | -510 | 508.43 | 0 | 0 | Yes
2030-07-17 12:00 | 2030 100% ECP | -700 | -526 | -510 | 508.87 | 0 | 0 | Yes
2030-07-17 13:00 | 2030 100% ECP | -700 | -526 | -510 | 473.08 | 0 | 0 | Yes
2030-07-17 14:00 | 2030 100% ECP | -700 | -526 | -510 | 448.52 | 0 | 0 | Yes
2030-07-17 15:00 | 2030 100% ECP | -700 | -526 | -510 | 463.38 | 0 | 0 | Yes
2030-07-17 16:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 17:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 18:00 | 2030 100% ECP | -347.77 | -526 | -510 | 496.3 | 0 | 0 | No
2030-07-17 19:00 | 2030 100% ECP | -123.1 | -526 | -510 | 504.03 | 0 | 0 | No
2030-07-17 20:00 | 2030 100% ECP | 0 | -526 | -510 | 498.42 | 0 | 0 | No
2030-07-17 21:00 | 2030 100% ECP | 0 | -526 | -510 | 483.96 | 0 | 0 | No
2030-07-17 22:00 | 2030 100% ECP | -197.54 | -526 | -510 | 443.85 | 0 | 0 | No
2030-07-17 23:00 | 2030 100% ECP | 0 | -526 | -510 | 292.51 | 0 | 0 | No
2030-07-18 | 2030 100% ECP | 0 | -226 | -510 | 187.7 | 0 | 0 | No
2030-07-18 01:00 | 2030 100% ECP | 0 | 0 | -510 | 252.21 | 0 | 0 | No
2030-07-18 02:00 | 2030 100% ECP | 0 | 0 | -368.35 | 230.14 | 0 | 0 | No
2030-07-18 03:00 | 2030 100% ECP | 0 | 0 | -351.52 | 173.45 | 0 | 0 | No
2030-07-18 04:00 | 2030 100% ECP | 0 | -72.18 | -510 | 140.7 | 0 | 0 | No
2030-07-18 05:00 | 2030 100% ECP | 0 | -372.18 | -510 | 33.69 | 0 | 0 | Yes
2030-07-18 06:00 | 2030 100% ECP | 0 | -526 | -510 | 108.6 | 0 | 0 | No
2030-07-18 07:00 | 2030 100% ECP | 0 | -526 | -510 | 208.42 | 0 | 0 | No
2030-07-18 08:00 | 2030 100% ECP | -280 | -526 | -510 | 158.67 | 0 | 0 | No
2030-07-18 09:00 | 2030 100% ECP | -700 | -526 | -510 | -56.26 | 0 | 0 | Yes
2030-07-18 10:00 | 2030 100% ECP | -700 | -526 | -510 | 183.7 | 0 | 0 | Yes
2030-07-18 11:00 | 2030 100% ECP | -700 | -526 | -510 | 41.14 | 0 | 0 | Yes
2030-07-18 12:00 | 2030 100% ECP | -700 | -526 | -510 | -258.86 | 0 | 0 | Yes
2030-07-18 13:00 | 2030 100% ECP | -700 | -526 | -510 | -222.42 | 0 | 0 | Yes
2030-07-18 14:00 | 2030 100% ECP | -700 | -526 | -510 | -79.8 | 0 | 0 | Yes
2030-07-18 15:00 | 2030 100% ECP | -700 | -526 | -510 | -240.92 | 0 | 0 | Yes
2030-07-18 16:00 | 2030 100% ECP | -700 | -526 | -510 | 59.08 | 0 | 0 | Yes
2030-07-18 17:00 | 2030 100% ECP | -280 | -526 | -510 | 90.35 | 0 | 0 | No
2030-07-18 18:00 | 2030 100% ECP | 59.8 | -526 | -510 | 119.46 | 0 | 0 | No
2030-07-18 19:00 | 2030 100% ECP | 479.8 | -526 | -510 | 304.3 | 0 | 0 | No
2030-07-18 20:00 | 2030 100% ECP | 700 | -526 | -510 | 182.67 | 0 | 0 | No
2030-07-18 21:00 | 2030 100% ECP | 700 | -526 | -510 | 252.08 | 0 | 0 | No
2030-07-18 22:00 | 2030 100% ECP | 700 | -526 | -510 | 310.52 | 0 | 0 | No
2030-07-18 23:00 | 2030 100% ECP | 700 | -526 | -510 | 233.81 | 0 | 0 | No
2030-07-19 | 2030 100% ECP | 700 | -526 | -510 | 117.25 | 0 | 0 | No
2030-07-19 01:00 | 2030 100% ECP | 700 | -424.17 | -510 | 87.05 | 0 | 0 | No
2030-07-19 02:00 | 2030 100% ECP | 700 | -124.17 | -510 | 58.29 | 0 | 0 | No
2030-07-19 03:00 | 2030 100% ECP | 700 | -88.5 | -510 | 136.46 | 0 | 0 | No
2030-07-19 04:00 | 2030 100% ECP | 560 | -388.5 | -510 | 106.23 | 0 | 0 | No
2030-07-19 05:00 | 2030 100% ECP | 140 | -226 | -510 | 62.63 | 0 | 0 | No
2030-07-19 06:00 | 2030 100% ECP | -280 | -526 | -510 | 156.1 | 0 | 0 | No
2030-07-19 07:00 | 2030 100% ECP | -700 | -526 | -510 | 126.44 | 0 | 0 | No
2030-07-19 08:00 | 2030 100% ECP | -700 | -526 | -510 | -173.56 | 0 | 0 | Yes
2030-07-19 09:00 | 2030 100% ECP | -700 | -526 | -510 | -205.25 | 0 | 0 | Yes
2030-07-19 10:00 | 2030 100% ECP | -700 | -526 | -510 | 1.32 | 0 | 0 | Yes
2030-07-19 11:00 | 2030 100% ECP | -700 | -526 | -510 | -298.68 | 0 | 0 | Yes
2030-07-19 12:00 | 2030 100% ECP | -700 | -526 | -510 | -243.74 | 0 | 0 | Yes
2030-07-19 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-07-19 14:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-07-19 15:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-07-19 16:00 | 2030 100% ECP | -700 | -526 | -510 | -289.07 | 0 | 0 | Yes
2030-07-19 17:00 | 2030 100% ECP | -404.91 | -526 | -510 | -259.46 | 0 | 0 | Yes
2030-07-19 18:00 | 2030 100% ECP | 15.09 | -526 | -510 | -228.33 | 0 | 0 | No
2030-07-19 19:00 | 2030 100% ECP | 435.09 | -300 | -510 | 0 | 0 | 0 | No
2030-07-19 20:00 | 2030 100% ECP | 700 | 0 | -510 | 155.24 | 0 | 0 | No
2030-07-19 21:00 | 2030 100% ECP | 700 | 0 | -510 | 288.43 | 0 | 0 | No
2030-07-19 22:00 | 2030 100% ECP | 700 | 0 | -510 | 114.61 | 0 | 0 | No
2030-07-19 23:00 | 2030 100% ECP | 700 | 0 | -510 | 114.61 | 0 | 0 | No
2030-07-20 | 2030 100% ECP | 700 | 0 | -510 | 65.75 | 0 | 0 | No
2030-07-20 01:00 | 2030 100% ECP | 700 | 0 | -510 | 137.93 | 0 | 0 | No
2030-07-20 02:00 | 2030 100% ECP | 700 | 0 | -510 | 105.34 | 0 | 0 | No
2030-07-20 03:00 | 2030 100% ECP | 700 | 0 | -510 | 55.43 | 0 | 0 | No
2030-07-20 04:00 | 2030 100% ECP | 700 | 0 | -510 | 126.36 | 0 | 0 | No
2030-07-20 05:00 | 2030 100% ECP | 654.35 | -226 | -510 | 59.25 | 0 | 0 | No
2030-07-20 06:00 | 2030 100% ECP | 234.35 | -526 | -510 | 35.36 | 0 | 0 | No
2030-07-20 07:00 | 2030 100% ECP | -185.65 | -526 | -510 | -4.48 | 0 | 0 | Yes
2030-07-20 08:00 | 2030 100% ECP | -605.65 | -526 | -510 | -116.79 | 0 | 0 | Yes
2030-07-20 09:00 | 2030 100% ECP | -700 | -526 | -510 | -148.89 | 0 | 0 | Yes
2030-07-20 10:00 | 2030 100% ECP | -700 | -526 | -510 | -214.9 | 0 | 0 | Yes
2030-07-20 11:00 | 2030 100% ECP | -700 | -526 | -510 | -187.96 | 0 | 0 | Yes
2030-07-20 12:00 | 2030 100% ECP | -700 | -526 | -510 | -108.19 | 0 | 0 | Yes
2030-07-20 13:00 | 2030 100% ECP | -700 | -526 | -510 | -84.37 | 0 | 0 | Yes
2030-07-20 14:00 | 2030 100% ECP | -700 | -526 | -510 | -264.46 | 0 | 0 | Yes
2030-07-20 15:00 | 2030 100% ECP | -700 | -526 | -510 | -223.5 | 0 | 0 | Yes
2030-07-20 16:00 | 2030 100% ECP | -280 | -526 | -510 | -51.8 | 0 | 0 | Yes
2030-07-20 17:00 | 2030 100% ECP | 140 | -526 | -510 | -2.56 | 0 | 0 | No
2030-07-20 18:00 | 2030 100% ECP | 560 | -526 | -510 | 114.15 | 0 | 0 | No
2030-07-20 19:00 | 2030 100% ECP | 700 | -526 | -510 | 122.09 | 0 | 0 | No
2030-07-20 20:00 | 2030 100% ECP | 700 | -256.7 | -510 | 188.24 | 0 | 0 | No
2030-07-20 21:00 | 2030 100% ECP | 700 | -245.97 | -510 | 204.31 | 0 | 0 | No
2030-07-20 22:00 | 2030 100% ECP | 700 | -113.85 | -510 | 262.87 | 0 | 0 | No
2030-07-20 23:00 | 2030 100% ECP | 700 | -113.85 | -510 | 262.87 | 0 | 0 | No
2030-07-21 | 2030 100% ECP | 700 | -135.33 | -510 | 180.13 | 0 | 0 | No
2030-07-21 01:00 | 2030 100% ECP | 700 | -435.33 | -510 | 0.95 | 0 | 0 | No
2030-07-21 02:00 | 2030 100% ECP | 700 | -313.71 | -510 | -33.47 | 0 | 0 | No
2030-07-21 03:00 | 2030 100% ECP | 700 | -526 | -510 | -91.07 | 0 | 0 | No
2030-07-21 04:00 | 2030 100% ECP | 700 | -526 | -510 | -101.62 | 0 | 0 | No
2030-07-21 05:00 | 2030 100% ECP | 678.25 | -526 | -510 | 85.77 | 0 | 0 | No
2030-07-21 06:00 | 2030 100% ECP | 258.25 | -526 | -510 | 64.99 | 0 | 0 | No
2030-07-21 07:00 | 2030 100% ECP | -161.75 | -526 | -510 | 64.85 | 0 | 0 | No
2030-07-21 08:00 | 2030 100% ECP | -581.75 | -526 | -510 | 5.91 | 0 | 0 | Yes
2030-07-21 09:00 | 2030 100% ECP | -700 | -526 | -510 | -170.72 | 0 | 0 | Yes
2030-07-21 10:00 | 2030 100% ECP | -700 | -526 | -510 | -137.12 | 0 | 0 | Yes
2030-07-21 11:00 | 2030 100% ECP | -700 | -526 | -510 | -76.21 | 0 | 0 | Yes
2030-07-21 12:00 | 2030 100% ECP | -700 | -526 | -510 | -72.8 | 0 | 0 | Yes
2030-07-21 13:00 | 2030 100% ECP | -700 | -526 | -510 | -85.6 | 0 | 0 | Yes
2030-07-21 14:00 | 2030 100% ECP | -700 | -526 | -510 | -137.7 | 0 | 0 | Yes
2030-07-21 15:00 | 2030 100% ECP | -700 | -526 | -510 | -133.2 | 0 | 0 | Yes
2030-07-21 16:00 | 2030 100% ECP | -420 | -526 | -510 | 166.8 | 0 | 0 | Yes
2030-07-21 17:00 | 2030 100% ECP | 0 | -526 | -510 | 224.78 | 0 | 0 | No
2030-07-21 18:00 | 2030 100% ECP | 420 | -526 | -510 | 291.74 | 0 | 0 | No
2030-07-21 19:00 | 2030 100% ECP | 700 | -526 | -510 | 306.01 | 0 | 0 | No
2030-07-21 20:00 | 2030 100% ECP | 700 | -526 | -510 | 284.08 | 0 | 0 | No
2030-07-21 21:00 | 2030 100% ECP | 700 | -526 | -510 | 223.87 | 0 | 0 | No
2030-07-21 22:00 | 2030 100% ECP | 700 | -526 | -510 | 210.56 | 0 | 0 | No
2030-07-21 23:00 | 2030 100% ECP | 700 | -526 | -510 | 90.33 | 0 | 0 | No
2030-07-22 | 2030 100% ECP | 700 | -526 | -510 | -76.76 | 0 | 0 | No
2030-07-22 01:00 | 2030 100% ECP | 700 | -526 | -510 | 97.18 | 0 | 0 | No
2030-07-22 02:00 | 2030 100% ECP | 700 | -526 | -510 | -39.76 | 0 | 0 | No
2030-07-22 03:00 | 2030 100% ECP | 700 | -526 | -510 | -151.48 | 0 | 0 | No
2030-07-22 04:00 | 2030 100% ECP | 700 | -526 | -510 | -272.49 | 0 | 0 | No
2030-07-22 05:00 | 2030 100% ECP | 700 | -526 | -510 | -376.47 | 0 | 0 | No
2030-07-22 06:00 | 2030 100% ECP | 700 | -526 | -510 | -438.24 | 0 | 0 | No
2030-07-22 07:00 | 2030 100% ECP | 606.03 | -526 | -510 | -138.24 | 0 | 0 | No
2030-07-22 08:00 | 2030 100% ECP | 186.03 | -526 | -510 | -292.83 | 0 | 0 | No
2030-07-22 09:00 | 2030 100% ECP | -233.97 | -526 | -510 | -15.76 | 0 | 0 | No
2030-07-22 10:00 | 2030 100% ECP | -653.97 | -526 | -510 | 175.48 | 0 | 0 | No
2030-07-22 11:00 | 2030 100% ECP | -700 | -526 | -510 | 193.57 | 0 | 0 | No
2030-07-22 12:00 | 2030 100% ECP | -700 | -526 | -510 | 42.7 | 0 | 0 | No
2030-07-22 13:00 | 2030 100% ECP | -700 | -526 | -510 | 291.96 | 0 | 0 | No
2030-07-22 14:00 | 2030 100% ECP | -700 | -526 | -510 | 12.14 | 0 | 0 | No
2030-07-22 15:00 | 2030 100% ECP | -340.07 | -526 | -510 | 133.65 | 0 | 0 | No
2030-07-22 16:00 | 2030 100% ECP | 79.93 | -526 | -510 | 388.62 | 0 | 0 | No
2030-07-22 17:00 | 2030 100% ECP | 499.93 | -526 | -510 | 484.87 | 0 | 0 | No
2030-07-22 18:00 | 2030 100% ECP | 700 | -526 | -510 | 495.46 | 0 | 0 | No
2030-07-22 19:00 | 2030 100% ECP | 280 | -526 | -510 | 463.59 | 0 | 0 | No
2030-07-22 20:00 | 2030 100% ECP | 0 | -526 | -510 | 332.56 | 0 | 0 | No
2030-07-22 21:00 | 2030 100% ECP | 0 | -526 | -510 | 407.59 | 0 | 0 | No
2030-07-22 22:00 | 2030 100% ECP | 280 | -526 | -510 | 149.06 | 0 | 0 | No
2030-07-22 23:00 | 2030 100% ECP | 700 | -526 | -510 | 131.08 | 0 | 0 | No
2030-07-23 | 2030 100% ECP | 700 | -526 | -510 | 58.52 | 0 | 0 | No
2030-07-23 01:00 | 2030 100% ECP | 700 | -484.75 | -510 | -10.01 | 0 | 0 | No
2030-07-23 02:00 | 2030 100% ECP | 700 | -184.75 | -510 | 59.99 | 0 | 0 | No
2030-07-23 03:00 | 2030 100% ECP | 280 | -484.75 | -510 | 33.13 | 0 | 0 | No
2030-07-23 04:00 | 2030 100% ECP | 0 | -526 | -510 | 79.76 | 0 | 0 | No
2030-07-23 05:00 | 2030 100% ECP | 266.72 | -526 | -510 | 58.39 | 0 | 0 | No
2030-07-23 06:00 | 2030 100% ECP | 686.72 | -526 | -510 | 150.47 | 0 | 0 | No
2030-07-23 07:00 | 2030 100% ECP | 266.72 | -526 | -510 | 286.1 | 0 | 0 | No
2030-07-23 08:00 | 2030 100% ECP | 239.23 | -526 | -510 | 399.62 | 0 | 0 | No
2030-07-23 09:00 | 2030 100% ECP | 279.51 | -526 | -510 | 257.93 | 0 | 0 | No
2030-07-23 10:00 | 2030 100% ECP | -140.49 | -526 | -510 | 248.8 | 0 | 0 | No
2030-07-23 11:00 | 2030 100% ECP | -560.49 | -526 | -510 | 249.68 | 0 | 0 | No
2030-07-23 12:00 | 2030 100% ECP | -700 | -526 | -510 | 279.93 | 0 | 0 | No
2030-07-23 13:00 | 2030 100% ECP | -700 | -526 | -510 | 259.37 | 0 | 0 | No
2030-07-23 14:00 | 2030 100% ECP | -280 | -526 | -510 | 228.85 | 0 | 0 | No
2030-07-23 15:00 | 2030 100% ECP | 140 | -526 | -510 | 108.65 | 0 | 0 | No
2030-07-23 16:00 | 2030 100% ECP | 320.93 | -526 | -510 | 229.93 | 0 | 0 | No
2030-07-23 17:00 | 2030 100% ECP | -99.07 | -526 | -510 | 325.57 | 0 | 0 | No
2030-07-23 18:00 | 2030 100% ECP | 320.93 | -226 | -510 | 418 | 0 | 0 | No
2030-07-23 19:00 | 2030 100% ECP | 700 | 0 | -210 | 162.64 | 0 | 0 | No
2030-07-23 20:00 | 2030 100% ECP | 700 | 0 | 0 | 371.57 | 0 | 0 | No
2030-07-23 21:00 | 2030 100% ECP | 700 | 0 | 0 | 248.41 | 0 | 0 | No
2030-07-23 22:00 | 2030 100% ECP | 700 | 0 | 0 | 297.8 | 0 | 0 | No
2030-07-23 23:00 | 2030 100% ECP | 700 | 0 | 0 | 288.94 | 0 | 0 | No
2030-07-24 | 2030 100% ECP | 700 | 0 | 168.88 | 140.98 | 0 | 0 | No
2030-07-24 01:00 | 2030 100% ECP | 700 | 0 | 0 | 109.68 | 0 | 0 | No
2030-07-24 02:00 | 2030 100% ECP | 700 | 0 | 22.07 | 218.33 | 0 | 0 | No
2030-07-24 03:00 | 2030 100% ECP | 700 | 0 | 0 | 214.68 | 0 | 0 | No
2030-07-24 04:00 | 2030 100% ECP | 700 | 0 | 300 | 228.94 | 0 | 0 | No
2030-07-24 05:00 | 2030 100% ECP | 560 | 0 | 0 | 229.09 | 0 | 0 | Yes
2030-07-24 06:00 | 2030 100% ECP | 140 | 0 | -119.66 | 280.2 | 0 | 0 | No
2030-07-24 07:00 | 2030 100% ECP | -280 | -300 | -419.66 | 377.74 | 0 | 0 | No
2030-07-24 08:00 | 2030 100% ECP | -700 | -526 | -510 | 396.92 | 0 | 0 | No
2030-07-24 09:00 | 2030 100% ECP | -700 | -526 | -510 | 379.9 | 0 | 0 | Yes
2030-07-24 10:00 | 2030 100% ECP | -700 | -526 | -510 | 295.33 | 0 | 0 | Yes
2030-07-24 11:00 | 2030 100% ECP | -700 | -526 | -510 | 372.43 | 0 | 0 | Yes
2030-07-24 12:00 | 2030 100% ECP | -700 | -526 | -510 | 265.56 | 0 | 0 | No
2030-07-24 13:00 | 2030 100% ECP | -700 | -526 | -510 | 136.71 | 0 | 0 | No
2030-07-24 14:00 | 2030 100% ECP | -700 | -526 | -510 | -18.65 | 0 | 0 | No
2030-07-24 15:00 | 2030 100% ECP | -280 | -526 | -510 | 142.61 | 0 | 0 | No
2030-07-24 16:00 | 2030 100% ECP | 140 | -526 | -510 | 278.42 | 0 | 0 | No
2030-07-24 17:00 | 2030 100% ECP | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-07-24 18:00 | 2030 100% ECP | -700 | -526 | -510 | 382.11 | 0 | 0 | No
2030-07-24 19:00 | 2030 100% ECP | -700 | -526 | -510 | 317.54 | 0 | 0 | No
2030-07-24 20:00 | 2030 100% ECP | -700 | -395 | -390 | 17.54 | 0 | 0 | No
2030-07-24 21:00 | 2030 100% ECP | -407.72 | -95 | -90 | -53.86 | 0 | 0 | No
2030-07-24 22:00 | 2030 100% ECP | 12.28 | 205 | 210 | 210 | 0 | 0 | No
2030-07-24 23:00 | 2030 100% ECP | 432.28 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 01:00 | 2030 100% ECP | 605.49 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 06:00 | 2030 100% ECP | 700 | 300 | 300 | 510 | 0 | 0 | No
2030-07-25 07:00 | 2030 100% ECP | 519.33 | 0 | 0 | 510 | 0 | 0 | No
2030-07-25 08:00 | 2030 100% ECP | 99.33 | 0 | 0 | 510 | 0 | 0 | No
2030-07-25 09:00 | 2030 100% ECP | 0 | 0 | 0 | 210 | 0 | 0 | No
2030-07-25 10:00 | 2030 100% ECP | 0 | 0 | 0 | 210 | 0 | 0 | No
2030-07-25 11:00 | 2030 100% ECP | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-07-25 12:00 | 2030 100% ECP | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-07-25 13:00 | 2030 100% ECP | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-07-25 14:00 | 2030 100% ECP | 0 | 74 | 90 | 510 | 0 | 0 | No
2030-07-25 15:00 | 2030 100% ECP | 331.36 | -226 | -210 | 510 | 0 | 0 | No
2030-07-25 16:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-25 17:00 | 2030 100% ECP | 440.98 | -526 | -510 | 510 | 0 | 0 | No
2030-07-25 18:00 | 2030 100% ECP | 20.98 | -526 | -510 | 510 | 0 | 0 | No
2030-07-25 19:00 | 2030 100% ECP | -399.02 | -526 | -510 | 510 | 0 | 0 | No
2030-07-25 20:00 | 2030 100% ECP | -397.48 | -526 | -510 | 510 | 0 | 0 | No
2030-07-25 21:00 | 2030 100% ECP | -397.03 | -435.98 | -510 | 510 | 0 | 0 | No
2030-07-25 22:00 | 2030 100% ECP | 22.97 | -135.98 | -210 | 510 | 0 | 0 | No
2030-07-25 23:00 | 2030 100% ECP | 442.97 | 164.02 | 90 | 510 | 0 | 0 | No
2030-07-26 | 2030 100% ECP | 700 | 464.02 | 390 | 510 | 0 | 0 | No
2030-07-26 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 05:00 | 2030 100% ECP | 700 | 293.31 | 510 | 510 | 0 | 0 | No
2030-07-26 06:00 | 2030 100% ECP | 420 | 110.38 | 210 | 510 | 0 | 0 | No
2030-07-26 07:00 | 2030 100% ECP | 0 | -189.62 | -90 | 510 | 0 | 0 | No
2030-07-26 08:00 | 2030 100% ECP | -420 | -489.62 | -390 | 510 | 0 | 0 | Yes
2030-07-26 09:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-07-26 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-07-26 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-07-26 12:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-07-26 13:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-07-26 14:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-07-26 15:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-07-26 16:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-07-26 17:00 | 2030 100% ECP | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-07-26 18:00 | 2030 100% ECP | -549.41 | -526 | -510 | 510 | 0 | 0 | No
2030-07-26 19:00 | 2030 100% ECP | -129.41 | -526 | -510 | 210 | 0 | 0 | No
2030-07-26 20:00 | 2030 100% ECP | -383.1 | -395 | -390 | 83.17 | 0 | 0 | No
2030-07-26 21:00 | 2030 100% ECP | -339.28 | -95 | -90 | 383.17 | 0 | 0 | No
2030-07-26 22:00 | 2030 100% ECP | 80.72 | 205 | 210 | 510 | 0 | 0 | No
2030-07-26 23:00 | 2030 100% ECP | 500.72 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 | 2030 100% ECP | 80.72 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 01:00 | 2030 100% ECP | -339.28 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 02:00 | 2030 100% ECP | -193.99 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 03:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 04:00 | 2030 100% ECP | 363.41 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 05:00 | 2030 100% ECP | 6.51 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 06:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 11:00 | 2030 100% ECP | -700 | 505 | 510 | 235.21 | 0 | 0 | Yes
2030-07-27 12:00 | 2030 100% ECP | -700 | 505 | 510 | 84.3 | 0 | 0 | Yes
2030-07-27 13:00 | 2030 100% ECP | -700 | 505 | 510 | 69.11 | 0 | 0 | Yes
2030-07-27 14:00 | 2030 100% ECP | -700 | 505 | 510 | 196.92 | 0 | 0 | Yes
2030-07-27 15:00 | 2030 100% ECP | -700 | 505 | 510 | 364.14 | 0 | 0 | Yes
2030-07-27 16:00 | 2030 100% ECP | -700 | 505 | 510 | 368.64 | 0 | 0 | Yes
2030-07-27 17:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 18:00 | 2030 100% ECP | -700 | 505 | 510 | 295.16 | 0 | 0 | Yes
2030-07-27 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 22:00 | 2030 100% ECP | -700 | 505 | 510 | 505.93 | 0 | 0 | Yes
2030-07-27 23:00 | 2030 100% ECP | -700 | 505 | 510 | 346.44 | 0 | 0 | Yes
2030-07-28 | 2030 100% ECP | -700 | 505 | 510 | 231.75 | 0 | 0 | Yes
2030-07-28 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 02:00 | 2030 100% ECP | -507.89 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 03:00 | 2030 100% ECP | -700 | 505 | 510 | 411.68 | 0 | 0 | Yes
2030-07-28 04:00 | 2030 100% ECP | -700 | 505 | 510 | 309.69 | 0 | 0 | Yes
2030-07-28 05:00 | 2030 100% ECP | -685.87 | 505 | 510 | 273.42 | 0 | 0 | Yes
2030-07-28 06:00 | 2030 100% ECP | -700 | 505 | 510 | 332.69 | 0 | 0 | Yes
2030-07-28 07:00 | 2030 100% ECP | -700 | 505 | 510 | 430.32 | 0 | 0 | Yes
2030-07-28 08:00 | 2030 100% ECP | -700 | 505 | 510 | 199.82 | 0 | 0 | Yes
2030-07-28 09:00 | 2030 100% ECP | -700 | 505 | 510 | 458.83 | 0 | 0 | Yes
2030-07-28 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 11:00 | 2030 100% ECP | -700 | 505 | 510 | 211.92 | 0 | 0 | Yes
2030-07-28 12:00 | 2030 100% ECP | -700 | 505 | 510 | 211.41 | 0 | 0 | Yes
2030-07-28 13:00 | 2030 100% ECP | -700 | 505 | 510 | 314.97 | 0 | 0 | Yes
2030-07-28 14:00 | 2030 100% ECP | -700 | 505 | 510 | 400.41 | 0 | 0 | Yes
2030-07-28 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 17:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 18:00 | 2030 100% ECP | -677.13 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 19:00 | 2030 100% ECP | -257.13 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 20:00 | 2030 100% ECP | 162.87 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 21:00 | 2030 100% ECP | 582.87 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 06:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 07:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 08:00 | 2030 100% ECP | 581.18 | 329.37 | 390 | 510 | 0 | 0 | No
2030-07-29 09:00 | 2030 100% ECP | 161.18 | 29.37 | 90 | 510 | 0 | 0 | No
2030-07-29 10:00 | 2030 100% ECP | 161.18 | -270.63 | -210 | 385.43 | 0 | 0 | No
2030-07-29 11:00 | 2030 100% ECP | 548.39 | -526 | -510 | 382.76 | 0 | 0 | No
2030-07-29 12:00 | 2030 100% ECP | 700 | -526 | -510 | 382.76 | 0 | 0 | No
2030-07-29 13:00 | 2030 100% ECP | 700 | -526 | -510 | 284.18 | 0 | 0 | No
2030-07-29 14:00 | 2030 100% ECP | 700 | -526 | -510 | 352.29 | 0 | 0 | No
2030-07-29 15:00 | 2030 100% ECP | 700 | -526 | -510 | 352.29 | 0 | 0 | No
2030-07-29 16:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-29 17:00 | 2030 100% ECP | 646.92 | -526 | -510 | 460.87 | 0 | 0 | No
2030-07-29 18:00 | 2030 100% ECP | 226.92 | -526 | -510 | 312.15 | 0 | 0 | No
2030-07-29 19:00 | 2030 100% ECP | -193.08 | -526 | -510 | 383.76 | 0 | 0 | No
2030-07-29 20:00 | 2030 100% ECP | -613.08 | -526 | -510 | 364.87 | 0 | 0 | No
2030-07-29 21:00 | 2030 100% ECP | -700 | -526 | -510 | 390.43 | 0 | 0 | No
2030-07-29 22:00 | 2030 100% ECP | -280 | -526 | -510 | 208.98 | 0 | 0 | No
2030-07-29 23:00 | 2030 100% ECP | 140 | -526 | -510 | 51.25 | 0 | 0 | No
2030-07-30 | 2030 100% ECP | 560 | -526 | -510 | 41.69 | 0 | 0 | No
2030-07-30 01:00 | 2030 100% ECP | 700 | -512.99 | -510 | -20.48 | 0 | 0 | No
2030-07-30 02:00 | 2030 100% ECP | 700 | -526 | -510 | -129.51 | 0 | 0 | No
2030-07-30 03:00 | 2030 100% ECP | 700 | -526 | -510 | -120.05 | 0 | 0 | No
2030-07-30 04:00 | 2030 100% ECP | 700 | -526 | -510 | -146.32 | 0 | 0 | No
2030-07-30 05:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-30 06:00 | 2030 100% ECP | 700 | -526 | -510 | 87.36 | 0 | 0 | No
2030-07-30 07:00 | 2030 100% ECP | 457.42 | -526 | -510 | 150.47 | 0 | 0 | No
2030-07-30 08:00 | 2030 100% ECP | 37.42 | -526 | -510 | 212.64 | 0 | 0 | No
2030-07-30 09:00 | 2030 100% ECP | -382.58 | -526 | -510 | 94.27 | 0 | 0 | Yes
2030-07-30 10:00 | 2030 100% ECP | -700 | -526 | -510 | 127.79 | 0 | 0 | Yes
2030-07-30 11:00 | 2030 100% ECP | -700 | -526 | -510 | -5.23 | 0 | 0 | Yes
2030-07-30 12:00 | 2030 100% ECP | -700 | -526 | -510 | 153.15 | 0 | 0 | Yes
2030-07-30 13:00 | 2030 100% ECP | -700 | -526 | -510 | 125.37 | 0 | 0 | Yes
2030-07-30 14:00 | 2030 100% ECP | -700 | -526 | -510 | 266 | 0 | 0 | Yes
2030-07-30 15:00 | 2030 100% ECP | -700 | -526 | -510 | 200.85 | 0 | 0 | Yes
2030-07-30 16:00 | 2030 100% ECP | -700 | -526 | -510 | 28.02 | 0 | 0 | Yes
2030-07-30 17:00 | 2030 100% ECP | -700 | -526 | -510 | -124.07 | 0 | 0 | Yes
2030-07-30 18:00 | 2030 100% ECP | -700 | -526 | -510 | -317.01 | 0 | 0 | No
2030-07-30 19:00 | 2030 100% ECP | -700 | -526 | -510 | -17.01 | 0 | 0 | No
2030-07-30 20:00 | 2030 100% ECP | -700 | -526 | -510 | -173.13 | 0 | 0 | No
2030-07-30 21:00 | 2030 100% ECP | -700 | -526 | -510 | -182.9 | 0 | 0 | No
2030-07-30 22:00 | 2030 100% ECP | -700 | -526 | -510 | 6.05 | 0 | 0 | No
2030-07-30 23:00 | 2030 100% ECP | -700 | -226 | -381.76 | -267.52 | 0 | 0 | No
2030-07-31 | 2030 100% ECP | -280 | 74 | -81.76 | 32.48 | 0 | 0 | No
2030-07-31 01:00 | 2030 100% ECP | -700 | 374 | 218.24 | 332.48 | 0 | 0 | No
2030-07-31 02:00 | 2030 100% ECP | -648.64 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 03:00 | 2030 100% ECP | -360.81 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 04:00 | 2030 100% ECP | -360.81 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 05:00 | 2030 100% ECP | 0 | 205 | 510 | 460.71 | 0 | 0 | No
2030-07-31 06:00 | 2030 100% ECP | -217.07 | 0 | 411.16 | 294.69 | 0 | 0 | No
2030-07-31 07:00 | 2030 100% ECP | -637.07 | 0 | 210 | 320.86 | 0 | 0 | No
2030-07-31 08:00 | 2030 100% ECP | -700 | 300 | 510 | 510 | 0 | 0 | Yes
2030-07-31 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-31 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-31 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-31 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-31 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-31 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-31 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-31 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-31 17:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-31 18:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 19:00 | 2030 100% ECP | 560 | 357.68 | 510 | 510 | 0 | 0 | No
2030-07-31 20:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 21:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 04:00 | 2030 100% ECP | 700 | 300 | 300 | 510 | 0 | 0 | No
2030-08-01 05:00 | 2030 100% ECP | 700 | 0 | 0 | 347.34 | 0 | 0 | No
2030-08-01 06:00 | 2030 100% ECP | 560 | -300 | -300 | 447.15 | 0 | 0 | No
2030-08-01 07:00 | 2030 100% ECP | 140 | -526 | -510 | 510 | 0 | 0 | No
2030-08-01 08:00 | 2030 100% ECP | -280 | -526 | -510 | 294.39 | 0 | 0 | Yes
2030-08-01 09:00 | 2030 100% ECP | -700 | -526 | -510 | 363.66 | 0 | 0 | Yes
2030-08-01 10:00 | 2030 100% ECP | -700 | -526 | -510 | 341.78 | 0 | 0 | Yes
2030-08-01 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-08-01 12:00 | 2030 100% ECP | -700 | -526 | -510 | 394.65 | 0 | 0 | Yes
2030-08-01 13:00 | 2030 100% ECP | -700 | -526 | -510 | 508.29 | 0 | 0 | Yes
2030-08-01 14:00 | 2030 100% ECP | -560 | -526 | -510 | 510 | 0 | 0 | Yes
2030-08-01 15:00 | 2030 100% ECP | -140 | -526 | -510 | 510 | 0 | 0 | No
2030-08-01 16:00 | 2030 100% ECP | 280 | -526 | -510 | 510 | 0 | 0 | No
2030-08-01 17:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-08-01 18:00 | 2030 100% ECP | 292.18 | -526 | -510 | 510 | 0 | 0 | No
2030-08-01 19:00 | 2030 100% ECP | -127.82 | -526 | -510 | 510 | 0 | 0 | No
2030-08-01 20:00 | 2030 100% ECP | -547.82 | -526 | -510 | 510 | 0 | 0 | No
2030-08-01 21:00 | 2030 100% ECP | -490.67 | -526 | -510 | 510 | 0 | 0 | No
2030-08-01 22:00 | 2030 100% ECP | -70.67 | -526 | -510 | 510 | 0 | 0 | No
2030-08-01 23:00 | 2030 100% ECP | 349.33 | -526 | -510 | 510 | 0 | 0 | No
2030-08-02 | 2030 100% ECP | 700 | -526 | -510 | 271.32 | 0 | 0 | No
2030-08-02 01:00 | 2030 100% ECP | 700 | -300 | -510 | 208.36 | 0 | 0 | No
2030-08-02 02:00 | 2030 100% ECP | 700 | 0 | -223.78 | 168.16 | 0 | 0 | No
2030-08-02 03:00 | 2030 100% ECP | 700 | -287.42 | -510 | 175.72 | 0 | 0 | No
2030-08-02 04:00 | 2030 100% ECP | 700 | -526 | -510 | 134.81 | 0 | 0 | No
2030-08-02 05:00 | 2030 100% ECP | 700 | -526 | -510 | 167.76 | 0 | 0 | No
2030-08-02 06:00 | 2030 100% ECP | 620.53 | -526 | -510 | 236.39 | 0 | 0 | No
2030-08-02 07:00 | 2030 100% ECP | 200.53 | -526 | -510 | 316.15 | 0 | 0 | No
2030-08-02 08:00 | 2030 100% ECP | -219.47 | -526 | -510 | 393.76 | 0 | 0 | No
2030-08-02 09:00 | 2030 100% ECP | -639.47 | -526 | -510 | 385.58 | 0 | 0 | Yes
2030-08-02 10:00 | 2030 100% ECP | -700 | -526 | -510 | 258.62 | 0 | 0 | Yes
2030-08-02 11:00 | 2030 100% ECP | -700 | -526 | -510 | 307.21 | 0 | 0 | Yes
2030-08-02 12:00 | 2030 100% ECP | -700 | -526 | -510 | 282.65 | 0 | 0 | Yes
2030-08-02 13:00 | 2030 100% ECP | -700 | -526 | -510 | 297.91 | 0 | 0 | Yes
2030-08-02 14:00 | 2030 100% ECP | -700 | -526 | -510 | 241.6 | 0 | 0 | Yes
2030-08-02 15:00 | 2030 100% ECP | -700 | -526 | -510 | 328.03 | 0 | 0 | No
2030-08-02 16:00 | 2030 100% ECP | -700 | -526 | -510 | 368.8 | 0 | 0 | No
2030-08-02 17:00 | 2030 100% ECP | -280 | -526 | -510 | 338.46 | 0 | 0 | No
2030-08-02 18:00 | 2030 100% ECP | -700 | -526 | -510 | 441.2 | 0 | 0 | No
2030-08-02 19:00 | 2030 100% ECP | -280 | -375.86 | -510 | 465.08 | 0 | 0 | No
2030-08-02 20:00 | 2030 100% ECP | 140 | -75.86 | -510 | 429.21 | 0 | 0 | No
2030-08-02 21:00 | 2030 100% ECP | 560 | 0 | -510 | 463.89 | 0 | 0 | No
2030-08-02 22:00 | 2030 100% ECP | 700 | 0 | -510 | 458.53 | 0 | 0 | No
2030-08-02 23:00 | 2030 100% ECP | 700 | 0 | -510 | 358.33 | 0 | 0 | No
2030-08-03 | 2030 100% ECP | 700 | 0 | -510 | 267.91 | 0 | 0 | No
2030-08-03 01:00 | 2030 100% ECP | 700 | 0 | -510 | 267.91 | 0 | 0 | No
2030-08-03 02:00 | 2030 100% ECP | 700 | 0 | -510 | 238.06 | 0 | 0 | No
2030-08-03 03:00 | 2030 100% ECP | 700 | 0 | -210 | 175.55 | 0 | 0 | No
2030-08-03 04:00 | 2030 100% ECP | 700 | 0 | -510 | 193.94 | 0 | 0 | No
2030-08-03 05:00 | 2030 100% ECP | 406.91 | 0 | -224.96 | 195.28 | 0 | 0 | No
2030-08-03 06:00 | 2030 100% ECP | -13.09 | -226 | -210 | 198.73 | 0 | 0 | No
2030-08-03 07:00 | 2030 100% ECP | -433.09 | -526 | -510 | 208.17 | 0 | 0 | No
2030-08-03 08:00 | 2030 100% ECP | -700 | -526 | -510 | 60.19 | 0 | 0 | Yes
2030-08-03 09:00 | 2030 100% ECP | -700 | -526 | -510 | 41.45 | 0 | 0 | Yes
2030-08-03 10:00 | 2030 100% ECP | -700 | -526 | -510 | 123.46 | 0 | 0 | Yes
2030-08-03 11:00 | 2030 100% ECP | -700 | -526 | -510 | 38.92 | 0 | 0 | Yes
2030-08-03 12:00 | 2030 100% ECP | -700 | -526 | -510 | 138.23 | 0 | 0 | Yes
2030-08-03 13:00 | 2030 100% ECP | -700 | -526 | -510 | 95.24 | 0 | 0 | Yes
2030-08-03 14:00 | 2030 100% ECP | -700 | -526 | -510 | 72.34 | 0 | 0 | Yes
2030-08-03 15:00 | 2030 100% ECP | -700 | -526 | -510 | 163.09 | 0 | 0 | Yes
2030-08-03 16:00 | 2030 100% ECP | -589.27 | -526 | -510 | 236.02 | 0 | 0 | Yes
2030-08-03 17:00 | 2030 100% ECP | -169.27 | -526 | -510 | 343.42 | 0 | 0 | No
2030-08-03 18:00 | 2030 100% ECP | 92.3 | -526 | -510 | 388.68 | 0 | 0 | No
2030-08-03 19:00 | 2030 100% ECP | 512.3 | -526 | -510 | 411.6 | 0 | 0 | No
2030-08-03 20:00 | 2030 100% ECP | 700 | -526 | -510 | 387.65 | 0 | 0 | No
2030-08-03 21:00 | 2030 100% ECP | 638.63 | -526 | -510 | 398.81 | 0 | 0 | No
2030-08-03 22:00 | 2030 100% ECP | 218.63 | -526 | -510 | 347.88 | 0 | 0 | No
2030-08-03 23:00 | 2030 100% ECP | -201.37 | -526 | -510 | 210.05 | 0 | 0 | No
2030-08-04 | 2030 100% ECP | -119.3 | -526 | -510 | 109.09 | 0 | 0 | No
2030-08-04 01:00 | 2030 100% ECP | -539.3 | -526 | -510 | 0 | 0 | 0 | No
2030-08-04 02:00 | 2030 100% ECP | -700 | -526 | -510 | 30.26 | 0 | 0 | No
2030-08-04 03:00 | 2030 100% ECP | -700 | -526 | -510 | -26.21 | 0 | 0 | Yes
2030-08-04 04:00 | 2030 100% ECP | -700 | -526 | -510 | -326.21 | 0 | 0 | Yes
2030-08-04 05:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-08-04 06:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-08-04 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-08-04 08:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-08-04 09:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-08-04 10:00 | 2030 100% ECP | -700 | 374 | 390 | 299.51 | 0 | 0 | Yes
2030-08-04 11:00 | 2030 100% ECP | -700 | 505 | 510 | 392.15 | 0 | 0 | Yes
2030-08-04 12:00 | 2030 100% ECP | -700 | 505 | 510 | 351.63 | 0 | 0 | Yes
2030-08-04 13:00 | 2030 100% ECP | -700 | 505 | 510 | 362.27 | 0 | 0 | Yes
2030-08-04 14:00 | 2030 100% ECP | -700 | 505 | 510 | 471.49 | 0 | 0 | Yes
2030-08-04 15:00 | 2030 100% ECP | -700 | 505 | 510 | 255.33 | 0 | 0 | Yes
2030-08-04 16:00 | 2030 100% ECP | -700 | 505 | 510 | 301.1 | 0 | 0 | Yes
2030-08-04 17:00 | 2030 100% ECP | -700 | 505 | 510 | 223.04 | 0 | 0 | Yes
2030-08-04 18:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 21:00 | 2030 100% ECP | -700 | 505 | 510 | 489.3 | 0 | 0 | Yes
2030-08-04 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-05 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 01:00 | 2030 100% ECP | -467.2 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 02:00 | 2030 100% ECP | -643.02 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 03:00 | 2030 100% ECP | -643.02 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 04:00 | 2030 100% ECP | -643.02 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-05 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-05 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-05 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-05 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-05 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-05 16:00 | 2030 100% ECP | -280 | 505 | 381.02 | 510 | 0 | 0 | Yes
2030-08-05 17:00 | 2030 100% ECP | 140 | 300 | 81.02 | 510 | 0 | 0 | No
2030-08-05 18:00 | 2030 100% ECP | 560 | 0 | -218.98 | 510 | 0 | 0 | No
2030-08-05 19:00 | 2030 100% ECP | 700 | 0 | -510 | 507.83 | 0 | 0 | No
2030-08-05 20:00 | 2030 100% ECP | 700 | 0 | -510 | 401.3 | 0 | 0 | No
2030-08-05 21:00 | 2030 100% ECP | 700 | 0 | -510 | 401.3 | 0 | 0 | No
2030-08-05 22:00 | 2030 100% ECP | 700 | 0 | -510 | 401.3 | 0 | 0 | No
2030-08-05 23:00 | 2030 100% ECP | 700 | 0 | -510 | 370.53 | 0 | 0 | No
2030-08-06 | 2030 100% ECP | 700 | 0 | -510 | 213.13 | 0 | 0 | No
2030-08-06 01:00 | 2030 100% ECP | 700 | -36.58 | -510 | 230.38 | 0 | 0 | No
2030-08-06 02:00 | 2030 100% ECP | 700 | -36.58 | -510 | 266.04 | 0 | 0 | No
2030-08-06 03:00 | 2030 100% ECP | 700 | -336.58 | -510 | 133.69 | 0 | 0 | No
2030-08-06 04:00 | 2030 100% ECP | 700 | -526 | -510 | 133.69 | 0 | 0 | No
2030-08-06 05:00 | 2030 100% ECP | 700 | -526 | -510 | 183.82 | 0 | 0 | No
2030-08-06 06:00 | 2030 100% ECP | 585.36 | -526 | -510 | 158.44 | 0 | 0 | No
2030-08-06 07:00 | 2030 100% ECP | 165.36 | -526 | -510 | 106.08 | 0 | 0 | No
2030-08-06 08:00 | 2030 100% ECP | -254.64 | -526 | -510 | -18.39 | 0 | 0 | Yes
2030-08-06 09:00 | 2030 100% ECP | -674.64 | -526 | -510 | -117.2 | 0 | 0 | Yes
2030-08-06 10:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-08-06 11:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-08-06 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-08-06 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-08-06 14:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-08-06 15:00 | 2030 100% ECP | -700 | -526 | -510 | -315.57 | 0 | 0 | Yes
2030-08-06 16:00 | 2030 100% ECP | -700 | -526 | -510 | -15.57 | 0 | 0 | Yes
2030-08-06 17:00 | 2030 100% ECP | -280 | -526 | -510 | 65.51 | 0 | 0 | No
2030-08-06 18:00 | 2030 100% ECP | -700 | -526 | -510 | 365.51 | 0 | 0 | No
2030-08-06 19:00 | 2030 100% ECP | -700 | -526 | -510 | 220.84 | 0 | 0 | No
2030-08-06 20:00 | 2030 100% ECP | -700 | -526 | -510 | 435.75 | 0 | 0 | No
2030-08-06 21:00 | 2030 100% ECP | -280 | -526 | -510 | 408.14 | 0 | 0 | No
2030-08-06 22:00 | 2030 100% ECP | 140 | -526 | -510 | 132.53 | 0 | 0 | No
2030-08-06 23:00 | 2030 100% ECP | 560 | -526 | -510 | 137.69 | 0 | 0 | No
2030-08-07 | 2030 100% ECP | 700 | -526 | -510 | 67.37 | 0 | 0 | No
2030-08-07 01:00 | 2030 100% ECP | 700 | -526 | -510 | 76.71 | 0 | 0 | No
2030-08-07 02:00 | 2030 100% ECP | 700 | -526 | -510 | -50.07 | 0 | 0 | No
2030-08-07 03:00 | 2030 100% ECP | 700 | -526 | -510 | -103.45 | 0 | 0 | No
2030-08-07 04:00 | 2030 100% ECP | 700 | -526 | -510 | -50.85 | 0 | 0 | No
2030-08-07 05:00 | 2030 100% ECP | 700 | -526 | -510 | -138.31 | 0 | 0 | No
2030-08-07 06:00 | 2030 100% ECP | 700 | -526 | -510 | -52.76 | 0 | 0 | No
2030-08-07 07:00 | 2030 100% ECP | 700 | -526 | -510 | 89.34 | 0 | 0 | No
2030-08-07 08:00 | 2030 100% ECP | 280 | -526 | -510 | 206.92 | 0 | 0 | No
2030-08-07 09:00 | 2030 100% ECP | -126.26 | -526 | -510 | 71.11 | 0 | 0 | No
2030-08-07 10:00 | 2030 100% ECP | -546.26 | -526 | -510 | -13.02 | 0 | 0 | No
2030-08-07 11:00 | 2030 100% ECP | -643.64 | -526 | -510 | 255.49 | 0 | 0 | No
2030-08-07 12:00 | 2030 100% ECP | -541.63 | -526 | -510 | 378.49 | 0 | 0 | No
2030-08-07 13:00 | 2030 100% ECP | -700 | -526 | -510 | 118.21 | 0 | 0 | No
2030-08-07 14:00 | 2030 100% ECP | -311.36 | -526 | -510 | 141.66 | 0 | 0 | No
2030-08-07 15:00 | 2030 100% ECP | 108.64 | -526 | -510 | 351.43 | 0 | 0 | No
2030-08-07 16:00 | 2030 100% ECP | 528.64 | -526 | -510 | 478.73 | 0 | 0 | No
2030-08-07 17:00 | 2030 100% ECP | 700 | -526 | -510 | 393.08 | 0 | 0 | No
2030-08-07 18:00 | 2030 100% ECP | 700 | -526 | -510 | 464.24 | 0 | 0 | No
2030-08-07 19:00 | 2030 100% ECP | 700 | -226 | -510 | 464.24 | 0 | 0 | No
2030-08-07 20:00 | 2030 100% ECP | 700 | -226 | -510 | 450.36 | 0 | 0 | No
2030-08-07 21:00 | 2030 100% ECP | 700 | -526 | -510 | 450.36 | 0 | 0 | No
2030-08-07 22:00 | 2030 100% ECP | 700 | -226 | -510 | 434.77 | 0 | 0 | No
2030-08-07 23:00 | 2030 100% ECP | 700 | 0 | -510 | 362.33 | 0 | 0 | No
2030-08-08 | 2030 100% ECP | 700 | 0 | -483.62 | 266.13 | 0 | 0 | No
2030-08-08 01:00 | 2030 100% ECP | 700 | 0 | -483.62 | 290.43 | 0 | 0 | No
2030-08-08 02:00 | 2030 100% ECP | 700 | 0 | -483.62 | 279.29 | 0 | 0 | No
2030-08-08 03:00 | 2030 100% ECP | 700 | 0 | -510 | 251.82 | 0 | 0 | No
2030-08-08 04:00 | 2030 100% ECP | 700 | 0 | -510 | 202.93 | 0 | 0 | No
2030-08-08 05:00 | 2030 100% ECP | 700 | 0 | -510 | 207.6 | 0 | 0 | No
2030-08-08 06:00 | 2030 100% ECP | 560 | -226 | -510 | 255.91 | 0 | 0 | No
2030-08-08 07:00 | 2030 100% ECP | 140 | -526 | -510 | 363.04 | 0 | 0 | No
2030-08-08 08:00 | 2030 100% ECP | -280 | -526 | -510 | 410.73 | 0 | 0 | Yes
2030-08-08 09:00 | 2030 100% ECP | -700 | -526 | -510 | 364.63 | 0 | 0 | Yes
2030-08-08 10:00 | 2030 100% ECP | -700 | -526 | -510 | 312.57 | 0 | 0 | Yes
2030-08-08 11:00 | 2030 100% ECP | -700 | -526 | -510 | 313.02 | 0 | 0 | Yes
2030-08-08 12:00 | 2030 100% ECP | -700 | -526 | -510 | 303.76 | 0 | 0 | Yes
2030-08-08 13:00 | 2030 100% ECP | -700 | -526 | -510 | 250.62 | 0 | 0 | Yes
2030-08-08 14:00 | 2030 100% ECP | -700 | -526 | -510 | 215.05 | 0 | 0 | Yes
2030-08-08 15:00 | 2030 100% ECP | -700 | -526 | -510 | 206.44 | 0 | 0 | Yes
2030-08-08 16:00 | 2030 100% ECP | -280 | -526 | -510 | 315.15 | 0 | 0 | Yes
2030-08-08 17:00 | 2030 100% ECP | 140 | -526 | -510 | 395.05 | 0 | 0 | No
2030-08-08 18:00 | 2030 100% ECP | 560 | -308.38 | -510 | 477.72 | 0 | 0 | No
2030-08-08 19:00 | 2030 100% ECP | 700 | -37.35 | -510 | 432.97 | 0 | 0 | No
2030-08-08 20:00 | 2030 100% ECP | 700 | 0 | -510 | 402.26 | 0 | 0 | No
2030-08-08 21:00 | 2030 100% ECP | 700 | 0 | -510 | 363.88 | 0 | 0 | No
2030-08-08 22:00 | 2030 100% ECP | 700 | 0 | -510 | 178.59 | 0 | 0 | No
2030-08-08 23:00 | 2030 100% ECP | 700 | 0 | -510 | 40.22 | 0 | 0 | No
2030-08-09 | 2030 100% ECP | 700 | 0 | -463.13 | 125.76 | 0 | 0 | No
2030-08-09 01:00 | 2030 100% ECP | 700 | 0 | -163.13 | 0 | 0 | 0 | No
2030-08-09 02:00 | 2030 100% ECP | 700 | 148.71 | 136.87 | 300 | 0 | 0 | No
2030-08-09 03:00 | 2030 100% ECP | 700 | 398.16 | 436.87 | 510 | 0 | 0 | No
2030-08-09 04:00 | 2030 100% ECP | 700 | 278.75 | 136.87 | 210 | 0 | 0 | No
2030-08-09 05:00 | 2030 100% ECP | 700 | 0 | -163.13 | -90 | 0 | 0 | No
2030-08-09 06:00 | 2030 100% ECP | 698.22 | -226 | -463.13 | -390 | 0 | 0 | No
2030-08-09 07:00 | 2030 100% ECP | 278.22 | -526 | -510 | -277.9 | 0 | 0 | No
2030-08-09 08:00 | 2030 100% ECP | -141.78 | -526 | -510 | -96.48 | 0 | 0 | Yes
2030-08-09 09:00 | 2030 100% ECP | -561.78 | -526 | -510 | 141.11 | 0 | 0 | Yes
2030-08-09 10:00 | 2030 100% ECP | -700 | -526 | -510 | 86.23 | 0 | 0 | Yes
2030-08-09 11:00 | 2030 100% ECP | -700 | -526 | -510 | 22.82 | 0 | 0 | Yes
2030-08-09 12:00 | 2030 100% ECP | -700 | -526 | -510 | 15.16 | 0 | 0 | Yes
2030-08-09 13:00 | 2030 100% ECP | -700 | -526 | -510 | 59.38 | 0 | 0 | Yes
2030-08-09 14:00 | 2030 100% ECP | -700 | -526 | -510 | 241.82 | 0 | 0 | Yes
2030-08-09 15:00 | 2030 100% ECP | -700 | -526 | -510 | 291.56 | 0 | 0 | Yes
2030-08-09 16:00 | 2030 100% ECP | -622.05 | -526 | -510 | 403.3 | 0 | 0 | Yes
2030-08-09 17:00 | 2030 100% ECP | -202.05 | -526 | -510 | 510 | 0 | 0 | No
2030-08-09 18:00 | 2030 100% ECP | 217.95 | -226 | -510 | 475.46 | 0 | 0 | No
2030-08-09 19:00 | 2030 100% ECP | 637.95 | 0 | -510 | 261.86 | 0 | 0 | No
2030-08-09 20:00 | 2030 100% ECP | 700 | 0 | -510 | 346.13 | 0 | 0 | No
2030-08-09 21:00 | 2030 100% ECP | 700 | 0 | -510 | 285.01 | 0 | 0 | No
2030-08-09 22:00 | 2030 100% ECP | 700 | 0 | -510 | 167.76 | 0 | 0 | No
2030-08-09 23:00 | 2030 100% ECP | 700 | 0 | -510 | 142.63 | 0 | 0 | No
2030-08-10 | 2030 100% ECP | 700 | 0 | -510 | -157.37 | 0 | 0 | No
2030-08-10 01:00 | 2030 100% ECP | 700 | 0 | -510 | -457.37 | 0 | 0 | No
2030-08-10 02:00 | 2030 100% ECP | 700 | 0 | -510 | -510 | 0 | 0 | No
2030-08-10 03:00 | 2030 100% ECP | 700 | 0 | -510 | -443.44 | 0 | 0 | No
2030-08-10 04:00 | 2030 100% ECP | 700 | 0 | -510 | -143.44 | 0 | 0 | No
2030-08-10 05:00 | 2030 100% ECP | 700 | 0 | -510 | -206.43 | 0 | 0 | No
2030-08-10 06:00 | 2030 100% ECP | 700 | -226 | -510 | -341.19 | 0 | 0 | No
2030-08-10 07:00 | 2030 100% ECP | 700 | -526 | -510 | -191.3 | 0 | 0 | No
2030-08-10 08:00 | 2030 100% ECP | 700 | -526 | -510 | 61.62 | 0 | 0 | No
2030-08-10 09:00 | 2030 100% ECP | 700 | -526 | -510 | 97.68 | 0 | 0 | No
2030-08-10 10:00 | 2030 100% ECP | 700 | -526 | -510 | 28.41 | 0 | 0 | No
2030-08-10 11:00 | 2030 100% ECP | 700 | -526 | -510 | 118.14 | 0 | 0 | No
2030-08-10 12:00 | 2030 100% ECP | 700 | -526 | -510 | 180.76 | 0 | 0 | No
2030-08-10 13:00 | 2030 100% ECP | 700 | -526 | -510 | 99.88 | 0 | 0 | No
2030-08-10 14:00 | 2030 100% ECP | 700 | -526 | -510 | 104.06 | 0 | 0 | No
2030-08-10 15:00 | 2030 100% ECP | 700 | -526 | -510 | 128.81 | 0 | 0 | No
2030-08-10 16:00 | 2030 100% ECP | 643.15 | -526 | -510 | 176.99 | 0 | 0 | No
2030-08-10 17:00 | 2030 100% ECP | 223.15 | -526 | -510 | 72.31 | 0 | 0 | No
2030-08-10 18:00 | 2030 100% ECP | 643.15 | -526 | -510 | 166.41 | 0 | 0 | No
2030-08-10 19:00 | 2030 100% ECP | 700 | -279.43 | -510 | -133.59 | 0 | 0 | No
2030-08-10 20:00 | 2030 100% ECP | 700 | 0 | -510 | 159.76 | 0 | 0 | No
2030-08-10 21:00 | 2030 100% ECP | 700 | 0 | -510 | 176.99 | 0 | 0 | No
2030-08-10 22:00 | 2030 100% ECP | 700 | -10.07 | -510 | -63.24 | 0 | 0 | No
2030-08-10 23:00 | 2030 100% ECP | 700 | -310.07 | -510 | 87.93 | 0 | 0 | No
2030-08-11 | 2030 100% ECP | 700 | -332.15 | -510 | -19.3 | 0 | 0 | No
2030-08-11 01:00 | 2030 100% ECP | 700 | -179.51 | -510 | 36.4 | 0 | 0 | No
2030-08-11 02:00 | 2030 100% ECP | 700 | -419.57 | -510 | 18.58 | 0 | 0 | No
2030-08-11 03:00 | 2030 100% ECP | 700 | -419.57 | -510 | 2.89 | 0 | 0 | No
2030-08-11 04:00 | 2030 100% ECP | 700 | -119.57 | -510 | 15.59 | 0 | 0 | No
2030-08-11 05:00 | 2030 100% ECP | 700 | -226 | -510 | -45.85 | 0 | 0 | No
2030-08-11 06:00 | 2030 100% ECP | 560 | -526 | -510 | -58.21 | 0 | 0 | No
2030-08-11 07:00 | 2030 100% ECP | 140 | -526 | -510 | -43.05 | 0 | 0 | No
2030-08-11 08:00 | 2030 100% ECP | -280 | -526 | -510 | -89.25 | 0 | 0 | Yes
2030-08-11 09:00 | 2030 100% ECP | -700 | -526 | -510 | -157.55 | 0 | 0 | Yes
2030-08-11 10:00 | 2030 100% ECP | -700 | -526 | -510 | -224.93 | 0 | 0 | Yes
2030-08-11 11:00 | 2030 100% ECP | -700 | -526 | -510 | -207.13 | 0 | 0 | Yes
2030-08-11 12:00 | 2030 100% ECP | -700 | -526 | -510 | -173.94 | 0 | 0 | Yes
2030-08-11 13:00 | 2030 100% ECP | -700 | -526 | -510 | -62.09 | 0 | 0 | Yes
2030-08-11 14:00 | 2030 100% ECP | -700 | -526 | -510 | -63.97 | 0 | 0 | Yes
2030-08-11 15:00 | 2030 100% ECP | -700 | -526 | -510 | -58.82 | 0 | 0 | Yes
2030-08-11 16:00 | 2030 100% ECP | -568.12 | -526 | -510 | 23.22 | 0 | 0 | No
2030-08-11 17:00 | 2030 100% ECP | -676.44 | -526 | -510 | 117.04 | 0 | 0 | No
2030-08-11 18:00 | 2030 100% ECP | -256.44 | -226 | -510 | 156.6 | 0 | 0 | No
2030-08-11 19:00 | 2030 100% ECP | 163.56 | 0 | -510 | 163.84 | 0 | 0 | No
2030-08-11 20:00 | 2030 100% ECP | 583.56 | 0 | -510 | 169.92 | 0 | 0 | No
2030-08-11 21:00 | 2030 100% ECP | 700 | 0 | -510 | 204.35 | 0 | 0 | No
2030-08-11 22:00 | 2030 100% ECP | 700 | -300 | -510 | 154.46 | 0 | 0 | No
2030-08-11 23:00 | 2030 100% ECP | 700 | 0 | -510 | 53.73 | 0 | 0 | No
2030-08-12 | 2030 100% ECP | 700 | -226 | -510 | 36.74 | 0 | 0 | No
2030-08-12 01:00 | 2030 100% ECP | 700 | -526 | -510 | -89.67 | 0 | 0 | No
2030-08-12 02:00 | 2030 100% ECP | 700 | -526 | -510 | -53.5 | 0 | 0 | No
2030-08-12 03:00 | 2030 100% ECP | 700 | -526 | -510 | -47.45 | 0 | 0 | No
2030-08-12 04:00 | 2030 100% ECP | 700 | -226 | -510 | -180.31 | 0 | 0 | No
2030-08-12 05:00 | 2030 100% ECP | 700 | -526 | -510 | -42.95 | 0 | 0 | No
2030-08-12 06:00 | 2030 100% ECP | 694.91 | -444.9 | -510 | -2.55 | 0 | 0 | No
2030-08-12 07:00 | 2030 100% ECP | 274.91 | -526 | -510 | 81.64 | 0 | 0 | No
2030-08-12 08:00 | 2030 100% ECP | -145.09 | -526 | -510 | 162.09 | 0 | 0 | Yes
2030-08-12 09:00 | 2030 100% ECP | -565.09 | -526 | -510 | 94.62 | 0 | 0 | Yes
2030-08-12 10:00 | 2030 100% ECP | -700 | -526 | -510 | -66.23 | 0 | 0 | Yes
2030-08-12 11:00 | 2030 100% ECP | -700 | -526 | -510 | -75.76 | 0 | 0 | Yes
2030-08-12 12:00 | 2030 100% ECP | -700 | -526 | -510 | -93.81 | 0 | 0 | Yes
2030-08-12 13:00 | 2030 100% ECP | -700 | -526 | -510 | -79.95 | 0 | 0 | Yes
2030-08-12 14:00 | 2030 100% ECP | -700 | -526 | -510 | -72.59 | 0 | 0 | Yes
2030-08-12 15:00 | 2030 100% ECP | -700 | -526 | -510 | -110.69 | 0 | 0 | Yes
2030-08-12 16:00 | 2030 100% ECP | -592.51 | -526 | -510 | 57.65 | 0 | 0 | No
2030-08-12 17:00 | 2030 100% ECP | -172.51 | -526 | -510 | 104.65 | 0 | 0 | No
2030-08-12 18:00 | 2030 100% ECP | -592.51 | -526 | -510 | -30.53 | 0 | 0 | No
2030-08-12 19:00 | 2030 100% ECP | -700 | -526 | -510 | -137.36 | 0 | 0 | No
2030-08-12 20:00 | 2030 100% ECP | -700 | -526 | -510 | -248.47 | 0 | 0 | No
2030-08-12 21:00 | 2030 100% ECP | -462.86 | -526 | -510 | -125.13 | 0 | 0 | No
2030-08-12 22:00 | 2030 100% ECP | -42.86 | -526 | -510 | -85.53 | 0 | 0 | No
2030-08-12 23:00 | 2030 100% ECP | 377.14 | -526 | -510 | 14.32 | 0 | 0 | No
2030-08-13 | 2030 100% ECP | 700 | -272.02 | -510 | -4.64 | 0 | 0 | No
2030-08-13 01:00 | 2030 100% ECP | 700 | -51.62 | -510 | 11.36 | 0 | 0 | No
2030-08-13 02:00 | 2030 100% ECP | 700 | -351.62 | -510 | 56.44 | 0 | 0 | No
2030-08-13 03:00 | 2030 100% ECP | 700 | -296.96 | -510 | -2 | 0 | 0 | No
2030-08-13 04:00 | 2030 100% ECP | 700 | -526 | -510 | -28.75 | 0 | 0 | No
2030-08-13 05:00 | 2030 100% ECP | 700 | -526 | -510 | -229.42 | 0 | 0 | No
2030-08-13 06:00 | 2030 100% ECP | 661.39 | -526 | -510 | -159.86 | 0 | 0 | No
2030-08-13 07:00 | 2030 100% ECP | 588.94 | -526 | -510 | 140.14 | 0 | 0 | No
2030-08-13 08:00 | 2030 100% ECP | 529.22 | -526 | -510 | 191.48 | 0 | 0 | No
2030-08-13 09:00 | 2030 100% ECP | 109.22 | -526 | -510 | 85.11 | 0 | 0 | No
2030-08-13 10:00 | 2030 100% ECP | -310.78 | -526 | -510 | 41.5 | 0 | 0 | No
2030-08-13 11:00 | 2030 100% ECP | -700 | -526 | -510 | 117.64 | 0 | 0 | No
2030-08-13 12:00 | 2030 100% ECP | -700 | -526 | -510 | 25.67 | 0 | 0 | No
2030-08-13 13:00 | 2030 100% ECP | -700 | -526 | -510 | -88.35 | 0 | 0 | No
2030-08-13 14:00 | 2030 100% ECP | -700 | -526 | -510 | -222.76 | 0 | 0 | No
2030-08-13 15:00 | 2030 100% ECP | -700 | -526 | -510 | -360.69 | 0 | 0 | No
2030-08-13 16:00 | 2030 100% ECP | -453.5 | -526 | -510 | -165.93 | 0 | 0 | No
2030-08-13 17:00 | 2030 100% ECP | -700 | -526 | -510 | 134.07 | 0 | 0 | No
2030-08-13 18:00 | 2030 100% ECP | -280 | -226 | -510 | 200.02 | 0 | 0 | No
2030-08-13 19:00 | 2030 100% ECP | 140 | 0 | -510 | 8.12 | 0 | 0 | No
2030-08-13 20:00 | 2030 100% ECP | 560 | 0 | -510 | -144.42 | 0 | 0 | No
2030-08-13 21:00 | 2030 100% ECP | 700 | 0 | -510 | -124.47 | 0 | 0 | No
2030-08-13 22:00 | 2030 100% ECP | 700 | 0 | -510 | -34.75 | 0 | 0 | No
2030-08-13 23:00 | 2030 100% ECP | 700 | 0 | -510 | -246.37 | 0 | 0 | No
2030-08-14 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-14 01:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-14 02:00 | 2030 100% ECP | 700 | 0 | -389.73 | 128.3 | 0 | 0 | No
2030-08-14 03:00 | 2030 100% ECP | 700 | 0 | -89.73 | 0 | 0 | 0 | No
2030-08-14 04:00 | 2030 100% ECP | 700 | 0 | -389.73 | 96.09 | 0 | 0 | No
2030-08-14 05:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-14 06:00 | 2030 100% ECP | 700 | -192.55 | -210 | 0 | 0 | 0 | No
2030-08-14 07:00 | 2030 100% ECP | 280 | -492.55 | -510 | -110.46 | 0 | 0 | No
2030-08-14 08:00 | 2030 100% ECP | -140 | -526 | -510 | 104.79 | 0 | 0 | No
2030-08-14 09:00 | 2030 100% ECP | -560 | -526 | -510 | 208.62 | 0 | 0 | Yes
2030-08-14 10:00 | 2030 100% ECP | -700 | -526 | -510 | 139.53 | 0 | 0 | Yes
2030-08-14 11:00 | 2030 100% ECP | -700 | -526 | -510 | 138.19 | 0 | 0 | Yes
2030-08-14 12:00 | 2030 100% ECP | -700 | -526 | -510 | 117.62 | 0 | 0 | Yes
2030-08-14 13:00 | 2030 100% ECP | -700 | -526 | -510 | 77.18 | 0 | 0 | Yes
2030-08-14 14:00 | 2030 100% ECP | -700 | -526 | -510 | 90.7 | 0 | 0 | Yes
2030-08-14 15:00 | 2030 100% ECP | -700 | -526 | -510 | 134.94 | 0 | 0 | Yes
2030-08-14 16:00 | 2030 100% ECP | -280 | -526 | -510 | 219.34 | 0 | 0 | Yes
2030-08-14 17:00 | 2030 100% ECP | 140 | -526 | -510 | 373.22 | 0 | 0 | No
2030-08-14 18:00 | 2030 100% ECP | 560 | -226 | -210 | 385.59 | 0 | 0 | No
2030-08-14 19:00 | 2030 100% ECP | 700 | -27.1 | -510 | 374.83 | 0 | 0 | No
2030-08-14 20:00 | 2030 100% ECP | 700 | 0 | -300 | 366.38 | 0 | 0 | No
2030-08-14 21:00 | 2030 100% ECP | 700 | 0 | 0 | 367.73 | 0 | 0 | No
2030-08-14 22:00 | 2030 100% ECP | 700 | 0 | 0 | 280.19 | 0 | 0 | No
2030-08-14 23:00 | 2030 100% ECP | 700 | 0 | 0 | 41.85 | 0 | 0 | No
2030-08-15 | 2030 100% ECP | 700 | 0 | -300 | 0 | 0 | 0 | No
2030-08-15 01:00 | 2030 100% ECP | 700 | 0 | -286.7 | 0 | 0 | 0 | No
2030-08-15 02:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-15 03:00 | 2030 100% ECP | 700 | 0 | -72.39 | 0 | 0 | 0 | No
2030-08-15 04:00 | 2030 100% ECP | 700 | 0 | -82.2 | 0 | 0 | 0 | No
2030-08-15 05:00 | 2030 100% ECP | 700 | 0 | -82.2 | 0 | 0 | 0 | No
2030-08-15 06:00 | 2030 100% ECP | 700 | 0 | -382.2 | 0 | 0 | 0 | No
2030-08-15 07:00 | 2030 100% ECP | 700 | -226 | -510 | 0 | 0 | 0 | No
2030-08-15 08:00 | 2030 100% ECP | 634.1 | -526 | -510 | 149.73 | 0 | 0 | No
2030-08-15 09:00 | 2030 100% ECP | 214.1 | -526 | -510 | 135.18 | 0 | 0 | No
2030-08-15 10:00 | 2030 100% ECP | -205.9 | -526 | -510 | 155.03 | 0 | 0 | No
2030-08-15 11:00 | 2030 100% ECP | -625.9 | -526 | -510 | 123.43 | 0 | 0 | No
2030-08-15 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-08-15 13:00 | 2030 100% ECP | -560 | -526 | -510 | 0 | 0 | 0 | No
2030-08-15 14:00 | 2030 100% ECP | -140 | -526 | -510 | 0 | 0 | 0 | No
2030-08-15 15:00 | 2030 100% ECP | 280 | -526 | -510 | 0 | 0 | 0 | No
2030-08-15 16:00 | 2030 100% ECP | 700 | -526 | -510 | 195.54 | 0 | 0 | No
2030-08-15 17:00 | 2030 100% ECP | 700 | -526 | -510 | -104.46 | 0 | 0 | No
2030-08-15 18:00 | 2030 100% ECP | 700 | -526 | -510 | -195 | 0 | 0 | No
2030-08-15 19:00 | 2030 100% ECP | 700 | -526 | -510 | -495 | 0 | 0 | No
2030-08-15 20:00 | 2030 100% ECP | 700 | -526 | -510 | -268.23 | 0 | 0 | No
2030-08-15 21:00 | 2030 100% ECP | 700 | -226 | -210 | 0 | 0 | 0 | No
2030-08-15 22:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-15 23:00 | 2030 100% ECP | 700 | 0 | 0 | -229.56 | 0 | 0 | No
2030-08-16 | 2030 100% ECP | 700 | 0 | 115.65 | -112.54 | 0 | 0 | No
2030-08-16 01:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 02:00 | 2030 100% ECP | 700 | 0 | 164.89 | 0 | 0 | 0 | No
2030-08-16 03:00 | 2030 100% ECP | 700 | 0 | 263.53 | 0 | 0 | 0 | No
2030-08-16 04:00 | 2030 100% ECP | 700 | 0 | 54.9 | 0 | 0 | 0 | No
2030-08-16 05:00 | 2030 100% ECP | 700 | 0 | -72.34 | 0 | 0 | 0 | No
2030-08-16 06:00 | 2030 100% ECP | 700 | 0 | 168.47 | 0 | 0 | 0 | No
2030-08-16 07:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 08:00 | 2030 100% ECP | 700 | -226 | -300 | -161.15 | 0 | 0 | No
2030-08-16 09:00 | 2030 100% ECP | 700 | -526 | -510 | -139 | 0 | 0 | No
2030-08-16 10:00 | 2030 100% ECP | 700 | -526 | -510 | -150.26 | 0 | 0 | No
2030-08-16 11:00 | 2030 100% ECP | 700 | -526 | -510 | -94.3 | 0 | 0 | No
2030-08-16 12:00 | 2030 100% ECP | 700 | -526 | -510 | -151.9 | 0 | 0 | No
2030-08-16 13:00 | 2030 100% ECP | 700 | -526 | -510 | -72.56 | 0 | 0 | No
2030-08-16 14:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-08-16 15:00 | 2030 100% ECP | 700 | -526 | -510 | -152.75 | 0 | 0 | No
2030-08-16 16:00 | 2030 100% ECP | 700 | -526 | -510 | -59.6 | 0 | 0 | No
2030-08-16 17:00 | 2030 100% ECP | 700 | -526 | -510 | -84.16 | 0 | 0 | No
2030-08-16 18:00 | 2030 100% ECP | 700 | -526 | -510 | -384.16 | 0 | 0 | No
2030-08-16 19:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-16 20:00 | 2030 100% ECP | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-08-16 21:00 | 2030 100% ECP | 700 | 0 | 90 | 90 | 0 | 0 | No
2030-08-16 22:00 | 2030 100% ECP | 700 | 0 | 390 | 319.51 | 0 | 0 | No
2030-08-16 23:00 | 2030 100% ECP | 700 | 0 | 510 | 256.11 | 0 | 0 | No
2030-08-17 | 2030 100% ECP | 700 | 0 | 510 | -7.49 | 0 | 0 | No
2030-08-17 01:00 | 2030 100% ECP | 700 | 0 | 510 | -118.89 | 0 | 0 | No
2030-08-17 02:00 | 2030 100% ECP | 700 | 0 | 510 | -35.61 | 0 | 0 | No
2030-08-17 03:00 | 2030 100% ECP | 700 | 0 | 510 | -149.92 | 0 | 0 | No
2030-08-17 04:00 | 2030 100% ECP | 700 | 0 | 510 | -95.6 | 0 | 0 | No
2030-08-17 05:00 | 2030 100% ECP | 700 | 0 | 510 | -6.85 | 0 | 0 | No
2030-08-17 06:00 | 2030 100% ECP | 700 | 0 | 368.79 | -306.85 | 0 | 0 | No
2030-08-17 07:00 | 2030 100% ECP | 700 | 0 | 307.92 | -6.85 | 0 | 0 | No
2030-08-17 08:00 | 2030 100% ECP | 700 | 0 | 7.92 | 4.93 | 0 | 0 | No
2030-08-17 09:00 | 2030 100% ECP | 700 | 0 | -292.08 | 80.91 | 0 | 0 | No
2030-08-17 10:00 | 2030 100% ECP | 700 | -56.46 | -510 | -68.48 | 0 | 0 | No
2030-08-17 11:00 | 2030 100% ECP | 700 | -302.11 | -510 | 79.07 | 0 | 0 | No
2030-08-17 12:00 | 2030 100% ECP | 700 | -262.16 | -510 | -8.99 | 0 | 0 | No
2030-08-17 13:00 | 2030 100% ECP | 700 | -526 | -510 | -10.98 | 0 | 0 | No
2030-08-17 14:00 | 2030 100% ECP | 700 | -526 | -510 | -41.24 | 0 | 0 | No
2030-08-17 15:00 | 2030 100% ECP | 700 | -526 | -510 | -18.07 | 0 | 0 | No
2030-08-17 16:00 | 2030 100% ECP | 700 | -300 | -462.83 | 29.73 | 0 | 0 | No
2030-08-17 17:00 | 2030 100% ECP | 700 | 0 | -162.83 | 329.73 | 0 | 0 | No
2030-08-17 18:00 | 2030 100% ECP | 700 | 0 | 137.17 | 462.91 | 0 | 0 | No
2030-08-17 19:00 | 2030 100% ECP | 700 | 0 | 437.17 | 470.8 | 0 | 0 | No
2030-08-17 20:00 | 2030 100% ECP | 700 | 0 | 510 | 470.8 | 0 | 0 | No
2030-08-17 21:00 | 2030 100% ECP | 700 | 0 | 510 | 470.8 | 0 | 0 | No
2030-08-17 22:00 | 2030 100% ECP | 700 | 0 | 510 | 300 | 0 | 0 | No
2030-08-17 23:00 | 2030 100% ECP | 700 | 0 | 373.41 | 0 | 0 | 0 | No
2030-08-18 | 2030 100% ECP | 700 | 0 | 73.41 | 0 | 0 | 0 | No
2030-08-18 01:00 | 2030 100% ECP | 700 | 0 | 208.43 | 0 | 0 | 0 | No
2030-08-18 02:00 | 2030 100% ECP | 700 | 0 | 102.11 | 2.52 | 0 | 0 | No
2030-08-18 03:00 | 2030 100% ECP | 700 | 0 | 250.99 | 0 | 0 | 0 | No
2030-08-18 04:00 | 2030 100% ECP | 700 | 0 | 0 | 92.92 | 0 | 0 | No
2030-08-18 05:00 | 2030 100% ECP | 700 | 0 | 151.15 | 67.41 | 0 | 0 | No
2030-08-18 06:00 | 2030 100% ECP | 700 | 0 | -14.29 | 73.13 | 0 | 0 | No
2030-08-18 07:00 | 2030 100% ECP | 700 | -226 | -314.29 | 114.02 | 0 | 0 | No
2030-08-18 08:00 | 2030 100% ECP | 700 | -526 | -510 | 102.38 | 0 | 0 | No
2030-08-18 09:00 | 2030 100% ECP | 280 | -526 | -510 | 140.26 | 0 | 0 | No
2030-08-18 10:00 | 2030 100% ECP | -140 | -526 | -510 | 152.64 | 0 | 0 | No
2030-08-18 11:00 | 2030 100% ECP | -366.82 | -526 | -510 | 174.85 | 0 | 0 | No
2030-08-18 12:00 | 2030 100% ECP | -700 | -526 | -510 | 291.61 | 0 | 0 | No
2030-08-18 13:00 | 2030 100% ECP | -700 | -526 | -510 | 262.01 | 0 | 0 | No
2030-08-18 14:00 | 2030 100% ECP | -560 | -526 | -510 | 248.71 | 0 | 0 | No
2030-08-18 15:00 | 2030 100% ECP | -140 | -526 | -510 | 235.79 | 0 | 0 | No
2030-08-18 16:00 | 2030 100% ECP | 280 | -526 | -510 | 266.88 | 0 | 0 | No
2030-08-18 17:00 | 2030 100% ECP | 700 | -526 | -510 | 351.87 | 0 | 0 | No
2030-08-18 18:00 | 2030 100% ECP | 700 | -226 | -510 | 309.81 | 0 | 0 | No
2030-08-18 19:00 | 2030 100% ECP | 700 | 0 | -510 | 115.31 | 0 | 0 | No
2030-08-18 20:00 | 2030 100% ECP | 700 | 0 | -510 | 338.68 | 0 | 0 | No
2030-08-18 21:00 | 2030 100% ECP | 700 | 0 | -510 | 393.42 | 0 | 0 | No
2030-08-18 22:00 | 2030 100% ECP | 700 | 0 | -233.58 | 336.85 | 0 | 0 | No
2030-08-18 23:00 | 2030 100% ECP | 700 | 0 | -510 | 244.17 | 0 | 0 | No
2030-08-19 | 2030 100% ECP | 700 | 0 | -510 | 262.27 | 0 | 0 | No
2030-08-19 01:00 | 2030 100% ECP | 700 | 0 | -510 | 222.13 | 0 | 0 | No
2030-08-19 02:00 | 2030 100% ECP | 700 | 0 | -510 | 200.97 | 0 | 0 | No
2030-08-19 03:00 | 2030 100% ECP | 700 | 0 | -510 | 184.48 | 0 | 0 | No
2030-08-19 04:00 | 2030 100% ECP | 700 | 0 | -510 | 62.13 | 0 | 0 | No
2030-08-19 05:00 | 2030 100% ECP | 700 | 0 | -510 | 61.07 | 0 | 0 | No
2030-08-19 06:00 | 2030 100% ECP | 700 | -59.03 | -510 | -45.93 | 0 | 0 | No
2030-08-19 07:00 | 2030 100% ECP | 700 | -359.03 | -510 | 58.8 | 0 | 0 | No
2030-08-19 08:00 | 2030 100% ECP | 700 | -526 | -510 | -46.12 | 0 | 0 | No
2030-08-19 09:00 | 2030 100% ECP | 560 | -526 | -510 | -38.37 | 0 | 0 | No
2030-08-19 10:00 | 2030 100% ECP | 140 | -526 | -510 | 88.91 | 0 | 0 | No
2030-08-19 11:00 | 2030 100% ECP | -280 | -526 | -510 | 50.26 | 0 | 0 | No
2030-08-19 12:00 | 2030 100% ECP | -700 | -226 | -210 | 350.26 | 0 | 0 | Yes
2030-08-19 13:00 | 2030 100% ECP | -700 | 74 | 90 | 442.83 | 0 | 0 | Yes
2030-08-19 14:00 | 2030 100% ECP | -700 | 374 | 390 | 259.6 | 0 | 0 | Yes
2030-08-19 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-19 16:00 | 2030 100% ECP | -700 | 505 | 510 | 422.63 | 0 | 0 | Yes
2030-08-19 17:00 | 2030 100% ECP | -700 | 505 | 510 | 340.31 | 0 | 0 | Yes
2030-08-19 18:00 | 2030 100% ECP | -700 | 505 | 510 | 203.45 | 0 | 0 | Yes
2030-08-19 19:00 | 2030 100% ECP | -700 | 505 | 510 | 184.09 | 0 | 0 | Yes
2030-08-19 20:00 | 2030 100% ECP | -700 | 505 | 510 | 137.31 | 0 | 0 | Yes
2030-08-19 21:00 | 2030 100% ECP | -700 | 505 | 510 | 300.32 | 0 | 0 | Yes
2030-08-19 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-19 23:00 | 2030 100% ECP | -700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-08-20 | 2030 100% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-20 01:00 | 2030 100% ECP | -700 | 505 | 510 | -75.19 | 0 | 0 | Yes
2030-08-20 02:00 | 2030 100% ECP | -700 | 505 | 510 | -92.23 | 0 | 0 | Yes
2030-08-20 03:00 | 2030 100% ECP | -700 | 505 | 510 | -126.27 | 0 | 0 | Yes
2030-08-20 04:00 | 2030 100% ECP | -700 | 505 | 510 | -96.55 | 0 | 0 | Yes
2030-08-20 05:00 | 2030 100% ECP | -700 | 505 | 510 | 50.41 | 0 | 0 | Yes
2030-08-20 06:00 | 2030 100% ECP | -700 | 505 | 510 | 56.65 | 0 | 0 | Yes
2030-08-20 07:00 | 2030 100% ECP | -700 | 505 | 510 | 115.49 | 0 | 0 | Yes
2030-08-20 08:00 | 2030 100% ECP | -700 | 505 | 510 | 201.23 | 0 | 0 | Yes
2030-08-20 09:00 | 2030 100% ECP | -700 | 505 | 510 | 185.86 | 0 | 0 | Yes
2030-08-20 10:00 | 2030 100% ECP | -700 | 505 | 510 | 138.09 | 0 | 0 | Yes
2030-08-20 11:00 | 2030 100% ECP | -700 | 505 | 510 | 173.05 | 0 | 0 | Yes
2030-08-20 12:00 | 2030 100% ECP | -700 | 505 | 510 | 349.71 | 0 | 0 | Yes
2030-08-20 13:00 | 2030 100% ECP | -700 | 505 | 510 | 401.62 | 0 | 0 | Yes
2030-08-20 14:00 | 2030 100% ECP | -700 | 505 | 510 | 101.62 | 0 | 0 | Yes
2030-08-20 15:00 | 2030 100% ECP | -700 | 505 | 510 | 58.42 | 0 | 0 | Yes
2030-08-20 16:00 | 2030 100% ECP | -700 | 505 | 510 | 240.92 | 0 | 0 | Yes
2030-08-20 17:00 | 2030 100% ECP | -700 | 505 | 510 | 274.36 | 0 | 0 | Yes
2030-08-20 18:00 | 2030 100% ECP | -700 | 342.38 | 510 | 199.78 | 0 | 0 | Yes
2030-08-20 19:00 | 2030 100% ECP | -700 | 42.38 | 210 | -100.22 | 0 | 0 | Yes
2030-08-20 20:00 | 2030 100% ECP | -700 | 342.38 | 510 | 199.78 | 0 | 0 | Yes
2030-08-20 21:00 | 2030 100% ECP | -700 | 505 | 510 | 159.76 | 0 | 0 | Yes
2030-08-20 22:00 | 2030 100% ECP | -700 | 505 | 510 | 44.84 | 0 | 0 | Yes
2030-08-20 23:00 | 2030 100% ECP | -700 | 505 | 510 | -63.49 | 0 | 0 | Yes
2030-08-21 | 2030 100% ECP | -700 | 505 | 510 | -117.84 | 0 | 0 | Yes
2030-08-21 01:00 | 2030 100% ECP | -700 | 505 | 510 | -36.31 | 0 | 0 | Yes
2030-08-21 02:00 | 2030 100% ECP | -700 | 505 | 510 | -79.53 | 0 | 0 | Yes
2030-08-21 03:00 | 2030 100% ECP | -700 | 505 | 510 | -71.59 | 0 | 0 | Yes
2030-08-21 04:00 | 2030 100% ECP | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-08-21 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 17:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 18:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 | 2030 100% ECP | -557.43 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 01:00 | 2030 100% ECP | -642.4 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 15:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-08-22 16:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-08-22 17:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-08-22 18:00 | 2030 100% ECP | -280 | -526 | -510 | 210 | 0 | 0 | No
2030-08-22 19:00 | 2030 100% ECP | -44.45 | -526 | -510 | -90 | 0 | 0 | No
2030-08-22 20:00 | 2030 100% ECP | -44.45 | -526 | -510 | 100.45 | 0 | 0 | No
2030-08-22 21:00 | 2030 100% ECP | 0 | -226 | -210 | 400.45 | 0 | 0 | No
2030-08-22 22:00 | 2030 100% ECP | 0 | 74 | 90 | 510 | 0 | 0 | No
2030-08-22 23:00 | 2030 100% ECP | 0 | 374 | 390 | 510 | 0 | 0 | No
2030-08-23 | 2030 100% ECP | 420 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 06:00 | 2030 100% ECP | 700 | 205 | 210 | 413.04 | 0 | 0 | No
2030-08-23 07:00 | 2030 100% ECP | 560 | -95 | -90 | 447.95 | 0 | 0 | No
2030-08-23 08:00 | 2030 100% ECP | 140 | -395 | -390 | 339.18 | 0 | 0 | No
2030-08-23 09:00 | 2030 100% ECP | -280 | -526 | -510 | 288.85 | 0 | 0 | Yes
2030-08-23 10:00 | 2030 100% ECP | -700 | -526 | -510 | 446.59 | 0 | 0 | Yes
2030-08-23 11:00 | 2030 100% ECP | -700 | -526 | -510 | 436.57 | 0 | 0 | Yes
2030-08-23 12:00 | 2030 100% ECP | -700 | -526 | -510 | 446.29 | 0 | 0 | Yes
2030-08-23 13:00 | 2030 100% ECP | -700 | -526 | -510 | 451.15 | 0 | 0 | Yes
2030-08-23 14:00 | 2030 100% ECP | -700 | -526 | -510 | 406.77 | 0 | 0 | Yes
2030-08-23 15:00 | 2030 100% ECP | -700 | -526 | -510 | 268.71 | 0 | 0 | Yes
2030-08-23 16:00 | 2030 100% ECP | -700 | -526 | -510 | 251.98 | 0 | 0 | No
2030-08-23 17:00 | 2030 100% ECP | -700 | -526 | -510 | 287.1 | 0 | 0 | No
2030-08-23 18:00 | 2030 100% ECP | -280 | -226 | -210 | 287.1 | 0 | 0 | No
2030-08-23 19:00 | 2030 100% ECP | 140 | 0 | 0 | 308.51 | 0 | 0 | No
2030-08-23 20:00 | 2030 100% ECP | 560 | 0 | 0 | 256.72 | 0 | 0 | No
2030-08-23 21:00 | 2030 100% ECP | 700 | 0 | 0 | 402.6 | 0 | 0 | No
2030-08-23 22:00 | 2030 100% ECP | 700 | 0 | 0 | 337.49 | 0 | 0 | No
2030-08-23 23:00 | 2030 100% ECP | 700 | 0 | 0 | 324.34 | 0 | 0 | No
2030-08-24 | 2030 100% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-08-24 01:00 | 2030 100% ECP | 700 | 0 | 300 | 210 | 0 | 0 | No
2030-08-24 02:00 | 2030 100% ECP | 700 | 0 | 250.43 | 53.87 | 0 | 0 | No
2030-08-24 03:00 | 2030 100% ECP | 700 | 0 | 0 | 20.08 | 0 | 0 | No
2030-08-24 04:00 | 2030 100% ECP | 700 | 0 | 5.65 | 21.13 | 0 | 0 | No
2030-08-24 05:00 | 2030 100% ECP | 700 | 0 | 305.65 | 22.08 | 0 | 0 | No
2030-08-24 06:00 | 2030 100% ECP | 448.44 | 0 | 5.65 | 304.31 | 0 | 0 | No
2030-08-24 07:00 | 2030 100% ECP | 28.44 | -226 | -210 | 68.52 | 0 | 0 | No
2030-08-24 08:00 | 2030 100% ECP | -391.56 | -526 | -510 | 175.83 | 0 | 0 | No
2030-08-24 09:00 | 2030 100% ECP | -700 | -526 | -510 | 17.35 | 0 | 0 | Yes
2030-08-24 10:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-08-24 11:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-08-24 12:00 | 2030 100% ECP | -700 | -526 | -510 | 67.68 | 0 | 0 | Yes
2030-08-24 13:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-08-24 14:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-08-24 15:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-08-24 16:00 | 2030 100% ECP | -700 | -526 | -510 | -29.98 | 0 | 0 | No
2030-08-24 17:00 | 2030 100% ECP | -700 | -526 | -510 | -329.98 | 0 | 0 | No
2030-08-24 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-24 19:00 | 2030 100% ECP | -700 | -526 | -510 | -429.05 | 0 | 0 | No
2030-08-24 20:00 | 2030 100% ECP | -700 | -526 | -510 | -129.05 | 0 | 0 | No
2030-08-24 21:00 | 2030 100% ECP | -700 | -526 | -510 | -296.5 | 0 | 0 | No
2030-08-24 22:00 | 2030 100% ECP | -700 | -526 | -510 | -282.46 | 0 | 0 | No
2030-08-24 23:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-08-25 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-08-25 01:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-08-25 02:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-08-25 03:00 | 2030 100% ECP | -700 | 374 | 390 | 0 | 0 | 0 | Yes
2030-08-25 04:00 | 2030 100% ECP | -700 | 505 | 510 | -186.71 | 0 | 0 | Yes
2030-08-25 05:00 | 2030 100% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 06:00 | 2030 100% ECP | -700 | 505 | 510 | -24.66 | 0 | 0 | Yes
2030-08-25 07:00 | 2030 100% ECP | -700 | 505 | 510 | -19.96 | 0 | 0 | Yes
2030-08-25 08:00 | 2030 100% ECP | -700 | 505 | 510 | 144.71 | 0 | 0 | Yes
2030-08-25 09:00 | 2030 100% ECP | -700 | 505 | 510 | 121.26 | 0 | 0 | Yes
2030-08-25 10:00 | 2030 100% ECP | -700 | 505 | 510 | -53.28 | 0 | 0 | Yes
2030-08-25 11:00 | 2030 100% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 12:00 | 2030 100% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 13:00 | 2030 100% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 14:00 | 2030 100% ECP | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 15:00 | 2030 100% ECP | -700 | 505 | 510 | 249.63 | 0 | 0 | Yes
2030-08-25 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 17:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 18:00 | 2030 100% ECP | -700 | 505 | 510 | 452.16 | 0 | 0 | Yes
2030-08-25 19:00 | 2030 100% ECP | -700 | 505 | 510 | 297.2 | 0 | 0 | Yes
2030-08-25 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-26 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 01:00 | 2030 100% ECP | -597.28 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 02:00 | 2030 100% ECP | -177.28 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 03:00 | 2030 100% ECP | -8.7 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 04:00 | 2030 100% ECP | 327.35 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 05:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 06:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 07:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-26 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-26 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-26 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-26 12:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-08-26 13:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-08-26 14:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-08-26 15:00 | 2030 100% ECP | -643.08 | -526 | -510 | 510 | 0 | 0 | Yes
2030-08-26 16:00 | 2030 100% ECP | -223.08 | -526 | -510 | 510 | 0 | 0 | No
2030-08-26 17:00 | 2030 100% ECP | 196.92 | -526 | -510 | 510 | 0 | 0 | No
2030-08-26 18:00 | 2030 100% ECP | 616.92 | -526 | -510 | 510 | 0 | 0 | No
2030-08-26 19:00 | 2030 100% ECP | 622.2 | -526 | -510 | 510 | 0 | 0 | No
2030-08-26 20:00 | 2030 100% ECP | 554.99 | -526 | -510 | 325.65 | 0 | 0 | No
2030-08-26 21:00 | 2030 100% ECP | 554.99 | -526 | -510 | 494.72 | 0 | 0 | No
2030-08-26 22:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-08-26 23:00 | 2030 100% ECP | 700 | -526 | -510 | 500.41 | 0 | 0 | No
2030-08-27 | 2030 100% ECP | 700 | -292.86 | -510 | 234.92 | 0 | 0 | No
2030-08-27 01:00 | 2030 100% ECP | 700 | 0 | -510 | 236.53 | 0 | 0 | No
2030-08-27 02:00 | 2030 100% ECP | 700 | 0 | -510 | 21.65 | 0 | 0 | No
2030-08-27 03:00 | 2030 100% ECP | 700 | 0 | -510 | 24.25 | 0 | 0 | No
2030-08-27 04:00 | 2030 100% ECP | 700 | -159.36 | -510 | 10.5 | 0 | 0 | No
2030-08-27 05:00 | 2030 100% ECP | 700 | -159.36 | -510 | 28.74 | 0 | 0 | No
2030-08-27 06:00 | 2030 100% ECP | 700 | -294.37 | -510 | 98.53 | 0 | 0 | No
2030-08-27 07:00 | 2030 100% ECP | 700 | -337.38 | -510 | 134.43 | 0 | 0 | No
2030-08-27 08:00 | 2030 100% ECP | 700 | -37.38 | -510 | 267.08 | 0 | 0 | No
2030-08-27 09:00 | 2030 100% ECP | 700 | -278.97 | -510 | 510 | 0 | 0 | No
2030-08-27 10:00 | 2030 100% ECP | 700 | -526 | -510 | 485.56 | 0 | 0 | No
2030-08-27 11:00 | 2030 100% ECP | 700 | -526 | -510 | 430.66 | 0 | 0 | No
2030-08-27 12:00 | 2030 100% ECP | 700 | -526 | -510 | 433.29 | 0 | 0 | No
2030-08-27 13:00 | 2030 100% ECP | 700 | -526 | -510 | 337.06 | 0 | 0 | No
2030-08-27 14:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-08-27 15:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-08-27 16:00 | 2030 100% ECP | 700 | -485.12 | -510 | 413.47 | 0 | 0 | No
2030-08-27 17:00 | 2030 100% ECP | 700 | -185.12 | -510 | 390.63 | 0 | 0 | No
2030-08-27 18:00 | 2030 100% ECP | 700 | 0 | -510 | 307.16 | 0 | 0 | No
2030-08-27 19:00 | 2030 100% ECP | 700 | 0 | -510 | 191.36 | 0 | 0 | No
2030-08-27 20:00 | 2030 100% ECP | 700 | 0 | -390 | 239.04 | 0 | 0 | No
2030-08-27 21:00 | 2030 100% ECP | 700 | 0 | -90 | 9.93 | 0 | 0 | No
2030-08-27 22:00 | 2030 100% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-08-27 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 | 2030 100% ECP | 589.64 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 01:00 | 2030 100% ECP | 169.64 | 307.92 | 510 | 354.84 | 0 | 0 | No
2030-08-28 02:00 | 2030 100% ECP | -250.36 | 505 | 510 | 373.36 | 0 | 0 | Yes
2030-08-28 03:00 | 2030 100% ECP | -670.36 | 505 | 510 | 73.36 | 0 | 0 | Yes
2030-08-28 04:00 | 2030 100% ECP | -700 | 505 | 510 | 373.36 | 0 | 0 | Yes
2030-08-28 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 06:00 | 2030 100% ECP | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-08-28 07:00 | 2030 100% ECP | -700 | 505 | 510 | 244.07 | 0 | 0 | Yes
2030-08-28 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 16:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-08-28 17:00 | 2030 100% ECP | -700 | 74 | 90 | 432.03 | 0 | 0 | Yes
2030-08-28 18:00 | 2030 100% ECP | -700 | -226 | -210 | 132.03 | 0 | 0 | No
2030-08-28 19:00 | 2030 100% ECP | -700 | -526 | -510 | -167.97 | 0 | 0 | No
2030-08-28 20:00 | 2030 100% ECP | -700 | -526 | -510 | -98.27 | 0 | 0 | No
2030-08-28 21:00 | 2030 100% ECP | -700 | -226 | -210 | 201.73 | 0 | 0 | No
2030-08-28 22:00 | 2030 100% ECP | -700 | 74 | 90 | 501.73 | 0 | 0 | No
2030-08-28 23:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-08-29 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 01:00 | 2030 100% ECP | -508.47 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 02:00 | 2030 100% ECP | -243.05 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 03:00 | 2030 100% ECP | -663.05 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 06:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 15:00 | 2030 100% ECP | -700 | 432.89 | 390 | 510 | 0 | 0 | Yes
2030-08-29 16:00 | 2030 100% ECP | -700 | 132.89 | 90 | 510 | 0 | 0 | Yes
2030-08-29 17:00 | 2030 100% ECP | -700 | -167.11 | -210 | 367.95 | 0 | 0 | No
2030-08-29 18:00 | 2030 100% ECP | -280 | -467.11 | -510 | 67.95 | 0 | 0 | No
2030-08-29 19:00 | 2030 100% ECP | -140 | -395 | -390 | -232.05 | 0 | 0 | No
2030-08-29 20:00 | 2030 100% ECP | 280 | -95 | -90 | 67.95 | 0 | 0 | No
2030-08-29 21:00 | 2030 100% ECP | 700 | 205 | 210 | 367.95 | 0 | 0 | No
2030-08-29 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 05:00 | 2030 100% ECP | 700 | 505 | 508.42 | 510 | 0 | 0 | No
2030-08-30 06:00 | 2030 100% ECP | 700 | 205 | 208.42 | 210 | 0 | 0 | No
2030-08-30 07:00 | 2030 100% ECP | 280 | -95 | -91.58 | 206.95 | 0 | 0 | No
2030-08-30 08:00 | 2030 100% ECP | -140 | -395 | -391.58 | 249.57 | 0 | 0 | No
2030-08-30 09:00 | 2030 100% ECP | -560 | -526 | -510 | 194.48 | 0 | 0 | Yes
2030-08-30 10:00 | 2030 100% ECP | -700 | -526 | -510 | -105.52 | 0 | 0 | Yes
2030-08-30 11:00 | 2030 100% ECP | -700 | -526 | -510 | 146.28 | 0 | 0 | Yes
2030-08-30 12:00 | 2030 100% ECP | -700 | -526 | -510 | 152.96 | 0 | 0 | Yes
2030-08-30 13:00 | 2030 100% ECP | -700 | -526 | -510 | 122.19 | 0 | 0 | Yes
2030-08-30 14:00 | 2030 100% ECP | -700 | -526 | -510 | 92.24 | 0 | 0 | Yes
2030-08-30 15:00 | 2030 100% ECP | -280 | -526 | -510 | 135.57 | 0 | 0 | No
2030-08-30 16:00 | 2030 100% ECP | 140 | -526 | -510 | 200.97 | 0 | 0 | No
2030-08-30 17:00 | 2030 100% ECP | 560 | -226 | -210 | 300 | 0 | 0 | No
2030-08-30 18:00 | 2030 100% ECP | 700 | -226 | -359.53 | 0 | 0 | 0 | No
2030-08-30 19:00 | 2030 100% ECP | 700 | -526 | -510 | -300 | 0 | 0 | No
2030-08-30 20:00 | 2030 100% ECP | 700 | -526 | -510 | -158.15 | 0 | 0 | No
2030-08-30 21:00 | 2030 100% ECP | 700 | -226 | -210 | 141.85 | 0 | 0 | No
2030-08-30 22:00 | 2030 100% ECP | 700 | 0 | 90 | 441.85 | 0 | 0 | No
2030-08-30 23:00 | 2030 100% ECP | 700 | 0 | 390 | 510 | 0 | 0 | No
2030-08-31 | 2030 100% ECP | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-31 01:00 | 2030 100% ECP | 700 | 0 | 510 | 318.51 | 0 | 0 | No
2030-08-31 02:00 | 2030 100% ECP | 700 | 0 | 476.11 | 18.51 | 0 | 0 | No
2030-08-31 03:00 | 2030 100% ECP | 700 | 0 | 209.33 | 0 | 0 | 0 | No
2030-08-31 04:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-31 05:00 | 2030 100% ECP | 560 | 0 | -298.25 | 0 | 0 | 0 | No
2030-08-31 06:00 | 2030 100% ECP | 140 | -8.93 | -210 | 189.51 | 0 | 0 | No
2030-08-31 07:00 | 2030 100% ECP | -280 | -308.93 | -510 | 0 | 0 | 0 | No
2030-08-31 08:00 | 2030 100% ECP | -700 | -526 | -510 | -141.87 | 0 | 0 | Yes
2030-08-31 09:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-08-31 10:00 | 2030 100% ECP | -700 | -526 | -510 | -111.52 | 0 | 0 | Yes
2030-08-31 11:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-08-31 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-08-31 13:00 | 2030 100% ECP | -700 | -526 | -510 | -386.14 | 0 | 0 | Yes
2030-08-31 14:00 | 2030 100% ECP | -700 | -526 | -510 | -430.52 | 0 | 0 | Yes
2030-08-31 15:00 | 2030 100% ECP | -700 | -526 | -510 | -141.75 | 0 | 0 | Yes
2030-08-31 16:00 | 2030 100% ECP | -700 | -526 | -510 | -141.75 | 0 | 0 | No
2030-08-31 17:00 | 2030 100% ECP | -700 | -526 | -510 | 77.81 | 0 | 0 | No
2030-08-31 18:00 | 2030 100% ECP | -700 | -526 | -510 | -222.19 | 0 | 0 | No
2030-08-31 19:00 | 2030 100% ECP | -596 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 20:00 | 2030 100% ECP | -596 | -526 | -510 | -210 | 0 | 0 | No
2030-08-31 21:00 | 2030 100% ECP | -596 | -526 | -510 | 90 | 0 | 0 | No
2030-08-31 22:00 | 2030 100% ECP | -461.41 | -526 | -510 | 67.75 | 0 | 0 | No
2030-08-31 23:00 | 2030 100% ECP | -41.41 | -526 | -510 | -31.15 | 0 | 0 | No
2030-09-01 | 2030 100% ECP | 378.59 | -526 | -510 | -113.56 | 0 | 0 | No
2030-09-01 01:00 | 2030 100% ECP | 700 | -526 | -510 | -88.64 | 0 | 0 | No
2030-09-01 02:00 | 2030 100% ECP | 700 | -504.07 | -510 | -79.55 | 0 | 0 | No
2030-09-01 03:00 | 2030 100% ECP | 700 | -504.07 | -510 | -96.61 | 0 | 0 | No
2030-09-01 04:00 | 2030 100% ECP | 700 | -526 | -510 | -144.19 | 0 | 0 | No
2030-09-01 05:00 | 2030 100% ECP | 700 | -526 | -510 | -330.87 | 0 | 0 | No
2030-09-01 06:00 | 2030 100% ECP | 700 | -526 | -510 | -142.05 | 0 | 0 | No
2030-09-01 07:00 | 2030 100% ECP | 676.16 | -526 | -510 | -228.97 | 0 | 0 | No
2030-09-01 08:00 | 2030 100% ECP | 256.16 | -526 | -510 | -215.81 | 0 | 0 | No
2030-09-01 09:00 | 2030 100% ECP | -163.84 | -526 | -510 | -278.9 | 0 | 0 | Yes
2030-09-01 10:00 | 2030 100% ECP | -583.84 | -526 | -510 | -298.72 | 0 | 0 | Yes
2030-09-01 11:00 | 2030 100% ECP | -700 | -526 | -510 | -371.67 | 0 | 0 | Yes
2030-09-01 12:00 | 2030 100% ECP | -700 | -526 | -510 | -261.7 | 0 | 0 | Yes
2030-09-01 13:00 | 2030 100% ECP | -700 | -526 | -510 | -351.94 | 0 | 0 | Yes
2030-09-01 14:00 | 2030 100% ECP | -700 | -526 | -510 | -258.81 | 0 | 0 | Yes
2030-09-01 15:00 | 2030 100% ECP | -700 | -526 | -510 | -432.57 | 0 | 0 | Yes
2030-09-01 16:00 | 2030 100% ECP | -700 | -526 | -510 | -148.31 | 0 | 0 | No
2030-09-01 17:00 | 2030 100% ECP | -682.67 | -526 | -510 | 15.33 | 0 | 0 | No
2030-09-01 18:00 | 2030 100% ECP | -700 | -526 | -510 | -28.19 | 0 | 0 | No
2030-09-01 19:00 | 2030 100% ECP | -700 | -526 | -510 | -93.5 | 0 | 0 | No
2030-09-01 20:00 | 2030 100% ECP | -700 | -526 | -510 | -151.31 | 0 | 0 | No
2030-09-01 21:00 | 2030 100% ECP | -700 | -526 | -510 | -116.03 | 0 | 0 | No
2030-09-01 22:00 | 2030 100% ECP | -700 | -526 | -510 | -259.68 | 0 | 0 | No
2030-09-01 23:00 | 2030 100% ECP | -700 | -526 | -510 | -269.33 | 0 | 0 | No
2030-09-02 | 2030 100% ECP | -700 | -526 | -510 | -416.61 | 0 | 0 | Yes
2030-09-02 01:00 | 2030 100% ECP | -700 | -526 | -510 | -318.8 | 0 | 0 | Yes
2030-09-02 02:00 | 2030 100% ECP | -700 | -526 | -510 | -253.53 | 0 | 0 | Yes
2030-09-02 03:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-09-02 04:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-09-02 05:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-09-02 06:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-09-02 07:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-09-02 08:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-09-02 09:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-09-02 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 17:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 18:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 07:00 | 2030 100% ECP | -700 | 205 | 510 | 448.51 | 0 | 0 | No
2030-09-03 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 15:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-09-03 16:00 | 2030 100% ECP | -700 | 74 | 90 | 243.25 | 0 | 0 | Yes
2030-09-03 17:00 | 2030 100% ECP | -700 | -226 | -210 | -56.75 | 0 | 0 | Yes
2030-09-03 18:00 | 2030 100% ECP | -700 | -526 | -510 | -356.75 | 0 | 0 | No
2030-09-03 19:00 | 2030 100% ECP | -700 | -395 | -510 | -390.18 | 0 | 0 | No
2030-09-03 20:00 | 2030 100% ECP | -700 | -95 | -210 | -90.18 | 0 | 0 | No
2030-09-03 21:00 | 2030 100% ECP | -280 | 205 | 90 | 209.82 | 0 | 0 | No
2030-09-03 22:00 | 2030 100% ECP | 140 | 505 | 390 | 509.82 | 0 | 0 | No
2030-09-03 23:00 | 2030 100% ECP | 234.77 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 | 2030 100% ECP | 654.77 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 04:00 | 2030 100% ECP | 567.91 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 05:00 | 2030 100% ECP | 147.91 | 505 | 510 | 412.57 | 0 | 0 | No
2030-09-04 06:00 | 2030 100% ECP | -272.09 | 205 | 210 | 112.57 | 0 | 0 | No
2030-09-04 07:00 | 2030 100% ECP | -692.09 | -95 | -90 | -187.43 | 0 | 0 | No
2030-09-04 08:00 | 2030 100% ECP | -700 | -107.44 | -390 | 94.3 | 0 | 0 | No
2030-09-04 09:00 | 2030 100% ECP | -700 | 192.56 | -90 | 394.3 | 0 | 0 | Yes
2030-09-04 10:00 | 2030 100% ECP | -700 | 258.51 | 210 | 510 | 0 | 0 | Yes
2030-09-04 11:00 | 2030 100% ECP | -700 | 0 | 19.12 | 210 | 0 | 0 | Yes
2030-09-04 12:00 | 2030 100% ECP | -700 | 300 | 319.12 | 510 | 0 | 0 | Yes
2030-09-04 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 14:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-09-04 15:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-09-04 16:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-09-04 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-09-04 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-09-04 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-09-04 20:00 | 2030 100% ECP | -700 | -381.29 | -390 | -210.01 | 0 | 0 | No
2030-09-04 21:00 | 2030 100% ECP | -700 | -81.29 | -90 | 89.99 | 0 | 0 | No
2030-09-04 22:00 | 2030 100% ECP | -280 | 218.71 | 210 | 389.99 | 0 | 0 | No
2030-09-04 23:00 | 2030 100% ECP | -439.88 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 | 2030 100% ECP | -19.88 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 01:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 02:00 | 2030 100% ECP | -110.45 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 03:00 | 2030 100% ECP | 42 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 04:00 | 2030 100% ECP | -182.46 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 05:00 | 2030 100% ECP | -182.46 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 06:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 07:00 | 2030 100% ECP | -280 | 205 | 510 | 299.06 | 0 | 0 | No
2030-09-05 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-05 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-05 10:00 | 2030 100% ECP | -700 | 341.32 | 210 | 510 | 0 | 0 | Yes
2030-09-05 11:00 | 2030 100% ECP | -700 | 41.32 | -90 | 510 | 0 | 0 | Yes
2030-09-05 12:00 | 2030 100% ECP | -700 | -258.68 | -390 | 472.61 | 0 | 0 | Yes
2030-09-05 13:00 | 2030 100% ECP | -700 | 0 | -379.02 | 510 | 0 | 0 | Yes
2030-09-05 14:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-09-05 15:00 | 2030 100% ECP | -700 | -526 | -510 | 509.98 | 0 | 0 | Yes
2030-09-05 16:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-05 17:00 | 2030 100% ECP | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-09-05 18:00 | 2030 100% ECP | 128.91 | -526 | -510 | 510 | 0 | 0 | No
2030-09-05 19:00 | 2030 100% ECP | 548.91 | -526 | -510 | 461.91 | 0 | 0 | No
2030-09-05 20:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-05 21:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-05 22:00 | 2030 100% ECP | 700 | -300 | -510 | 510 | 0 | 0 | No
2030-09-05 23:00 | 2030 100% ECP | 420 | 0 | -432.4 | 465.94 | 0 | 0 | No
2030-09-06 | 2030 100% ECP | 336.86 | 0 | -132.4 | 165.94 | 0 | 0 | No
2030-09-06 01:00 | 2030 100% ECP | 700 | 0 | 0 | 22.51 | 0 | 0 | No
2030-09-06 02:00 | 2030 100% ECP | 700 | 0 | -210 | 0 | 0 | 0 | No
2030-09-06 03:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-06 04:00 | 2030 100% ECP | 700 | -300 | -510 | -67.37 | 0 | 0 | No
2030-09-06 05:00 | 2030 100% ECP | 700 | -61.54 | -510 | 0 | 0 | 0 | No
2030-09-06 06:00 | 2030 100% ECP | 560 | -325.3 | -510 | 0 | 0 | 0 | No
2030-09-06 07:00 | 2030 100% ECP | 140 | -325.3 | -510 | -142.97 | 0 | 0 | No
2030-09-06 08:00 | 2030 100% ECP | -280 | -526 | -510 | -85.97 | 0 | 0 | No
2030-09-06 09:00 | 2030 100% ECP | -700 | -526 | -510 | -109.32 | 0 | 0 | No
2030-09-06 10:00 | 2030 100% ECP | -700 | -526 | -510 | -200.49 | 0 | 0 | No
2030-09-06 11:00 | 2030 100% ECP | -700 | -526 | -510 | -156.3 | 0 | 0 | No
2030-09-06 12:00 | 2030 100% ECP | -700 | -526 | -510 | -171.28 | 0 | 0 | No
2030-09-06 13:00 | 2030 100% ECP | -700 | -526 | -510 | -72.41 | 0 | 0 | No
2030-09-06 14:00 | 2030 100% ECP | -700 | -526 | -510 | -283.63 | 0 | 0 | No
2030-09-06 15:00 | 2030 100% ECP | -700 | -526 | -510 | -152.41 | 0 | 0 | No
2030-09-06 16:00 | 2030 100% ECP | -700 | -526 | -510 | -419.35 | 0 | 0 | No
2030-09-06 17:00 | 2030 100% ECP | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-09-06 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-09-06 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-09-06 20:00 | 2030 100% ECP | -280 | -526 | -510 | -399.26 | 0 | 0 | No
2030-09-06 21:00 | 2030 100% ECP | 140 | -526 | -510 | -399.26 | 0 | 0 | No
2030-09-06 22:00 | 2030 100% ECP | 560 | -226 | -510 | -217.43 | 0 | 0 | No
2030-09-06 23:00 | 2030 100% ECP | 700 | -40.09 | -510 | -376.38 | 0 | 0 | No
2030-09-07 | 2030 100% ECP | 382.53 | -340.09 | -510 | -209.93 | 0 | 0 | No
2030-09-07 01:00 | 2030 100% ECP | -34.09 | -526 | -510 | -166.1 | 0 | 0 | No
2030-09-07 02:00 | 2030 100% ECP | -280 | -457.63 | -510 | -59.16 | 0 | 0 | No
2030-09-07 03:00 | 2030 100% ECP | -700 | -526 | -510 | -25.41 | 0 | 0 | No
2030-09-07 04:00 | 2030 100% ECP | -700 | -526 | -510 | -246.89 | 0 | 0 | No
2030-09-07 05:00 | 2030 100% ECP | -700 | -526 | -510 | -194.07 | 0 | 0 | No
2030-09-07 06:00 | 2030 100% ECP | -700 | -526 | -510 | -196.79 | 0 | 0 | No
2030-09-07 07:00 | 2030 100% ECP | -700 | -526 | -510 | 39.69 | 0 | 0 | No
2030-09-07 08:00 | 2030 100% ECP | -700 | -526 | -510 | 134.26 | 0 | 0 | No
2030-09-07 09:00 | 2030 100% ECP | -700 | -526 | -510 | 80.92 | 0 | 0 | No
2030-09-07 10:00 | 2030 100% ECP | -700 | -526 | -510 | 203.54 | 0 | 0 | Yes
2030-09-07 11:00 | 2030 100% ECP | -700 | -226 | -210 | 503.54 | 0 | 0 | Yes
2030-09-07 12:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-09-07 13:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-09-07 14:00 | 2030 100% ECP | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-09-07 15:00 | 2030 100% ECP | -700 | 248.49 | 90 | 510 | 0 | 0 | Yes
2030-09-07 16:00 | 2030 100% ECP | -700 | -51.51 | -210 | 510 | 0 | 0 | No
2030-09-07 17:00 | 2030 100% ECP | -700 | -351.51 | -510 | 210 | 0 | 0 | No
2030-09-07 18:00 | 2030 100% ECP | -700 | -526 | -510 | -90 | 0 | 0 | No
2030-09-07 19:00 | 2030 100% ECP | -700 | -395 | -433.61 | -253.88 | 0 | 0 | No
2030-09-07 20:00 | 2030 100% ECP | -700 | -95 | -133.61 | 46.12 | 0 | 0 | No
2030-09-07 21:00 | 2030 100% ECP | -280 | 205 | 166.39 | 346.12 | 0 | 0 | No
2030-09-07 22:00 | 2030 100% ECP | 140 | 505 | 466.39 | 510 | 0 | 0 | No
2030-09-07 23:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 06:00 | 2030 100% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-09-08 07:00 | 2030 100% ECP | 560 | 300 | 185.07 | 510 | 0 | 0 | No
2030-09-08 08:00 | 2030 100% ECP | 140 | 0 | -114.93 | 510 | 0 | 0 | No
2030-09-08 09:00 | 2030 100% ECP | -280 | -300 | -414.93 | 510 | 0 | 0 | No
2030-09-08 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-08 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-08 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-08 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-08 14:00 | 2030 100% ECP | -700 | -526 | -510 | 415.75 | 0 | 0 | No
2030-09-08 15:00 | 2030 100% ECP | -700 | -526 | -510 | 240.9 | 0 | 0 | No
2030-09-08 16:00 | 2030 100% ECP | -700 | -526 | -510 | 322.74 | 0 | 0 | No
2030-09-08 17:00 | 2030 100% ECP | -700 | -526 | -510 | 249.18 | 0 | 0 | No
2030-09-08 18:00 | 2030 100% ECP | -700 | -472.81 | -510 | 75.89 | 0 | 0 | No
2030-09-08 19:00 | 2030 100% ECP | -700 | -172.81 | -210 | 375.89 | 0 | 0 | No
2030-09-08 20:00 | 2030 100% ECP | -700 | 127.19 | 90 | 510 | 0 | 0 | No
2030-09-08 21:00 | 2030 100% ECP | -700 | 427.19 | 390 | 510 | 0 | 0 | No
2030-09-08 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 02:00 | 2030 100% ECP | -549.68 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 03:00 | 2030 100% ECP | -129.68 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 04:00 | 2030 100% ECP | -549.68 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 05:00 | 2030 100% ECP | -211.21 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 06:00 | 2030 100% ECP | -631.21 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 14:00 | 2030 100% ECP | -700 | 488.88 | 390 | 510 | 0 | 0 | Yes
2030-09-09 15:00 | 2030 100% ECP | -700 | 188.88 | 90 | 510 | 0 | 0 | Yes
2030-09-09 16:00 | 2030 100% ECP | -280 | -111.12 | -210 | 510 | 0 | 0 | Yes
2030-09-09 17:00 | 2030 100% ECP | 140 | -411.12 | -510 | 312.73 | 0 | 0 | No
2030-09-09 18:00 | 2030 100% ECP | 560 | -111.12 | -510 | 510 | 0 | 0 | No
2030-09-09 19:00 | 2030 100% ECP | 700 | 0 | -210 | 510 | 0 | 0 | No
2030-09-09 20:00 | 2030 100% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-09-09 21:00 | 2030 100% ECP | 700 | 0 | -210 | 510 | 0 | 0 | No
2030-09-09 22:00 | 2030 100% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-09-09 23:00 | 2030 100% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-09-10 | 2030 100% ECP | 700 | 0 | -210 | 255.24 | 0 | 0 | No
2030-09-10 01:00 | 2030 100% ECP | 700 | 0 | -336.99 | 226.1 | 0 | 0 | No
2030-09-10 02:00 | 2030 100% ECP | 700 | 0 | -36.99 | 186.03 | 0 | 0 | No
2030-09-10 03:00 | 2030 100% ECP | 700 | 0 | -336.99 | 166.44 | 0 | 0 | No
2030-09-10 04:00 | 2030 100% ECP | 700 | 0 | -36.99 | 179.31 | 0 | 0 | No
2030-09-10 05:00 | 2030 100% ECP | 700 | 0 | -29.18 | 222.4 | 0 | 0 | No
2030-09-10 06:00 | 2030 100% ECP | 478.37 | 0 | -213.02 | 322.14 | 0 | 0 | No
2030-09-10 07:00 | 2030 100% ECP | 58.37 | -226 | -386.13 | 341.58 | 0 | 0 | No
2030-09-10 08:00 | 2030 100% ECP | -361.63 | -526 | -510 | 492.82 | 0 | 0 | No
2030-09-10 09:00 | 2030 100% ECP | -700 | -526 | -510 | 492.82 | 0 | 0 | No
2030-09-10 10:00 | 2030 100% ECP | -700 | -526 | -510 | 291.46 | 0 | 0 | No
2030-09-10 11:00 | 2030 100% ECP | -700 | -526 | -510 | 291.46 | 0 | 0 | No
2030-09-10 12:00 | 2030 100% ECP | -700 | -526 | -510 | 139.86 | 0 | 0 | No
2030-09-10 13:00 | 2030 100% ECP | -700 | -526 | -510 | 151.17 | 0 | 0 | No
2030-09-10 14:00 | 2030 100% ECP | -700 | -526 | -510 | 189.44 | 0 | 0 | No
2030-09-10 15:00 | 2030 100% ECP | -700 | -526 | -510 | 272.46 | 0 | 0 | No
2030-09-10 16:00 | 2030 100% ECP | -700 | -526 | -510 | 478.8 | 0 | 0 | No
2030-09-10 17:00 | 2030 100% ECP | -700 | -526 | -510 | 448.64 | 0 | 0 | No
2030-09-10 18:00 | 2030 100% ECP | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-09-10 19:00 | 2030 100% ECP | -111.19 | -526 | -510 | 510 | 0 | 0 | No
2030-09-10 20:00 | 2030 100% ECP | -531.19 | -526 | -510 | 378.89 | 0 | 0 | No
2030-09-10 21:00 | 2030 100% ECP | -345.98 | -526 | -510 | 183.47 | 0 | 0 | No
2030-09-10 22:00 | 2030 100% ECP | 74.02 | -336.81 | -510 | 264.11 | 0 | 0 | No
2030-09-10 23:00 | 2030 100% ECP | 140 | -36.81 | -210 | 73.73 | 0 | 0 | No
2030-09-11 | 2030 100% ECP | -257.23 | 263.19 | 90 | 373.73 | 0 | 0 | No
2030-09-11 01:00 | 2030 100% ECP | -677.23 | 505 | 390 | 510 | 0 | 0 | Yes
2030-09-11 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 17:00 | 2030 100% ECP | -280 | 348.19 | 510 | 510 | 0 | 0 | No
2030-09-11 18:00 | 2030 100% ECP | -700 | 48.19 | 210 | 210 | 0 | 0 | No
2030-09-11 19:00 | 2030 100% ECP | -358.16 | -251.81 | -90 | -90 | 0 | 0 | No
2030-09-11 20:00 | 2030 100% ECP | 61.84 | 0 | -90 | -90 | 0 | 0 | No
2030-09-11 21:00 | 2030 100% ECP | 280 | 300 | 210 | 210 | 0 | 0 | No
2030-09-11 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 23:00 | 2030 100% ECP | 345.36 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 01:00 | 2030 100% ECP | -420 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 02:00 | 2030 100% ECP | -681.81 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 03:00 | 2030 100% ECP | -604.05 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 04:00 | 2030 100% ECP | -184.05 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 05:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 06:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 07:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-12 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-12 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-12 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-12 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-12 13:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-09-12 14:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-09-12 15:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-09-12 16:00 | 2030 100% ECP | -700 | -526 | -510 | 260.7 | 0 | 0 | Yes
2030-09-12 17:00 | 2030 100% ECP | -700 | -526 | -510 | -21.68 | 0 | 0 | Yes
2030-09-12 18:00 | 2030 100% ECP | -700 | -526 | -510 | -321.68 | 0 | 0 | Yes
2030-09-12 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-09-12 20:00 | 2030 100% ECP | -700 | -526 | -510 | -374.02 | 0 | 0 | Yes
2030-09-12 21:00 | 2030 100% ECP | -700 | -226 | -210 | -74.02 | 0 | 0 | Yes
2030-09-12 22:00 | 2030 100% ECP | -700 | 74 | 90 | 225.98 | 0 | 0 | Yes
2030-09-12 23:00 | 2030 100% ECP | -700 | 374 | 390 | 373.08 | 0 | 0 | Yes
2030-09-13 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-13 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-13 02:00 | 2030 100% ECP | -700 | 505 | 300 | 510 | 0 | 0 | Yes
2030-09-13 03:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 04:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 05:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 06:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 07:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 08:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 09:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 10:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 11:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 12:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 13:00 | 2030 100% ECP | -700 | 374 | 0 | 510 | 0 | 0 | Yes
2030-09-13 14:00 | 2030 100% ECP | -700 | 74 | 0 | 510 | 0 | 0 | Yes
2030-09-13 15:00 | 2030 100% ECP | -700 | -226 | 0 | 510 | 0 | 0 | Yes
2030-09-13 16:00 | 2030 100% ECP | -700 | -526 | 0 | 395.26 | 0 | 0 | Yes
2030-09-13 17:00 | 2030 100% ECP | -700 | -526 | 0 | 167.95 | 0 | 0 | Yes
2030-09-13 18:00 | 2030 100% ECP | -700 | -526 | 0 | 467.95 | 0 | 0 | No
2030-09-13 19:00 | 2030 100% ECP | -700 | -526 | 0 | 510 | 0 | 0 | No
2030-09-13 20:00 | 2030 100% ECP | -700 | -526 | 0 | 407.43 | 0 | 0 | No
2030-09-13 21:00 | 2030 100% ECP | -700 | -526 | 0 | 440.84 | 0 | 0 | No
2030-09-13 22:00 | 2030 100% ECP | -280 | -526 | 0 | 289.73 | 0 | 0 | No
2030-09-13 23:00 | 2030 100% ECP | 140 | -526 | 0 | 210 | 0 | 0 | No
2030-09-14 | 2030 100% ECP | 300.43 | -226 | 0 | 510 | 0 | 0 | No
2030-09-14 01:00 | 2030 100% ECP | 700 | -15.85 | 0 | 510 | 0 | 0 | No
2030-09-14 02:00 | 2030 100% ECP | 700 | -315.85 | 0 | 295.83 | 0 | 0 | No
2030-09-14 03:00 | 2030 100% ECP | 700 | -526 | 0 | 7.05 | 0 | 0 | No
2030-09-14 04:00 | 2030 100% ECP | 552.02 | -526 | 0 | 7.05 | 0 | 0 | No
2030-09-14 05:00 | 2030 100% ECP | 132.02 | -526 | 0 | 13.81 | 0 | 0 | No
2030-09-14 06:00 | 2030 100% ECP | -287.98 | -526 | 0 | 44.08 | 0 | 0 | No
2030-09-14 07:00 | 2030 100% ECP | -560 | -526 | 0 | 137.69 | 0 | 0 | No
2030-09-14 08:00 | 2030 100% ECP | -140 | -526 | 0 | 168.05 | 0 | 0 | No
2030-09-14 09:00 | 2030 100% ECP | 280 | -526 | 0 | 191.54 | 0 | 0 | No
2030-09-14 10:00 | 2030 100% ECP | 700 | -526 | 0 | 214.65 | 0 | 0 | No
2030-09-14 11:00 | 2030 100% ECP | 700 | -526 | 0 | 219.75 | 0 | 0 | No
2030-09-14 12:00 | 2030 100% ECP | 700 | -526 | 0 | 214.64 | 0 | 0 | No
2030-09-14 13:00 | 2030 100% ECP | 700 | -526 | 0 | 158.06 | 0 | 0 | No
2030-09-14 14:00 | 2030 100% ECP | 700 | -526 | 0 | 137.61 | 0 | 0 | No
2030-09-14 15:00 | 2030 100% ECP | 700 | -526 | 0 | 158.22 | 0 | 0 | No
2030-09-14 16:00 | 2030 100% ECP | 399.7 | -526 | 0 | 172.4 | 0 | 0 | No
2030-09-14 17:00 | 2030 100% ECP | -20.3 | -526 | 0 | -127.6 | 0 | 0 | No
2030-09-14 18:00 | 2030 100% ECP | -440.3 | -526 | 0 | -427.6 | 0 | 0 | No
2030-09-14 19:00 | 2030 100% ECP | -700 | -526 | 0 | -409.26 | 0 | 0 | No
2030-09-14 20:00 | 2030 100% ECP | -700 | -526 | 0 | -109.26 | 0 | 0 | No
2030-09-14 21:00 | 2030 100% ECP | -376.81 | -526 | 0 | 190.74 | 0 | 0 | No
2030-09-14 22:00 | 2030 100% ECP | 43.19 | -526 | 0 | 127.94 | 0 | 0 | No
2030-09-14 23:00 | 2030 100% ECP | 463.19 | -526 | 0 | 22.2 | 0 | 0 | No
2030-09-15 | 2030 100% ECP | 700 | -226 | 0 | 0 | 0 | 0 | No
2030-09-15 01:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-15 02:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-15 03:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-15 04:00 | 2030 100% ECP | 700 | -122.96 | -510 | 0 | 0 | 0 | No
2030-09-15 05:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-15 06:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-15 07:00 | 2030 100% ECP | 700 | -268.22 | -510 | 0.4 | 0 | 0 | No
2030-09-15 08:00 | 2030 100% ECP | 280 | -526 | -510 | 0 | 0 | 0 | No
2030-09-15 09:00 | 2030 100% ECP | -140 | -526 | -510 | 5.69 | 0 | 0 | Yes
2030-09-15 10:00 | 2030 100% ECP | -560 | -526 | -510 | 0 | 0 | 0 | Yes
2030-09-15 11:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-09-15 12:00 | 2030 100% ECP | -700 | -526 | -510 | 13.44 | 0 | 0 | Yes
2030-09-15 13:00 | 2030 100% ECP | -700 | -526 | -510 | 36.36 | 0 | 0 | Yes
2030-09-15 14:00 | 2030 100% ECP | -700 | -526 | -510 | 50.8 | 0 | 0 | Yes
2030-09-15 15:00 | 2030 100% ECP | -700 | -526 | -510 | 78.7 | 0 | 0 | Yes
2030-09-15 16:00 | 2030 100% ECP | -280 | -526 | -510 | 155.51 | 0 | 0 | No
2030-09-15 17:00 | 2030 100% ECP | 140 | -226 | -510 | 313.93 | 0 | 0 | No
2030-09-15 18:00 | 2030 100% ECP | 560 | -526 | -510 | 13.93 | 0 | 0 | No
2030-09-15 19:00 | 2030 100% ECP | 700 | -526 | -510 | 210 | 0 | 0 | No
2030-09-15 20:00 | 2030 100% ECP | 700 | -226 | -510 | 510 | 0 | 0 | No
2030-09-15 21:00 | 2030 100% ECP | 700 | 0 | -211.81 | 510 | 0 | 0 | No
2030-09-15 22:00 | 2030 100% ECP | 700 | 0 | -211.81 | 449.93 | 0 | 0 | No
2030-09-15 23:00 | 2030 100% ECP | 700 | 0 | -211.81 | 300.71 | 0 | 0 | No
2030-09-16 | 2030 100% ECP | 700 | 0 | -510 | 335.16 | 0 | 0 | No
2030-09-16 01:00 | 2030 100% ECP | 700 | 0 | -210 | 334.11 | 0 | 0 | No
2030-09-16 02:00 | 2030 100% ECP | 700 | 0 | 0 | 331.18 | 0 | 0 | No
2030-09-16 03:00 | 2030 100% ECP | 700 | 0 | -300 | 290.59 | 0 | 0 | No
2030-09-16 04:00 | 2030 100% ECP | 700 | 0 | -154.34 | 290.79 | 0 | 0 | No
2030-09-16 05:00 | 2030 100% ECP | 700 | 0 | -193.06 | 322.1 | 0 | 0 | No
2030-09-16 06:00 | 2030 100% ECP | 700 | 0 | -439.86 | 431.39 | 0 | 0 | No
2030-09-16 07:00 | 2030 100% ECP | 700 | 0 | -139.86 | 510 | 0 | 0 | No
2030-09-16 08:00 | 2030 100% ECP | 700 | 0 | -139.86 | 468.2 | 0 | 0 | No
2030-09-16 09:00 | 2030 100% ECP | 280 | -124.62 | -439.86 | 510 | 0 | 0 | No
2030-09-16 10:00 | 2030 100% ECP | 0 | -424.62 | -510 | 510 | 0 | 0 | No
2030-09-16 11:00 | 2030 100% ECP | -265.62 | -526 | -510 | 510 | 0 | 0 | No
2030-09-16 12:00 | 2030 100% ECP | -685.62 | -526 | -510 | 510 | 0 | 0 | No
2030-09-16 13:00 | 2030 100% ECP | -354.23 | -526 | -510 | 510 | 0 | 0 | No
2030-09-16 14:00 | 2030 100% ECP | 0 | -484.76 | -510 | 510 | 0 | 0 | No
2030-09-16 15:00 | 2030 100% ECP | 280 | -526 | -510 | 510 | 0 | 0 | No
2030-09-16 16:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-16 17:00 | 2030 100% ECP | 700 | -313.62 | -510 | 510 | 0 | 0 | No
2030-09-16 18:00 | 2030 100% ECP | 700 | -13.62 | -510 | 510 | 0 | 0 | No
2030-09-16 19:00 | 2030 100% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-09-16 20:00 | 2030 100% ECP | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-09-16 21:00 | 2030 100% ECP | 700 | 0 | -510 | 450.21 | 0 | 0 | No
2030-09-16 22:00 | 2030 100% ECP | 700 | 0 | -300 | 230.6 | 0 | 0 | No
2030-09-16 23:00 | 2030 100% ECP | 700 | 193.34 | 0 | 510 | 0 | 0 | No
2030-09-17 | 2030 100% ECP | 700 | 0 | 48.1 | 210 | 0 | 0 | No
2030-09-17 01:00 | 2030 100% ECP | 700 | 0 | 163.97 | 264.37 | 0 | 0 | No
2030-09-17 02:00 | 2030 100% ECP | 700 | 0 | -18.23 | 151.06 | 0 | 0 | No
2030-09-17 03:00 | 2030 100% ECP | 700 | 0 | -318.23 | -20.78 | 0 | 0 | No
2030-09-17 04:00 | 2030 100% ECP | 700 | 0 | -510 | -23.65 | 0 | 0 | No
2030-09-17 05:00 | 2030 100% ECP | 700 | 0 | -510 | -19.23 | 0 | 0 | No
2030-09-17 06:00 | 2030 100% ECP | 700 | -48.59 | -510 | -68.13 | 0 | 0 | No
2030-09-17 07:00 | 2030 100% ECP | 560 | -348.59 | -510 | 137.31 | 0 | 0 | No
2030-09-17 08:00 | 2030 100% ECP | 140 | -526 | -510 | 174.57 | 0 | 0 | No
2030-09-17 09:00 | 2030 100% ECP | -280 | -526 | -510 | 217.43 | 0 | 0 | Yes
2030-09-17 10:00 | 2030 100% ECP | -700 | -526 | -510 | 206.06 | 0 | 0 | Yes
2030-09-17 11:00 | 2030 100% ECP | -700 | -526 | -510 | 224.6 | 0 | 0 | Yes
2030-09-17 12:00 | 2030 100% ECP | -700 | -526 | -510 | 135.59 | 0 | 0 | Yes
2030-09-17 13:00 | 2030 100% ECP | -700 | -526 | -510 | 183.26 | 0 | 0 | Yes
2030-09-17 14:00 | 2030 100% ECP | -700 | -526 | -510 | 218.86 | 0 | 0 | Yes
2030-09-17 15:00 | 2030 100% ECP | -280 | -526 | -510 | 226.51 | 0 | 0 | Yes
2030-09-17 16:00 | 2030 100% ECP | 140 | -526 | -510 | 347.63 | 0 | 0 | No
2030-09-17 17:00 | 2030 100% ECP | 560 | -441.76 | -510 | 464.12 | 0 | 0 | No
2030-09-17 18:00 | 2030 100% ECP | 700 | -141.76 | -510 | 380.63 | 0 | 0 | No
2030-09-17 19:00 | 2030 100% ECP | 700 | -141.76 | -510 | 341.44 | 0 | 0 | No
2030-09-17 20:00 | 2030 100% ECP | 700 | -349.4 | -510 | 510 | 0 | 0 | No
2030-09-17 21:00 | 2030 100% ECP | 700 | -64.14 | -510 | 510 | 0 | 0 | No
2030-09-17 22:00 | 2030 100% ECP | 700 | -300 | -510 | 260.29 | 0 | 0 | No
2030-09-17 23:00 | 2030 100% ECP | 700 | 0 | -293.97 | 462.32 | 0 | 0 | No
2030-09-18 | 2030 100% ECP | 700 | 0 | -229.94 | 510 | 0 | 0 | No
2030-09-18 01:00 | 2030 100% ECP | 700 | 0 | -482.23 | 510 | 0 | 0 | No
2030-09-18 02:00 | 2030 100% ECP | 700 | -93.68 | -510 | 510 | 0 | 0 | No
2030-09-18 03:00 | 2030 100% ECP | 700 | 0 | -510 | 210 | 0 | 0 | No
2030-09-18 04:00 | 2030 100% ECP | 700 | -161.26 | -510 | 10.17 | 0 | 0 | No
2030-09-18 05:00 | 2030 100% ECP | 700 | -77.16 | -510 | 76.84 | 0 | 0 | No
2030-09-18 06:00 | 2030 100% ECP | 700 | -226 | -510 | 196.12 | 0 | 0 | No
2030-09-18 07:00 | 2030 100% ECP | 560 | -526 | -510 | 382.39 | 0 | 0 | No
2030-09-18 08:00 | 2030 100% ECP | 140 | -526 | -510 | 445.42 | 0 | 0 | No
2030-09-18 09:00 | 2030 100% ECP | -280 | -526 | -510 | 365.74 | 0 | 0 | Yes
2030-09-18 10:00 | 2030 100% ECP | -700 | -526 | -510 | 212.69 | 0 | 0 | Yes
2030-09-18 11:00 | 2030 100% ECP | -700 | -526 | -510 | 240.25 | 0 | 0 | Yes
2030-09-18 12:00 | 2030 100% ECP | -700 | -526 | -510 | 222.28 | 0 | 0 | Yes
2030-09-18 13:00 | 2030 100% ECP | -700 | -526 | -510 | 223.56 | 0 | 0 | Yes
2030-09-18 14:00 | 2030 100% ECP | -700 | -526 | -510 | 82.02 | 0 | 0 | Yes
2030-09-18 15:00 | 2030 100% ECP | -700 | -526 | -510 | 173.5 | 0 | 0 | Yes
2030-09-18 16:00 | 2030 100% ECP | -700 | -526 | -510 | 345.39 | 0 | 0 | Yes
2030-09-18 17:00 | 2030 100% ECP | -650.65 | -526 | -510 | 510 | 0 | 0 | No
2030-09-18 18:00 | 2030 100% ECP | -230.65 | -526 | -510 | 510 | 0 | 0 | No
2030-09-18 19:00 | 2030 100% ECP | 189.35 | -526 | -510 | 510 | 0 | 0 | No
2030-09-18 20:00 | 2030 100% ECP | 609.35 | -300 | -390 | 385.12 | 0 | 0 | No
2030-09-18 21:00 | 2030 100% ECP | 423.12 | 0 | -90 | 455.55 | 0 | 0 | No
2030-09-18 22:00 | 2030 100% ECP | 700 | 300 | 210 | 510 | 0 | 0 | No
2030-09-18 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 04:00 | 2030 100% ECP | 700 | 505 | 506.59 | 510 | 0 | 0 | No
2030-09-19 05:00 | 2030 100% ECP | 280 | 205 | 206.59 | 210 | 0 | 0 | No
2030-09-19 06:00 | 2030 100% ECP | 560 | -95 | -93.41 | 194.01 | 0 | 0 | No
2030-09-19 07:00 | 2030 100% ECP | 140 | -395 | -393.41 | 412.9 | 0 | 0 | No
2030-09-19 08:00 | 2030 100% ECP | -280 | -526 | -510 | 134.94 | 0 | 0 | No
2030-09-19 09:00 | 2030 100% ECP | -700 | -526 | -510 | 105.87 | 0 | 0 | Yes
2030-09-19 10:00 | 2030 100% ECP | -700 | -526 | -510 | 289.21 | 0 | 0 | Yes
2030-09-19 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-09-19 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-09-19 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-09-19 14:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-09-19 15:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-09-19 16:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-19 17:00 | 2030 100% ECP | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-09-19 18:00 | 2030 100% ECP | 140 | -404.43 | -510 | 510 | 0 | 0 | No
2030-09-19 19:00 | 2030 100% ECP | 560 | -112.65 | -510 | 510 | 0 | 0 | No
2030-09-19 20:00 | 2030 100% ECP | 700 | -112.65 | -510 | 337.15 | 0 | 0 | No
2030-09-19 21:00 | 2030 100% ECP | 700 | -112.65 | -510 | 445.3 | 0 | 0 | No
2030-09-19 22:00 | 2030 100% ECP | 700 | -300 | -510 | 465.06 | 0 | 0 | No
2030-09-19 23:00 | 2030 100% ECP | 700 | 0 | -210 | 354.16 | 0 | 0 | No
2030-09-20 | 2030 100% ECP | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-09-20 01:00 | 2030 100% ECP | 700 | 0 | 390 | 210 | 0 | 0 | No
2030-09-20 02:00 | 2030 100% ECP | 700 | 0 | 510 | 210 | 0 | 0 | No
2030-09-20 03:00 | 2030 100% ECP | 700 | 43.39 | 510 | 510 | 0 | 0 | No
2030-09-20 04:00 | 2030 100% ECP | 700 | 43.66 | 510 | 507.55 | 0 | 0 | No
2030-09-20 05:00 | 2030 100% ECP | 700 | 0 | 210 | 207.55 | 0 | 0 | No
2030-09-20 06:00 | 2030 100% ECP | 560 | 0 | 3.85 | 124.91 | 0 | 0 | No
2030-09-20 07:00 | 2030 100% ECP | 140 | 0 | 3.85 | 270.38 | 0 | 0 | No
2030-09-20 08:00 | 2030 100% ECP | -280 | -226 | -210 | 405.56 | 0 | 0 | No
2030-09-20 09:00 | 2030 100% ECP | -700 | -526 | -510 | 364.68 | 0 | 0 | Yes
2030-09-20 10:00 | 2030 100% ECP | -700 | -526 | -510 | 243.52 | 0 | 0 | Yes
2030-09-20 11:00 | 2030 100% ECP | -700 | -526 | -510 | 242.03 | 0 | 0 | Yes
2030-09-20 12:00 | 2030 100% ECP | -700 | -526 | -510 | 212.38 | 0 | 0 | Yes
2030-09-20 13:00 | 2030 100% ECP | -700 | -526 | -510 | 186.15 | 0 | 0 | Yes
2030-09-20 14:00 | 2030 100% ECP | -700 | -526 | -510 | 177.04 | 0 | 0 | Yes
2030-09-20 15:00 | 2030 100% ECP | -700 | -526 | -510 | 207.55 | 0 | 0 | Yes
2030-09-20 16:00 | 2030 100% ECP | -560 | -526 | -510 | 303.47 | 0 | 0 | No
2030-09-20 17:00 | 2030 100% ECP | -140 | -226 | -210 | 300 | 0 | 0 | No
2030-09-20 18:00 | 2030 100% ECP | 280 | -526 | -510 | 0 | 0 | 0 | No
2030-09-20 19:00 | 2030 100% ECP | 700 | -526 | -510 | 105.04 | 0 | 0 | No
2030-09-20 20:00 | 2030 100% ECP | 700 | -226 | -210 | 405.04 | 0 | 0 | No
2030-09-20 21:00 | 2030 100% ECP | 700 | 0 | 0 | 252.54 | 0 | 0 | No
2030-09-20 22:00 | 2030 100% ECP | 700 | 0 | 0 | 169.58 | 0 | 0 | No
2030-09-20 23:00 | 2030 100% ECP | 700 | 0 | 0 | 97.51 | 0 | 0 | No
2030-09-21 | 2030 100% ECP | 700 | 0 | 150.79 | 329.88 | 0 | 0 | No
2030-09-21 01:00 | 2030 100% ECP | 700 | 0 | 450.79 | 29.88 | 0 | 0 | No
2030-09-21 02:00 | 2030 100% ECP | 700 | 0 | 150.79 | 86 | 0 | 0 | No
2030-09-21 03:00 | 2030 100% ECP | 700 | 0 | 381.27 | 0 | 0 | 0 | No
2030-09-21 04:00 | 2030 100% ECP | 700 | 0 | 107.24 | 0 | 0 | 0 | No
2030-09-21 05:00 | 2030 100% ECP | 700 | 0 | 107.24 | 0 | 0 | 0 | No
2030-09-21 06:00 | 2030 100% ECP | 481.71 | 0 | 90 | 165.08 | 0 | 0 | No
2030-09-21 07:00 | 2030 100% ECP | 61.71 | -226 | -210 | 465.08 | 0 | 0 | No
2030-09-21 08:00 | 2030 100% ECP | -358.29 | -526 | -510 | 465.08 | 0 | 0 | No
2030-09-21 09:00 | 2030 100% ECP | -700 | -526 | -510 | 165.08 | 0 | 0 | Yes
2030-09-21 10:00 | 2030 100% ECP | -700 | -526 | -510 | 48.51 | 0 | 0 | Yes
2030-09-21 11:00 | 2030 100% ECP | -700 | -526 | -510 | 11.88 | 0 | 0 | Yes
2030-09-21 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-09-21 13:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-09-21 14:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-09-21 15:00 | 2030 100% ECP | -700 | -526 | -510 | 75.47 | 0 | 0 | Yes
2030-09-21 16:00 | 2030 100% ECP | -700 | -526 | -510 | 75.47 | 0 | 0 | No
2030-09-21 17:00 | 2030 100% ECP | -280 | -526 | -510 | -224.53 | 0 | 0 | No
2030-09-21 18:00 | 2030 100% ECP | 140 | -526 | -510 | -510 | 0 | 0 | No
2030-09-21 19:00 | 2030 100% ECP | 560 | -526 | -510 | -253.78 | 0 | 0 | No
2030-09-21 20:00 | 2030 100% ECP | 700 | -526 | -510 | -11.6 | 0 | 0 | No
2030-09-21 21:00 | 2030 100% ECP | 700 | -226 | -372.91 | 287.52 | 0 | 0 | No
2030-09-21 22:00 | 2030 100% ECP | 700 | 0 | -372.91 | 134.77 | 0 | 0 | No
2030-09-21 23:00 | 2030 100% ECP | 700 | 0 | -372.91 | 17.25 | 0 | 0 | No
2030-09-22 | 2030 100% ECP | 700 | 0 | -344.08 | 0 | 0 | 0 | No
2030-09-22 01:00 | 2030 100% ECP | 700 | 0 | -510 | -23.07 | 0 | 0 | No
2030-09-22 02:00 | 2030 100% ECP | 700 | -274.71 | -510 | -115.92 | 0 | 0 | No
2030-09-22 03:00 | 2030 100% ECP | 280 | -526 | -510 | -155.04 | 0 | 0 | No
2030-09-22 04:00 | 2030 100% ECP | 700 | -526 | -510 | -200.8 | 0 | 0 | No
2030-09-22 05:00 | 2030 100% ECP | 325.69 | -526 | -510 | -269.46 | 0 | 0 | No
2030-09-22 06:00 | 2030 100% ECP | -94.31 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 07:00 | 2030 100% ECP | -514.31 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 09:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-09-22 10:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-09-22 11:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-09-22 12:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-09-22 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-22 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-22 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-22 16:00 | 2030 100% ECP | -430.4 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-22 17:00 | 2030 100% ECP | -10.4 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 18:00 | 2030 100% ECP | 409.6 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 19:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 20:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 21:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 05:00 | 2030 100% ECP | 700 | 208.39 | 210 | 510 | 0 | 0 | No
2030-09-23 06:00 | 2030 100% ECP | 700 | -19.95 | -90 | 229.83 | 0 | 0 | No
2030-09-23 07:00 | 2030 100% ECP | 700 | -263.53 | -390 | 406.69 | 0 | 0 | No
2030-09-23 08:00 | 2030 100% ECP | 700 | -526 | -510 | 488.04 | 0 | 0 | No
2030-09-23 09:00 | 2030 100% ECP | 700 | -526 | -510 | 488.04 | 0 | 0 | No
2030-09-23 10:00 | 2030 100% ECP | 700 | -526 | -510 | 488.04 | 0 | 0 | No
2030-09-23 11:00 | 2030 100% ECP | 700 | -526 | -510 | 475.64 | 0 | 0 | No
2030-09-23 12:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-23 13:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-23 14:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-23 15:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-23 16:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-23 17:00 | 2030 100% ECP | 700 | -526 | -510 | 478.16 | 0 | 0 | No
2030-09-23 18:00 | 2030 100% ECP | 700 | -526 | -510 | 478.16 | 0 | 0 | No
2030-09-23 19:00 | 2030 100% ECP | 700 | -526 | -510 | 478.16 | 0 | 0 | No
2030-09-23 20:00 | 2030 100% ECP | 700 | -259.82 | -510 | 474.1 | 0 | 0 | No
2030-09-23 21:00 | 2030 100% ECP | 700 | -259.82 | -210 | 419.59 | 0 | 0 | No
2030-09-23 22:00 | 2030 100% ECP | 700 | 1.57 | 90 | 270.92 | 0 | 0 | No
2030-09-23 23:00 | 2030 100% ECP | 380.31 | 301.57 | 390 | 510 | 0 | 0 | No
2030-09-24 | 2030 100% ECP | 23.14 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 01:00 | 2030 100% ECP | -396.86 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 05:00 | 2030 100% ECP | -700 | 258.57 | 210 | 390 | 0 | 0 | No
2030-09-24 06:00 | 2030 100% ECP | -280 | -41.43 | -90 | 90 | 0 | 0 | No
2030-09-24 07:00 | 2030 100% ECP | 25.21 | -341.43 | -390 | -210 | 0 | 0 | No
2030-09-24 08:00 | 2030 100% ECP | 25.21 | -526 | -510 | -510 | 0 | 0 | No
2030-09-24 09:00 | 2030 100% ECP | -280 | -526 | -510 | -210 | 0 | 0 | No
2030-09-24 10:00 | 2030 100% ECP | -700 | -272.08 | -510 | 90 | 0 | 0 | No
2030-09-24 11:00 | 2030 100% ECP | -700 | -380.44 | -510 | 390 | 0 | 0 | No
2030-09-24 12:00 | 2030 100% ECP | -700 | -526 | -510 | 90.82 | 0 | 0 | No
2030-09-24 13:00 | 2030 100% ECP | -700 | -374.54 | -510 | 183.61 | 0 | 0 | Yes
2030-09-24 14:00 | 2030 100% ECP | -700 | -526 | -510 | -116.39 | 0 | 0 | Yes
2030-09-24 15:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-09-24 16:00 | 2030 100% ECP | -700 | -526 | -510 | 102.2 | 0 | 0 | No
2030-09-24 17:00 | 2030 100% ECP | -700 | -526 | -510 | 402.2 | 0 | 0 | No
2030-09-24 18:00 | 2030 100% ECP | -420 | -526 | -510 | 280.54 | 0 | 0 | No
2030-09-24 19:00 | 2030 100% ECP | 0 | -526 | -510 | 510 | 0 | 0 | No
2030-09-24 20:00 | 2030 100% ECP | 0 | -526 | -510 | 499.17 | 0 | 0 | No
2030-09-24 21:00 | 2030 100% ECP | 0 | -526 | -510 | 510 | 0 | 0 | No
2030-09-24 22:00 | 2030 100% ECP | -144.18 | -324.66 | -510 | 510 | 0 | 0 | No
2030-09-24 23:00 | 2030 100% ECP | -564.18 | -24.66 | -210 | 510 | 0 | 0 | No
2030-09-25 | 2030 100% ECP | -700 | 275.34 | 90 | 510 | 0 | 0 | No
2030-09-25 01:00 | 2030 100% ECP | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-09-25 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 17:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 18:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 19:00 | 2030 100% ECP | 560 | 505 | 510 | 477.24 | 0 | 0 | No
2030-09-25 20:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 21:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 06:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 07:00 | 2030 100% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 08:00 | 2030 100% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 09:00 | 2030 100% ECP | -560 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-26 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-26 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-26 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-26 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-26 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-26 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-26 16:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-26 17:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 18:00 | 2030 100% ECP | 560 | 205 | 210 | 510 | 0 | 0 | No
2030-09-26 19:00 | 2030 100% ECP | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-09-26 20:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 21:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 06:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 07:00 | 2030 100% ECP | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-09-27 08:00 | 2030 100% ECP | 280 | -86.81 | -90 | 510 | 0 | 0 | No
2030-09-27 09:00 | 2030 100% ECP | -140 | -386.81 | -390 | 510 | 0 | 0 | No
2030-09-27 10:00 | 2030 100% ECP | -560 | -526 | -510 | 510 | 0 | 0 | Yes
2030-09-27 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-09-27 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-09-27 13:00 | 2030 100% ECP | -700 | -526 | -510 | 339.28 | 0 | 0 | Yes
2030-09-27 14:00 | 2030 100% ECP | -700 | -526 | -510 | 340.27 | 0 | 0 | No
2030-09-27 15:00 | 2030 100% ECP | -280 | -526 | -510 | 383.61 | 0 | 0 | No
2030-09-27 16:00 | 2030 100% ECP | 140 | -526 | -510 | 488.18 | 0 | 0 | No
2030-09-27 17:00 | 2030 100% ECP | 560 | -526 | -510 | 510 | 0 | 0 | No
2030-09-27 18:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-27 19:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-27 20:00 | 2030 100% ECP | 700 | -526 | -510 | 494.9 | 0 | 0 | No
2030-09-27 21:00 | 2030 100% ECP | 700 | -339.92 | -510 | 510 | 0 | 0 | No
2030-09-27 22:00 | 2030 100% ECP | 700 | -526 | -510 | 349.4 | 0 | 0 | No
2030-09-27 23:00 | 2030 100% ECP | 700 | -526 | -510 | 195.83 | 0 | 0 | No
2030-09-28 | 2030 100% ECP | 700 | -226 | -510 | -77.53 | 0 | 0 | No
2030-09-28 01:00 | 2030 100% ECP | 700 | -311.68 | -510 | -103.63 | 0 | 0 | No
2030-09-28 02:00 | 2030 100% ECP | 700 | -526 | -510 | -99.12 | 0 | 0 | No
2030-09-28 03:00 | 2030 100% ECP | 700 | -498.88 | -510 | -63.38 | 0 | 0 | No
2030-09-28 04:00 | 2030 100% ECP | 700 | -198.88 | -510 | 0 | 0 | 0 | No
2030-09-28 05:00 | 2030 100% ECP | 700 | 0 | -510 | -96.77 | 0 | 0 | No
2030-09-28 06:00 | 2030 100% ECP | 560 | 0 | -510 | -123.6 | 0 | 0 | No
2030-09-28 07:00 | 2030 100% ECP | 140 | 0 | -239.18 | 151 | 0 | 0 | No
2030-09-28 08:00 | 2030 100% ECP | -280 | -226 | -239.18 | 275.35 | 0 | 0 | No
2030-09-28 09:00 | 2030 100% ECP | -700 | -526 | -510 | 327 | 0 | 0 | No
2030-09-28 10:00 | 2030 100% ECP | -700 | -526 | -510 | 288.34 | 0 | 0 | No
2030-09-28 11:00 | 2030 100% ECP | -700 | -526 | -510 | 290.5 | 0 | 0 | No
2030-09-28 12:00 | 2030 100% ECP | -700 | -526 | -510 | 250.97 | 0 | 0 | No
2030-09-28 13:00 | 2030 100% ECP | -700 | -526 | -510 | 55.01 | 0 | 0 | No
2030-09-28 14:00 | 2030 100% ECP | -700 | -526 | -510 | -244.99 | 0 | 0 | No
2030-09-28 15:00 | 2030 100% ECP | -560 | -526 | -510 | -237.62 | 0 | 0 | No
2030-09-28 16:00 | 2030 100% ECP | -140 | -526 | -510 | 36.75 | 0 | 0 | No
2030-09-28 17:00 | 2030 100% ECP | 280 | -226 | -451.43 | 0 | 0 | 0 | No
2030-09-28 18:00 | 2030 100% ECP | 700 | 0 | -151.43 | 300 | 0 | 0 | No
2030-09-28 19:00 | 2030 100% ECP | 700 | 0 | 0 | 172.13 | 0 | 0 | No
2030-09-28 20:00 | 2030 100% ECP | 700 | 0 | 0 | 165.82 | 0 | 0 | No
2030-09-28 21:00 | 2030 100% ECP | 700 | 0 | 0 | 165.82 | 0 | 0 | No
2030-09-28 22:00 | 2030 100% ECP | 700 | 0 | 0 | 150.34 | 0 | 0 | No
2030-09-28 23:00 | 2030 100% ECP | 700 | 0 | 0 | 275.95 | 0 | 0 | No
2030-09-29 | 2030 100% ECP | 700 | 0 | -300 | 421.1 | 0 | 0 | No
2030-09-29 01:00 | 2030 100% ECP | 700 | 0 | -266.32 | 428.76 | 0 | 0 | No
2030-09-29 02:00 | 2030 100% ECP | 700 | 0 | -340.85 | 447.32 | 0 | 0 | No
2030-09-29 03:00 | 2030 100% ECP | 700 | 0 | -210 | 416.61 | 0 | 0 | No
2030-09-29 04:00 | 2030 100% ECP | 700 | 0 | -510 | 407.69 | 0 | 0 | No
2030-09-29 05:00 | 2030 100% ECP | 700 | 0 | -244.31 | 385.87 | 0 | 0 | No
2030-09-29 06:00 | 2030 100% ECP | 560 | 0 | -315.99 | 415.6 | 0 | 0 | No
2030-09-29 07:00 | 2030 100% ECP | 140 | -82.06 | -510 | 478.25 | 0 | 0 | No
2030-09-29 08:00 | 2030 100% ECP | -280 | -382.06 | -510 | 270.58 | 0 | 0 | No
2030-09-29 09:00 | 2030 100% ECP | -700 | -526 | -510 | 236.81 | 0 | 0 | Yes
2030-09-29 10:00 | 2030 100% ECP | -700 | -526 | -510 | 199.8 | 0 | 0 | Yes
2030-09-29 11:00 | 2030 100% ECP | -700 | -526 | -510 | 103.64 | 0 | 0 | Yes
2030-09-29 12:00 | 2030 100% ECP | -700 | -526 | -510 | 126.79 | 0 | 0 | Yes
2030-09-29 13:00 | 2030 100% ECP | -700 | -526 | -510 | 90.57 | 0 | 0 | Yes
2030-09-29 14:00 | 2030 100% ECP | -700 | -526 | -510 | 0.01 | 0 | 0 | Yes
2030-09-29 15:00 | 2030 100% ECP | -700 | -526 | -510 | 4.67 | 0 | 0 | Yes
2030-09-29 16:00 | 2030 100% ECP | -700 | -526 | -510 | 232.33 | 0 | 0 | No
2030-09-29 17:00 | 2030 100% ECP | -700 | -526 | -510 | 178.61 | 0 | 0 | No
2030-09-29 18:00 | 2030 100% ECP | -700 | -526 | -510 | 157.61 | 0 | 0 | No
2030-09-29 19:00 | 2030 100% ECP | -700 | -526 | -510 | 178.29 | 0 | 0 | No
2030-09-29 20:00 | 2030 100% ECP | -700 | -526 | -510 | -117.28 | 0 | 0 | Yes
2030-09-29 21:00 | 2030 100% ECP | -700 | -526 | -510 | -298.52 | 0 | 0 | Yes
2030-09-29 22:00 | 2030 100% ECP | -700 | -526 | -510 | -321.92 | 0 | 0 | Yes
2030-09-29 23:00 | 2030 100% ECP | -700 | -526 | -510 | -262.92 | 0 | 0 | Yes
2030-09-30 | 2030 100% ECP | -280 | -226 | -210 | 37.08 | 0 | 0 | No
2030-09-30 01:00 | 2030 100% ECP | 0 | 74 | 90 | 337.08 | 0 | 0 | No
2030-09-30 02:00 | 2030 100% ECP | 62.86 | 374 | 390 | 510 | 0 | 0 | No
2030-09-30 03:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 04:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 05:00 | 2030 100% ECP | 420 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 06:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 07:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 08:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 09:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 10:00 | 2030 100% ECP | 420 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 11:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 12:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 13:00 | 2030 100% ECP | 83.91 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 14:00 | 2030 100% ECP | 503.91 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 15:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 16:00 | 2030 100% ECP | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-09-30 17:00 | 2030 100% ECP | 700 | 141.26 | 300 | 510 | 0 | 0 | No
2030-09-30 18:00 | 2030 100% ECP | 700 | -156.69 | 0 | 510 | 0 | 0 | No
2030-09-30 19:00 | 2030 100% ECP | 700 | 3.98 | 300 | 510 | 0 | 0 | No
2030-09-30 20:00 | 2030 100% ECP | 700 | 205 | 224.79 | 510 | 0 | 0 | No
2030-09-30 21:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-30 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-01 04:00 | 2030 100% ECP | 700 | 300 | 387.7 | 510 | 0 | 0 | No
2030-10-01 05:00 | 2030 100% ECP | 700 | 0 | 87.7 | 210 | 0 | 0 | No
2030-10-01 06:00 | 2030 100% ECP | 700 | 0 | -120.38 | 0 | 0 | 0 | No
2030-10-01 07:00 | 2030 100% ECP | 700 | 0 | -276.17 | 75.34 | 0 | 0 | No
2030-10-01 08:00 | 2030 100% ECP | 700 | -226 | -510 | 154.99 | 0 | 0 | No
2030-10-01 09:00 | 2030 100% ECP | 700 | -526 | -510 | 126.21 | 0 | 0 | No
2030-10-01 10:00 | 2030 100% ECP | 280 | -526 | -510 | 63.76 | 0 | 0 | No
2030-10-01 11:00 | 2030 100% ECP | -140 | -526 | -510 | 0 | 0 | 0 | No
2030-10-01 12:00 | 2030 100% ECP | -243.85 | -526 | -510 | 0 | 0 | 0 | No
2030-10-01 13:00 | 2030 100% ECP | 176.15 | -526 | -510 | 0 | 0 | 0 | No
2030-10-01 14:00 | 2030 100% ECP | 596.15 | -526 | -510 | 0 | 0 | 0 | No
2030-10-01 15:00 | 2030 100% ECP | 700 | -526 | -510 | 22.46 | 0 | 0 | No
2030-10-01 16:00 | 2030 100% ECP | 700 | -526 | -510 | -277.54 | 0 | 0 | No
2030-10-01 17:00 | 2030 100% ECP | 700 | -526 | -510 | -277.54 | 0 | 0 | No
2030-10-01 18:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-01 19:00 | 2030 100% ECP | 700 | -526 | -510 | -402.47 | 0 | 0 | No
2030-10-01 20:00 | 2030 100% ECP | 700 | -526 | -510 | -102.47 | 0 | 0 | No
2030-10-01 21:00 | 2030 100% ECP | 700 | -226 | -510 | 0 | 0 | 0 | No
2030-10-01 22:00 | 2030 100% ECP | 700 | 0 | -510 | 197.15 | 0 | 0 | No
2030-10-01 23:00 | 2030 100% ECP | 700 | -80.64 | -510 | 110.46 | 0 | 0 | No
2030-10-02 | 2030 100% ECP | 700 | -380.64 | -510 | -14.73 | 0 | 0 | No
2030-10-02 01:00 | 2030 100% ECP | 700 | -526 | -510 | -0.4 | 0 | 0 | No
2030-10-02 02:00 | 2030 100% ECP | 280 | -226 | -328.69 | 210 | 0 | 0 | No
2030-10-02 03:00 | 2030 100% ECP | -140 | 74 | -28.69 | 510 | 0 | 0 | No
2030-10-02 04:00 | 2030 100% ECP | -560 | 374 | 271.31 | 510 | 0 | 0 | No
2030-10-02 05:00 | 2030 100% ECP | -420 | 81.92 | -28.69 | 510 | 0 | 0 | No
2030-10-02 06:00 | 2030 100% ECP | 0 | -218.08 | -328.69 | 210 | 0 | 0 | No
2030-10-02 07:00 | 2030 100% ECP | 0 | -105.13 | -398.82 | 510 | 0 | 0 | No
2030-10-02 08:00 | 2030 100% ECP | -420 | -405.13 | -510 | 510 | 0 | 0 | No
2030-10-02 09:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-10-02 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-10-02 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-10-02 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-10-02 13:00 | 2030 100% ECP | -700 | -526 | -510 | 307.57 | 0 | 0 | Yes
2030-10-02 14:00 | 2030 100% ECP | -700 | -526 | -510 | 472.83 | 0 | 0 | Yes
2030-10-02 15:00 | 2030 100% ECP | -700 | -526 | -510 | 172.83 | 0 | 0 | Yes
2030-10-02 16:00 | 2030 100% ECP | -700 | -526 | -510 | 343.44 | 0 | 0 | Yes
2030-10-02 17:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-02 18:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-02 19:00 | 2030 100% ECP | -410.46 | -395 | -390 | 332.95 | 0 | 0 | No
2030-10-02 20:00 | 2030 100% ECP | 9.54 | -95 | -90 | 261.91 | 0 | 0 | No
2030-10-02 21:00 | 2030 100% ECP | 429.54 | 205 | 210 | 510 | 0 | 0 | No
2030-10-02 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-02 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-03 06:00 | 2030 100% ECP | 281.87 | 205 | 210 | 458.72 | 0 | 0 | No
2030-10-03 07:00 | 2030 100% ECP | -138.13 | -95 | -90 | 307.91 | 0 | 0 | No
2030-10-03 08:00 | 2030 100% ECP | 93.09 | -226 | -300 | 510 | 0 | 0 | No
2030-10-03 09:00 | 2030 100% ECP | 513.09 | 74 | 0 | 510 | 0 | 0 | No
2030-10-03 10:00 | 2030 100% ECP | 93.09 | -226 | -210 | 406.83 | 0 | 0 | No
2030-10-03 11:00 | 2030 100% ECP | -326.91 | -526 | -510 | 106.83 | 0 | 0 | No
2030-10-03 12:00 | 2030 100% ECP | -700 | -526 | -510 | -193.17 | 0 | 0 | No
2030-10-03 13:00 | 2030 100% ECP | -700 | -526 | -510 | -18.35 | 0 | 0 | No
2030-10-03 14:00 | 2030 100% ECP | -700 | -526 | -510 | 63.96 | 0 | 0 | No
2030-10-03 15:00 | 2030 100% ECP | -700 | -526 | -510 | 231.15 | 0 | 0 | No
2030-10-03 16:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-10-03 17:00 | 2030 100% ECP | -560 | -526 | -510 | 0 | 0 | 0 | No
2030-10-03 18:00 | 2030 100% ECP | -140 | -395 | -390 | 0 | 0 | 0 | No
2030-10-03 19:00 | 2030 100% ECP | 280 | -95 | -90 | 120.78 | 0 | 0 | No
2030-10-03 20:00 | 2030 100% ECP | 700 | 205 | 210 | 420.78 | 0 | 0 | No
2030-10-03 21:00 | 2030 100% ECP | 393.28 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-03 22:00 | 2030 100% ECP | -26.72 | 505 | 510 | 366.12 | 0 | 0 | Yes
2030-10-03 23:00 | 2030 100% ECP | -446.72 | 505 | 510 | 82.61 | 0 | 0 | Yes
2030-10-04 | 2030 100% ECP | -700 | 505 | 510 | 147.83 | 0 | 0 | Yes
2030-10-04 01:00 | 2030 100% ECP | -700 | 505 | 510 | 396.93 | 0 | 0 | Yes
2030-10-04 02:00 | 2030 100% ECP | -700 | 505 | 510 | 396.93 | 0 | 0 | Yes
2030-10-04 03:00 | 2030 100% ECP | -700 | 505 | 510 | 96.93 | 0 | 0 | Yes
2030-10-04 04:00 | 2030 100% ECP | -700 | 386.63 | 390 | 396.93 | 0 | 0 | Yes
2030-10-04 05:00 | 2030 100% ECP | -700 | 86.63 | 90 | 152.15 | 0 | 0 | Yes
2030-10-04 06:00 | 2030 100% ECP | -700 | -213.37 | -210 | -147.85 | 0 | 0 | Yes
2030-10-04 07:00 | 2030 100% ECP | -700 | -513.37 | -510 | -447.85 | 0 | 0 | Yes
2030-10-04 08:00 | 2030 100% ECP | -700 | -526 | -510 | -147.85 | 0 | 0 | Yes
2030-10-04 09:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-10-04 10:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | Yes
2030-10-04 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-10-04 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-10-04 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-10-04 14:00 | 2030 100% ECP | -700 | -395.14 | -510 | 510 | 0 | 0 | Yes
2030-10-04 15:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-10-04 16:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-10-04 17:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-10-04 18:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-04 19:00 | 2030 100% ECP | -700 | -526 | -510 | 419.62 | 0 | 0 | No
2030-10-04 20:00 | 2030 100% ECP | -700 | -526 | -510 | 419.62 | 0 | 0 | No
2030-10-04 21:00 | 2030 100% ECP | -700 | -526 | -510 | 419.62 | 0 | 0 | No
2030-10-04 22:00 | 2030 100% ECP | -700 | -526 | -510 | 148.56 | 0 | 0 | No
2030-10-04 23:00 | 2030 100% ECP | -700 | -526 | -510 | 448.56 | 0 | 0 | No
2030-10-05 | 2030 100% ECP | -280 | -430.11 | -510 | 510 | 0 | 0 | No
2030-10-05 01:00 | 2030 100% ECP | 0 | -300 | -300 | 510 | 0 | 0 | No
2030-10-05 02:00 | 2030 100% ECP | -15 | 0 | 0 | 510 | 0 | 0 | No
2030-10-05 03:00 | 2030 100% ECP | 0 | 0 | -139.77 | 510 | 0 | 0 | No
2030-10-05 04:00 | 2030 100% ECP | -227.44 | -300 | -439.77 | 432.22 | 0 | 0 | No
2030-10-05 05:00 | 2030 100% ECP | 0 | -526 | -510 | 132.22 | 0 | 0 | No
2030-10-05 06:00 | 2030 100% ECP | 0 | -526 | -510 | 231.38 | 0 | 0 | No
2030-10-05 07:00 | 2030 100% ECP | 280 | -526 | -510 | 0 | 0 | 0 | No
2030-10-05 08:00 | 2030 100% ECP | 700 | -526 | -510 | 231 | 0 | 0 | No
2030-10-05 09:00 | 2030 100% ECP | 280 | -526 | -510 | 492.86 | 0 | 0 | No
2030-10-05 10:00 | 2030 100% ECP | -138.44 | -526 | -510 | 503.41 | 0 | 0 | No
2030-10-05 11:00 | 2030 100% ECP | -558.44 | -526 | -510 | 409.8 | 0 | 0 | No
2030-10-05 12:00 | 2030 100% ECP | -558.44 | -526 | -510 | 109.8 | 0 | 0 | No
2030-10-05 13:00 | 2030 100% ECP | -138.44 | -526 | -510 | -111.61 | 0 | 0 | No
2030-10-05 14:00 | 2030 100% ECP | 109.56 | -526 | -510 | -199.91 | 0 | 0 | No
2030-10-05 15:00 | 2030 100% ECP | 529.56 | -526 | -510 | 37.62 | 0 | 0 | No
2030-10-05 16:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-10-05 17:00 | 2030 100% ECP | 700 | -526 | -510 | 201.21 | 0 | 0 | No
2030-10-05 18:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-10-05 19:00 | 2030 100% ECP | 700 | -526 | -510 | 300 | 0 | 0 | No
2030-10-05 20:00 | 2030 100% ECP | 700 | -526 | -510 | 386.13 | 0 | 0 | No
2030-10-05 21:00 | 2030 100% ECP | 560 | -526 | -510 | 510 | 0 | 0 | No
2030-10-05 22:00 | 2030 100% ECP | 140 | -300 | -430.8 | 434.18 | 0 | 0 | No
2030-10-05 23:00 | 2030 100% ECP | -280 | 0 | -130.8 | 510 | 0 | 0 | No
2030-10-06 | 2030 100% ECP | -700 | 300 | 169.2 | 510 | 0 | 0 | No
2030-10-06 01:00 | 2030 100% ECP | -700 | 505 | 469.2 | 510 | 0 | 0 | Yes
2030-10-06 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-06 03:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-10-06 04:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | No
2030-10-06 05:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-10-06 06:00 | 2030 100% ECP | -700 | -526 | -510 | 383.77 | 0 | 0 | No
2030-10-06 07:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-06 08:00 | 2030 100% ECP | -700 | -526 | -510 | 473.62 | 0 | 0 | No
2030-10-06 09:00 | 2030 100% ECP | -700 | -526 | -510 | 402.71 | 0 | 0 | Yes
2030-10-06 10:00 | 2030 100% ECP | -700 | -526 | -510 | 282.64 | 0 | 0 | Yes
2030-10-06 11:00 | 2030 100% ECP | -700 | -526 | -510 | 147.32 | 0 | 0 | Yes
2030-10-06 12:00 | 2030 100% ECP | -700 | -526 | -510 | 19.48 | 0 | 0 | Yes
2030-10-06 13:00 | 2030 100% ECP | -700 | -526 | -510 | 30.83 | 0 | 0 | Yes
2030-10-06 14:00 | 2030 100% ECP | -700 | -476.56 | -510 | 330.83 | 0 | 0 | Yes
2030-10-06 15:00 | 2030 100% ECP | -700 | -526 | -510 | 30.83 | 0 | 0 | Yes
2030-10-06 16:00 | 2030 100% ECP | -700 | -526 | -510 | -269.17 | 0 | 0 | Yes
2030-10-06 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-06 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-06 19:00 | 2030 100% ECP | -700 | -526 | -510 | -314.85 | 0 | 0 | No
2030-10-06 20:00 | 2030 100% ECP | -700 | -226 | -210 | -14.85 | 0 | 0 | No
2030-10-06 21:00 | 2030 100% ECP | -700 | 74 | 90 | 285.15 | 0 | 0 | No
2030-10-06 22:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-10-06 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 01:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 02:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 06:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 07:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 08:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 09:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 10:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 11:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 12:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 13:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 14:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 15:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-07 16:00 | 2030 100% ECP | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-10-07 17:00 | 2030 100% ECP | 700 | -95 | -90 | 510 | 0 | 0 | No
2030-10-07 18:00 | 2030 100% ECP | 280 | -395 | -390 | 510 | 0 | 0 | No
2030-10-07 19:00 | 2030 100% ECP | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-07 20:00 | 2030 100% ECP | 700 | -526 | -510 | 439.26 | 0 | 0 | No
2030-10-07 21:00 | 2030 100% ECP | 700 | -300 | -387.37 | 439.26 | 0 | 0 | No
2030-10-07 22:00 | 2030 100% ECP | 700 | 0 | -87.37 | 418.19 | 0 | 0 | No
2030-10-07 23:00 | 2030 100% ECP | 700 | 300 | 212.63 | 510 | 0 | 0 | No
2030-10-08 | 2030 100% ECP | 700 | 174.99 | 510 | 510 | 0 | 0 | No
2030-10-08 01:00 | 2030 100% ECP | 700 | 440.14 | 510 | 510 | 0 | 0 | No
2030-10-08 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 06:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-08 07:00 | 2030 100% ECP | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-10-08 08:00 | 2030 100% ECP | 700 | 0 | -15.99 | 510 | 0 | 0 | No
2030-10-08 09:00 | 2030 100% ECP | 700 | 0 | -27.62 | 510 | 0 | 0 | No
2030-10-08 10:00 | 2030 100% ECP | 280 | 0 | 0 | 510 | 0 | 0 | No
2030-10-08 11:00 | 2030 100% ECP | 0 | 0 | -99.6 | 510 | 0 | 0 | No
2030-10-08 12:00 | 2030 100% ECP | 0 | 0 | -67.33 | 510 | 0 | 0 | No
2030-10-08 13:00 | 2030 100% ECP | 0 | 0 | -124.85 | 510 | 0 | 0 | No
2030-10-08 14:00 | 2030 100% ECP | 0 | -226 | -210 | 510 | 0 | 0 | No
2030-10-08 15:00 | 2030 100% ECP | 211.88 | -526 | -510 | 210 | 0 | 0 | No
2030-10-08 16:00 | 2030 100% ECP | 631.88 | -526 | -510 | 395.99 | 0 | 0 | No
2030-10-08 17:00 | 2030 100% ECP | 211.88 | -526 | -510 | 510 | 0 | 0 | No
2030-10-08 18:00 | 2030 100% ECP | -208.12 | -526 | -510 | 510 | 0 | 0 | No
2030-10-08 19:00 | 2030 100% ECP | -628.12 | -526 | -510 | 510 | 0 | 0 | No
2030-10-08 20:00 | 2030 100% ECP | -612.92 | -526 | -510 | 397 | 0 | 0 | No
2030-10-08 21:00 | 2030 100% ECP | -192.92 | -526 | -510 | 97 | 0 | 0 | No
2030-10-08 22:00 | 2030 100% ECP | 227.08 | -526 | -510 | -203 | 0 | 0 | No
2030-10-08 23:00 | 2030 100% ECP | 647.08 | -395 | -510 | -30.44 | 0 | 0 | No
2030-10-09 | 2030 100% ECP | 700 | -95 | -210 | 210 | 0 | 0 | No
2030-10-09 01:00 | 2030 100% ECP | 700 | 205 | 90 | 510 | 0 | 0 | No
2030-10-09 02:00 | 2030 100% ECP | 700 | 505 | 390 | 510 | 0 | 0 | No
2030-10-09 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-09 05:00 | 2030 100% ECP | 280 | 205 | 210 | 210 | 0 | 0 | No
2030-10-09 06:00 | 2030 100% ECP | 0 | -95 | -90 | -90 | 0 | 0 | No
2030-10-09 07:00 | 2030 100% ECP | 0 | -395 | -390 | -390 | 0 | 0 | No
2030-10-09 08:00 | 2030 100% ECP | 0 | -526 | -510 | -449.03 | 0 | 0 | No
2030-10-09 09:00 | 2030 100% ECP | -361.52 | -526 | -510 | -149.03 | 0 | 0 | No
2030-10-09 10:00 | 2030 100% ECP | -700 | -422.31 | -510 | 150.97 | 0 | 0 | No
2030-10-09 11:00 | 2030 100% ECP | -700 | -122.31 | -210 | 450.97 | 0 | 0 | Yes
2030-10-09 12:00 | 2030 100% ECP | -700 | 177.69 | 90 | 510 | 0 | 0 | Yes
2030-10-09 13:00 | 2030 100% ECP | -700 | 440.09 | 390 | 510 | 0 | 0 | Yes
2030-10-09 14:00 | 2030 100% ECP | -700 | 140.09 | 90 | 510 | 0 | 0 | Yes
2030-10-09 15:00 | 2030 100% ECP | -700 | -159.91 | -210 | 510 | 0 | 0 | Yes
2030-10-09 16:00 | 2030 100% ECP | -280 | -459.91 | -510 | 280.1 | 0 | 0 | No
2030-10-09 17:00 | 2030 100% ECP | -700 | -526 | -510 | 117.68 | 0 | 0 | No
2030-10-09 18:00 | 2030 100% ECP | -560 | -526 | -510 | 417.68 | 0 | 0 | No
2030-10-09 19:00 | 2030 100% ECP | -140 | -300 | -233.22 | 210 | 0 | 0 | No
2030-10-09 20:00 | 2030 100% ECP | 280 | 0 | 66.78 | 510 | 0 | 0 | No
2030-10-09 21:00 | 2030 100% ECP | 700 | 300 | 366.78 | 510 | 0 | 0 | No
2030-10-09 22:00 | 2030 100% ECP | 638.02 | 365.56 | 510 | 510 | 0 | 0 | No
2030-10-09 23:00 | 2030 100% ECP | 218.02 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 01:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 02:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 03:00 | 2030 100% ECP | -326.63 | 505 | 510 | 510 | 0 | 0 | No
2030-10-10 04:00 | 2030 100% ECP | 0 | 374 | 390 | 510 | 0 | 0 | No
2030-10-10 05:00 | 2030 100% ECP | -280 | 74 | 90 | 210 | 0 | 0 | No
2030-10-10 06:00 | 2030 100% ECP | -700 | -226 | -210 | -90 | 0 | 0 | No
2030-10-10 07:00 | 2030 100% ECP | -700 | -526 | -510 | -390 | 0 | 0 | No
2030-10-10 08:00 | 2030 100% ECP | -700 | -526 | -510 | -133.13 | 0 | 0 | No
2030-10-10 09:00 | 2030 100% ECP | -700 | -526 | -510 | 166.87 | 0 | 0 | No
2030-10-10 10:00 | 2030 100% ECP | -700 | -226 | -210 | 466.87 | 0 | 0 | No
2030-10-10 11:00 | 2030 100% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-10-10 12:00 | 2030 100% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-10-10 13:00 | 2030 100% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-10-10 14:00 | 2030 100% ECP | -535.71 | 0 | -199.96 | 510 | 0 | 0 | No
2030-10-10 15:00 | 2030 100% ECP | -182.55 | -162.7 | -478.29 | 467.72 | 0 | 0 | No
2030-10-10 16:00 | 2030 100% ECP | -158.03 | -462.7 | -510 | 167.72 | 0 | 0 | No
2030-10-10 17:00 | 2030 100% ECP | -578.03 | -526 | -510 | 391.16 | 0 | 0 | No
2030-10-10 18:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-10 19:00 | 2030 100% ECP | -700 | -526 | -510 | 381.25 | 0 | 0 | No
2030-10-10 20:00 | 2030 100% ECP | -442.66 | -395 | -396.35 | 81.25 | 0 | 0 | No
2030-10-10 21:00 | 2030 100% ECP | -22.66 | -95 | -96.35 | 81.25 | 0 | 0 | No
2030-10-10 22:00 | 2030 100% ECP | 397.34 | 205 | 203.65 | 258.58 | 0 | 0 | No
2030-10-10 23:00 | 2030 100% ECP | 700 | 505 | 503.65 | 510 | 0 | 0 | No
2030-10-11 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-11 06:00 | 2030 100% ECP | 562.96 | 205 | 210 | 210 | 0 | 0 | No
2030-10-11 07:00 | 2030 100% ECP | 632.34 | 0 | 0 | 272.19 | 0 | 0 | No
2030-10-11 08:00 | 2030 100% ECP | 212.34 | 0 | 0 | 114.48 | 0 | 0 | No
2030-10-11 09:00 | 2030 100% ECP | -207.66 | -226 | -210 | 380 | 0 | 0 | No
2030-10-11 10:00 | 2030 100% ECP | -627.66 | -526 | -510 | 267.88 | 0 | 0 | No
2030-10-11 11:00 | 2030 100% ECP | -700 | -526 | -510 | 184.41 | 0 | 0 | No
2030-10-11 12:00 | 2030 100% ECP | -700 | -526 | -510 | 248.87 | 0 | 0 | No
2030-10-11 13:00 | 2030 100% ECP | -700 | -526 | -510 | 253.22 | 0 | 0 | No
2030-10-11 14:00 | 2030 100% ECP | -542.25 | -526 | -510 | 195.78 | 0 | 0 | No
2030-10-11 15:00 | 2030 100% ECP | -122.25 | -526 | -510 | 275.82 | 0 | 0 | No
2030-10-11 16:00 | 2030 100% ECP | 297.75 | -226 | -210 | 466.91 | 0 | 0 | No
2030-10-11 17:00 | 2030 100% ECP | 700 | -226 | -210 | 327.19 | 0 | 0 | No
2030-10-11 18:00 | 2030 100% ECP | 700 | -526 | -510 | 27.19 | 0 | 0 | No
2030-10-11 19:00 | 2030 100% ECP | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-10-11 20:00 | 2030 100% ECP | 700 | -525.09 | -510 | 300 | 0 | 0 | No
2030-10-11 21:00 | 2030 100% ECP | 700 | -225.09 | -210 | 369.44 | 0 | 0 | No
2030-10-11 22:00 | 2030 100% ECP | 700 | 0 | -314.58 | 158.41 | 0 | 0 | No
2030-10-11 23:00 | 2030 100% ECP | 700 | -147 | -510 | 78.21 | 0 | 0 | No
2030-10-12 | 2030 100% ECP | 700 | -160.01 | -510 | -42.15 | 0 | 0 | No
2030-10-12 01:00 | 2030 100% ECP | 700 | -406.7 | -510 | 5.64 | 0 | 0 | No
2030-10-12 02:00 | 2030 100% ECP | 700 | -526 | -510 | 60.99 | 0 | 0 | No
2030-10-12 03:00 | 2030 100% ECP | 280 | -373.47 | -510 | -113.07 | 0 | 0 | No
2030-10-12 04:00 | 2030 100% ECP | -140 | -526 | -510 | -193.41 | 0 | 0 | No
2030-10-12 05:00 | 2030 100% ECP | -560 | -526 | -510 | -141.53 | 0 | 0 | No
2030-10-12 06:00 | 2030 100% ECP | -700 | -526 | -510 | -43.01 | 0 | 0 | No
2030-10-12 07:00 | 2030 100% ECP | -700 | -526 | -510 | -343.01 | 0 | 0 | No
2030-10-12 08:00 | 2030 100% ECP | -700 | -526 | -510 | -481.09 | 0 | 0 | No
2030-10-12 09:00 | 2030 100% ECP | -700 | -526 | -510 | -458.75 | 0 | 0 | No
2030-10-12 10:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-10-12 11:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-10-12 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-10-12 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 14:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-10-12 15:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-12 16:00 | 2030 100% ECP | -700 | -526 | -510 | -400.94 | 0 | 0 | No
2030-10-12 17:00 | 2030 100% ECP | -700 | -526 | -510 | -100.94 | 0 | 0 | No
2030-10-12 18:00 | 2030 100% ECP | -700 | -526 | -510 | 157.45 | 0 | 0 | No
2030-10-12 19:00 | 2030 100% ECP | -700 | -526 | -510 | 8.45 | 0 | 0 | No
2030-10-12 20:00 | 2030 100% ECP | -359.67 | -526 | -510 | 210 | 0 | 0 | No
2030-10-12 21:00 | 2030 100% ECP | 0 | -526 | -510 | 510 | 0 | 0 | No
2030-10-12 22:00 | 2030 100% ECP | 0 | -462.94 | -510 | 448.09 | 0 | 0 | No
2030-10-12 23:00 | 2030 100% ECP | 0 | -227.69 | -300 | 280.01 | 0 | 0 | No
2030-10-13 | 2030 100% ECP | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-10-13 01:00 | 2030 100% ECP | -128.33 | 0 | 0 | 510 | 0 | 0 | No
2030-10-13 02:00 | 2030 100% ECP | -86.2 | 0 | 0 | 510 | 0 | 0 | No
2030-10-13 03:00 | 2030 100% ECP | 0 | 0 | 45.01 | 510 | 0 | 0 | No
2030-10-13 04:00 | 2030 100% ECP | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-10-13 05:00 | 2030 100% ECP | 0 | -71.48 | -300 | 315.6 | 0 | 0 | No
2030-10-13 06:00 | 2030 100% ECP | 0 | -107.33 | -510 | 200.77 | 0 | 0 | No
2030-10-13 07:00 | 2030 100% ECP | 0 | -254.65 | -510 | -99.23 | 0 | 0 | No
2030-10-13 08:00 | 2030 100% ECP | -180.45 | -526 | -510 | -399.23 | 0 | 0 | No
2030-10-13 09:00 | 2030 100% ECP | -600.45 | -226 | -510 | -422.83 | 0 | 0 | No
2030-10-13 10:00 | 2030 100% ECP | -700 | 74 | -210 | -122.83 | 0 | 0 | Yes
2030-10-13 11:00 | 2030 100% ECP | -700 | 374 | 90 | 177.17 | 0 | 0 | Yes
2030-10-13 12:00 | 2030 100% ECP | -700 | 505 | 390 | 477.17 | 0 | 0 | Yes
2030-10-13 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-13 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-13 15:00 | 2030 100% ECP | -700 | 338.08 | 210 | 275.5 | 0 | 0 | Yes
2030-10-13 16:00 | 2030 100% ECP | -700 | 38.08 | -90 | -24.5 | 0 | 0 | No
2030-10-13 17:00 | 2030 100% ECP | -700 | -261.92 | -390 | -324.5 | 0 | 0 | No
2030-10-13 18:00 | 2030 100% ECP | -700 | 0 | -90 | -354.84 | 0 | 0 | No
2030-10-13 19:00 | 2030 100% ECP | -700 | 205 | 210 | -54.84 | 0 | 0 | No
2030-10-13 20:00 | 2030 100% ECP | -700 | 505 | 510 | 245.16 | 0 | 0 | Yes
2030-10-13 21:00 | 2030 100% ECP | -700 | 505 | 510 | 282.25 | 0 | 0 | Yes
2030-10-13 22:00 | 2030 100% ECP | -700 | 505 | 510 | 387.19 | 0 | 0 | Yes
2030-10-13 23:00 | 2030 100% ECP | -700 | 505 | 510 | 471.54 | 0 | 0 | Yes
2030-10-14 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 01:00 | 2030 100% ECP | 42.79 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-14 02:00 | 2030 100% ECP | 462.79 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-14 03:00 | 2030 100% ECP | 42.79 | 505 | 510 | 475.41 | 0 | 0 | Yes
2030-10-14 04:00 | 2030 100% ECP | 462.79 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-14 05:00 | 2030 100% ECP | 700 | 505 | 510 | 495.4 | 0 | 0 | Yes
2030-10-14 06:00 | 2030 100% ECP | 700 | 505 | 510 | 195.4 | 0 | 0 | Yes
2030-10-14 07:00 | 2030 100% ECP | 700 | 505 | 510 | 161.23 | 0 | 0 | No
2030-10-14 08:00 | 2030 100% ECP | 700 | 505 | 510 | 461.23 | 0 | 0 | No
2030-10-14 09:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 10:00 | 2030 100% ECP | 550.22 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 11:00 | 2030 100% ECP | 282.88 | 469.49 | 510 | 510 | 0 | 0 | No
2030-10-14 12:00 | 2030 100% ECP | 0 | 356.78 | 510 | 510 | 0 | 0 | No
2030-10-14 13:00 | 2030 100% ECP | 420 | 285.95 | 390 | 510 | 0 | 0 | No
2030-10-14 14:00 | 2030 100% ECP | 700 | 82.09 | 90 | 510 | 0 | 0 | No
2030-10-14 15:00 | 2030 100% ECP | 700 | 0 | -210 | 510 | 0 | 0 | No
2030-10-14 16:00 | 2030 100% ECP | 700 | -300 | -510 | 210 | 0 | 0 | No
2030-10-14 17:00 | 2030 100% ECP | 700 | -106.51 | -510 | -23.9 | 0 | 0 | No
2030-10-14 18:00 | 2030 100% ECP | 700 | -106.51 | -510 | -277.27 | 0 | 0 | No
2030-10-14 19:00 | 2030 100% ECP | 700 | -106.51 | -300 | -112.84 | 0 | 0 | No
2030-10-14 20:00 | 2030 100% ECP | 700 | 0 | 0 | 60.58 | 0 | 0 | No
2030-10-14 21:00 | 2030 100% ECP | 700 | 300 | 300 | 360.58 | 0 | 0 | No
2030-10-14 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-14 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 | 2030 100% ECP | 700 | 416.14 | 510 | 510 | 0 | 0 | No
2030-10-15 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-15 04:00 | 2030 100% ECP | 700 | 205 | 428.64 | 210 | 0 | 0 | No
2030-10-15 05:00 | 2030 100% ECP | 700 | 0 | 128.64 | 0 | 0 | 0 | No
2030-10-15 06:00 | 2030 100% ECP | 700 | 0 | 360.2 | 210 | 0 | 0 | No
2030-10-15 07:00 | 2030 100% ECP | 700 | 0 | 457.81 | 510 | 0 | 0 | No
2030-10-15 08:00 | 2030 100% ECP | 700 | 141.41 | 157.81 | 510 | 0 | 0 | No
2030-10-15 09:00 | 2030 100% ECP | 280 | -158.59 | -142.19 | 510 | 0 | 0 | No
2030-10-15 10:00 | 2030 100% ECP | -140 | -458.59 | -442.19 | 368.68 | 0 | 0 | No
2030-10-15 11:00 | 2030 100% ECP | -560 | -526 | -510 | 353.91 | 0 | 0 | No
2030-10-15 12:00 | 2030 100% ECP | -700 | -526 | -510 | 346.06 | 0 | 0 | No
2030-10-15 13:00 | 2030 100% ECP | -700 | -526 | -510 | 279.35 | 0 | 0 | No
2030-10-15 14:00 | 2030 100% ECP | -560 | -526 | -510 | 290.04 | 0 | 0 | No
2030-10-15 15:00 | 2030 100% ECP | -140 | -384.84 | -510 | 309.18 | 0 | 0 | No
2030-10-15 16:00 | 2030 100% ECP | 280 | -84.84 | -210 | 439.76 | 0 | 0 | No
2030-10-15 17:00 | 2030 100% ECP | 700 | -143.21 | -210 | 206.23 | 0 | 0 | No
2030-10-15 18:00 | 2030 100% ECP | 700 | -443.21 | -510 | -93.77 | 0 | 0 | No
2030-10-15 19:00 | 2030 100% ECP | 700 | -143.21 | -210 | 206.23 | 0 | 0 | No
2030-10-15 20:00 | 2030 100% ECP | 700 | 156.79 | 90 | 506.23 | 0 | 0 | No
2030-10-15 21:00 | 2030 100% ECP | 700 | 0 | 339.66 | 313.72 | 0 | 0 | No
2030-10-15 22:00 | 2030 100% ECP | 700 | 0 | 344.51 | 285.59 | 0 | 0 | No
2030-10-15 23:00 | 2030 100% ECP | 700 | 0 | 75.64 | 193.54 | 0 | 0 | No
2030-10-16 | 2030 100% ECP | 700 | 0 | -224.36 | 0 | 0 | 0 | No
2030-10-16 01:00 | 2030 100% ECP | 700 | 0 | -282.39 | 0 | 0 | 0 | No
2030-10-16 02:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-16 03:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-16 04:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-16 05:00 | 2030 100% ECP | 700 | 0 | -510 | -50.62 | 0 | 0 | No
2030-10-16 06:00 | 2030 100% ECP | 700 | 0 | -510 | -93.43 | 0 | 0 | No
2030-10-16 07:00 | 2030 100% ECP | 575.75 | 0 | -300 | 0 | 0 | 0 | No
2030-10-16 08:00 | 2030 100% ECP | 155.75 | 0 | 0 | 0 | 0 | 0 | No
2030-10-16 09:00 | 2030 100% ECP | -264.25 | -226 | -300 | -26.24 | 0 | 0 | No
2030-10-16 10:00 | 2030 100% ECP | -684.25 | -526 | -510 | -86.78 | 0 | 0 | No
2030-10-16 11:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-10-16 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-10-16 13:00 | 2030 100% ECP | -700 | -526 | -510 | -69.44 | 0 | 0 | No
2030-10-16 14:00 | 2030 100% ECP | -700 | -526 | -510 | -134.57 | 0 | 0 | No
2030-10-16 15:00 | 2030 100% ECP | -700 | -526 | -510 | -137.48 | 0 | 0 | No
2030-10-16 16:00 | 2030 100% ECP | -280 | -526 | -510 | -319.24 | 0 | 0 | No
2030-10-16 17:00 | 2030 100% ECP | 140 | -526 | -510 | -434.19 | 0 | 0 | No
2030-10-16 18:00 | 2030 100% ECP | 73.72 | -526 | -510 | -434.19 | 0 | 0 | No
2030-10-16 19:00 | 2030 100% ECP | 493.72 | -526 | -510 | -352.39 | 0 | 0 | No
2030-10-16 20:00 | 2030 100% ECP | 700 | -226 | -510 | -52.39 | 0 | 0 | No
2030-10-16 21:00 | 2030 100% ECP | 700 | 0 | -510 | -8.58 | 0 | 0 | No
2030-10-16 22:00 | 2030 100% ECP | 700 | 0 | -510 | -148.9 | 0 | 0 | No
2030-10-16 23:00 | 2030 100% ECP | 700 | -120.58 | -510 | -336.98 | 0 | 0 | No
2030-10-17 | 2030 100% ECP | 700 | 0 | -510 | -50.56 | 0 | 0 | No
2030-10-17 01:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 02:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 03:00 | 2030 100% ECP | 700 | 0 | -510 | -223.48 | 0 | 0 | No
2030-10-17 04:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-17 05:00 | 2030 100% ECP | 700 | 0 | -510 | -184.39 | 0 | 0 | No
2030-10-17 06:00 | 2030 100% ECP | 700 | 0 | -510 | -148.97 | 0 | 0 | No
2030-10-17 07:00 | 2030 100% ECP | 700 | 0 | -473.23 | 0 | 0 | 0 | No
2030-10-17 08:00 | 2030 100% ECP | 420 | 0 | -173.23 | 265.78 | 0 | 0 | No
2030-10-17 09:00 | 2030 100% ECP | 0 | -300 | -473.23 | 0 | 0 | 0 | No
2030-10-17 10:00 | 2030 100% ECP | -420 | -526 | -510 | -19.58 | 0 | 0 | No
2030-10-17 11:00 | 2030 100% ECP | -700 | -526 | -510 | -191.08 | 0 | 0 | No
2030-10-17 12:00 | 2030 100% ECP | -700 | -526 | -510 | -106.96 | 0 | 0 | No
2030-10-17 13:00 | 2030 100% ECP | -700 | -526 | -510 | -110.07 | 0 | 0 | No
2030-10-17 14:00 | 2030 100% ECP | -700 | -526 | -510 | -160.36 | 0 | 0 | No
2030-10-17 15:00 | 2030 100% ECP | -381.34 | -526 | -510 | 0 | 0 | 0 | No
2030-10-17 16:00 | 2030 100% ECP | 38.66 | -514.16 | -510 | -189.77 | 0 | 0 | No
2030-10-17 17:00 | 2030 100% ECP | 0 | -526 | -510 | -489.77 | 0 | 0 | No
2030-10-17 18:00 | 2030 100% ECP | -420 | -526 | -510 | -510 | 0 | 0 | No
2030-10-17 19:00 | 2030 100% ECP | 0 | -327.7 | -510 | -210 | 0 | 0 | No
2030-10-17 20:00 | 2030 100% ECP | 420 | -27.7 | -210 | 90 | 0 | 0 | No
2030-10-17 21:00 | 2030 100% ECP | 700 | 0 | 89.98 | 0 | 0 | 0 | No
2030-10-17 22:00 | 2030 100% ECP | 700 | 0 | -210.02 | -166.25 | 0 | 0 | No
2030-10-17 23:00 | 2030 100% ECP | 700 | 0 | -510 | -205.8 | 0 | 0 | No
2030-10-18 | 2030 100% ECP | 700 | 0 | -510 | -148.02 | 0 | 0 | No
2030-10-18 01:00 | 2030 100% ECP | 700 | 0 | -510 | -292.58 | 0 | 0 | No
2030-10-18 02:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-18 03:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-18 04:00 | 2030 100% ECP | 700 | 0 | -510 | -21.15 | 0 | 0 | No
2030-10-18 05:00 | 2030 100% ECP | 700 | -11.2 | -510 | 0 | 0 | 0 | No
2030-10-18 06:00 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-10-18 07:00 | 2030 100% ECP | 700 | -226 | -428.22 | 0 | 0 | 0 | No
2030-10-18 08:00 | 2030 100% ECP | 508.72 | -526 | -510 | -223.76 | 0 | 0 | No
2030-10-18 09:00 | 2030 100% ECP | 88.72 | -526 | -510 | 76.24 | 0 | 0 | No
2030-10-18 10:00 | 2030 100% ECP | -331.28 | -526 | -510 | 52.93 | 0 | 0 | No
2030-10-18 11:00 | 2030 100% ECP | -700 | -526 | -510 | 14.9 | 0 | 0 | No
2030-10-18 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-10-18 13:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-10-18 14:00 | 2030 100% ECP | -639.87 | -526 | -510 | 0 | 0 | 0 | No
2030-10-18 15:00 | 2030 100% ECP | -219.87 | -467.26 | -510 | -5.49 | 0 | 0 | No
2030-10-18 16:00 | 2030 100% ECP | 200.13 | -526 | -510 | -305.49 | 0 | 0 | No
2030-10-18 17:00 | 2030 100% ECP | -219.87 | -526 | -510 | -305.49 | 0 | 0 | No
2030-10-18 18:00 | 2030 100% ECP | -639.87 | -526 | -510 | -326.02 | 0 | 0 | No
2030-10-18 19:00 | 2030 100% ECP | -219.87 | -526 | -510 | -510 | 0 | 0 | No
2030-10-18 20:00 | 2030 100% ECP | 200.13 | -526 | -510 | -300 | 0 | 0 | No
2030-10-18 21:00 | 2030 100% ECP | 620.13 | -226 | -510 | 0 | 0 | 0 | No
2030-10-18 22:00 | 2030 100% ECP | 672.52 | -526 | -510 | -229.93 | 0 | 0 | No
2030-10-18 23:00 | 2030 100% ECP | 554.37 | -526 | -510 | -13.41 | 0 | 0 | No
2030-10-19 | 2030 100% ECP | 560 | -526 | -510 | 6.67 | 0 | 0 | No
2030-10-19 01:00 | 2030 100% ECP | 140 | -526 | -510 | 148.25 | 0 | 0 | No
2030-10-19 02:00 | 2030 100% ECP | -280 | -337.06 | -510 | 448.25 | 0 | 0 | No
2030-10-19 03:00 | 2030 100% ECP | -700 | -226 | -408.11 | 399.7 | 0 | 0 | No
2030-10-19 04:00 | 2030 100% ECP | -700 | -526 | -510 | 99.7 | 0 | 0 | Yes
2030-10-19 05:00 | 2030 100% ECP | -700 | -526 | -510 | -200.3 | 0 | 0 | No
2030-10-19 06:00 | 2030 100% ECP | -700 | -526 | -510 | -500.3 | 0 | 0 | No
2030-10-19 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-19 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-10-19 09:00 | 2030 100% ECP | -700 | -526 | -510 | -390 | 0 | 0 | No
2030-10-19 10:00 | 2030 100% ECP | -700 | -226 | -210 | -90 | 0 | 0 | Yes
2030-10-19 11:00 | 2030 100% ECP | -700 | 74 | 90 | 210 | 0 | 0 | Yes
2030-10-19 12:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-10-19 13:00 | 2030 100% ECP | -700 | 374 | 390 | 473.97 | 0 | 0 | Yes
2030-10-19 14:00 | 2030 100% ECP | -700 | 74 | 90 | 173.97 | 0 | 0 | Yes
2030-10-19 15:00 | 2030 100% ECP | -700 | -226 | -210 | -126.03 | 0 | 0 | No
2030-10-19 16:00 | 2030 100% ECP | -700 | -526 | -510 | -426.03 | 0 | 0 | No
2030-10-19 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-19 18:00 | 2030 100% ECP | -700 | -526 | -510 | -464.43 | 0 | 0 | No
2030-10-19 19:00 | 2030 100% ECP | -700 | -226 | -346.78 | -164.43 | 0 | 0 | No
2030-10-19 20:00 | 2030 100% ECP | -700 | 74 | -46.78 | 135.57 | 0 | 0 | Yes
2030-10-19 21:00 | 2030 100% ECP | -700 | 374 | 253.22 | 435.57 | 0 | 0 | Yes
2030-10-19 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-19 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 01:00 | 2030 100% ECP | -700 | 505 | 510 | 223.07 | 0 | 0 | Yes
2030-10-20 02:00 | 2030 100% ECP | -700 | 505 | 510 | 335.6 | 0 | 0 | Yes
2030-10-20 03:00 | 2030 100% ECP | -700 | 505 | 510 | 242.33 | 0 | 0 | Yes
2030-10-20 04:00 | 2030 100% ECP | -700 | 505 | 510 | 361.48 | 0 | 0 | Yes
2030-10-20 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 11:00 | 2030 100% ECP | -700 | 505 | 510 | 353.94 | 0 | 0 | Yes
2030-10-20 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 13:00 | 2030 100% ECP | -700 | 505 | 510 | 341.58 | 0 | 0 | Yes
2030-10-20 14:00 | 2030 100% ECP | -700 | 505 | 510 | 294.75 | 0 | 0 | Yes
2030-10-20 15:00 | 2030 100% ECP | -700 | 505 | 352.52 | 273.49 | 0 | 0 | Yes
2030-10-20 16:00 | 2030 100% ECP | -700 | 205 | 52.52 | -26.51 | 0 | 0 | Yes
2030-10-20 17:00 | 2030 100% ECP | -700 | -95 | -247.48 | -326.51 | 0 | 0 | Yes
2030-10-20 18:00 | 2030 100% ECP | -700 | 205 | 52.52 | -26.51 | 0 | 0 | Yes
2030-10-20 19:00 | 2030 100% ECP | -700 | 505 | 352.52 | 273.49 | 0 | 0 | Yes
2030-10-20 20:00 | 2030 100% ECP | -700 | 505 | 510 | 431.3 | 0 | 0 | Yes
2030-10-20 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-20 22:00 | 2030 100% ECP | -700 | 505 | 510 | 440.85 | 0 | 0 | Yes
2030-10-20 23:00 | 2030 100% ECP | -700 | 505 | 510 | 393.46 | 0 | 0 | Yes
2030-10-21 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 01:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 02:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-21 06:00 | 2030 100% ECP | 700 | 417.19 | 390 | 510 | 0 | 0 | No
2030-10-21 07:00 | 2030 100% ECP | 700 | 117.19 | 90 | 510 | 0 | 0 | No
2030-10-21 08:00 | 2030 100% ECP | 700 | -182.81 | -210 | 510 | 0 | 0 | No
2030-10-21 09:00 | 2030 100% ECP | 280 | -482.81 | -510 | 510 | 0 | 0 | No
2030-10-21 10:00 | 2030 100% ECP | -140 | -526 | -510 | 300 | 0 | 0 | No
2030-10-21 11:00 | 2030 100% ECP | -560 | -526 | -510 | 0 | 0 | 0 | No
2030-10-21 12:00 | 2030 100% ECP | -700 | -526 | -510 | 195.05 | 0 | 0 | No
2030-10-21 13:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-10-21 14:00 | 2030 100% ECP | -560 | -526 | -510 | -210 | 0 | 0 | No
2030-10-21 15:00 | 2030 100% ECP | -140 | -526 | -510 | -510 | 0 | 0 | No
2030-10-21 16:00 | 2030 100% ECP | 280 | -526 | -510 | -510 | 0 | 0 | No
2030-10-21 17:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-21 18:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-21 19:00 | 2030 100% ECP | 700 | -487.75 | -510 | -501.15 | 0 | 0 | No
2030-10-21 20:00 | 2030 100% ECP | 700 | -187.75 | -210 | -510 | 0 | 0 | No
2030-10-21 21:00 | 2030 100% ECP | 700 | 112.25 | 90 | -210 | 0 | 0 | Yes
2030-10-21 22:00 | 2030 100% ECP | 448.9 | 412.25 | 390 | 90 | 0 | 0 | Yes
2030-10-21 23:00 | 2030 100% ECP | 28.9 | 505 | 510 | 27.06 | 0 | 0 | Yes
2030-10-22 | 2030 100% ECP | 448.9 | 505 | 510 | 327.06 | 0 | 0 | Yes
2030-10-22 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-22 02:00 | 2030 100% ECP | 700 | 505 | 510 | 375.32 | 0 | 0 | Yes
2030-10-22 03:00 | 2030 100% ECP | 700 | 505 | 510 | 426.05 | 0 | 0 | Yes
2030-10-22 04:00 | 2030 100% ECP | 700 | 505 | 510 | 426.05 | 0 | 0 | Yes
2030-10-22 05:00 | 2030 100% ECP | 700 | 505 | 510 | 126.05 | 0 | 0 | Yes
2030-10-22 06:00 | 2030 100% ECP | 280 | 205 | 210 | -57.51 | 0 | 0 | No
2030-10-22 07:00 | 2030 100% ECP | 561.69 | 0 | 0 | 0 | 0 | 0 | No
2030-10-22 08:00 | 2030 100% ECP | 141.69 | 0 | 0 | 0 | 0 | 0 | No
2030-10-22 09:00 | 2030 100% ECP | -278.31 | -226 | -210 | 49.67 | 0 | 0 | No
2030-10-22 10:00 | 2030 100% ECP | -698.31 | -526 | -510 | 60.7 | 0 | 0 | No
2030-10-22 11:00 | 2030 100% ECP | -700 | -526 | -510 | 119.49 | 0 | 0 | No
2030-10-22 12:00 | 2030 100% ECP | -700 | -526 | -510 | -44.84 | 0 | 0 | No
2030-10-22 13:00 | 2030 100% ECP | -700 | -526 | -510 | -37.6 | 0 | 0 | No
2030-10-22 14:00 | 2030 100% ECP | -700 | -526 | -510 | -47.52 | 0 | 0 | No
2030-10-22 15:00 | 2030 100% ECP | -280 | -226 | -392.15 | 161.61 | 0 | 0 | No
2030-10-22 16:00 | 2030 100% ECP | 140 | -226 | -210 | 393.8 | 0 | 0 | No
2030-10-22 17:00 | 2030 100% ECP | -280 | -526 | -510 | 177.6 | 0 | 0 | No
2030-10-22 18:00 | 2030 100% ECP | -700 | -526 | -510 | -122.4 | 0 | 0 | No
2030-10-22 19:00 | 2030 100% ECP | -280 | -526 | -510 | -250.22 | 0 | 0 | No
2030-10-22 20:00 | 2030 100% ECP | 140 | -526 | -510 | -135.67 | 0 | 0 | No
2030-10-22 21:00 | 2030 100% ECP | -137.98 | -226 | -383.99 | 83.68 | 0 | 0 | No
2030-10-22 22:00 | 2030 100% ECP | -557.98 | -526 | -510 | -1.11 | 0 | 0 | No
2030-10-22 23:00 | 2030 100% ECP | -137.98 | -526 | -510 | -96.45 | 0 | 0 | No
2030-10-23 | 2030 100% ECP | 280 | -526 | -510 | -387.39 | 0 | 0 | No
2030-10-23 01:00 | 2030 100% ECP | 700 | -526 | -510 | -183.32 | 0 | 0 | No
2030-10-23 02:00 | 2030 100% ECP | 700 | -300 | -510 | -34.14 | 0 | 0 | No
2030-10-23 03:00 | 2030 100% ECP | 700 | 0 | -210 | 265.86 | 0 | 0 | No
2030-10-23 04:00 | 2030 100% ECP | 700 | 300 | 90 | 510 | 0 | 0 | No
2030-10-23 05:00 | 2030 100% ECP | 280 | 0 | -210 | 210 | 0 | 0 | No
2030-10-23 06:00 | 2030 100% ECP | 656.03 | -300 | -510 | 139.53 | 0 | 0 | No
2030-10-23 07:00 | 2030 100% ECP | 560 | -526 | -510 | 439.53 | 0 | 0 | No
2030-10-23 08:00 | 2030 100% ECP | 140 | -526 | -510 | 491.35 | 0 | 0 | No
2030-10-23 09:00 | 2030 100% ECP | -280 | -526 | -510 | 472.15 | 0 | 0 | No
2030-10-23 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-23 11:00 | 2030 100% ECP | -700 | -526 | -510 | 485.13 | 0 | 0 | No
2030-10-23 12:00 | 2030 100% ECP | -700 | -526 | -510 | 185.13 | 0 | 0 | No
2030-10-23 13:00 | 2030 100% ECP | -700 | -526 | -510 | -114.87 | 0 | 0 | No
2030-10-23 14:00 | 2030 100% ECP | -700 | -526 | -510 | 50.12 | 0 | 0 | No
2030-10-23 15:00 | 2030 100% ECP | -700 | -526 | -510 | 333.38 | 0 | 0 | No
2030-10-23 16:00 | 2030 100% ECP | -700 | -526 | -510 | 428.17 | 0 | 0 | No
2030-10-23 17:00 | 2030 100% ECP | -700 | -526 | -510 | 428.17 | 0 | 0 | No
2030-10-23 18:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-10-23 19:00 | 2030 100% ECP | -700 | -526 | -510 | 441.47 | 0 | 0 | No
2030-10-23 20:00 | 2030 100% ECP | -700 | -526 | -510 | 246.4 | 0 | 0 | Yes
2030-10-23 21:00 | 2030 100% ECP | -700 | -526 | -510 | -29.96 | 0 | 0 | Yes
2030-10-23 22:00 | 2030 100% ECP | -700 | -338.89 | -390 | -329.96 | 0 | 0 | Yes
2030-10-23 23:00 | 2030 100% ECP | -700 | -38.89 | -90 | -29.96 | 0 | 0 | Yes
2030-10-24 | 2030 100% ECP | -700 | 261.11 | 210 | 270.04 | 0 | 0 | Yes
2030-10-24 01:00 | 2030 100% ECP | -700 | 505 | 510 | 256.38 | 0 | 0 | Yes
2030-10-24 02:00 | 2030 100% ECP | -700 | 505 | 510 | 421.48 | 0 | 0 | Yes
2030-10-24 03:00 | 2030 100% ECP | -700 | 505 | 510 | 471.19 | 0 | 0 | Yes
2030-10-24 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-24 14:00 | 2030 100% ECP | -700 | 374 | 342.39 | 510 | 0 | 0 | Yes
2030-10-24 15:00 | 2030 100% ECP | -700 | 74 | 42.39 | 510 | 0 | 0 | Yes
2030-10-24 16:00 | 2030 100% ECP | -700 | -226 | -257.61 | 255.38 | 0 | 0 | No
2030-10-24 17:00 | 2030 100% ECP | -700 | -526 | -510 | 62.1 | 0 | 0 | No
2030-10-24 18:00 | 2030 100% ECP | -700 | -526 | -510 | 362.1 | 0 | 0 | No
2030-10-24 19:00 | 2030 100% ECP | -700 | -526 | -510 | 62.1 | 0 | 0 | No
2030-10-24 20:00 | 2030 100% ECP | -700 | -526 | -510 | 319.72 | 0 | 0 | No
2030-10-24 21:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-10-24 22:00 | 2030 100% ECP | -700 | 74 | 90 | 323.23 | 0 | 0 | Yes
2030-10-24 23:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-10-25 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 07:00 | 2030 100% ECP | -700 | 300 | 339.29 | 499.22 | 0 | 0 | Yes
2030-10-25 08:00 | 2030 100% ECP | -700 | 0 | 39.29 | 199.22 | 0 | 0 | Yes
2030-10-25 09:00 | 2030 100% ECP | -700 | 300 | 339.29 | 499.22 | 0 | 0 | Yes
2030-10-25 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-25 13:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-10-25 14:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-10-25 15:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-10-25 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-25 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-25 18:00 | 2030 100% ECP | -700 | -526 | -510 | -409.45 | 0 | 0 | No
2030-10-25 19:00 | 2030 100% ECP | -700 | -526 | -510 | -109.45 | 0 | 0 | No
2030-10-25 20:00 | 2030 100% ECP | -700 | -226 | -210 | 190.55 | 0 | 0 | No
2030-10-25 21:00 | 2030 100% ECP | -700 | 74 | 90 | 490.55 | 0 | 0 | Yes
2030-10-25 22:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-10-25 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 04:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-10-26 05:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-10-26 06:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-10-26 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-10-26 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-10-26 09:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-10-26 10:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-10-26 11:00 | 2030 100% ECP | -700 | 0 | -82.88 | 0 | 0 | 0 | Yes
2030-10-26 12:00 | 2030 100% ECP | -700 | 300 | 217.12 | 300 | 0 | 0 | Yes
2030-10-26 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-26 14:00 | 2030 100% ECP | -700 | 374 | 362.44 | 510 | 0 | 0 | Yes
2030-10-26 15:00 | 2030 100% ECP | -700 | 74 | 62.44 | 210 | 0 | 0 | Yes
2030-10-26 16:00 | 2030 100% ECP | -280 | -226 | -237.56 | -90 | 0 | 0 | No
2030-10-26 17:00 | 2030 100% ECP | -700 | -526 | -510 | -321.31 | 0 | 0 | No
2030-10-26 18:00 | 2030 100% ECP | -560 | -526 | -510 | -21.31 | 0 | 0 | No
2030-10-26 19:00 | 2030 100% ECP | -140 | -395 | -390 | 38.54 | 0 | 0 | No
2030-10-26 20:00 | 2030 100% ECP | 280 | -95 | -90 | 338.54 | 0 | 0 | No
2030-10-26 21:00 | 2030 100% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-10-26 22:00 | 2030 100% ECP | 298.22 | 505 | 510 | 510 | 0 | 0 | No
2030-10-26 23:00 | 2030 100% ECP | -121.78 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 | 2030 100% ECP | -541.78 | 505 | 510 | 510 | 0 | 0 | No
2030-10-27 01:00 | 2030 100% ECP | -700 | 229.35 | 390 | 510 | 0 | 0 | No
2030-10-27 02:00 | 2030 100% ECP | -700 | 190.35 | 90 | 510 | 0 | 0 | No
2030-10-27 03:00 | 2030 100% ECP | -700 | -109.65 | -210 | 510 | 0 | 0 | No
2030-10-27 04:00 | 2030 100% ECP | -700 | -409.65 | -510 | 510 | 0 | 0 | No
2030-10-27 05:00 | 2030 100% ECP | -700 | -462.37 | -510 | 324.81 | 0 | 0 | No
2030-10-27 06:00 | 2030 100% ECP | -700 | -526 | -510 | 24.81 | 0 | 0 | No
2030-10-27 07:00 | 2030 100% ECP | -700 | -526 | -510 | 304.56 | 0 | 0 | No
2030-10-27 08:00 | 2030 100% ECP | -700 | -526 | -510 | 107.57 | 0 | 0 | No
2030-10-27 09:00 | 2030 100% ECP | -700 | -526 | -510 | 333.76 | 0 | 0 | No
2030-10-27 10:00 | 2030 100% ECP | -700 | -526 | -510 | 465.46 | 0 | 0 | No
2030-10-27 11:00 | 2030 100% ECP | -700 | -526 | -510 | 356.2 | 0 | 0 | Yes
2030-10-27 12:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-10-27 13:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-10-27 14:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-10-27 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-27 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-27 17:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-27 18:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-27 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-27 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-27 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-27 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-27 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 14:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-10-28 15:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-10-28 16:00 | 2030 100% ECP | -700 | -226 | -210 | 210 | 0 | 0 | Yes
2030-10-28 17:00 | 2030 100% ECP | -700 | -526 | -510 | -90 | 0 | 0 | No
2030-10-28 18:00 | 2030 100% ECP | -700 | -526 | -510 | -134.48 | 0 | 0 | No
2030-10-28 19:00 | 2030 100% ECP | -700 | -226 | -210 | 165.52 | 0 | 0 | No
2030-10-28 20:00 | 2030 100% ECP | -700 | 74 | 90 | 465.52 | 0 | 0 | Yes
2030-10-28 21:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-10-28 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-28 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-29 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-29 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-29 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-29 03:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-10-29 04:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-10-29 05:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-10-29 06:00 | 2030 100% ECP | -700 | -526 | -510 | 453.65 | 0 | 0 | Yes
2030-10-29 07:00 | 2030 100% ECP | -700 | -526 | -510 | 153.65 | 0 | 0 | Yes
2030-10-29 08:00 | 2030 100% ECP | -700 | -526 | -510 | -106.39 | 0 | 0 | Yes
2030-10-29 09:00 | 2030 100% ECP | -700 | -526 | -510 | -50.15 | 0 | 0 | Yes
2030-10-29 10:00 | 2030 100% ECP | -700 | -526 | -510 | 249.85 | 0 | 0 | Yes
2030-10-29 11:00 | 2030 100% ECP | -700 | -267.6 | -510 | 251.52 | 0 | 0 | Yes
2030-10-29 12:00 | 2030 100% ECP | -700 | 32.4 | -210 | 510 | 0 | 0 | Yes
2030-10-29 13:00 | 2030 100% ECP | -700 | 332.4 | 90 | 510 | 0 | 0 | Yes
2030-10-29 14:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-10-29 15:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-10-29 16:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-10-29 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-10-29 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-10-29 19:00 | 2030 100% ECP | -700 | -226 | -276.71 | -210 | 0 | 0 | Yes
2030-10-29 20:00 | 2030 100% ECP | -700 | 74 | 23.29 | 90 | 0 | 0 | Yes
2030-10-29 21:00 | 2030 100% ECP | -700 | 374 | 323.29 | 390 | 0 | 0 | Yes
2030-10-29 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-29 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-10-30 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 01:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 02:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 06:00 | 2030 100% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-10-30 07:00 | 2030 100% ECP | 455.79 | 205 | 210 | 210 | 0 | 0 | No
2030-10-30 08:00 | 2030 100% ECP | 560 | -95 | -90 | 371.27 | 0 | 0 | No
2030-10-30 09:00 | 2030 100% ECP | 140 | -46.79 | -390 | 349.7 | 0 | 0 | No
2030-10-30 10:00 | 2030 100% ECP | -280 | -226 | -471.8 | 299.3 | 0 | 0 | No
2030-10-30 11:00 | 2030 100% ECP | -700 | -526 | -510 | 94.16 | 0 | 0 | No
2030-10-30 12:00 | 2030 100% ECP | -700 | -526 | -510 | 49.74 | 0 | 0 | No
2030-10-30 13:00 | 2030 100% ECP | -700 | -526 | -510 | 129.68 | 0 | 0 | No
2030-10-30 14:00 | 2030 100% ECP | -280 | -526 | -510 | 75.43 | 0 | 0 | No
2030-10-30 15:00 | 2030 100% ECP | -280 | -270.34 | -510 | 132.47 | 0 | 0 | No
2030-10-30 16:00 | 2030 100% ECP | -700 | -497.45 | -510 | 432.47 | 0 | 0 | No
2030-10-30 17:00 | 2030 100% ECP | -700 | -526 | -510 | 132.47 | 0 | 0 | No
2030-10-30 18:00 | 2030 100% ECP | -700 | -526 | -510 | -167.53 | 0 | 0 | No
2030-10-30 19:00 | 2030 100% ECP | -700 | -526 | -510 | 132.47 | 0 | 0 | No
2030-10-30 20:00 | 2030 100% ECP | -700 | -526 | -510 | 432.47 | 0 | 0 | No
2030-10-30 21:00 | 2030 100% ECP | -700 | -526 | -510 | 371.28 | 0 | 0 | No
2030-10-30 22:00 | 2030 100% ECP | -700 | -526 | -510 | 71.28 | 0 | 0 | No
2030-10-30 23:00 | 2030 100% ECP | -700 | -526 | -510 | -171.23 | 0 | 0 | Yes
2030-10-31 | 2030 100% ECP | -700 | -526 | 0 | -471.23 | 0 | 0 | Yes
2030-10-31 01:00 | 2030 100% ECP | -700 | -226 | 0 | -171.23 | 0 | 0 | Yes
2030-10-31 02:00 | 2030 100% ECP | -700 | 74 | 0 | 0 | 0 | 0 | Yes
2030-10-31 03:00 | 2030 100% ECP | -700 | 374 | 0 | 27.28 | 0 | 0 | Yes
2030-10-31 04:00 | 2030 100% ECP | -700 | 505 | 0 | 94.13 | 0 | 0 | Yes
2030-10-31 05:00 | 2030 100% ECP | -700 | 505 | 0 | -21.19 | 0 | 0 | Yes
2030-10-31 06:00 | 2030 100% ECP | -700 | 505 | 0 | 54.17 | 0 | 0 | Yes
2030-10-31 07:00 | 2030 100% ECP | -700 | 505 | 0 | 239.09 | 0 | 0 | Yes
2030-10-31 08:00 | 2030 100% ECP | -700 | 505 | 0 | 426.93 | 0 | 0 | Yes
2030-10-31 09:00 | 2030 100% ECP | -700 | 505 | 0 | 431.97 | 0 | 0 | Yes
2030-10-31 10:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 11:00 | 2030 100% ECP | -700 | 505 | 0 | 388.54 | 0 | 0 | Yes
2030-10-31 12:00 | 2030 100% ECP | -700 | 505 | 0 | 345.91 | 0 | 0 | Yes
2030-10-31 13:00 | 2030 100% ECP | -700 | 505 | 0 | 309.21 | 0 | 0 | Yes
2030-10-31 14:00 | 2030 100% ECP | -700 | 505 | 0 | 271.48 | 0 | 0 | Yes
2030-10-31 15:00 | 2030 100% ECP | -700 | 505 | 0 | 302.43 | 0 | 0 | Yes
2030-10-31 16:00 | 2030 100% ECP | -700 | 505 | 0 | 381.42 | 0 | 0 | Yes
2030-10-31 17:00 | 2030 100% ECP | -700 | 505 | 0 | 470.39 | 0 | 0 | Yes
2030-10-31 18:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 19:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 20:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 21:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 22:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-10-31 23:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 01:00 | 2030 100% ECP | -700 | 505 | 0 | 506.7 | 0 | 0 | Yes
2030-11-01 02:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 03:00 | 2030 100% ECP | -700 | 505 | 0 | 273.27 | 0 | 0 | Yes
2030-11-01 04:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 05:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 06:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 07:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 08:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 09:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 10:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 11:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 12:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 13:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 14:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 15:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 16:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-11-01 17:00 | 2030 100% ECP | -700 | 422.34 | 0 | 510 | 0 | 0 | No
2030-11-01 18:00 | 2030 100% ECP | -700 | 122.34 | 0 | 261.58 | 0 | 0 | No
2030-11-01 19:00 | 2030 100% ECP | -700 | 408.5 | 0 | 510 | 0 | 0 | No
2030-11-01 20:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 21:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 22:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-01 23:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-02 | 2030 100% ECP | -700 | 505 | 300 | 510 | 0 | 0 | No
2030-11-02 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-02 05:00 | 2030 100% ECP | -700 | 505 | 475.35 | 510 | 0 | 0 | No
2030-11-02 06:00 | 2030 100% ECP | -700 | 205 | 175.35 | 510 | 0 | 0 | No
2030-11-02 07:00 | 2030 100% ECP | -700 | -95 | -124.65 | 510 | 0 | 0 | No
2030-11-02 08:00 | 2030 100% ECP | -700 | -395 | -424.65 | 390.18 | 0 | 0 | No
2030-11-02 09:00 | 2030 100% ECP | -700 | -95 | -124.65 | 510 | 0 | 0 | No
2030-11-02 10:00 | 2030 100% ECP | -700 | 205 | 175.35 | 510 | 0 | 0 | Yes
2030-11-02 11:00 | 2030 100% ECP | -700 | 505 | 475.35 | 510 | 0 | 0 | Yes
2030-11-02 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-02 13:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-11-02 14:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-11-02 15:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-11-02 16:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-11-02 17:00 | 2030 100% ECP | -700 | -526 | -510 | -59.06 | 0 | 0 | No
2030-11-02 18:00 | 2030 100% ECP | -700 | -526 | -510 | -226.14 | 0 | 0 | No
2030-11-02 19:00 | 2030 100% ECP | -700 | -526 | -510 | -226.14 | 0 | 0 | No
2030-11-02 20:00 | 2030 100% ECP | -700 | -526 | -510 | -336.15 | 0 | 0 | No
2030-11-02 21:00 | 2030 100% ECP | -700 | -226 | -210 | -36.15 | 0 | 0 | No
2030-11-02 22:00 | 2030 100% ECP | -700 | 74 | 90 | 263.85 | 0 | 0 | No
2030-11-02 23:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-11-03 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-03 07:00 | 2030 100% ECP | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-11-03 08:00 | 2030 100% ECP | -280 | -95 | -90 | 210 | 0 | 0 | No
2030-11-03 09:00 | 2030 100% ECP | -280 | -226 | -330.38 | 510 | 0 | 0 | No
2030-11-03 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-11-03 11:00 | 2030 100% ECP | -700 | -526 | -510 | 439.01 | 0 | 0 | No
2030-11-03 12:00 | 2030 100% ECP | -700 | -300 | -482.45 | 510 | 0 | 0 | No
2030-11-03 13:00 | 2030 100% ECP | -569.02 | 0 | -182.45 | 243.02 | 0 | 0 | No
2030-11-03 14:00 | 2030 100% ECP | -149.02 | 300 | 117.55 | 510 | 0 | 0 | No
2030-11-03 15:00 | 2030 100% ECP | 270.98 | 144.33 | 0 | 510 | 0 | 0 | No
2030-11-03 16:00 | 2030 100% ECP | 690.98 | -139.3 | -300 | 439.29 | 0 | 0 | No
2030-11-03 17:00 | 2030 100% ECP | 700 | 0 | -510 | 465.78 | 0 | 0 | No
2030-11-03 18:00 | 2030 100% ECP | 700 | 0 | -510 | 465.78 | 0 | 0 | No
2030-11-03 19:00 | 2030 100% ECP | 700 | 0 | -510 | 292.18 | 0 | 0 | No
2030-11-03 20:00 | 2030 100% ECP | 700 | 0 | -510 | 161.25 | 0 | 0 | No
2030-11-03 21:00 | 2030 100% ECP | 700 | 0 | -510 | 461.25 | 0 | 0 | No
2030-11-03 22:00 | 2030 100% ECP | 700 | -29.46 | -300 | 314.8 | 0 | 0 | No
2030-11-03 23:00 | 2030 100% ECP | 700 | 0 | 0 | 197.5 | 0 | 0 | No
2030-11-04 | 2030 100% ECP | 700 | 180.71 | 210 | 368.89 | 0 | 0 | No
2030-11-04 01:00 | 2030 100% ECP | 700 | 480.71 | 510 | 510 | 0 | 0 | No
2030-11-04 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 06:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-04 07:00 | 2030 100% ECP | 280 | 205 | 210 | 236.33 | 0 | 0 | No
2030-11-04 08:00 | 2030 100% ECP | 700 | 58.48 | 300 | 510 | 0 | 0 | No
2030-11-04 09:00 | 2030 100% ECP | 573.48 | 0 | 0 | 397.49 | 0 | 0 | No
2030-11-04 10:00 | 2030 100% ECP | 153.48 | -300 | 0 | 277.21 | 0 | 0 | No
2030-11-04 11:00 | 2030 100% ECP | -266.52 | -526 | 0 | 193.2 | 0 | 0 | No
2030-11-04 12:00 | 2030 100% ECP | -686.52 | -526 | 0 | 53.72 | 0 | 0 | No
2030-11-04 13:00 | 2030 100% ECP | -560 | -526 | 0 | 223.81 | 0 | 0 | No
2030-11-04 14:00 | 2030 100% ECP | -140 | -526 | 0 | 255.74 | 0 | 0 | No
2030-11-04 15:00 | 2030 100% ECP | 280 | -508.57 | 0 | 300.81 | 0 | 0 | No
2030-11-04 16:00 | 2030 100% ECP | 700 | -249.83 | 0 | 0.81 | 0 | 0 | No
2030-11-04 17:00 | 2030 100% ECP | 700 | -526 | 0 | -299.19 | 0 | 0 | No
2030-11-04 18:00 | 2030 100% ECP | 700 | -347.6 | 0 | 0.81 | 0 | 0 | No
2030-11-04 19:00 | 2030 100% ECP | 700 | -47.6 | 0 | 300.81 | 0 | 0 | No
2030-11-04 20:00 | 2030 100% ECP | 700 | 252.4 | 0 | 510 | 0 | 0 | No
2030-11-04 21:00 | 2030 100% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-04 22:00 | 2030 100% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-04 23:00 | 2030 100% ECP | 700 | 205 | 0 | 252.73 | 0 | 0 | No
2030-11-05 | 2030 100% ECP | 700 | 205 | 0 | 252.73 | 0 | 0 | No
2030-11-05 01:00 | 2030 100% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-05 02:00 | 2030 100% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-05 03:00 | 2030 100% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-05 04:00 | 2030 100% ECP | 700 | 333.7 | 0 | 510 | 0 | 0 | No
2030-11-05 05:00 | 2030 100% ECP | 700 | 33.7 | 0 | 210 | 0 | 0 | No
2030-11-05 06:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-11-05 07:00 | 2030 100% ECP | 700 | 0 | 0 | 210 | 0 | 0 | No
2030-11-05 08:00 | 2030 100% ECP | 700 | 161.35 | 0 | 510 | 0 | 0 | No
2030-11-05 09:00 | 2030 100% ECP | 700 | 20.3 | 0 | 510 | 0 | 0 | No
2030-11-05 10:00 | 2030 100% ECP | 700 | 0 | 0 | 279.81 | 0 | 0 | No
2030-11-05 11:00 | 2030 100% ECP | 560 | 0 | 0 | 140.73 | 0 | 0 | No
2030-11-05 12:00 | 2030 100% ECP | 140 | 0 | 0 | 139.96 | 0 | 0 | No
2030-11-05 13:00 | 2030 100% ECP | -280 | -226 | 0 | 120.75 | 0 | 0 | No
2030-11-05 14:00 | 2030 100% ECP | -700 | -526 | 0 | -179.25 | 0 | 0 | No
2030-11-05 15:00 | 2030 100% ECP | -280 | -226 | 0 | -200.16 | 0 | 0 | No
2030-11-05 16:00 | 2030 100% ECP | 140 | -226 | 0 | -210 | 0 | 0 | No
2030-11-05 17:00 | 2030 100% ECP | 560 | -526 | 0 | -510 | 0 | 0 | No
2030-11-05 18:00 | 2030 100% ECP | 700 | -526 | 0 | -510 | 0 | 0 | No
2030-11-05 19:00 | 2030 100% ECP | 700 | -526 | 0 | -510 | 0 | 0 | No
2030-11-05 20:00 | 2030 100% ECP | 700 | -226 | 0 | -210 | 0 | 0 | No
2030-11-05 21:00 | 2030 100% ECP | 700 | 0 | 0 | -56.59 | 0 | 0 | No
2030-11-05 22:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-11-05 23:00 | 2030 100% ECP | 700 | 13.28 | 0 | 300 | 0 | 0 | No
2030-11-06 | 2030 100% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-11-06 01:00 | 2030 100% ECP | 700 | 0 | 0 | 210 | 0 | 0 | No
2030-11-06 02:00 | 2030 100% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-11-06 03:00 | 2030 100% ECP | 700 | 0 | 0 | 268.04 | 0 | 0 | No
2030-11-06 04:00 | 2030 100% ECP | 462.56 | 0 | 0 | 0 | 0 | 0 | No
2030-11-06 05:00 | 2030 100% ECP | 42.56 | -226 | 0 | -210 | 0 | 0 | No
2030-11-06 06:00 | 2030 100% ECP | -377.44 | -526 | 0 | -510 | 0 | 0 | No
2030-11-06 07:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-11-06 08:00 | 2030 100% ECP | -559.31 | -526 | 0 | -510 | 0 | 0 | No
2030-11-06 09:00 | 2030 100% ECP | -139.31 | -526 | -510 | -357.96 | 0 | 0 | No
2030-11-06 10:00 | 2030 100% ECP | -559.31 | -526 | -510 | -57.96 | 0 | 0 | No
2030-11-06 11:00 | 2030 100% ECP | -700 | -526 | -510 | 242.04 | 0 | 0 | No
2030-11-06 12:00 | 2030 100% ECP | -700 | -526 | -510 | 61.61 | 0 | 0 | No
2030-11-06 13:00 | 2030 100% ECP | -700 | -526 | -510 | -238.39 | 0 | 0 | No
2030-11-06 14:00 | 2030 100% ECP | -700 | -526 | -510 | -377.76 | 0 | 0 | No
2030-11-06 15:00 | 2030 100% ECP | -700 | -526 | -510 | -228.79 | 0 | 0 | No
2030-11-06 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-06 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-06 18:00 | 2030 100% ECP | -700 | -526 | -510 | -493.62 | 0 | 0 | No
2030-11-06 19:00 | 2030 100% ECP | -572.29 | -526 | -510 | -193.62 | 0 | 0 | No
2030-11-06 20:00 | 2030 100% ECP | -152.29 | -226 | -210 | 106.38 | 0 | 0 | No
2030-11-06 21:00 | 2030 100% ECP | 267.71 | 0 | 90 | 406.38 | 0 | 0 | No
2030-11-06 22:00 | 2030 100% ECP | 687.71 | 0 | 277.51 | 106.38 | 0 | 0 | No
2030-11-06 23:00 | 2030 100% ECP | 700 | 0 | -22.49 | -102.42 | 0 | 0 | No
2030-11-07 | 2030 100% ECP | 700 | 300 | 277.51 | 197.58 | 0 | 0 | No
2030-11-07 01:00 | 2030 100% ECP | 700 | 505 | 510 | 497.58 | 0 | 0 | No
2030-11-07 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-07 03:00 | 2030 100% ECP | 700 | 505 | 507.48 | 510 | 0 | 0 | No
2030-11-07 04:00 | 2030 100% ECP | 700 | 300 | 207.48 | 210 | 0 | 0 | No
2030-11-07 05:00 | 2030 100% ECP | 280 | 0 | -92.52 | -90 | 0 | 0 | No
2030-11-07 06:00 | 2030 100% ECP | -140 | -300 | -392.52 | -390 | 0 | 0 | No
2030-11-07 07:00 | 2030 100% ECP | -280 | -526 | -510 | -410.81 | 0 | 0 | No
2030-11-07 08:00 | 2030 100% ECP | -700 | -526 | -510 | -219.85 | 0 | 0 | No
2030-11-07 09:00 | 2030 100% ECP | -299.44 | -526 | -510 | -219.85 | 0 | 0 | No
2030-11-07 10:00 | 2030 100% ECP | -700 | -526 | -510 | -242.39 | 0 | 0 | No
2030-11-07 11:00 | 2030 100% ECP | -700 | -526 | -510 | -481.34 | 0 | 0 | No
2030-11-07 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 14:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 15:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 18:00 | 2030 100% ECP | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-07 20:00 | 2030 100% ECP | -280 | -526 | -510 | -499.93 | 0 | 0 | No
2030-11-07 21:00 | 2030 100% ECP | 0 | -420.04 | -510 | -379.89 | 0 | 0 | No
2030-11-07 22:00 | 2030 100% ECP | 280 | -120.04 | -210 | -79.89 | 0 | 0 | No
2030-11-07 23:00 | 2030 100% ECP | 700 | -219.88 | -510 | -248.34 | 0 | 0 | No
2030-11-08 | 2030 100% ECP | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-11-08 01:00 | 2030 100% ECP | 700 | 0 | -353.79 | 0 | 0 | 0 | No
2030-11-08 02:00 | 2030 100% ECP | 560 | 0 | -300 | 0 | 0 | 0 | No
2030-11-08 03:00 | 2030 100% ECP | 140 | 0 | 0 | 0 | 0 | 0 | No
2030-11-08 04:00 | 2030 100% ECP | -280 | 0 | 0 | 0 | 0 | 0 | No
2030-11-08 05:00 | 2030 100% ECP | -700 | 0 | -51.71 | 0 | 0 | 0 | No
2030-11-08 06:00 | 2030 100% ECP | -700 | 0 | -212.39 | 0 | 0 | 0 | No
2030-11-08 07:00 | 2030 100% ECP | -700 | -300 | -510 | -78.32 | 0 | 0 | No
2030-11-08 08:00 | 2030 100% ECP | -700 | -526 | -510 | -233.98 | 0 | 0 | No
2030-11-08 09:00 | 2030 100% ECP | -700 | -300 | -510 | 18.79 | 0 | 0 | No
2030-11-08 10:00 | 2030 100% ECP | -700 | 0 | -385.38 | 318.79 | 0 | 0 | No
2030-11-08 11:00 | 2030 100% ECP | -700 | 0 | -85.38 | 366.18 | 0 | 0 | No
2030-11-08 12:00 | 2030 100% ECP | -700 | -226 | -385.38 | 312.95 | 0 | 0 | No
2030-11-08 13:00 | 2030 100% ECP | -700 | -526 | -510 | 146.34 | 0 | 0 | No
2030-11-08 14:00 | 2030 100% ECP | -700 | -526 | -510 | 212.3 | 0 | 0 | No
2030-11-08 15:00 | 2030 100% ECP | -700 | -526 | -510 | 205.27 | 0 | 0 | No
2030-11-08 16:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-11-08 17:00 | 2030 100% ECP | -700 | -526 | -510 | 163.3 | 0 | 0 | No
2030-11-08 18:00 | 2030 100% ECP | -700 | -526 | -510 | 90.82 | 0 | 0 | No
2030-11-08 19:00 | 2030 100% ECP | -407.11 | -526 | -510 | 0 | 0 | 0 | No
2030-11-08 20:00 | 2030 100% ECP | 12.89 | -526 | -510 | 107.89 | 0 | 0 | No
2030-11-08 21:00 | 2030 100% ECP | -67.06 | -526 | -510 | 407.89 | 0 | 0 | No
2030-11-08 22:00 | 2030 100% ECP | -294.79 | -526 | -510 | 207.22 | 0 | 0 | No
2030-11-08 23:00 | 2030 100% ECP | -379.18 | -526 | -510 | 124.27 | 0 | 0 | No
2030-11-09 | 2030 100% ECP | 40.82 | -226 | -210 | 324.06 | 0 | 0 | No
2030-11-09 01:00 | 2030 100% ECP | 460.82 | 0 | 90 | 324.06 | 0 | 0 | No
2030-11-09 02:00 | 2030 100% ECP | 700 | 0 | 253.52 | 137.56 | 0 | 0 | No
2030-11-09 03:00 | 2030 100% ECP | 700 | 0 | 253.52 | 178.13 | 0 | 0 | No
2030-11-09 04:00 | 2030 100% ECP | 560 | 0 | 161.64 | 2.22 | 0 | 0 | No
2030-11-09 05:00 | 2030 100% ECP | 140 | 0 | 0 | 0 | 0 | 0 | No
2030-11-09 06:00 | 2030 100% ECP | -280 | -226 | -210 | -151.6 | 0 | 0 | No
2030-11-09 07:00 | 2030 100% ECP | -700 | -526 | -510 | -451.6 | 0 | 0 | No
2030-11-09 08:00 | 2030 100% ECP | -700 | -526 | -510 | -151.6 | 0 | 0 | No
2030-11-09 09:00 | 2030 100% ECP | -700 | -526 | -510 | -62.45 | 0 | 0 | No
2030-11-09 10:00 | 2030 100% ECP | -700 | -526 | -510 | 34.04 | 0 | 0 | No
2030-11-09 11:00 | 2030 100% ECP | -602.01 | -526 | -510 | 98.18 | 0 | 0 | No
2030-11-09 12:00 | 2030 100% ECP | -700 | -526 | -510 | 157.18 | 0 | 0 | No
2030-11-09 13:00 | 2030 100% ECP | -700 | -526 | -510 | 83.3 | 0 | 0 | No
2030-11-09 14:00 | 2030 100% ECP | -318.19 | -526 | -510 | 0 | 0 | 0 | No
2030-11-09 15:00 | 2030 100% ECP | -87.85 | -526 | -510 | 92.92 | 0 | 0 | No
2030-11-09 16:00 | 2030 100% ECP | 0 | -526 | -510 | 92.92 | 0 | 0 | No
2030-11-09 17:00 | 2030 100% ECP | 0 | -526 | -510 | -205.98 | 0 | 0 | No
2030-11-09 18:00 | 2030 100% ECP | 0 | -526 | -510 | -57.15 | 0 | 0 | No
2030-11-09 19:00 | 2030 100% ECP | 0 | -526 | -510 | 242.85 | 0 | 0 | No
2030-11-09 20:00 | 2030 100% ECP | 0 | -404.24 | -510 | 325.92 | 0 | 0 | No
2030-11-09 21:00 | 2030 100% ECP | 280 | -104.24 | -210 | 238.05 | 0 | 0 | No
2030-11-09 22:00 | 2030 100% ECP | 700 | 195.76 | 90 | 510 | 0 | 0 | No
2030-11-09 23:00 | 2030 100% ECP | 700 | 0 | 274.33 | 210 | 0 | 0 | No
2030-11-10 | 2030 100% ECP | 700 | 0 | 450.8 | 60.18 | 0 | 0 | No
2030-11-10 01:00 | 2030 100% ECP | 700 | 0 | 265.33 | 0 | 0 | 0 | No
2030-11-10 02:00 | 2030 100% ECP | 700 | 0 | 141.78 | 46.35 | 0 | 0 | No
2030-11-10 03:00 | 2030 100% ECP | 700 | 0 | 265.95 | 0 | 0 | 0 | No
2030-11-10 04:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-11-10 05:00 | 2030 100% ECP | 280 | 0 | 145.6 | 0 | 0 | 0 | No
2030-11-10 06:00 | 2030 100% ECP | -140 | 0 | 95.24 | 114.26 | 0 | 0 | No
2030-11-10 07:00 | 2030 100% ECP | -560 | 0 | -204.76 | -134.73 | 0 | 0 | No
2030-11-10 08:00 | 2030 100% ECP | -700 | 0 | -504.76 | -371.31 | 0 | 0 | No
2030-11-10 09:00 | 2030 100% ECP | -502.28 | -300 | -510 | -383.54 | 0 | 0 | No
2030-11-10 10:00 | 2030 100% ECP | -700 | -526 | -510 | -83.54 | 0 | 0 | No
2030-11-10 11:00 | 2030 100% ECP | -700 | -526 | -510 | -237.85 | 0 | 0 | No
2030-11-10 12:00 | 2030 100% ECP | -700 | -526 | -510 | -464.2 | 0 | 0 | Yes
2030-11-10 13:00 | 2030 100% ECP | -700 | -526 | -510 | -278.37 | 0 | 0 | Yes
2030-11-10 14:00 | 2030 100% ECP | -700 | -526 | -510 | -284.39 | 0 | 0 | Yes
2030-11-10 15:00 | 2030 100% ECP | -700 | -526 | -510 | -436.42 | 0 | 0 | No
2030-11-10 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-11-10 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-11-10 18:00 | 2030 100% ECP | -700 | -526 | -510 | -373.41 | 0 | 0 | No
2030-11-10 19:00 | 2030 100% ECP | -700 | -526 | -510 | -73.41 | 0 | 0 | No
2030-11-10 20:00 | 2030 100% ECP | -700 | -526 | -510 | -71.82 | 0 | 0 | No
2030-11-10 21:00 | 2030 100% ECP | -700 | -526 | -510 | -3.35 | 0 | 0 | No
2030-11-10 22:00 | 2030 100% ECP | -700 | -526 | -510 | -66.72 | 0 | 0 | Yes
2030-11-10 23:00 | 2030 100% ECP | -700 | -526 | -510 | 7.22 | 0 | 0 | Yes
2030-11-11 | 2030 100% ECP | -700 | -526 | -510 | -133.07 | 0 | 0 | Yes
2030-11-11 01:00 | 2030 100% ECP | -700 | -226 | -210 | 166.93 | 0 | 0 | Yes
2030-11-11 02:00 | 2030 100% ECP | -700 | 74 | 90 | 466.93 | 0 | 0 | Yes
2030-11-11 03:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-11-11 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 16:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-11 17:00 | 2030 100% ECP | -700 | 320.87 | 510 | 453.4 | 0 | 0 | No
2030-11-11 18:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 19:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-11 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-12 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 01:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 02:00 | 2030 100% ECP | -26.62 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 03:00 | 2030 100% ECP | -446.62 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-12 06:00 | 2030 100% ECP | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-11-12 07:00 | 2030 100% ECP | -700 | -95 | -90 | 387.94 | 0 | 0 | No
2030-11-12 08:00 | 2030 100% ECP | -700 | -395 | -390 | 87.94 | 0 | 0 | No
2030-11-12 09:00 | 2030 100% ECP | -700 | -526 | -510 | 173.93 | 0 | 0 | No
2030-11-12 10:00 | 2030 100% ECP | -700 | -526 | -510 | 473.93 | 0 | 0 | Yes
2030-11-12 11:00 | 2030 100% ECP | -700 | -526 | -510 | 339.8 | 0 | 0 | Yes
2030-11-12 12:00 | 2030 100% ECP | -700 | -526 | -510 | 39.8 | 0 | 0 | Yes
2030-11-12 13:00 | 2030 100% ECP | -700 | -526 | -510 | -17.54 | 0 | 0 | Yes
2030-11-12 14:00 | 2030 100% ECP | -700 | -526 | -510 | -317.54 | 0 | 0 | Yes
2030-11-12 15:00 | 2030 100% ECP | -700 | -526 | -510 | -97.55 | 0 | 0 | Yes
2030-11-12 16:00 | 2030 100% ECP | -700 | -526 | -510 | -102.29 | 0 | 0 | Yes
2030-11-12 17:00 | 2030 100% ECP | -700 | -526 | -510 | -64.22 | 0 | 0 | No
2030-11-12 18:00 | 2030 100% ECP | -700 | -526 | -510 | -105.22 | 0 | 0 | No
2030-11-12 19:00 | 2030 100% ECP | -700 | -526 | -510 | -270.18 | 0 | 0 | No
2030-11-12 20:00 | 2030 100% ECP | -700 | -526 | -510 | -304.33 | 0 | 0 | No
2030-11-12 21:00 | 2030 100% ECP | -700 | -226 | -210 | -4.33 | 0 | 0 | No
2030-11-12 22:00 | 2030 100% ECP | -700 | 74 | 90 | 295.67 | 0 | 0 | No
2030-11-12 23:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-11-13 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 01:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 02:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 04:00 | 2030 100% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 05:00 | 2030 100% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 06:00 | 2030 100% ECP | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-11-13 07:00 | 2030 100% ECP | -700 | 205 | 210 | 490.84 | 0 | 0 | No
2030-11-13 08:00 | 2030 100% ECP | -700 | -95 | -90 | 190.84 | 0 | 0 | No
2030-11-13 09:00 | 2030 100% ECP | -700 | -256.22 | -390 | 480.34 | 0 | 0 | No
2030-11-13 10:00 | 2030 100% ECP | -700 | -300 | -418.22 | 510 | 0 | 0 | No
2030-11-13 11:00 | 2030 100% ECP | -700 | 0 | -118.22 | 510 | 0 | 0 | No
2030-11-13 12:00 | 2030 100% ECP | -700 | 300 | 109.93 | 510 | 0 | 0 | No
2030-11-13 13:00 | 2030 100% ECP | -700 | 0 | -190.07 | 279.84 | 0 | 0 | No
2030-11-13 14:00 | 2030 100% ECP | -700 | -300 | -490.07 | 150.87 | 0 | 0 | No
2030-11-13 15:00 | 2030 100% ECP | -700 | -526 | -510 | 396.1 | 0 | 0 | No
2030-11-13 16:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-11-13 17:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-11-13 18:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-11-13 19:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-11-13 20:00 | 2030 100% ECP | -603.77 | -526 | -510 | 510 | 0 | 0 | No
2030-11-13 21:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-11-13 22:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-11-13 23:00 | 2030 100% ECP | -700 | -226 | -384.33 | 327.88 | 0 | 0 | No
2030-11-14 | 2030 100% ECP | -700 | 74 | -84.33 | 510 | 0 | 0 | Yes
2030-11-14 01:00 | 2030 100% ECP | -700 | 374 | 215.67 | 510 | 0 | 0 | Yes
2030-11-14 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-14 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-14 04:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-11-14 05:00 | 2030 100% ECP | -700 | 74 | 90 | 381.44 | 0 | 0 | Yes
2030-11-14 06:00 | 2030 100% ECP | -700 | -226 | -210 | 81.44 | 0 | 0 | Yes
2030-11-14 07:00 | 2030 100% ECP | -700 | -526 | -510 | -218.56 | 0 | 0 | Yes
2030-11-14 08:00 | 2030 100% ECP | -700 | -526 | -510 | 81.44 | 0 | 0 | Yes
2030-11-14 09:00 | 2030 100% ECP | -700 | -526 | -510 | 381.44 | 0 | 0 | Yes
2030-11-14 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-14 11:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-14 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-14 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-14 14:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-14 15:00 | 2030 100% ECP | -700 | -388.77 | -510 | 510 | 0 | 0 | Yes
2030-11-14 16:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | Yes
2030-11-14 17:00 | 2030 100% ECP | -700 | -526 | -510 | -90 | 0 | 0 | No
2030-11-14 18:00 | 2030 100% ECP | -700 | -526 | -510 | -371.66 | 0 | 0 | No
2030-11-14 19:00 | 2030 100% ECP | -700 | -526 | -510 | -71.66 | 0 | 0 | No
2030-11-14 20:00 | 2030 100% ECP | -700 | -226 | -210 | 228.34 | 0 | 0 | No
2030-11-14 21:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-11-14 22:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-11-14 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-15 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-15 07:00 | 2030 100% ECP | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-11-15 08:00 | 2030 100% ECP | -568.18 | -95 | -90 | 510 | 0 | 0 | No
2030-11-15 09:00 | 2030 100% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-11-15 10:00 | 2030 100% ECP | -632.41 | 0 | 0 | 510 | 0 | 0 | No
2030-11-15 11:00 | 2030 100% ECP | -700 | 0 | -96.63 | 510 | 0 | 0 | No
2030-11-15 12:00 | 2030 100% ECP | -597.89 | 0 | -17.23 | 510 | 0 | 0 | No
2030-11-15 13:00 | 2030 100% ECP | -700 | -300 | -317.23 | 510 | 0 | 0 | No
2030-11-15 14:00 | 2030 100% ECP | -700 | -68.89 | -210 | 510 | 0 | 0 | No
2030-11-15 15:00 | 2030 100% ECP | -700 | -368.89 | -510 | 210 | 0 | 0 | No
2030-11-15 16:00 | 2030 100% ECP | -700 | -526 | -510 | -90 | 0 | 0 | No
2030-11-15 17:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-11-15 18:00 | 2030 100% ECP | -700 | -526 | -510 | 96.79 | 0 | 0 | No
2030-11-15 19:00 | 2030 100% ECP | -700 | -526 | -510 | 96.79 | 0 | 0 | No
2030-11-15 20:00 | 2030 100% ECP | -700 | -526 | -510 | -110.28 | 0 | 0 | Yes
2030-11-15 21:00 | 2030 100% ECP | -700 | -526 | -510 | -410.28 | 0 | 0 | Yes
2030-11-15 22:00 | 2030 100% ECP | -700 | -226 | -210 | -110.28 | 0 | 0 | Yes
2030-11-15 23:00 | 2030 100% ECP | -700 | 74 | 90 | 189.72 | 0 | 0 | Yes
2030-11-16 | 2030 100% ECP | -700 | 374 | 390 | 428.96 | 0 | 0 | Yes
2030-11-16 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-16 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-16 03:00 | 2030 100% ECP | -700 | 505 | 510 | 488.37 | 0 | 0 | Yes
2030-11-16 04:00 | 2030 100% ECP | -700 | 505 | 510 | 390.08 | 0 | 0 | Yes
2030-11-16 05:00 | 2030 100% ECP | -700 | 505 | 510 | 440.73 | 0 | 0 | Yes
2030-11-16 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-16 07:00 | 2030 100% ECP | -700 | 505 | 424.73 | 510 | 0 | 0 | No
2030-11-16 08:00 | 2030 100% ECP | -700 | 205 | 124.73 | 510 | 0 | 0 | No
2030-11-16 09:00 | 2030 100% ECP | -700 | -95 | -175.27 | 510 | 0 | 0 | No
2030-11-16 10:00 | 2030 100% ECP | -700 | 205 | 124.73 | 510 | 0 | 0 | Yes
2030-11-16 11:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-11-16 12:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-11-16 13:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-11-16 14:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-16 15:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-16 16:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-16 17:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-16 18:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-16 19:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-16 20:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-16 21:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-16 22:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-11-16 23:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-11-17 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-11-17 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-17 13:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-11-17 14:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-11-17 15:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-11-17 16:00 | 2030 100% ECP | -700 | -526 | -510 | 400.52 | 0 | 0 | Yes
2030-11-17 17:00 | 2030 100% ECP | -700 | -526 | -510 | 442.92 | 0 | 0 | Yes
2030-11-17 18:00 | 2030 100% ECP | -700 | -526 | -510 | 505.8 | 0 | 0 | Yes
2030-11-17 19:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-11-17 20:00 | 2030 100% ECP | -700 | -353.89 | -390 | 510 | 0 | 0 | Yes
2030-11-17 21:00 | 2030 100% ECP | -700 | -53.89 | -90 | 438.92 | 0 | 0 | Yes
2030-11-17 22:00 | 2030 100% ECP | -700 | 246.11 | 210 | 510 | 0 | 0 | Yes
2030-11-17 23:00 | 2030 100% ECP | -700 | 505 | 510 | 504.05 | 0 | 0 | Yes
2030-11-18 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 03:00 | 2030 100% ECP | -700 | 505 | 510 | 304.27 | 0 | 0 | Yes
2030-11-18 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 07:00 | 2030 100% ECP | -700 | 505 | 510 | 509.72 | 0 | 0 | Yes
2030-11-18 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 14:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-11-18 15:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-11-18 16:00 | 2030 100% ECP | -700 | -226 | -210 | 300 | 0 | 0 | Yes
2030-11-18 17:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-11-18 18:00 | 2030 100% ECP | -700 | -526 | -510 | -4.52 | 0 | 0 | Yes
2030-11-18 19:00 | 2030 100% ECP | -700 | -226 | -350.45 | 295.48 | 0 | 0 | Yes
2030-11-18 20:00 | 2030 100% ECP | -700 | 74 | -50.45 | 510 | 0 | 0 | Yes
2030-11-18 21:00 | 2030 100% ECP | -700 | 374 | 249.55 | 510 | 0 | 0 | Yes
2030-11-18 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-18 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-19 06:00 | 2030 100% ECP | -700 | 300 | 404.6 | 510 | 0 | 0 | No
2030-11-19 07:00 | 2030 100% ECP | -700 | 0 | 104.6 | 360.31 | 0 | 0 | No
2030-11-19 08:00 | 2030 100% ECP | -330.51 | 0 | 137.29 | 60.31 | 0 | 0 | No
2030-11-19 09:00 | 2030 100% ECP | -165.37 | 0 | 0 | 108.2 | 0 | 0 | No
2030-11-19 10:00 | 2030 100% ECP | -17.25 | 0 | 0 | 195.8 | 0 | 0 | No
2030-11-19 11:00 | 2030 100% ECP | -280 | 0 | -201.22 | 158.36 | 0 | 0 | No
2030-11-19 12:00 | 2030 100% ECP | -700 | -157.66 | -446.05 | 159.48 | 0 | 0 | No
2030-11-19 13:00 | 2030 100% ECP | -700 | 0 | -146.05 | 62.47 | 0 | 0 | No
2030-11-19 14:00 | 2030 100% ECP | -700 | 208.76 | 153.95 | 362.47 | 0 | 0 | No
2030-11-19 15:00 | 2030 100% ECP | -700 | 195.9 | 90 | 510 | 0 | 0 | No
2030-11-19 16:00 | 2030 100% ECP | -700 | -104.1 | -210 | 210 | 0 | 0 | No
2030-11-19 17:00 | 2030 100% ECP | -700 | -404.1 | -510 | -1.2 | 0 | 0 | No
2030-11-19 18:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-11-19 19:00 | 2030 100% ECP | -700 | -526 | -510 | -26.61 | 0 | 0 | No
2030-11-19 20:00 | 2030 100% ECP | -700 | -526 | -510 | -326.61 | 0 | 0 | No
2030-11-19 21:00 | 2030 100% ECP | -700 | -526 | -510 | -132.49 | 0 | 0 | No
2030-11-19 22:00 | 2030 100% ECP | -700 | -526 | -510 | -60.52 | 0 | 0 | No
2030-11-19 23:00 | 2030 100% ECP | -700 | -526 | -510 | -228.3 | 0 | 0 | No
2030-11-20 | 2030 100% ECP | -591.13 | -367 | -510 | 25.37 | 0 | 0 | No
2030-11-20 01:00 | 2030 100% ECP | -700 | -526 | -510 | -44.45 | 0 | 0 | No
2030-11-20 02:00 | 2030 100% ECP | -700 | -526 | -510 | -28.91 | 0 | 0 | No
2030-11-20 03:00 | 2030 100% ECP | -700 | -526 | -510 | 53.07 | 0 | 0 | No
2030-11-20 04:00 | 2030 100% ECP | -700 | -526 | -510 | 78.15 | 0 | 0 | No
2030-11-20 05:00 | 2030 100% ECP | -700 | -526 | -510 | -221.85 | 0 | 0 | No
2030-11-20 06:00 | 2030 100% ECP | -700 | -526 | -510 | -104.89 | 0 | 0 | No
2030-11-20 07:00 | 2030 100% ECP | -700 | -526 | -510 | -8.45 | 0 | 0 | No
2030-11-20 08:00 | 2030 100% ECP | -700 | -526 | -510 | 167.81 | 0 | 0 | No
2030-11-20 09:00 | 2030 100% ECP | -700 | -526 | -510 | 34.77 | 0 | 0 | No
2030-11-20 10:00 | 2030 100% ECP | -700 | -526 | -510 | 230.36 | 0 | 0 | No
2030-11-20 11:00 | 2030 100% ECP | -700 | -526 | -510 | 466.67 | 0 | 0 | No
2030-11-20 12:00 | 2030 100% ECP | -700 | -526 | -510 | 298.46 | 0 | 0 | No
2030-11-20 13:00 | 2030 100% ECP | -700 | -526 | -510 | -1.54 | 0 | 0 | No
2030-11-20 14:00 | 2030 100% ECP | -700 | -526 | -510 | -5.38 | 0 | 0 | No
2030-11-20 15:00 | 2030 100% ECP | -700 | -526 | -510 | -221.7 | 0 | 0 | No
2030-11-20 16:00 | 2030 100% ECP | -700 | -526 | -510 | -485.73 | 0 | 0 | No
2030-11-20 17:00 | 2030 100% ECP | -700 | -526 | -510 | -185.73 | 0 | 0 | No
2030-11-20 18:00 | 2030 100% ECP | -700 | -526 | -510 | 78.93 | 0 | 0 | No
2030-11-20 19:00 | 2030 100% ECP | -700 | -300 | -390 | -2.03 | 0 | 0 | No
2030-11-20 20:00 | 2030 100% ECP | -700 | 0 | -90 | 210 | 0 | 0 | No
2030-11-20 21:00 | 2030 100% ECP | -700 | 300 | 210 | 510 | 0 | 0 | No
2030-11-20 22:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-20 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-21 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 15:00 | 2030 100% ECP | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-11-21 16:00 | 2030 100% ECP | -700 | 0 | -90 | 510 | 0 | 0 | No
2030-11-21 17:00 | 2030 100% ECP | -700 | 0 | -56.06 | 510 | 0 | 0 | No
2030-11-21 18:00 | 2030 100% ECP | -700 | 0 | -166.18 | 510 | 0 | 0 | No
2030-11-21 19:00 | 2030 100% ECP | -700 | 0 | -90 | 510 | 0 | 0 | No
2030-11-21 20:00 | 2030 100% ECP | -420 | 0 | 210 | 510 | 0 | 0 | No
2030-11-21 21:00 | 2030 100% ECP | 0 | 300 | 510 | 510 | 0 | 0 | No
2030-11-21 22:00 | 2030 100% ECP | -2.63 | 505 | 510 | 510 | 0 | 0 | No
2030-11-21 23:00 | 2030 100% ECP | -291.18 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 | 2030 100% ECP | 128.82 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 01:00 | 2030 100% ECP | 548.82 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 02:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 03:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 04:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 07:00 | 2030 100% ECP | -700 | 242.29 | 510 | 510 | 0 | 0 | No
2030-11-22 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 10:00 | 2030 100% ECP | -700 | 205 | 510 | 389.63 | 0 | 0 | No
2030-11-22 11:00 | 2030 100% ECP | -700 | 0 | 305.08 | 204.49 | 0 | 0 | No
2030-11-22 12:00 | 2030 100% ECP | -700 | 0 | 5.08 | 0 | 0 | 0 | No
2030-11-22 13:00 | 2030 100% ECP | -700 | 0 | 5.08 | 0 | 0 | 0 | No
2030-11-22 14:00 | 2030 100% ECP | -700 | 205 | 305.08 | 0 | 0 | 0 | No
2030-11-22 15:00 | 2030 100% ECP | -700 | 505 | 510 | 265.59 | 0 | 0 | No
2030-11-22 16:00 | 2030 100% ECP | -700 | 505 | 510 | 427.26 | 0 | 0 | No
2030-11-22 17:00 | 2030 100% ECP | -700 | 205 | 210 | 127.26 | 0 | 0 | No
2030-11-22 18:00 | 2030 100% ECP | -700 | 0 | 0 | 0 | 0 | 0 | No
2030-11-22 19:00 | 2030 100% ECP | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-11-22 20:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 21:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-22 22:00 | 2030 100% ECP | -387.57 | 205 | 210 | 210 | 0 | 0 | No
2030-11-22 23:00 | 2030 100% ECP | -176.95 | -95 | -90 | -90 | 0 | 0 | No
2030-11-23 | 2030 100% ECP | -29.97 | -395 | -390 | -371.23 | 0 | 0 | No
2030-11-23 01:00 | 2030 100% ECP | -145.33 | -526 | -510 | -140.11 | 0 | 0 | No
2030-11-23 02:00 | 2030 100% ECP | -106.42 | -526 | -510 | 159.89 | 0 | 0 | No
2030-11-23 03:00 | 2030 100% ECP | -449.86 | -526 | -510 | 85.93 | 0 | 0 | No
2030-11-23 04:00 | 2030 100% ECP | -700 | -526 | -510 | -89.52 | 0 | 0 | No
2030-11-23 05:00 | 2030 100% ECP | -700 | -526 | -510 | -381.12 | 0 | 0 | Yes
2030-11-23 06:00 | 2030 100% ECP | -700 | -526 | -510 | -268.92 | 0 | 0 | Yes
2030-11-23 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-11-23 08:00 | 2030 100% ECP | -700 | -526 | -510 | -395.17 | 0 | 0 | Yes
2030-11-23 09:00 | 2030 100% ECP | -700 | -526 | -510 | -95.17 | 0 | 0 | Yes
2030-11-23 10:00 | 2030 100% ECP | -700 | -526 | -510 | -28.73 | 0 | 0 | Yes
2030-11-23 11:00 | 2030 100% ECP | -700 | -526 | -510 | -267.75 | 0 | 0 | Yes
2030-11-23 12:00 | 2030 100% ECP | -700 | -526 | -510 | 32.25 | 0 | 0 | Yes
2030-11-23 13:00 | 2030 100% ECP | -700 | -226 | -210 | 332.25 | 0 | 0 | Yes
2030-11-23 14:00 | 2030 100% ECP | -700 | 74 | 90 | 486.6 | 0 | 0 | Yes
2030-11-23 15:00 | 2030 100% ECP | -700 | -226 | -210 | 186.6 | 0 | 0 | Yes
2030-11-23 16:00 | 2030 100% ECP | -700 | -526 | -510 | -113.4 | 0 | 0 | Yes
2030-11-23 17:00 | 2030 100% ECP | -700 | -526 | -510 | -413.4 | 0 | 0 | Yes
2030-11-23 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-11-23 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-23 20:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-11-23 21:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-11-23 22:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-11-23 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-11-24 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 15:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-24 16:00 | 2030 100% ECP | -700 | 205 | 210 | 507.35 | 0 | 0 | No
2030-11-24 17:00 | 2030 100% ECP | -700 | -95 | -90 | 510 | 0 | 0 | No
2030-11-24 18:00 | 2030 100% ECP | -700 | -375.78 | -390 | 510 | 0 | 0 | No
2030-11-24 19:00 | 2030 100% ECP | -280 | -75.78 | -90 | 510 | 0 | 0 | No
2030-11-24 20:00 | 2030 100% ECP | 140 | 224.22 | 210 | 510 | 0 | 0 | No
2030-11-24 21:00 | 2030 100% ECP | 199.89 | 0 | 0 | 510 | 0 | 0 | No
2030-11-24 22:00 | 2030 100% ECP | 280 | 80.55 | 210 | 510 | 0 | 0 | No
2030-11-24 23:00 | 2030 100% ECP | 700 | 380.55 | 510 | 510 | 0 | 0 | No
2030-11-25 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-25 06:00 | 2030 100% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-11-25 07:00 | 2030 100% ECP | 700 | 0 | -90 | 0 | 0 | 0 | No
2030-11-25 08:00 | 2030 100% ECP | 700 | 0 | 18.53 | 131.93 | 0 | 0 | No
2030-11-25 09:00 | 2030 100% ECP | 700 | 0 | 300 | 431.93 | 0 | 0 | No
2030-11-25 10:00 | 2030 100% ECP | 700 | 0 | 0 | 220.93 | 0 | 0 | No
2030-11-25 11:00 | 2030 100% ECP | 700 | 0 | -131.59 | 225.43 | 0 | 0 | No
2030-11-25 12:00 | 2030 100% ECP | 700 | 0 | -131.59 | 167.32 | 0 | 0 | No
2030-11-25 13:00 | 2030 100% ECP | 280 | 0 | -131.59 | 104.41 | 0 | 0 | No
2030-11-25 14:00 | 2030 100% ECP | 0 | 0 | 0 | 0 | 0 | 0 | No
2030-11-25 15:00 | 2030 100% ECP | 337.28 | 0 | -210 | 0 | 0 | 0 | No
2030-11-25 16:00 | 2030 100% ECP | -76.51 | -300 | -510 | -133.76 | 0 | 0 | No
2030-11-25 17:00 | 2030 100% ECP | -496.51 | -526 | -510 | -376.34 | 0 | 0 | No
2030-11-25 18:00 | 2030 100% ECP | -700 | -526 | -510 | -214.22 | 0 | 0 | No
2030-11-25 19:00 | 2030 100% ECP | -420 | -526 | -510 | 0 | 0 | 0 | No
2030-11-25 20:00 | 2030 100% ECP | 0 | -300 | -418.43 | 0 | 0 | 0 | No
2030-11-25 21:00 | 2030 100% ECP | 420 | 0 | -118.43 | 195.03 | 0 | 0 | No
2030-11-25 22:00 | 2030 100% ECP | 700 | 101.08 | 181.57 | 495.03 | 0 | 0 | No
2030-11-25 23:00 | 2030 100% ECP | 700 | 0 | 211.22 | 195.03 | 0 | 0 | No
2030-11-26 | 2030 100% ECP | 700 | 300 | 510 | 495.03 | 0 | 0 | No
2030-11-26 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-26 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-26 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-26 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-26 05:00 | 2030 100% ECP | 700 | 505 | 510 | 210 | 0 | 0 | No
2030-11-26 06:00 | 2030 100% ECP | 700 | 451.95 | 390 | -90 | 0 | 0 | No
2030-11-26 07:00 | 2030 100% ECP | 395.54 | 151.95 | 90 | -210 | 0 | 0 | No
2030-11-26 08:00 | 2030 100% ECP | 0 | -148.05 | -210 | -510 | 0 | 0 | No
2030-11-26 09:00 | 2030 100% ECP | 24.78 | -448.05 | -510 | -510 | 0 | 0 | No
2030-11-26 10:00 | 2030 100% ECP | 420 | -148.05 | -210 | -210 | 0 | 0 | No
2030-11-26 11:00 | 2030 100% ECP | 0 | -226 | -210 | -210 | 0 | 0 | No
2030-11-26 12:00 | 2030 100% ECP | -420 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 14:00 | 2030 100% ECP | -574.67 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 15:00 | 2030 100% ECP | -154.67 | -233.29 | -510 | -510 | 0 | 0 | No
2030-11-26 16:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 17:00 | 2030 100% ECP | 163.13 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 18:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 19:00 | 2030 100% ECP | 280 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 20:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-26 21:00 | 2030 100% ECP | 700 | -226 | -255.46 | -499.59 | 0 | 0 | No
2030-11-26 22:00 | 2030 100% ECP | 700 | 74 | 44.54 | -199.59 | 0 | 0 | No
2030-11-26 23:00 | 2030 100% ECP | 700 | 0 | -255.46 | -255.42 | 0 | 0 | No
2030-11-27 | 2030 100% ECP | 700 | 300 | 44.54 | 0 | 0 | 0 | No
2030-11-27 01:00 | 2030 100% ECP | 700 | 505 | 344.54 | 0 | 0 | 0 | No
2030-11-27 02:00 | 2030 100% ECP | 700 | 505 | 510 | 0 | 0 | 0 | No
2030-11-27 03:00 | 2030 100% ECP | 700 | 505 | 510 | 0 | 0 | 0 | No
2030-11-27 04:00 | 2030 100% ECP | 420 | 505 | 510 | 0 | 0 | 0 | No
2030-11-27 05:00 | 2030 100% ECP | 0 | 205 | 210 | 0 | 0 | 0 | No
2030-11-27 06:00 | 2030 100% ECP | -420 | -95 | -90 | -210 | 0 | 0 | No
2030-11-27 07:00 | 2030 100% ECP | -700 | -395 | -390 | -510 | 0 | 0 | No
2030-11-27 08:00 | 2030 100% ECP | -439.98 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 09:00 | 2030 100% ECP | -19.98 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 10:00 | 2030 100% ECP | -19.98 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 11:00 | 2030 100% ECP | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 14:00 | 2030 100% ECP | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 15:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 16:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 17:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 18:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 19:00 | 2030 100% ECP | 280 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 20:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-11-27 21:00 | 2030 100% ECP | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-11-27 22:00 | 2030 100% ECP | 700 | 0 | -456.24 | -154.42 | 0 | 0 | No
2030-11-27 23:00 | 2030 100% ECP | 659.01 | 0 | -156.24 | 0 | 0 | 0 | No
2030-11-28 | 2030 100% ECP | 700 | 300 | 143.76 | 300 | 0 | 0 | No
2030-11-28 01:00 | 2030 100% ECP | 700 | 505 | 443.76 | 510 | 0 | 0 | No
2030-11-28 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-28 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-11-28 04:00 | 2030 100% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-11-28 05:00 | 2030 100% ECP | -140 | 408.22 | 390 | 485.54 | 0 | 0 | No
2030-11-28 06:00 | 2030 100% ECP | -560 | 108.22 | 90 | 185.54 | 0 | 0 | No
2030-11-28 07:00 | 2030 100% ECP | -503.28 | -191.78 | -210 | -114.46 | 0 | 0 | No
2030-11-28 08:00 | 2030 100% ECP | -83.28 | 0 | -510 | -414.46 | 0 | 0 | No
2030-11-28 09:00 | 2030 100% ECP | 71.74 | 0 | -510 | -510 | 0 | 0 | No
2030-11-28 10:00 | 2030 100% ECP | 12.95 | 0 | -210 | -210 | 0 | 0 | No
2030-11-28 11:00 | 2030 100% ECP | -44.31 | -226 | -510 | -128.83 | 0 | 0 | No
2030-11-28 12:00 | 2030 100% ECP | -464.31 | -526 | -510 | -218.7 | 0 | 0 | No
2030-11-28 13:00 | 2030 100% ECP | -328.64 | -300 | -510 | -193.12 | 0 | 0 | No
2030-11-28 14:00 | 2030 100% ECP | 0 | 0 | -348.22 | -260.12 | 0 | 0 | No
2030-11-28 15:00 | 2030 100% ECP | 37.17 | 0 | -48.22 | 0 | 0 | 0 | No
2030-11-28 16:00 | 2030 100% ECP | -205.44 | -226 | -210 | -210 | 0 | 0 | No
2030-11-28 17:00 | 2030 100% ECP | -625.44 | -526 | -510 | -510 | 0 | 0 | No
2030-11-28 18:00 | 2030 100% ECP | -205.44 | -526 | -510 | -446.45 | 0 | 0 | No
2030-11-28 19:00 | 2030 100% ECP | 214.56 | -258.12 | -510 | -146.45 | 0 | 0 | No
2030-11-28 20:00 | 2030 100% ECP | 634.56 | 0 | 0 | 153.55 | 0 | 0 | No
2030-11-28 21:00 | 2030 100% ECP | 700 | 0 | 0 | 453.55 | 0 | 0 | No
2030-11-28 22:00 | 2030 100% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-11-28 23:00 | 2030 100% ECP | 700 | 113.56 | 0 | 510 | 0 | 0 | No
2030-11-29 | 2030 100% ECP | 700 | 413.56 | 0 | 510 | 0 | 0 | No
2030-11-29 01:00 | 2030 100% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 02:00 | 2030 100% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 03:00 | 2030 100% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 04:00 | 2030 100% ECP | 700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-29 05:00 | 2030 100% ECP | 700 | 505 | 0 | 361.35 | 0 | 0 | No
2030-11-29 06:00 | 2030 100% ECP | 700 | 376.25 | 0 | 61.35 | 0 | 0 | No
2030-11-29 07:00 | 2030 100% ECP | 700 | 76.25 | 0 | -30.51 | 0 | 0 | No
2030-11-29 08:00 | 2030 100% ECP | 614.46 | 73.28 | 0 | -300 | 0 | 0 | No
2030-11-29 09:00 | 2030 100% ECP | 700 | 373.28 | 0 | 0 | 0 | 0 | No
2030-11-29 10:00 | 2030 100% ECP | 700 | 505 | 0 | 0 | 0 | 0 | No
2030-11-29 11:00 | 2030 100% ECP | 700 | 294.19 | 0 | 10.6 | 0 | 0 | No
2030-11-29 12:00 | 2030 100% ECP | 700 | 505 | 0 | 10.6 | 0 | 0 | No
2030-11-29 13:00 | 2030 100% ECP | 700 | 374 | 0 | 0 | 0 | 0 | No
2030-11-29 14:00 | 2030 100% ECP | 700 | 74 | 0 | 0 | 0 | 0 | No
2030-11-29 15:00 | 2030 100% ECP | 486.85 | -226 | 0 | -210 | 0 | 0 | No
2030-11-29 16:00 | 2030 100% ECP | 66.85 | -526 | 0 | -510 | 0 | 0 | No
2030-11-29 17:00 | 2030 100% ECP | -140 | -526 | 0 | -510 | 0 | 0 | No
2030-11-29 18:00 | 2030 100% ECP | 280 | -526 | 0 | -510 | 0 | 0 | No
2030-11-29 19:00 | 2030 100% ECP | 700 | -300 | 0 | -510 | 0 | 0 | No
2030-11-29 20:00 | 2030 100% ECP | 700 | 0 | 0 | -210 | 0 | 0 | No
2030-11-29 21:00 | 2030 100% ECP | 700 | 300 | 0 | -39.32 | 0 | 0 | No
2030-11-29 22:00 | 2030 100% ECP | 667.61 | 0 | 0 | -167.84 | 0 | 0 | No
2030-11-29 23:00 | 2030 100% ECP | 700 | 0 | 0 | 33.57 | 0 | 0 | No
2030-11-30 | 2030 100% ECP | 325.47 | 0 | 0 | 0 | 0 | 0 | No
2030-11-30 01:00 | 2030 100% ECP | 351.55 | 0 | 0 | 0 | 0 | 0 | No
2030-11-30 02:00 | 2030 100% ECP | 37.82 | -300 | 0 | -91.6 | 0 | 0 | No
2030-11-30 03:00 | 2030 100% ECP | -275.89 | -526 | 0 | 102.61 | 0 | 0 | No
2030-11-30 04:00 | 2030 100% ECP | -451.54 | -526 | 0 | -197.39 | 0 | 0 | No
2030-11-30 05:00 | 2030 100% ECP | -700 | -526 | 0 | -375.55 | 0 | 0 | No
2030-11-30 06:00 | 2030 100% ECP | -700 | -526 | 0 | -479.09 | 0 | 0 | No
2030-11-30 07:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-11-30 08:00 | 2030 100% ECP | -700 | -395 | 0 | -390 | 0 | 0 | No
2030-11-30 09:00 | 2030 100% ECP | -700 | -95 | 0 | -90 | 0 | 0 | No
2030-11-30 10:00 | 2030 100% ECP | -700 | 205 | 0 | 210 | 0 | 0 | No
2030-11-30 11:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 12:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 13:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 14:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 15:00 | 2030 100% ECP | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-11-30 16:00 | 2030 100% ECP | -700 | 205 | 0 | 510 | 0 | 0 | No
2030-11-30 17:00 | 2030 100% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-11-30 18:00 | 2030 100% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-11-30 19:00 | 2030 100% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-11-30 20:00 | 2030 100% ECP | -280 | 0 | -510 | 510 | 0 | 0 | No
2030-11-30 21:00 | 2030 100% ECP | 140 | 0 | -300 | 510 | 0 | 0 | No
2030-11-30 22:00 | 2030 100% ECP | 560 | 0 | 0 | 510 | 0 | 0 | No
2030-11-30 23:00 | 2030 100% ECP | 700 | 300 | 300 | 510 | 0 | 0 | No
2030-12-01 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 04:00 | 2030 100% ECP | 634.3 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 05:00 | 2030 100% ECP | 352.34 | 505 | 510 | 510 | 0 | 0 | No
2030-12-01 06:00 | 2030 100% ECP | 221.18 | 205 | 210 | 210 | 0 | 0 | No
2030-12-01 07:00 | 2030 100% ECP | 134.61 | 0 | 0 | 0 | 0 | 0 | No
2030-12-01 08:00 | 2030 100% ECP | 0 | 0 | 300 | 84.8 | 0 | 0 | No
2030-12-01 09:00 | 2030 100% ECP | 403.94 | 0 | 510 | 137.14 | 0 | 0 | No
2030-12-01 10:00 | 2030 100% ECP | 340.66 | 0 | 414.84 | 70.22 | 0 | 0 | No
2030-12-01 11:00 | 2030 100% ECP | 0 | 0 | 114.84 | 0 | 0 | 0 | No
2030-12-01 12:00 | 2030 100% ECP | -212.13 | 0 | 0 | 39.21 | 0 | 0 | No
2030-12-01 13:00 | 2030 100% ECP | -3.69 | 0 | 0 | 113.89 | 0 | 0 | No
2030-12-01 14:00 | 2030 100% ECP | 10.14 | 0 | 0 | 72.31 | 0 | 0 | No
2030-12-01 15:00 | 2030 100% ECP | -118.35 | 74 | 90 | 109.12 | 0 | 0 | No
2030-12-01 16:00 | 2030 100% ECP | -538.35 | -226 | -210 | -190.88 | 0 | 0 | No
2030-12-01 17:00 | 2030 100% ECP | -700 | -526 | -510 | -490.88 | 0 | 0 | No
2030-12-01 18:00 | 2030 100% ECP | -420 | -300 | -300 | -190.88 | 0 | 0 | No
2030-12-01 19:00 | 2030 100% ECP | 0 | 0 | 0 | 109.12 | 0 | 0 | No
2030-12-01 20:00 | 2030 100% ECP | 420 | 0 | -210.57 | 123.67 | 0 | 0 | No
2030-12-01 21:00 | 2030 100% ECP | 0 | 0 | -76.39 | 0 | 0 | 0 | No
2030-12-01 22:00 | 2030 100% ECP | 145.64 | 0 | -376.39 | -71.7 | 0 | 0 | No
2030-12-01 23:00 | 2030 100% ECP | 565.64 | 0 | -510 | 177.55 | 0 | 0 | No
2030-12-02 | 2030 100% ECP | 535.01 | -105.65 | -510 | 195.05 | 0 | 0 | No
2030-12-02 01:00 | 2030 100% ECP | 115.01 | -402.38 | -510 | 65.4 | 0 | 0 | No
2030-12-02 02:00 | 2030 100% ECP | -304.99 | -526 | -510 | 47.59 | 0 | 0 | No
2030-12-02 03:00 | 2030 100% ECP | -126.69 | -226 | -510 | -252.41 | 0 | 0 | No
2030-12-02 04:00 | 2030 100% ECP | -546.69 | -526 | -510 | -419.63 | 0 | 0 | No
2030-12-02 05:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-02 06:00 | 2030 100% ECP | -700 | -526 | -510 | -447.12 | 0 | 0 | No
2030-12-02 07:00 | 2030 100% ECP | -700 | -300 | -400.43 | -147.12 | 0 | 0 | No
2030-12-02 08:00 | 2030 100% ECP | -700 | 0 | -100.43 | 152.88 | 0 | 0 | No
2030-12-02 09:00 | 2030 100% ECP | -700 | 300 | 130.13 | 452.88 | 0 | 0 | No
2030-12-02 10:00 | 2030 100% ECP | -700 | 0 | -169.87 | 416.88 | 0 | 0 | No
2030-12-02 11:00 | 2030 100% ECP | -700 | -300 | -469.87 | 116.88 | 0 | 0 | No
2030-12-02 12:00 | 2030 100% ECP | -700 | -526 | -510 | 121.55 | 0 | 0 | No
2030-12-02 13:00 | 2030 100% ECP | -700 | -526 | -510 | 140.79 | 0 | 0 | No
2030-12-02 14:00 | 2030 100% ECP | -700 | -526 | -510 | 440.79 | 0 | 0 | No
2030-12-02 15:00 | 2030 100% ECP | -700 | -300 | -358.24 | 428.08 | 0 | 0 | No
2030-12-02 16:00 | 2030 100% ECP | -700 | 0 | -58.24 | 455.02 | 0 | 0 | No
2030-12-02 17:00 | 2030 100% ECP | -700 | -269.19 | -300 | 510 | 0 | 0 | No
2030-12-02 18:00 | 2030 100% ECP | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-12-02 19:00 | 2030 100% ECP | -700 | 0 | 35.02 | 456.2 | 0 | 0 | No
2030-12-02 20:00 | 2030 100% ECP | -280 | 0 | 66.18 | 363.11 | 0 | 0 | No
2030-12-02 21:00 | 2030 100% ECP | -57.53 | 0 | 66.18 | 291.02 | 0 | 0 | No
2030-12-02 22:00 | 2030 100% ECP | -371.75 | 300 | 366.18 | 510 | 0 | 0 | No
2030-12-02 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 01:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 02:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 03:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 04:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 05:00 | 2030 100% ECP | -280 | 505 | 510 | 392.2 | 0 | 0 | No
2030-12-03 06:00 | 2030 100% ECP | -700 | 505 | 510 | 392.2 | 0 | 0 | No
2030-12-03 07:00 | 2030 100% ECP | -700 | 505 | 510 | 300 | 0 | 0 | No
2030-12-03 08:00 | 2030 100% ECP | -700 | 205 | 210 | 0 | 0 | 0 | No
2030-12-03 09:00 | 2030 100% ECP | -636.84 | 0 | 0 | 0 | 0 | 0 | No
2030-12-03 10:00 | 2030 100% ECP | -216.84 | 0 | 300 | 236.49 | 0 | 0 | No
2030-12-03 11:00 | 2030 100% ECP | 203.16 | 300 | 510 | 510 | 0 | 0 | No
2030-12-03 12:00 | 2030 100% ECP | 623.16 | 183.71 | 510 | 510 | 0 | 0 | No
2030-12-03 13:00 | 2030 100% ECP | 203.16 | 176.2 | 510 | 510 | 0 | 0 | No
2030-12-03 14:00 | 2030 100% ECP | 280 | 176.2 | 510 | 510 | 0 | 0 | No
2030-12-03 15:00 | 2030 100% ECP | 700 | 300 | 397.46 | 300 | 0 | 0 | No
2030-12-03 16:00 | 2030 100% ECP | 420 | 0 | 97.46 | 0 | 0 | 0 | No
2030-12-03 17:00 | 2030 100% ECP | 0 | -95 | -90 | -90 | 0 | 0 | No
2030-12-03 18:00 | 2030 100% ECP | 280 | 205 | 210 | 210 | 0 | 0 | No
2030-12-03 19:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-03 20:00 | 2030 100% ECP | 700 | 205 | 510 | 434.66 | 0 | 0 | No
2030-12-03 21:00 | 2030 100% ECP | 700 | 0 | 510 | 360.35 | 0 | 0 | No
2030-12-03 22:00 | 2030 100% ECP | 700 | 0 | 385.68 | 60.35 | 0 | 0 | No
2030-12-03 23:00 | 2030 100% ECP | 700 | 205 | 487.23 | 232.85 | 0 | 0 | No
2030-12-04 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-12-04 01:00 | 2030 100% ECP | 140 | 205 | 403.33 | 210 | 0 | 0 | No
2030-12-04 02:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-04 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-04 04:00 | 2030 100% ECP | -700 | 374 | 390 | 390 | 0 | 0 | No
2030-12-04 05:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | No
2030-12-04 06:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-12-04 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-04 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-04 09:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-04 10:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-04 11:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-04 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-04 13:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-12-04 14:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-12-04 15:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-12-04 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-04 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-04 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-04 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-04 20:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-04 21:00 | 2030 100% ECP | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-12-04 22:00 | 2030 100% ECP | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-12-04 23:00 | 2030 100% ECP | -700 | 374 | 390 | 267.75 | 0 | 0 | Yes
2030-12-05 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-05 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-05 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-05 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-05 04:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-12-05 05:00 | 2030 100% ECP | -700 | 74 | 90 | 293.99 | 0 | 0 | Yes
2030-12-05 06:00 | 2030 100% ECP | -700 | -226 | -210 | -6.01 | 0 | 0 | Yes
2030-12-05 07:00 | 2030 100% ECP | -700 | -526 | -510 | -276.73 | 0 | 0 | Yes
2030-12-05 08:00 | 2030 100% ECP | -700 | -526 | -510 | -15.41 | 0 | 0 | Yes
2030-12-05 09:00 | 2030 100% ECP | -700 | -526 | -510 | -170.34 | 0 | 0 | No
2030-12-05 10:00 | 2030 100% ECP | -700 | -526 | -510 | -88.24 | 0 | 0 | No
2030-12-05 11:00 | 2030 100% ECP | -700 | -526 | -510 | 211.76 | 0 | 0 | No
2030-12-05 12:00 | 2030 100% ECP | -700 | -526 | -510 | -55.5 | 0 | 0 | No
2030-12-05 13:00 | 2030 100% ECP | -568.65 | -526 | -510 | -174.5 | 0 | 0 | No
2030-12-05 14:00 | 2030 100% ECP | -440.05 | -526 | -510 | -87.68 | 0 | 0 | No
2030-12-05 15:00 | 2030 100% ECP | -20.05 | -526 | -510 | -339.79 | 0 | 0 | No
2030-12-05 16:00 | 2030 100% ECP | -440.05 | -340.15 | -510 | -339.79 | 0 | 0 | No
2030-12-05 17:00 | 2030 100% ECP | -700 | -40.15 | -510 | -271.9 | 0 | 0 | No
2030-12-05 18:00 | 2030 100% ECP | -330.32 | 0 | -510 | 0 | 0 | 0 | No
2030-12-05 19:00 | 2030 100% ECP | 0 | -299.29 | -510 | 0 | 0 | 0 | No
2030-12-05 20:00 | 2030 100% ECP | 0 | -299.29 | -510 | 0 | 0 | 0 | No
2030-12-05 21:00 | 2030 100% ECP | 0 | -299.29 | -300 | 0 | 0 | 0 | No
2030-12-05 22:00 | 2030 100% ECP | 280 | 0 | 0 | 79.44 | 0 | 0 | No
2030-12-05 23:00 | 2030 100% ECP | 700 | 300 | 300 | 379.44 | 0 | 0 | No
2030-12-06 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-06 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-06 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-06 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-06 04:00 | 2030 100% ECP | 700 | 505 | 510 | 418.94 | 0 | 0 | No
2030-12-06 05:00 | 2030 100% ECP | 700 | 505 | 510 | 118.94 | 0 | 0 | No
2030-12-06 06:00 | 2030 100% ECP | 280 | 505 | 510 | -111.47 | 0 | 0 | No
2030-12-06 07:00 | 2030 100% ECP | 280 | 251.15 | 210 | -289.74 | 0 | 0 | No
2030-12-06 08:00 | 2030 100% ECP | 700 | -48.85 | -90 | -349.51 | 0 | 0 | No
2030-12-06 09:00 | 2030 100% ECP | 700 | 0 | 0 | -49.51 | 0 | 0 | No
2030-12-06 10:00 | 2030 100% ECP | 700 | 0 | -300 | -15.12 | 0 | 0 | No
2030-12-06 11:00 | 2030 100% ECP | 280 | -33.06 | -510 | -208.49 | 0 | 0 | No
2030-12-06 12:00 | 2030 100% ECP | 232.19 | -333.06 | -510 | -507.71 | 0 | 0 | No
2030-12-06 13:00 | 2030 100% ECP | 568.7 | -526 | -510 | -510 | 0 | 0 | No
2030-12-06 14:00 | 2030 100% ECP | 700 | -270.64 | -510 | -510 | 0 | 0 | No
2030-12-06 15:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-06 16:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-06 17:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-06 18:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-06 19:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-06 20:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-06 21:00 | 2030 100% ECP | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-06 22:00 | 2030 100% ECP | 598.97 | -226 | -210 | -210 | 0 | 0 | No
2030-12-06 23:00 | 2030 100% ECP | 700 | 0 | 65.44 | 0 | 0 | 0 | No
2030-12-07 | 2030 100% ECP | 700 | 0 | 365.44 | 0 | 0 | 0 | No
2030-12-07 01:00 | 2030 100% ECP | 700 | 59.71 | 510 | 0 | 0 | 0 | No
2030-12-07 02:00 | 2030 100% ECP | 700 | 359.71 | 510 | 300 | 0 | 0 | No
2030-12-07 03:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-12-07 04:00 | 2030 100% ECP | 140 | 471.32 | 510 | 300 | 0 | 0 | No
2030-12-07 05:00 | 2030 100% ECP | -280 | 171.32 | 510 | 0 | 0 | 0 | No
2030-12-07 06:00 | 2030 100% ECP | -700 | 62.51 | 300 | -54.45 | 0 | 0 | No
2030-12-07 07:00 | 2030 100% ECP | -700 | 0 | 0 | -354.45 | 0 | 0 | No
2030-12-07 08:00 | 2030 100% ECP | -700 | 0 | -300 | -510 | 0 | 0 | No
2030-12-07 09:00 | 2030 100% ECP | -700 | 0 | -90 | -354.23 | 0 | 0 | No
2030-12-07 10:00 | 2030 100% ECP | -700 | 149.01 | 210 | -54.23 | 0 | 0 | No
2030-12-07 11:00 | 2030 100% ECP | -700 | 449.01 | 510 | 245.77 | 0 | 0 | No
2030-12-07 12:00 | 2030 100% ECP | -700 | 149.01 | 510 | 151.32 | 0 | 0 | No
2030-12-07 13:00 | 2030 100% ECP | -700 | 205 | 300 | 154.71 | 0 | 0 | No
2030-12-07 14:00 | 2030 100% ECP | -463.22 | 505 | 0 | 101.89 | 0 | 0 | No
2030-12-07 15:00 | 2030 100% ECP | -43.22 | 505 | 0 | 105.96 | 0 | 0 | No
2030-12-07 16:00 | 2030 100% ECP | -296.22 | 505 | 0 | 71.89 | 0 | 0 | No
2030-12-07 17:00 | 2030 100% ECP | 123.78 | 505 | 0 | 168.29 | 0 | 0 | No
2030-12-07 18:00 | 2030 100% ECP | 543.78 | 505 | 0 | 425.81 | 0 | 0 | No
2030-12-07 19:00 | 2030 100% ECP | 700 | 389.22 | 0 | 320.62 | 0 | 0 | No
2030-12-07 20:00 | 2030 100% ECP | 673.4 | 505 | 0 | 378.69 | 0 | 0 | No
2030-12-07 21:00 | 2030 100% ECP | 618.27 | 505 | 0 | 510 | 0 | 0 | No
2030-12-07 22:00 | 2030 100% ECP | 198.27 | 435.03 | 0 | 478.74 | 0 | 0 | No
2030-12-07 23:00 | 2030 100% ECP | 618.27 | 135.03 | 0 | 343.84 | 0 | 0 | No
2030-12-08 | 2030 100% ECP | 700 | 8.35 | 0 | 336.99 | 0 | 0 | No
2030-12-08 01:00 | 2030 100% ECP | 700 | 0 | 0 | 230.18 | 0 | 0 | No
2030-12-08 02:00 | 2030 100% ECP | 420 | 0 | 0 | 193.23 | 0 | 0 | No
2030-12-08 03:00 | 2030 100% ECP | 0 | 0 | 0 | 60.24 | 0 | 0 | No
2030-12-08 04:00 | 2030 100% ECP | -420 | -300 | 0 | -239.76 | 0 | 0 | No
2030-12-08 05:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 06:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 07:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 08:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 09:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 10:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 11:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 12:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 13:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 14:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 15:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 16:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 17:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 18:00 | 2030 100% ECP | -700 | -526 | 0 | -510 | 0 | 0 | No
2030-12-08 19:00 | 2030 100% ECP | -700 | -394.28 | 0 | -210 | 0 | 0 | No
2030-12-08 20:00 | 2030 100% ECP | -280 | -94.28 | 0 | 49.11 | 0 | 0 | No
2030-12-08 21:00 | 2030 100% ECP | 0 | 0 | 0 | 349.11 | 0 | 0 | No
2030-12-08 22:00 | 2030 100% ECP | 234.52 | 0 | 0 | 140.25 | 0 | 0 | No
2030-12-08 23:00 | 2030 100% ECP | 470.35 | -300 | 0 | -159.75 | 0 | 0 | No
2030-12-09 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-09 01:00 | 2030 100% ECP | 700 | 0 | 0 | -97.22 | 0 | 0 | No
2030-12-09 02:00 | 2030 100% ECP | 700 | 0 | 0 | -97.22 | 0 | 0 | No
2030-12-09 03:00 | 2030 100% ECP | 700 | 0 | 0 | -180.86 | 0 | 0 | No
2030-12-09 04:00 | 2030 100% ECP | 700 | 0 | 0 | 27.72 | 0 | 0 | No
2030-12-09 05:00 | 2030 100% ECP | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-12-09 06:00 | 2030 100% ECP | 472.02 | 0 | 0 | 0 | 0 | 0 | No
2030-12-09 07:00 | 2030 100% ECP | 52.02 | -282.15 | 0 | 0 | 0 | 0 | No
2030-12-09 08:00 | 2030 100% ECP | -367.98 | -526 | 0 | 74.92 | 0 | 0 | No
2030-12-09 09:00 | 2030 100% ECP | -700 | -526 | 0 | 238.75 | 0 | 0 | No
2030-12-09 10:00 | 2030 100% ECP | -700 | -526 | 0 | -33.62 | 0 | 0 | No
2030-12-09 11:00 | 2030 100% ECP | -700 | -526 | 0 | -19.87 | 0 | 0 | No
2030-12-09 12:00 | 2030 100% ECP | -700 | -526 | 0 | 280.13 | 0 | 0 | No
2030-12-09 13:00 | 2030 100% ECP | -700 | -526 | 0 | 47.28 | 0 | 0 | No
2030-12-09 14:00 | 2030 100% ECP | -388.79 | -526 | -510 | 0 | 0 | 0 | No
2030-12-09 15:00 | 2030 100% ECP | -280 | -226 | -395.51 | -124.88 | 0 | 0 | No
2030-12-09 16:00 | 2030 100% ECP | -700 | -526 | -510 | -424.88 | 0 | 0 | No
2030-12-09 17:00 | 2030 100% ECP | -700 | -526 | -510 | -124.88 | 0 | 0 | No
2030-12-09 18:00 | 2030 100% ECP | -280 | -226 | -210 | 175.12 | 0 | 0 | No
2030-12-09 19:00 | 2030 100% ECP | 140 | 0 | -349.09 | 0.31 | 0 | 0 | No
2030-12-09 20:00 | 2030 100% ECP | 560 | 0 | -163.43 | 15.67 | 0 | 0 | No
2030-12-09 21:00 | 2030 100% ECP | 700 | 0 | -69.43 | 27.87 | 0 | 0 | No
2030-12-09 22:00 | 2030 100% ECP | 280 | 0 | 94.94 | 117.47 | 0 | 0 | No
2030-12-09 23:00 | 2030 100% ECP | 700 | 300 | 394.94 | 417.47 | 0 | 0 | No
2030-12-10 | 2030 100% ECP | 700 | 293.7 | 510 | 510 | 0 | 0 | No
2030-12-10 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 05:00 | 2030 100% ECP | 587.88 | 205 | 210 | 210 | 0 | 0 | No
2030-12-10 06:00 | 2030 100% ECP | 700 | 0 | 510 | 210 | 0 | 0 | No
2030-12-10 07:00 | 2030 100% ECP | 418.77 | 0 | 510 | 510 | 0 | 0 | No
2030-12-10 08:00 | 2030 100% ECP | 0 | 0 | 510 | 497.7 | 0 | 0 | No
2030-12-10 09:00 | 2030 100% ECP | 0 | 0 | 390 | 497.7 | 0 | 0 | No
2030-12-10 10:00 | 2030 100% ECP | 0 | 0 | 90 | 497.7 | 0 | 0 | No
2030-12-10 11:00 | 2030 100% ECP | -305.91 | -226 | -210 | 348.59 | 0 | 0 | No
2030-12-10 12:00 | 2030 100% ECP | -700 | -526 | -510 | 259.65 | 0 | 0 | No
2030-12-10 13:00 | 2030 100% ECP | -700 | -526 | -510 | 42.68 | 0 | 0 | No
2030-12-10 14:00 | 2030 100% ECP | -700 | -526 | -510 | -141.17 | 0 | 0 | No
2030-12-10 15:00 | 2030 100% ECP | -700 | -526 | -510 | 47.42 | 0 | 0 | No
2030-12-10 16:00 | 2030 100% ECP | -700 | -526 | -510 | 215.62 | 0 | 0 | No
2030-12-10 17:00 | 2030 100% ECP | -700 | -526 | -510 | 153.15 | 0 | 0 | No
2030-12-10 18:00 | 2030 100% ECP | -560 | -526 | -510 | 425.53 | 0 | 0 | No
2030-12-10 19:00 | 2030 100% ECP | -140 | -226 | -210 | 510 | 0 | 0 | No
2030-12-10 20:00 | 2030 100% ECP | 280 | 74 | 90 | 465.82 | 0 | 0 | No
2030-12-10 21:00 | 2030 100% ECP | 700 | 374 | 390 | 510 | 0 | 0 | No
2030-12-10 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-10 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 05:00 | 2030 100% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 06:00 | 2030 100% ECP | -21.71 | 505 | 510 | 510 | 0 | 0 | No
2030-12-11 07:00 | 2030 100% ECP | 398.29 | 205 | 210 | 210 | 0 | 0 | No
2030-12-11 08:00 | 2030 100% ECP | 342.21 | 211.95 | 510 | 510 | 0 | 0 | No
2030-12-11 09:00 | 2030 100% ECP | 700 | 430.07 | 510 | 510 | 0 | 0 | No
2030-12-11 10:00 | 2030 100% ECP | 495.83 | 494.51 | 510 | 510 | 0 | 0 | No
2030-12-11 11:00 | 2030 100% ECP | 75.83 | 194.51 | 210 | 483.42 | 0 | 0 | No
2030-12-11 12:00 | 2030 100% ECP | -344.17 | 0 | 0 | 510 | 0 | 0 | No
2030-12-11 13:00 | 2030 100% ECP | -700 | -27.41 | -300 | 499.22 | 0 | 0 | No
2030-12-11 14:00 | 2030 100% ECP | -700 | 0 | -210 | 510 | 0 | 0 | No
2030-12-11 15:00 | 2030 100% ECP | -700 | -300 | -510 | 384.45 | 0 | 0 | No
2030-12-11 16:00 | 2030 100% ECP | -700 | -526 | -510 | 333.31 | 0 | 0 | No
2030-12-11 17:00 | 2030 100% ECP | -700 | -526 | -510 | 33.31 | 0 | 0 | No
2030-12-11 18:00 | 2030 100% ECP | -700 | -526 | -510 | 300 | 0 | 0 | No
2030-12-11 19:00 | 2030 100% ECP | -592.87 | -526 | -510 | 0 | 0 | 0 | No
2030-12-11 20:00 | 2030 100% ECP | -172.87 | -526 | -510 | 0 | 0 | 0 | No
2030-12-11 21:00 | 2030 100% ECP | 247.13 | -226 | -210 | 215.26 | 0 | 0 | No
2030-12-11 22:00 | 2030 100% ECP | 300.84 | -526 | -510 | 72.41 | 0 | 0 | No
2030-12-11 23:00 | 2030 100% ECP | 700 | -484.03 | -510 | -24.78 | 0 | 0 | No
2030-12-12 | 2030 100% ECP | 700 | -184.03 | -210 | 275.22 | 0 | 0 | No
2030-12-12 01:00 | 2030 100% ECP | 700 | 115.97 | 90 | 510 | 0 | 0 | No
2030-12-12 02:00 | 2030 100% ECP | 700 | 367.43 | 390 | 510 | 0 | 0 | No
2030-12-12 03:00 | 2030 100% ECP | 700 | 367.43 | 510 | 510 | 0 | 0 | No
2030-12-12 04:00 | 2030 100% ECP | 700 | 374 | 390 | 510 | 0 | 0 | No
2030-12-12 05:00 | 2030 100% ECP | 280 | 74 | 90 | 370.77 | 0 | 0 | No
2030-12-12 06:00 | 2030 100% ECP | -140 | -226 | -210 | 70.77 | 0 | 0 | No
2030-12-12 07:00 | 2030 100% ECP | -560 | -526 | -510 | -229.23 | 0 | 0 | No
2030-12-12 08:00 | 2030 100% ECP | -140 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 09:00 | 2030 100% ECP | 0 | -526 | -510 | -326.14 | 0 | 0 | No
2030-12-12 10:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 11:00 | 2030 100% ECP | -132.49 | -526 | -510 | -257.04 | 0 | 0 | No
2030-12-12 12:00 | 2030 100% ECP | -508.93 | -526 | -510 | -136.13 | 0 | 0 | No
2030-12-12 13:00 | 2030 100% ECP | -88.93 | -526 | -510 | -168.39 | 0 | 0 | No
2030-12-12 14:00 | 2030 100% ECP | 0 | -526 | -510 | -170.96 | 0 | 0 | No
2030-12-12 15:00 | 2030 100% ECP | 0 | -526 | -510 | -210 | 0 | 0 | No
2030-12-12 16:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 17:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 18:00 | 2030 100% ECP | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 19:00 | 2030 100% ECP | -98.54 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 20:00 | 2030 100% ECP | -518.54 | -526 | -510 | -510 | 0 | 0 | No
2030-12-12 21:00 | 2030 100% ECP | -700 | -526 | -510 | -504.68 | 0 | 0 | No
2030-12-12 22:00 | 2030 100% ECP | -700 | -526 | -510 | -244.32 | 0 | 0 | No
2030-12-12 23:00 | 2030 100% ECP | -700 | -526 | -510 | -52.77 | 0 | 0 | Yes
2030-12-13 | 2030 100% ECP | -700 | -526 | -510 | -111.44 | 0 | 0 | No
2030-12-13 01:00 | 2030 100% ECP | -700 | -526 | -510 | -42.07 | 0 | 0 | No
2030-12-13 02:00 | 2030 100% ECP | -700 | -526 | -510 | -302.09 | 0 | 0 | No
2030-12-13 03:00 | 2030 100% ECP | -700 | -526 | -510 | -271.78 | 0 | 0 | No
2030-12-13 04:00 | 2030 100% ECP | -700 | -526 | -510 | -429.61 | 0 | 0 | No
2030-12-13 05:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-13 06:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-13 07:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-13 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-13 09:00 | 2030 100% ECP | -290.08 | -526 | -510 | -480.03 | 0 | 0 | No
2030-12-13 10:00 | 2030 100% ECP | -700 | -300 | -389.78 | -180.03 | 0 | 0 | No
2030-12-13 11:00 | 2030 100% ECP | -700 | 0 | -89.78 | 119.97 | 0 | 0 | No
2030-12-13 12:00 | 2030 100% ECP | -700 | -100.28 | -292.23 | 210 | 0 | 0 | No
2030-12-13 13:00 | 2030 100% ECP | -700 | 199.72 | 7.77 | 510 | 0 | 0 | No
2030-12-13 14:00 | 2030 100% ECP | -700 | 374 | 307.77 | 510 | 0 | 0 | No
2030-12-13 15:00 | 2030 100% ECP | -700 | 74 | 7.77 | 510 | 0 | 0 | No
2030-12-13 16:00 | 2030 100% ECP | -700 | -226 | -292.23 | 357.32 | 0 | 0 | No
2030-12-13 17:00 | 2030 100% ECP | -700 | -526 | -510 | 57.32 | 0 | 0 | No
2030-12-13 18:00 | 2030 100% ECP | -700 | -526 | -510 | 313.76 | 0 | 0 | No
2030-12-13 19:00 | 2030 100% ECP | -700 | -526 | -510 | 240.45 | 0 | 0 | No
2030-12-13 20:00 | 2030 100% ECP | -700 | -526 | -510 | 34.29 | 0 | 0 | No
2030-12-13 21:00 | 2030 100% ECP | -609.54 | -240.12 | -510 | 170.77 | 0 | 0 | No
2030-12-13 22:00 | 2030 100% ECP | -700 | 59.88 | -210 | 470.77 | 0 | 0 | Yes
2030-12-13 23:00 | 2030 100% ECP | -700 | 359.88 | 90 | 510 | 0 | 0 | Yes
2030-12-14 | 2030 100% ECP | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-12-14 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-14 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-14 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-14 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-14 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-14 09:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-14 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-14 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-14 12:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-12-14 13:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | No
2030-12-14 14:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-12-14 15:00 | 2030 100% ECP | -700 | -526 | -510 | 357.59 | 0 | 0 | No
2030-12-14 16:00 | 2030 100% ECP | -700 | -526 | -510 | 151.61 | 0 | 0 | No
2030-12-14 17:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-12-14 18:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-12-14 19:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-12-14 20:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-12-14 21:00 | 2030 100% ECP | -700 | -526 | -510 | 78.34 | 0 | 0 | No
2030-12-14 22:00 | 2030 100% ECP | -700 | -526 | -510 | 202.69 | 0 | 0 | No
2030-12-14 23:00 | 2030 100% ECP | -700 | -465.74 | -510 | 422.97 | 0 | 0 | No
2030-12-15 | 2030 100% ECP | -280 | -165.74 | -210 | 510 | 0 | 0 | No
2030-12-15 01:00 | 2030 100% ECP | 140 | 134.26 | 90 | 510 | 0 | 0 | No
2030-12-15 02:00 | 2030 100% ECP | 560 | 434.26 | 390 | 510 | 0 | 0 | No
2030-12-15 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-15 06:00 | 2030 100% ECP | 280 | 392.35 | 390 | 510 | 0 | 0 | No
2030-12-15 07:00 | 2030 100% ECP | -140 | 92.35 | 90 | 210 | 0 | 0 | No
2030-12-15 08:00 | 2030 100% ECP | -560 | -207.65 | -210 | 320.31 | 0 | 0 | No
2030-12-15 09:00 | 2030 100% ECP | -700 | -507.65 | -510 | 486.16 | 0 | 0 | No
2030-12-15 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-12-15 11:00 | 2030 100% ECP | -700 | -526 | -510 | 421.55 | 0 | 0 | No
2030-12-15 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-12-15 13:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-12-15 14:00 | 2030 100% ECP | -700 | -526 | -510 | 391.32 | 0 | 0 | No
2030-12-15 15:00 | 2030 100% ECP | -700 | -526 | -510 | 177.72 | 0 | 0 | No
2030-12-15 16:00 | 2030 100% ECP | -700 | -526 | -510 | 396.92 | 0 | 0 | No
2030-12-15 17:00 | 2030 100% ECP | -700 | -526 | -510 | 397.96 | 0 | 0 | No
2030-12-15 18:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-12-15 19:00 | 2030 100% ECP | -700 | -526 | -510 | 404.52 | 0 | 0 | No
2030-12-15 20:00 | 2030 100% ECP | -584.71 | -526 | -510 | 404.52 | 0 | 0 | No
2030-12-15 21:00 | 2030 100% ECP | -280 | -526 | -510 | 436.74 | 0 | 0 | No
2030-12-15 22:00 | 2030 100% ECP | -700 | -226 | -430.72 | 439.99 | 0 | 0 | Yes
2030-12-15 23:00 | 2030 100% ECP | -700 | -169.39 | -390 | 301.52 | 0 | 0 | Yes
2030-12-16 | 2030 100% ECP | -700 | 130.61 | -90 | 510 | 0 | 0 | Yes
2030-12-16 01:00 | 2030 100% ECP | -700 | 430.61 | 210 | 510 | 0 | 0 | Yes
2030-12-16 02:00 | 2030 100% ECP | -700 | 505 | 510 | 440.92 | 0 | 0 | Yes
2030-12-16 03:00 | 2030 100% ECP | -700 | 505 | 510 | 140.92 | 0 | 0 | Yes
2030-12-16 04:00 | 2030 100% ECP | -700 | 505 | 510 | 440.92 | 0 | 0 | Yes
2030-12-16 05:00 | 2030 100% ECP | -700 | 505 | 510 | 236.98 | 0 | 0 | Yes
2030-12-16 06:00 | 2030 100% ECP | -700 | 505 | 510 | 378.28 | 0 | 0 | Yes
2030-12-16 07:00 | 2030 100% ECP | -700 | 505 | 510 | 78.28 | 0 | 0 | Yes
2030-12-16 08:00 | 2030 100% ECP | -700 | 505 | 510 | 323.3 | 0 | 0 | Yes
2030-12-16 09:00 | 2030 100% ECP | -700 | 505 | 510 | 420.33 | 0 | 0 | Yes
2030-12-16 10:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 11:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-16 15:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 16:00 | 2030 100% ECP | -65.97 | 348.22 | 510 | 510 | 0 | 0 | No
2030-12-16 17:00 | 2030 100% ECP | -485.97 | 48.22 | 210 | 510 | 0 | 0 | No
2030-12-16 18:00 | 2030 100% ECP | -170.14 | 0 | 0 | 214.55 | 0 | 0 | No
2030-12-16 19:00 | 2030 100% ECP | 0 | 0 | 149.11 | 510 | 0 | 0 | No
2030-12-16 20:00 | 2030 100% ECP | 0 | 205 | 449.11 | 510 | 0 | 0 | No
2030-12-16 21:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 22:00 | 2030 100% ECP | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-12-16 23:00 | 2030 100% ECP | -5.04 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 | 2030 100% ECP | 414.96 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 04:00 | 2030 100% ECP | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 05:00 | 2030 100% ECP | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 06:00 | 2030 100% ECP | -560 | 280.3 | 210 | 510 | 0 | 0 | No
2030-12-17 07:00 | 2030 100% ECP | -280 | -19.7 | -90 | 210 | 0 | 0 | No
2030-12-17 08:00 | 2030 100% ECP | -700 | -174.99 | -390 | 366.4 | 0 | 0 | No
2030-12-17 09:00 | 2030 100% ECP | -280 | -474.99 | -510 | 494.19 | 0 | 0 | No
2030-12-17 10:00 | 2030 100% ECP | -280 | -526 | -510 | 455.89 | 0 | 0 | No
2030-12-17 11:00 | 2030 100% ECP | -700 | -526 | -510 | 485.87 | 0 | 0 | No
2030-12-17 12:00 | 2030 100% ECP | -700 | -526 | -510 | 410.56 | 0 | 0 | No
2030-12-17 13:00 | 2030 100% ECP | -700 | -526 | -510 | 206.84 | 0 | 0 | No
2030-12-17 14:00 | 2030 100% ECP | -700 | -526 | -510 | 394.9 | 0 | 0 | No
2030-12-17 15:00 | 2030 100% ECP | -700 | -526 | -510 | 436.69 | 0 | 0 | No
2030-12-17 16:00 | 2030 100% ECP | -700 | -526 | -510 | 273.96 | 0 | 0 | No
2030-12-17 17:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-12-17 18:00 | 2030 100% ECP | -405.34 | -526 | -510 | -182.97 | 0 | 0 | No
2030-12-17 19:00 | 2030 100% ECP | -203.5 | -300 | -300 | 0.41 | 0 | 0 | No
2030-12-17 20:00 | 2030 100% ECP | -431.89 | 0 | 0 | 210 | 0 | 0 | No
2030-12-17 21:00 | 2030 100% ECP | -11.89 | 300 | 300 | 510 | 0 | 0 | No
2030-12-17 22:00 | 2030 100% ECP | 286.45 | 505 | 510 | 510 | 0 | 0 | No
2030-12-17 23:00 | 2030 100% ECP | -63.79 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 | 2030 100% ECP | -397.81 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 06:00 | 2030 100% ECP | -700 | 217.08 | 210 | 504.46 | 0 | 0 | No
2030-12-18 07:00 | 2030 100% ECP | -700 | -82.92 | -90 | 204.46 | 0 | 0 | No
2030-12-18 08:00 | 2030 100% ECP | -700 | -382.92 | -390 | -95.54 | 0 | 0 | No
2030-12-18 09:00 | 2030 100% ECP | -700 | -395 | -390 | -270.39 | 0 | 0 | No
2030-12-18 10:00 | 2030 100% ECP | -700 | -95 | -90 | 29.61 | 0 | 0 | No
2030-12-18 11:00 | 2030 100% ECP | -700 | 205 | 210 | 329.61 | 0 | 0 | No
2030-12-18 12:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 13:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-18 15:00 | 2030 100% ECP | -700 | 300 | 291.7 | 510 | 0 | 0 | No
2030-12-18 16:00 | 2030 100% ECP | -700 | 0 | -8.3 | 510 | 0 | 0 | No
2030-12-18 17:00 | 2030 100% ECP | -700 | -300 | -308.3 | 363.96 | 0 | 0 | No
2030-12-18 18:00 | 2030 100% ECP | -700 | -526 | -510 | 363.96 | 0 | 0 | No
2030-12-18 19:00 | 2030 100% ECP | -700 | -526 | -510 | 276.42 | 0 | 0 | No
2030-12-18 20:00 | 2030 100% ECP | -280 | -300 | -339.76 | 338.83 | 0 | 0 | No
2030-12-18 21:00 | 2030 100% ECP | -280 | 0 | -39.76 | 510 | 0 | 0 | No
2030-12-18 22:00 | 2030 100% ECP | -700 | 300 | 260.24 | 510 | 0 | 0 | No
2030-12-18 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-19 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-19 05:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-12-19 06:00 | 2030 100% ECP | -700 | 74 | 90 | 452.5 | 0 | 0 | No
2030-12-19 07:00 | 2030 100% ECP | -700 | -226 | -210 | 152.5 | 0 | 0 | No
2030-12-19 08:00 | 2030 100% ECP | -700 | -526 | -510 | -147.5 | 0 | 0 | No
2030-12-19 09:00 | 2030 100% ECP | -700 | -526 | -510 | -38.41 | 0 | 0 | No
2030-12-19 10:00 | 2030 100% ECP | -700 | -226 | -210 | 261.59 | 0 | 0 | No
2030-12-19 11:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | No
2030-12-19 12:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-12-19 13:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-12-19 14:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | No
2030-12-19 15:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-12-19 16:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-12-19 17:00 | 2030 100% ECP | -700 | -526 | -510 | 121.4 | 0 | 0 | No
2030-12-19 18:00 | 2030 100% ECP | -700 | -526 | -510 | 318.58 | 0 | 0 | No
2030-12-19 19:00 | 2030 100% ECP | -700 | -526 | -510 | 37.76 | 0 | 0 | No
2030-12-19 20:00 | 2030 100% ECP | -700 | -226 | -318.77 | 337.76 | 0 | 0 | No
2030-12-19 21:00 | 2030 100% ECP | -700 | 74 | -18.77 | 510 | 0 | 0 | No
2030-12-19 22:00 | 2030 100% ECP | -700 | 374 | 281.23 | 510 | 0 | 0 | No
2030-12-19 23:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 01:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 02:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 03:00 | 2030 100% ECP | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 04:00 | 2030 100% ECP | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 05:00 | 2030 100% ECP | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 08:00 | 2030 100% ECP | -700 | 205 | 210 | 477.96 | 0 | 0 | No
2030-12-20 09:00 | 2030 100% ECP | -700 | -95 | -90 | 510 | 0 | 0 | No
2030-12-20 10:00 | 2030 100% ECP | -700 | -311.46 | -390 | 510 | 0 | 0 | No
2030-12-20 11:00 | 2030 100% ECP | -700 | -452.64 | -510 | 489.78 | 0 | 0 | No
2030-12-20 12:00 | 2030 100% ECP | -700 | -526 | -510 | 304.39 | 0 | 0 | No
2030-12-20 13:00 | 2030 100% ECP | -700 | -526 | -510 | 395.72 | 0 | 0 | No
2030-12-20 14:00 | 2030 100% ECP | -700 | -526 | -510 | 428.11 | 0 | 0 | No
2030-12-20 15:00 | 2030 100% ECP | -700 | -526 | -510 | 128.11 | 0 | 0 | No
2030-12-20 16:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-12-20 17:00 | 2030 100% ECP | -700 | -526 | -510 | -31.03 | 0 | 0 | No
2030-12-20 18:00 | 2030 100% ECP | -656.32 | -526 | -510 | 0 | 0 | 0 | No
2030-12-20 19:00 | 2030 100% ECP | -236.32 | -395 | -390 | -27.88 | 0 | 0 | No
2030-12-20 20:00 | 2030 100% ECP | 183.68 | -95 | -90 | -90 | 0 | 0 | No
2030-12-20 21:00 | 2030 100% ECP | 603.68 | 205 | 210 | 210 | 0 | 0 | No
2030-12-20 22:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-20 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 06:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-21 07:00 | 2030 100% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-12-21 08:00 | 2030 100% ECP | 684.71 | -95 | -90 | 339.42 | 0 | 0 | No
2030-12-21 09:00 | 2030 100% ECP | 700 | 0 | 6.56 | 509.16 | 0 | 0 | No
2030-12-21 10:00 | 2030 100% ECP | 700 | 0 | 6.56 | 433.07 | 0 | 0 | No
2030-12-21 11:00 | 2030 100% ECP | 700 | 0 | -159.8 | 442.75 | 0 | 0 | No
2030-12-21 12:00 | 2030 100% ECP | 654.49 | -300 | -459.8 | 442.75 | 0 | 0 | No
2030-12-21 13:00 | 2030 100% ECP | 700 | -36.56 | -510 | 510 | 0 | 0 | No
2030-12-21 14:00 | 2030 100% ECP | 700 | 0 | -351.02 | 375.34 | 0 | 0 | No
2030-12-21 15:00 | 2030 100% ECP | 700 | 0 | -259.15 | 337.13 | 0 | 0 | No
2030-12-21 16:00 | 2030 100% ECP | 700 | -153.18 | -300 | 145.07 | 0 | 0 | No
2030-12-21 17:00 | 2030 100% ECP | 700 | 0 | 0 | 310.55 | 0 | 0 | No
2030-12-21 18:00 | 2030 100% ECP | 700 | 0 | 0 | 467.55 | 0 | 0 | No
2030-12-21 19:00 | 2030 100% ECP | 700 | 0 | 0 | 428.98 | 0 | 0 | No
2030-12-21 20:00 | 2030 100% ECP | 700 | 0 | 0 | 468.92 | 0 | 0 | No
2030-12-21 21:00 | 2030 100% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-12-21 22:00 | 2030 100% ECP | 700 | 205 | 210 | 385.4 | 0 | 0 | No
2030-12-21 23:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 01:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 02:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 03:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 04:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 05:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 06:00 | 2030 100% ECP | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-22 07:00 | 2030 100% ECP | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-12-22 08:00 | 2030 100% ECP | 700 | 0 | -5.82 | -0.92 | 0 | 0 | No
2030-12-22 09:00 | 2030 100% ECP | 700 | 0 | 294.18 | 0 | 0 | 0 | No
2030-12-22 10:00 | 2030 100% ECP | 700 | 0 | 23.6 | 0 | 0 | 0 | No
2030-12-22 11:00 | 2030 100% ECP | 700 | 0 | 42.64 | 0 | 0 | 0 | No
2030-12-22 12:00 | 2030 100% ECP | 700 | 0 | -257.36 | -3.29 | 0 | 0 | No
2030-12-22 13:00 | 2030 100% ECP | 700 | 0 | -441.83 | 56.14 | 0 | 0 | No
2030-12-22 14:00 | 2030 100% ECP | 700 | 0 | -348.12 | 96.86 | 0 | 0 | No
2030-12-22 15:00 | 2030 100% ECP | 700 | -226 | -210 | 274.71 | 0 | 0 | No
2030-12-22 16:00 | 2030 100% ECP | 700 | -526 | -510 | -25.29 | 0 | 0 | No
2030-12-22 17:00 | 2030 100% ECP | 700 | -526 | -510 | -201.15 | 0 | 0 | No
2030-12-22 18:00 | 2030 100% ECP | 700 | -526 | -510 | -397.93 | 0 | 0 | No
2030-12-22 19:00 | 2030 100% ECP | 700 | -526 | -510 | -149.49 | 0 | 0 | No
2030-12-22 20:00 | 2030 100% ECP | 700 | -526 | -510 | -261.61 | 0 | 0 | No
2030-12-22 21:00 | 2030 100% ECP | 554.8 | -526 | -510 | 36.39 | 0 | 0 | No
2030-12-22 22:00 | 2030 100% ECP | 700 | -526 | -510 | 336.39 | 0 | 0 | No
2030-12-22 23:00 | 2030 100% ECP | 700 | -526 | -510 | 232.79 | 0 | 0 | No
2030-12-23 | 2030 100% ECP | 700 | -526 | -510 | 175.07 | 0 | 0 | No
2030-12-23 01:00 | 2030 100% ECP | 673.61 | -526 | -510 | -29.66 | 0 | 0 | No
2030-12-23 02:00 | 2030 100% ECP | 253.61 | -526 | -510 | 46.03 | 0 | 0 | No
2030-12-23 03:00 | 2030 100% ECP | -166.39 | -526 | -510 | 98.6 | 0 | 0 | No
2030-12-23 04:00 | 2030 100% ECP | -550.16 | -526 | -510 | 7.07 | 0 | 0 | No
2030-12-23 05:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-12-23 06:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-12-23 07:00 | 2030 100% ECP | -700 | -526 | -510 | 388.86 | 0 | 0 | Yes
2030-12-23 08:00 | 2030 100% ECP | -700 | -526 | -510 | 88.86 | 0 | 0 | Yes
2030-12-23 09:00 | 2030 100% ECP | -700 | -526 | -510 | -105.97 | 0 | 0 | Yes
2030-12-23 10:00 | 2030 100% ECP | -700 | -526 | -510 | -262.22 | 0 | 0 | Yes
2030-12-23 11:00 | 2030 100% ECP | -700 | -526 | -510 | -126.45 | 0 | 0 | Yes
2030-12-23 12:00 | 2030 100% ECP | -700 | -526 | -510 | -43.5 | 0 | 0 | Yes
2030-12-23 13:00 | 2030 100% ECP | -700 | -226 | -210 | 256.5 | 0 | 0 | Yes
2030-12-23 14:00 | 2030 100% ECP | -700 | -526 | -510 | 503.78 | 0 | 0 | Yes
2030-12-23 15:00 | 2030 100% ECP | -700 | -526 | -510 | 203.78 | 0 | 0 | Yes
2030-12-23 16:00 | 2030 100% ECP | -700 | -526 | -510 | 52.05 | 0 | 0 | Yes
2030-12-23 17:00 | 2030 100% ECP | -700 | -526 | -510 | -117.82 | 0 | 0 | Yes
2030-12-23 18:00 | 2030 100% ECP | -700 | -526 | -510 | 182.18 | 0 | 0 | Yes
2030-12-23 19:00 | 2030 100% ECP | -700 | -526 | -510 | 188.53 | 0 | 0 | Yes
2030-12-23 20:00 | 2030 100% ECP | -700 | -526 | -510 | 378.87 | 0 | 0 | No
2030-12-23 21:00 | 2030 100% ECP | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-12-23 22:00 | 2030 100% ECP | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-12-23 23:00 | 2030 100% ECP | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-12-24 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-12-24 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 03:00 | 2030 100% ECP | -656.3 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 08:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-24 09:00 | 2030 100% ECP | -280 | 205 | 210 | 210 | 0 | 0 | No
2030-12-24 10:00 | 2030 100% ECP | 6.81 | 74 | 90 | 510 | 0 | 0 | No
2030-12-24 11:00 | 2030 100% ECP | -413.19 | -226 | -210 | 510 | 0 | 0 | No
2030-12-24 12:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-12-24 13:00 | 2030 100% ECP | -700 | -260.02 | -510 | 298.62 | 0 | 0 | No
2030-12-24 14:00 | 2030 100% ECP | -700 | -225.83 | -300 | 488.06 | 0 | 0 | No
2030-12-24 15:00 | 2030 100% ECP | -280 | 0 | 0 | 510 | 0 | 0 | No
2030-12-24 16:00 | 2030 100% ECP | 140 | 0 | -268.68 | 255.83 | 0 | 0 | No
2030-12-24 17:00 | 2030 100% ECP | 560 | 0 | 0 | 181.22 | 0 | 0 | No
2030-12-24 18:00 | 2030 100% ECP | 700 | 0 | 0 | 481.22 | 0 | 0 | No
2030-12-24 19:00 | 2030 100% ECP | 700 | 0 | 0 | 384.25 | 0 | 0 | No
2030-12-24 20:00 | 2030 100% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-12-24 21:00 | 2030 100% ECP | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-12-24 22:00 | 2030 100% ECP | 700 | 33.1 | 210 | 392.08 | 0 | 0 | No
2030-12-24 23:00 | 2030 100% ECP | 700 | 333.1 | 510 | 510 | 0 | 0 | No
2030-12-25 | 2030 100% ECP | 700 | 33.1 | 510 | 510 | 0 | 0 | No
2030-12-25 01:00 | 2030 100% ECP | 700 | 46.48 | 510 | 480 | 0 | 0 | No
2030-12-25 02:00 | 2030 100% ECP | 700 | 346.48 | 510 | 510 | 0 | 0 | No
2030-12-25 03:00 | 2030 100% ECP | 280 | 436.46 | 510 | 510 | 0 | 0 | No
2030-12-25 04:00 | 2030 100% ECP | 0 | 198.69 | 510 | 510 | 0 | 0 | No
2030-12-25 05:00 | 2030 100% ECP | 0 | 300 | 300 | 387.08 | 0 | 0 | No
2030-12-25 06:00 | 2030 100% ECP | 420 | 0 | 0 | 87.08 | 0 | 0 | No
2030-12-25 07:00 | 2030 100% ECP | 700 | 0 | -300 | 3.93 | 0 | 0 | No
2030-12-25 08:00 | 2030 100% ECP | 700 | 0 | -408.38 | 44.38 | 0 | 0 | No
2030-12-25 09:00 | 2030 100% ECP | 700 | 0 | -510 | 115.21 | 0 | 0 | No
2030-12-25 10:00 | 2030 100% ECP | 700 | -20.68 | -510 | 24.55 | 0 | 0 | No
2030-12-25 11:00 | 2030 100% ECP | 280 | -320.68 | -510 | 255.25 | 0 | 0 | No
2030-12-25 12:00 | 2030 100% ECP | 0 | -526 | -510 | 148.12 | 0 | 0 | No
2030-12-25 13:00 | 2030 100% ECP | -68.07 | -526 | -510 | 203.79 | 0 | 0 | No
2030-12-25 14:00 | 2030 100% ECP | -21.85 | -526 | -510 | 333.44 | 0 | 0 | No
2030-12-25 15:00 | 2030 100% ECP | 398.15 | -231.11 | -510 | 83.93 | 0 | 0 | No
2030-12-25 16:00 | 2030 100% ECP | 182.62 | -383.88 | -510 | 270.34 | 0 | 0 | No
2030-12-25 17:00 | 2030 100% ECP | -237.38 | -526 | -510 | 335.48 | 0 | 0 | No
2030-12-25 18:00 | 2030 100% ECP | -657.38 | -526 | -510 | 142.25 | 0 | 0 | No
2030-12-25 19:00 | 2030 100% ECP | -700 | -526 | -510 | 162.71 | 0 | 0 | No
2030-12-25 20:00 | 2030 100% ECP | -280 | -526 | -510 | -137.29 | 0 | 0 | No
2030-12-25 21:00 | 2030 100% ECP | -700 | -226 | -395.02 | -336.21 | 0 | 0 | No
2030-12-25 22:00 | 2030 100% ECP | -700 | 74 | -95.02 | -36.21 | 0 | 0 | No
2030-12-25 23:00 | 2030 100% ECP | -700 | 374 | 204.98 | 191.78 | 0 | 0 | Yes
2030-12-26 | 2030 100% ECP | -700 | 505 | 504.98 | 288.58 | 0 | 0 | Yes
2030-12-26 01:00 | 2030 100% ECP | -700 | 505 | 510 | 323.79 | 0 | 0 | Yes
2030-12-26 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 05:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 06:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 07:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 08:00 | 2030 100% ECP | -700 | 505 | 510 | 367.13 | 0 | 0 | Yes
2030-12-26 09:00 | 2030 100% ECP | -700 | 505 | 510 | 333.6 | 0 | 0 | Yes
2030-12-26 10:00 | 2030 100% ECP | -700 | 505 | 510 | 492.68 | 0 | 0 | Yes
2030-12-26 11:00 | 2030 100% ECP | -700 | 505 | 510 | 479.82 | 0 | 0 | Yes
2030-12-26 12:00 | 2030 100% ECP | -700 | 505 | 510 | 472.3 | 0 | 0 | Yes
2030-12-26 13:00 | 2030 100% ECP | -700 | 505 | 510 | 489.97 | 0 | 0 | Yes
2030-12-26 14:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-26 15:00 | 2030 100% ECP | -700 | 505 | 510 | 412.23 | 0 | 0 | Yes
2030-12-26 16:00 | 2030 100% ECP | -700 | 505 | 510 | 293.28 | 0 | 0 | Yes
2030-12-26 17:00 | 2030 100% ECP | -700 | 505 | 510 | 254.96 | 0 | 0 | Yes
2030-12-26 18:00 | 2030 100% ECP | -700 | 505 | 510 | 217.04 | 0 | 0 | Yes
2030-12-26 19:00 | 2030 100% ECP | -700 | 505 | 510 | 224.85 | 0 | 0 | Yes
2030-12-26 20:00 | 2030 100% ECP | -700 | 505 | 510 | 292.88 | 0 | 0 | Yes
2030-12-26 21:00 | 2030 100% ECP | -700 | 505 | 510 | 460.83 | 0 | 0 | Yes
2030-12-26 22:00 | 2030 100% ECP | -700 | 505 | 510 | 283.21 | 0 | 0 | Yes
2030-12-26 23:00 | 2030 100% ECP | -700 | 505 | 510 | 317.66 | 0 | 0 | Yes
2030-12-27 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-27 01:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-27 02:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-27 03:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-27 04:00 | 2030 100% ECP | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-12-27 05:00 | 2030 100% ECP | -700 | 469.44 | 390 | 510 | 0 | 0 | Yes
2030-12-27 06:00 | 2030 100% ECP | -700 | 169.44 | 90 | 510 | 0 | 0 | Yes
2030-12-27 07:00 | 2030 100% ECP | -700 | -130.56 | -210 | 454.35 | 0 | 0 | Yes
2030-12-27 08:00 | 2030 100% ECP | -700 | -430.56 | -510 | 154.35 | 0 | 0 | No
2030-12-27 09:00 | 2030 100% ECP | -700 | -526 | -510 | 234.82 | 0 | 0 | No
2030-12-27 10:00 | 2030 100% ECP | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-12-27 11:00 | 2030 100% ECP | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-12-27 12:00 | 2030 100% ECP | -700 | -526 | -510 | 83.86 | 0 | 0 | No
2030-12-27 13:00 | 2030 100% ECP | -700 | -526 | -510 | 167.47 | 0 | 0 | No
2030-12-27 14:00 | 2030 100% ECP | -700 | -526 | -510 | 120.33 | 0 | 0 | No
2030-12-27 15:00 | 2030 100% ECP | -700 | -526 | -510 | -179.67 | 0 | 0 | No
2030-12-27 16:00 | 2030 100% ECP | -700 | -526 | -510 | 120.33 | 0 | 0 | No
2030-12-27 17:00 | 2030 100% ECP | -700 | -526 | -510 | -179.67 | 0 | 0 | No
2030-12-27 18:00 | 2030 100% ECP | -700 | -526 | -510 | -380.08 | 0 | 0 | No
2030-12-27 19:00 | 2030 100% ECP | -700 | -526 | -510 | -80.08 | 0 | 0 | No
2030-12-27 20:00 | 2030 100% ECP | -700 | -526 | -510 | 120.19 | 0 | 0 | No
2030-12-27 21:00 | 2030 100% ECP | -700 | -526 | -510 | 341.84 | 0 | 0 | No
2030-12-27 22:00 | 2030 100% ECP | -700 | -526 | -510 | 340.5 | 0 | 0 | Yes
2030-12-27 23:00 | 2030 100% ECP | -700 | -526 | -510 | 268.77 | 0 | 0 | Yes
2030-12-28 | 2030 100% ECP | -700 | -526 | -510 | 159.04 | 0 | 0 | Yes
2030-12-28 01:00 | 2030 100% ECP | -700 | -526 | -510 | -140.96 | 0 | 0 | Yes
2030-12-28 02:00 | 2030 100% ECP | -700 | -526 | -510 | -440.96 | 0 | 0 | Yes
2030-12-28 03:00 | 2030 100% ECP | -700 | -526 | -510 | -399.26 | 0 | 0 | Yes
2030-12-28 04:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-28 05:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-28 06:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-28 07:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-12-28 08:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-12-28 09:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-12-28 10:00 | 2030 100% ECP | -700 | -526 | -510 | 250.51 | 0 | 0 | Yes
2030-12-28 11:00 | 2030 100% ECP | -700 | -526 | -510 | 297.78 | 0 | 0 | Yes
2030-12-28 12:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-12-28 13:00 | 2030 100% ECP | -700 | -526 | -510 | -235.52 | 0 | 0 | Yes
2030-12-28 14:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-28 15:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-28 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-28 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-28 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-28 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-28 20:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-12-28 21:00 | 2030 100% ECP | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-12-28 22:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-12-28 23:00 | 2030 100% ECP | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-12-29 | 2030 100% ECP | -700 | -526 | -510 | -122.49 | 0 | 0 | Yes
2030-12-29 01:00 | 2030 100% ECP | -700 | -526 | -510 | 177.51 | 0 | 0 | No
2030-12-29 02:00 | 2030 100% ECP | -700 | -526 | -510 | 204.68 | 0 | 0 | Yes
2030-12-29 03:00 | 2030 100% ECP | -700 | -526 | -510 | 238.25 | 0 | 0 | Yes
2030-12-29 04:00 | 2030 100% ECP | -700 | -526 | -510 | -45.18 | 0 | 0 | Yes
2030-12-29 05:00 | 2030 100% ECP | -700 | -526 | -510 | -263.23 | 0 | 0 | Yes
2030-12-29 06:00 | 2030 100% ECP | -700 | -526 | -510 | -139.33 | 0 | 0 | No
2030-12-29 07:00 | 2030 100% ECP | -700 | -526 | -510 | -15.06 | 0 | 0 | No
2030-12-29 08:00 | 2030 100% ECP | -700 | -526 | -510 | -158.63 | 0 | 0 | Yes
2030-12-29 09:00 | 2030 100% ECP | -700 | -526 | -510 | 111.32 | 0 | 0 | Yes
2030-12-29 10:00 | 2030 100% ECP | -700 | -526 | -510 | -86.02 | 0 | 0 | Yes
2030-12-29 11:00 | 2030 100% ECP | -700 | -526 | -510 | 213.98 | 0 | 0 | Yes
2030-12-29 12:00 | 2030 100% ECP | -700 | -526 | -510 | 345.25 | 0 | 0 | No
2030-12-29 13:00 | 2030 100% ECP | -700 | -526 | -510 | 45.25 | 0 | 0 | No
2030-12-29 14:00 | 2030 100% ECP | -700 | -526 | -510 | -7.34 | 0 | 0 | No
2030-12-29 15:00 | 2030 100% ECP | -700 | -526 | -510 | -307.34 | 0 | 0 | No
2030-12-29 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-29 17:00 | 2030 100% ECP | -700 | -526 | -510 | -300 | 0 | 0 | No
2030-12-29 18:00 | 2030 100% ECP | -700 | -226 | -309.48 | 0 | 0 | 0 | No
2030-12-29 19:00 | 2030 100% ECP | -280 | 0 | -510 | 300 | 0 | 0 | No
2030-12-29 20:00 | 2030 100% ECP | 36.58 | 0 | -510 | 292.22 | 0 | 0 | No
2030-12-29 21:00 | 2030 100% ECP | 164.44 | 0 | -210 | 145.21 | 0 | 0 | No
2030-12-29 22:00 | 2030 100% ECP | 584.44 | 0 | -210 | 400.85 | 0 | 0 | No
2030-12-29 23:00 | 2030 100% ECP | 164.44 | 0 | 0 | 379.85 | 0 | 0 | No
2030-12-30 | 2030 100% ECP | 584.44 | 0 | 300 | 79.85 | 0 | 0 | No
2030-12-30 01:00 | 2030 100% ECP | 700 | 0 | 115.2 | 0 | 0 | 0 | No
2030-12-30 02:00 | 2030 100% ECP | 700 | 0 | 375.28 | 0 | 0 | 0 | No
2030-12-30 03:00 | 2030 100% ECP | 700 | 0 | 280.77 | 0 | 0 | 0 | No
2030-12-30 04:00 | 2030 100% ECP | 700 | 0 | 210 | 0 | 0 | 0 | No
2030-12-30 05:00 | 2030 100% ECP | 700 | 0 | 210 | 0 | 0 | 0 | No
2030-12-30 06:00 | 2030 100% ECP | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-12-30 07:00 | 2030 100% ECP | 700 | 0 | 210 | 0 | 0 | 0 | No
2030-12-30 08:00 | 2030 100% ECP | 700 | 0 | 510 | 50.31 | 0 | 0 | No
2030-12-30 09:00 | 2030 100% ECP | 700 | 0 | 510 | 332.23 | 0 | 0 | No
2030-12-30 10:00 | 2030 100% ECP | 700 | 39.73 | 510 | 510 | 0 | 0 | No
2030-12-30 11:00 | 2030 100% ECP | 700 | 0 | 210 | 210 | 0 | 0 | No
2030-12-30 12:00 | 2030 100% ECP | 700 | 0 | 243.54 | 190.46 | 0 | 0 | No
2030-12-30 13:00 | 2030 100% ECP | 700 | 0 | 0 | 198.14 | 0 | 0 | No
2030-12-30 14:00 | 2030 100% ECP | 700 | 0 | 0 | 149.01 | 0 | 0 | No
2030-12-30 15:00 | 2030 100% ECP | 700 | -120.92 | -210 | 51.3 | 0 | 0 | No
2030-12-30 16:00 | 2030 100% ECP | 280 | -420.92 | -510 | -248.7 | 0 | 0 | No
2030-12-30 17:00 | 2030 100% ECP | -140 | -526 | -510 | -384.51 | 0 | 0 | No
2030-12-30 18:00 | 2030 100% ECP | -560 | -526 | -510 | -384.51 | 0 | 0 | No
2030-12-30 19:00 | 2030 100% ECP | -250.41 | -526 | -510 | -299.73 | 0 | 0 | No
2030-12-30 20:00 | 2030 100% ECP | 169.59 | -226 | -248.34 | 0.27 | 0 | 0 | No
2030-12-30 21:00 | 2030 100% ECP | 589.59 | 74 | 51.66 | 300.27 | 0 | 0 | No
2030-12-30 22:00 | 2030 100% ECP | 700 | 0 | 351.66 | 69.13 | 0 | 0 | No
2030-12-30 23:00 | 2030 100% ECP | 700 | 0 | 296.57 | 16.1 | 0 | 0 | No
2030-12-31 | 2030 100% ECP | 700 | 0 | -3.43 | 0 | 0 | 0 | No
2030-12-31 01:00 | 2030 100% ECP | 700 | 0 | -303.43 | -168.69 | 0 | 0 | No
2030-12-31 02:00 | 2030 100% ECP | 700 | 0 | -510 | -120.47 | 0 | 0 | No
2030-12-31 03:00 | 2030 100% ECP | 560 | 0 | -510 | -141.58 | 0 | 0 | No
2030-12-31 04:00 | 2030 100% ECP | 140 | 0 | -510 | -380.01 | 0 | 0 | No
2030-12-31 05:00 | 2030 100% ECP | -280 | 0 | -510 | -300 | 0 | 0 | No
2030-12-31 06:00 | 2030 100% ECP | -700 | 0 | -447.48 | 0 | 0 | 0 | No
2030-12-31 07:00 | 2030 100% ECP | -700 | -226 | -510 | -210 | 0 | 0 | No
2030-12-31 08:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 09:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 10:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 11:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 12:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 13:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 14:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 15:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 16:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 17:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 18:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 19:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 20:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 21:00 | 2030 100% ECP | -700 | -526 | -510 | -492.75 | 0 | 0 | No
2030-12-31 22:00 | 2030 100% ECP | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-12-31 23:00 | 2030 100% ECP | -585.01 | -300 | -510 | -510 | 0 | 0 | No
2030-01-01 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -158.4 | -175.32 | 0 | 0 | No
2030-01-01 01:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 74 | 141.6 | 124.68 | 0 | 0 | No
2030-01-01 02:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 374 | 441.6 | 424.68 | 0 | 0 | No
2030-01-01 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 74 | 312.07 | 124.68 | 0 | 0 | No
2030-01-01 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 361.81 | 0 | 0 | 0 | No
2030-01-01 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 216.81 | 0 | 0 | 0 | No
2030-01-01 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 99.11 | 0 | 0 | 0 | No
2030-01-01 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-01 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 88.35 | 221 | 0 | 0 | No
2030-01-01 09:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | 388.35 | 244 | 0 | 0 | No
2030-01-01 10:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | 300 | 161.38 | 300 | 0 | 0 | No
2030-01-01 11:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | 0 | -138.62 | 0 | 0 | 0 | No
2030-01-01 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -121.6 | 0 | 0 | 0 | No
2030-01-01 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 145.1 | 178.4 | 300 | 0 | 0 | No
2030-01-01 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 189.03 | 90 | 510 | 0 | 0 | No
2030-01-01 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -110.97 | -210 | 210 | 0 | 0 | No
2030-01-01 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -410.97 | -510 | -20.03 | 0 | 0 | No
2030-01-01 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -89.35 | 0 | 0 | No
2030-01-01 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -343.34 | 0 | 0 | No
2030-01-01 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -254.35 | 0 | 0 | No
2030-01-01 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 43.71 | 0 | 0 | No
2030-01-01 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -10.79 | 0 | 0 | No
2030-01-01 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -25.94 | 0 | 0 | No
2030-01-01 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 274.06 | 0 | 0 | Yes
2030-01-02 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-01-02 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-02 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-02 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-02 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-01-02 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 330.67 | 0 | 0 | Yes
2030-01-02 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 30.67 | 0 | 0 | No
2030-01-02 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-01-02 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 300 | 0 | 0 | No
2030-01-02 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -406.09 | -510 | 13.2 | 0 | 0 | No
2030-01-02 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -106.09 | -210 | 247.59 | 0 | 0 | No
2030-01-02 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 193.91 | 90 | 510 | 0 | 0 | Yes
2030-01-02 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 493.91 | 390 | 510 | 0 | 0 | Yes
2030-01-02 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 318.25 | 0 | 0 | Yes
2030-01-03 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 04:00 | 2030 33% ECP + 1.3 GW Offshore | -611.08 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-03 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 210 | 413.53 | 0 | 0 | No
2030-01-03 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 277.57 | 0 | 0 | No
2030-01-03 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-01-03 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-01-03 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-01-03 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -190.23 | 510 | 0 | 0 | No
2030-01-03 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -153.89 | 508.97 | 0 | 0 | No
2030-01-03 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -33.26 | 494.36 | 0 | 0 | No
2030-01-03 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 266.74 | 421.46 | 0 | 0 | No
2030-01-03 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 204.04 | 178.76 | 0 | 0 | No
2030-01-03 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 504.04 | 478.76 | 0 | 0 | No
2030-01-03 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 504.04 | 510 | 0 | 0 | No
2030-01-03 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-03 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 433.04 | 365.93 | 0 | 0 | No
2030-01-03 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 433.04 | 217.54 | 0 | 0 | No
2030-01-03 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 510 | 496.95 | 0 | 0 | No
2030-01-03 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-04 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-04 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-04 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-04 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-04 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-04 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | 0 | -1.91 | 0 | 0 | No
2030-01-04 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 44.67 | 300 | 298.09 | 0 | 0 | No
2030-01-04 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 172.64 | 510 | 510 | 0 | 0 | No
2030-01-04 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 61.38 | 510 | 510 | 0 | 0 | No
2030-01-04 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 331 | 210 | 0 | 0 | No
2030-01-04 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 510 | 401.14 | 0 | 0 | No
2030-01-04 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 292.47 | 330.43 | 0 | 0 | No
2030-01-04 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -7.53 | 207.02 | 0 | 0 | No
2030-01-04 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -300 | -307.53 | -92.98 | 0 | 0 | No
2030-01-04 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -305.53 | 0 | 0 | No
2030-01-04 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-04 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -504.42 | 0 | 0 | No
2030-01-04 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -204.42 | 0 | 0 | No
2030-01-04 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -243.44 | 53.27 | 0 | 0 | No
2030-01-04 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -356.85 | 0 | 0 | 0 | No
2030-01-04 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -493.28 | 0 | 0 | 0 | No
2030-01-05 | 2030 33% ECP + 1.3 GW Offshore | -700 | -108.34 | -390 | -83.17 | 0 | 0 | No
2030-01-05 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -89.98 | -90 | 53.75 | 0 | 0 | No
2030-01-05 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 210.02 | 210 | 353.75 | 0 | 0 | No
2030-01-05 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-05 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-05 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-05 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 210 | 300 | 0 | 0 | No
2030-01-05 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -90 | 0 | 0 | 0 | No
2030-01-05 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -395 | -390 | 183.43 | 0 | 0 | No
2030-01-05 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -116.57 | 0 | 0 | No
2030-01-05 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 183.43 | 0 | 0 | No
2030-01-05 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 202.11 | 0 | 0 | No
2030-01-05 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 333.43 | 0 | 0 | No
2030-01-05 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 327.01 | 0 | 0 | No
2030-01-05 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 294.57 | 0 | 0 | No
2030-01-05 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -5.43 | 0 | 0 | No
2030-01-05 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 264.67 | 0 | 0 | No
2030-01-05 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-01-05 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-01-05 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 451.46 | 0 | 0 | No
2030-01-05 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 373.76 | 0 | 0 | No
2030-01-05 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 122.51 | 0 | 0 | No
2030-01-05 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -177.49 | 0 | 0 | Yes
2030-01-05 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 122.51 | 0 | 0 | Yes
2030-01-06 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 422.51 | 0 | 0 | Yes
2030-01-06 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-06 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 387.72 | 0 | 0 | Yes
2030-01-06 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-01-06 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-01-06 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 93.8 | 0 | 0 | Yes
2030-01-06 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 307.42 | 0 | 0 | Yes
2030-01-06 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 7.42 | 0 | 0 | Yes
2030-01-06 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 307.42 | 0 | 0 | Yes
2030-01-06 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 246.1 | 0 | 0 | Yes
2030-01-06 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-06 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 468.65 | 510 | 0 | 0 | Yes
2030-01-06 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 168.65 | 210 | 0 | 0 | No
2030-01-06 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-01-06 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 73.48 | 510 | 0 | 0 | No
2030-01-06 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-01-06 20:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | 0 | 510 | 0 | 0 | No
2030-01-06 21:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-01-06 22:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | 210.3 | 510 | 0 | 0 | No
2030-01-06 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 510 | 510 | 0 | 0 | Yes
2030-01-07 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 260.24 | 0 | 0 | Yes
2030-01-07 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 353.29 | 0 | 0 | Yes
2030-01-07 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 408.28 | 0 | 0 | Yes
2030-01-07 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 494.12 | 0 | 0 | Yes
2030-01-07 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 398.77 | 210 | 0 | 0 | Yes
2030-01-07 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-07 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-08 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-08 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-08 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-08 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 434.47 | 210 | 0 | 0 | No
2030-01-08 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 71.24 | 510 | 219.83 | 0 | 0 | No
2030-01-08 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 371.24 | 510 | 510 | 0 | 0 | No
2030-01-08 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 504 | 510 | 510 | 0 | 0 | No
2030-01-08 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 204 | 510 | 393.16 | 0 | 0 | No
2030-01-08 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 510 | 366.27 | 0 | 0 | No
2030-01-08 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 510 | 489.37 | 0 | 0 | No
2030-01-08 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 183.54 | 510 | 391.17 | 0 | 0 | No
2030-01-08 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 483.54 | 510 | 440.15 | 0 | 0 | No
2030-01-08 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 490.58 | 409.07 | 510 | 0 | 0 | No
2030-01-08 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 190.58 | 109.07 | 210 | 0 | 0 | No
2030-01-08 18:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | -109.42 | -190.93 | -90 | 0 | 0 | No
2030-01-08 19:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -490.93 | -121.14 | 0 | 0 | No
2030-01-08 20:00 | 2030 33% ECP + 1.3 GW Offshore | 411.4 | 0 | -233.9 | 143.83 | 0 | 0 | No
2030-01-08 21:00 | 2030 33% ECP + 1.3 GW Offshore | -8.6 | -300 | -510 | 67.12 | 0 | 0 | No
2030-01-08 22:00 | 2030 33% ECP + 1.3 GW Offshore | 411.4 | -157.97 | -510 | 173.05 | 0 | 0 | No
2030-01-08 23:00 | 2030 33% ECP + 1.3 GW Offshore | 507.55 | -300 | -510 | 37.1 | 0 | 0 | No
2030-01-09 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | -288.26 | 0 | 0 | 0 | No
2030-01-09 01:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -300 | -119.23 | -90 | 0 | 0 | No
2030-01-09 02:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | 180.77 | 210 | 0 | 0 | No
2030-01-09 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 480.77 | 510 | 0 | 0 | No
2030-01-09 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 05:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 300 | 485.54 | 300 | 0 | 0 | No
2030-01-09 06:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | 0 | 185.54 | 0 | 0 | 0 | No
2030-01-09 07:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 268.28 | 210 | 0 | 0 | No
2030-01-09 08:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 173.41 | 510 | 510 | 0 | 0 | No
2030-01-09 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 317.59 | 510 | 510 | 0 | 0 | No
2030-01-09 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 427.51 | 510 | 510 | 0 | 0 | No
2030-01-09 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 344.73 | 510 | 510 | 0 | 0 | No
2030-01-09 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 44.73 | 510 | 375.88 | 0 | 0 | No
2030-01-09 13:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 314.53 | 510 | 510 | 0 | 0 | No
2030-01-09 14:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-09 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-09 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -90 | 254.27 | 0 | 0 | No
2030-01-09 17:00 | 2030 33% ECP + 1.3 GW Offshore | 446.79 | -226 | -390 | 244.97 | 0 | 0 | No
2030-01-09 18:00 | 2030 33% ECP + 1.3 GW Offshore | 446.79 | -526 | -510 | -55.03 | 0 | 0 | No
2030-01-09 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 54.46 | 0 | 0 | No
2030-01-09 20:00 | 2030 33% ECP + 1.3 GW Offshore | 610.58 | -526 | -510 | 292.22 | 0 | 0 | No
2030-01-09 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -453.93 | -510 | 295.83 | 0 | 0 | No
2030-01-09 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -221.58 | -510 | 22.13 | 0 | 0 | No
2030-01-09 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -294.52 | 0 | 0 | 0 | No
2030-01-10 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 5.48 | 0 | 0 | 0 | No
2030-01-10 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 42.43 | 0 | 0 | 0 | No
2030-01-10 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 273.44 | 0 | 0 | 0 | No
2030-01-10 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 278.67 | 0 | 0 | No
2030-01-10 04:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | 0 | 268.67 | 0 | 0 | 0 | No
2030-01-10 05:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 25.91 | 0 | 0 | 0 | No
2030-01-10 06:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | 0 | 182.19 | 0 | 0 | 0 | No
2030-01-10 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 275.79 | 90 | 90 | 0 | 0 | No
2030-01-10 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -24.21 | -210 | -210 | 0 | 0 | No
2030-01-10 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -324.21 | -510 | -510 | 0 | 0 | No
2030-01-10 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-01-10 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -198.56 | 0 | 0 | No
2030-01-10 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -102.2 | 0 | 0 | Yes
2030-01-10 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -332.91 | 0 | 0 | Yes
2030-01-10 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -293.1 | 0 | 0 | Yes
2030-01-10 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -288.26 | 0 | 0 | Yes
2030-01-10 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -450.3 | 0 | 0 | Yes
2030-01-10 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -212.21 | 0 | 0 | Yes
2030-01-10 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -161.32 | 0 | 0 | No
2030-01-10 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -303.89 | 0 | 0 | No
2030-01-10 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -353.33 | 0 | 0 | No
2030-01-10 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -53.33 | 0 | 0 | Yes
2030-01-10 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 246.67 | 0 | 0 | Yes
2030-01-10 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 365.05 | 0 | 0 | Yes
2030-01-11 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 270.98 | 0 | 0 | Yes
2030-01-11 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 413.41 | 0 | 0 | Yes
2030-01-11 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 216.03 | 0 | 0 | Yes
2030-01-11 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 91.95 | 0 | 0 | Yes
2030-01-11 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 286.66 | 0 | 0 | Yes
2030-01-11 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-11 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 364.17 | 210 | 0 | 0 | No
2030-01-11 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-11 18:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | 0 | 510 | 510 | 0 | 0 | No
2030-01-11 19:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | 226.66 | 510 | 510 | 0 | 0 | No
2030-01-11 20:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | 510 | 510 | 0 | 0 | No
2030-01-11 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-01-11 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-11 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-12 05:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 205 | 210 | 391.98 | 0 | 0 | No
2030-01-12 06:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -95 | -90 | 226.14 | 0 | 0 | No
2030-01-12 07:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | 0 | -380.34 | 219.87 | 0 | 0 | No
2030-01-12 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -209.3 | 420.67 | 0 | 0 | No
2030-01-12 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | -118.9 | 420.67 | 0 | 0 | No
2030-01-12 10:00 | 2030 33% ECP + 1.3 GW Offshore | -639.71 | 0 | 0 | 268.47 | 0 | 0 | No
2030-01-12 11:00 | 2030 33% ECP + 1.3 GW Offshore | -219.71 | 0 | 0 | 461.2 | 0 | 0 | No
2030-01-12 12:00 | 2030 33% ECP + 1.3 GW Offshore | -76.27 | 0 | 0 | 453.33 | 0 | 0 | No
2030-01-12 13:00 | 2030 33% ECP + 1.3 GW Offshore | -202.16 | 0 | 0 | 380.6 | 0 | 0 | No
2030-01-12 14:00 | 2030 33% ECP + 1.3 GW Offshore | -561.68 | 0 | 0 | 258.02 | 0 | 0 | No
2030-01-12 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 314.86 | 0 | 0 | No
2030-01-12 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 450.39 | 0 | 0 | No
2030-01-12 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -86.1 | 510 | 0 | 0 | No
2030-01-12 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 510 | 0 | 0 | No
2030-01-12 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 391.44 | 0 | 0 | No
2030-01-12 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 91.44 | 0 | 0 | No
2030-01-12 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -175.34 | -210 | 60.19 | 0 | 0 | No
2030-01-12 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -475.34 | -510 | 60.19 | 0 | 0 | No
2030-01-12 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 360.19 | 0 | 0 | No
2030-01-13 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-01-13 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-01-13 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-13 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 324.37 | 210 | 0 | 0 | Yes
2030-01-13 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 328.83 | 0 | 0 | 0 | Yes
2030-01-13 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 88.34 | 0 | 0 | Yes
2030-01-13 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 183.5 | 0 | 0 | Yes
2030-01-13 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 228.25 | 0 | 0 | Yes
2030-01-13 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 382.26 | 0 | 0 | Yes
2030-01-13 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-01-13 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-01-13 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-01-13 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-01-13 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-01-13 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-01-13 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-01-13 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-01-13 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-13 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 323.25 | 0 | 0 | Yes
2030-01-14 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 298.99 | 0 | 0 | Yes
2030-01-14 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 251.03 | 0 | 0 | Yes
2030-01-14 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 383.13 | 0 | 0 | Yes
2030-01-14 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 08:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 09:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 10:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-14 16:00 | 2030 33% ECP + 1.3 GW Offshore | 442.73 | 205 | 210 | 510 | 0 | 0 | No
2030-01-14 17:00 | 2030 33% ECP + 1.3 GW Offshore | 22.73 | -95 | -90 | 510 | 0 | 0 | No
2030-01-14 18:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 7.27 | 210 | 510 | 0 | 0 | No
2030-01-14 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 307.27 | 510 | 510 | 0 | 0 | No
2030-01-14 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-14 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-01-15 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 258.4 | 90 | 510 | 0 | 0 | Yes
2030-01-15 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -41.6 | -210 | 510 | 0 | 0 | Yes
2030-01-15 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -341.6 | -510 | 363.79 | 0 | 0 | No
2030-01-15 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -395 | -390 | 510 | 0 | 0 | No
2030-01-15 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -90 | 510 | 0 | 0 | No
2030-01-15 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-01-15 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-15 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-15 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 510 | 463.19 | 0 | 0 | Yes
2030-01-16 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 210 | 163.19 | 0 | 0 | Yes
2030-01-16 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 221.96 | 210 | 0 | 0 | Yes
2030-01-16 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-16 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 246.99 | 510 | 0 | 0 | Yes
2030-01-16 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | -53.01 | 510 | 0 | 0 | Yes
2030-01-16 17:00 | 2030 33% ECP + 1.3 GW Offshore | -560.14 | -226 | -353.01 | 510 | 0 | 0 | No
2030-01-16 18:00 | 2030 33% ECP + 1.3 GW Offshore | -141.74 | -526 | -510 | 510 | 0 | 0 | No
2030-01-16 19:00 | 2030 33% ECP + 1.3 GW Offshore | -141.74 | -300 | -300 | 510 | 0 | 0 | No
2030-01-16 20:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | 0 | 0 | 505.8 | 0 | 0 | No
2030-01-16 21:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 300 | 300 | 510 | 0 | 0 | No
2030-01-16 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-16 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 04:00 | 2030 33% ECP + 1.3 GW Offshore | 539.61 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 05:00 | 2030 33% ECP + 1.3 GW Offshore | 119.61 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 06:00 | 2030 33% ECP + 1.3 GW Offshore | -300.39 | 205 | 210 | 210 | 0 | 0 | No
2030-01-17 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -90 | 399.27 | 0 | 0 | No
2030-01-17 08:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | 61.12 | 387.12 | 0 | 0 | No
2030-01-17 09:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 237.09 | 510 | 0 | 0 | No
2030-01-17 10:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | 510 | 510 | 0 | 0 | No
2030-01-17 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 210 | 510 | 0 | 0 | No
2030-01-17 12:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -49.15 | -90 | 510 | 0 | 0 | No
2030-01-17 13:00 | 2030 33% ECP + 1.3 GW Offshore | -63.93 | -188.16 | -368.68 | 248.84 | 0 | 0 | No
2030-01-17 14:00 | 2030 33% ECP + 1.3 GW Offshore | 217.76 | 0 | -68.68 | 510 | 0 | 0 | No
2030-01-17 15:00 | 2030 33% ECP + 1.3 GW Offshore | 637.76 | 0 | 173.46 | 510 | 0 | 0 | No
2030-01-17 16:00 | 2030 33% ECP + 1.3 GW Offshore | 272.19 | 0 | 473.46 | 510 | 0 | 0 | No
2030-01-17 17:00 | 2030 33% ECP + 1.3 GW Offshore | -147.81 | 0 | 510 | 510 | 0 | 0 | No
2030-01-17 18:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 510 | 510 | 0 | 0 | No
2030-01-17 19:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | 0 | 510 | 510 | 0 | 0 | No
2030-01-17 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 496.16 | 0 | 0 | No
2030-01-17 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-01-17 22:00 | 2030 33% ECP + 1.3 GW Offshore | 495.69 | 505 | 510 | 510 | 0 | 0 | No
2030-01-17 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 04:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 05:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 06:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 08:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 09:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 10:00 | 2030 33% ECP + 1.3 GW Offshore | -202.98 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 11:00 | 2030 33% ECP + 1.3 GW Offshore | -536.13 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 13:00 | 2030 33% ECP + 1.3 GW Offshore | -636.75 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 14:00 | 2030 33% ECP + 1.3 GW Offshore | -413.23 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 15:00 | 2030 33% ECP + 1.3 GW Offshore | 6.77 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 16:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 17:00 | 2030 33% ECP + 1.3 GW Offshore | 324.87 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-18 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-19 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 510 | 267.42 | 0 | 0 | No
2030-01-19 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 145.5 | 0 | 0 | No
2030-01-19 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-19 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-19 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-19 05:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | 0 | 510 | 0 | 0 | 0 | No
2030-01-19 06:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 364.17 | 0 | 0 | 0 | No
2030-01-19 07:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | 64.17 | 104.65 | 0 | 0 | No
2030-01-19 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -135.76 | -235.83 | -165.78 | 0 | 0 | No
2030-01-19 09:00 | 2030 33% ECP + 1.3 GW Offshore | -613.56 | -435.76 | -510 | -465.78 | 0 | 0 | No
2030-01-19 10:00 | 2030 33% ECP + 1.3 GW Offshore | -193.56 | -135.76 | -210 | -165.78 | 0 | 0 | No
2030-01-19 11:00 | 2030 33% ECP + 1.3 GW Offshore | -596.29 | -435.76 | -510 | 0 | 0 | 0 | No
2030-01-19 12:00 | 2030 33% ECP + 1.3 GW Offshore | -176.29 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 13:00 | 2030 33% ECP + 1.3 GW Offshore | -176.29 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 14:00 | 2030 33% ECP + 1.3 GW Offshore | -227.15 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 15:00 | 2030 33% ECP + 1.3 GW Offshore | -354.13 | -526 | -510 | 0 | 0 | 0 | No
2030-01-19 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -426.05 | -150.14 | 0 | 0 | No
2030-01-19 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -450.14 | 0 | 0 | No
2030-01-19 18:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -397.85 | 0 | 0 | No
2030-01-19 19:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -342.88 | -510 | -97.85 | 0 | 0 | No
2030-01-19 20:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -42.88 | -260.19 | 74.8 | 0 | 0 | No
2030-01-19 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -31.78 | -475.44 | 11.77 | 0 | 0 | No
2030-01-19 22:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -331.78 | -510 | -252.92 | 0 | 0 | No
2030-01-19 23:00 | 2030 33% ECP + 1.3 GW Offshore | -31.37 | -526 | -510 | -370.99 | 0 | 0 | No
2030-01-20 | 2030 33% ECP + 1.3 GW Offshore | -156.71 | -510.47 | -510 | -82.88 | 0 | 0 | No
2030-01-20 01:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -210.47 | -210 | 57.2 | 0 | 0 | No
2030-01-20 02:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 89.53 | 90 | 357.2 | 0 | 0 | No
2030-01-20 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 389.53 | 390 | 510 | 0 | 0 | No
2030-01-20 04:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 505 | 502.67 | 510 | 0 | 0 | No
2030-01-20 05:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 205 | 202.67 | 510 | 0 | 0 | No
2030-01-20 06:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -95 | -97.33 | 210 | 0 | 0 | No
2030-01-20 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -395 | -397.33 | -37.52 | 0 | 0 | No
2030-01-20 08:00 | 2030 33% ECP + 1.3 GW Offshore | -425.44 | -526 | -510 | 0 | 0 | 0 | No
2030-01-20 09:00 | 2030 33% ECP + 1.3 GW Offshore | -223.72 | -526 | -510 | 75.61 | 0 | 0 | No
2030-01-20 10:00 | 2030 33% ECP + 1.3 GW Offshore | -286.68 | -526 | -510 | 355.29 | 0 | 0 | No
2030-01-20 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 397 | 0 | 0 | No
2030-01-20 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 456.87 | 0 | 0 | No
2030-01-20 13:00 | 2030 33% ECP + 1.3 GW Offshore | -545.93 | -526 | -510 | 449.98 | 0 | 0 | No
2030-01-20 14:00 | 2030 33% ECP + 1.3 GW Offshore | -125.93 | -377.29 | -510 | 442.53 | 0 | 0 | No
2030-01-20 15:00 | 2030 33% ECP + 1.3 GW Offshore | 294.07 | -77.29 | -390.01 | 333.35 | 0 | 0 | No
2030-01-20 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -265.23 | 175.87 | 0 | 0 | No
2030-01-20 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 249.4 | 0 | 0 | No
2030-01-20 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 450.69 | 0 | 0 | No
2030-01-20 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 463.78 | 0 | 0 | No
2030-01-20 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 452.78 | 0 | 0 | No
2030-01-20 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 155.18 | 0 | 0 | No
2030-01-20 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-20 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 210 | 189.1 | 0 | 0 | No
2030-01-21 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 210 | 0 | 0 | No
2030-01-21 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-21 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 210 | 0 | 0 | No
2030-01-21 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 205.06 | 0 | 0 | No
2030-01-21 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-21 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-21 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-21 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 36.47 | 0 | 0 | No
2030-01-21 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 336.47 | 0 | 0 | No
2030-01-21 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 70.59 | 510 | 510 | 0 | 0 | No
2030-01-21 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 419.18 | 210 | 0 | 0 | No
2030-01-21 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 119.18 | 0 | 0 | 0 | No
2030-01-21 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 147.63 | 210 | 210 | 0 | 0 | No
2030-01-21 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 447.63 | 510 | 510 | 0 | 0 | No
2030-01-21 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-01-21 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 304.53 | 0 | 0 | 0 | No
2030-01-21 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-01-21 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 52.55 | 0 | 0 | No
2030-01-21 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 35.95 | 0 | 0 | No
2030-01-21 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 35.95 | 0 | 0 | No
2030-01-21 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 510 | 273.9 | 0 | 0 | No
2030-01-21 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-21 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 510 | 402.67 | 0 | 0 | No
2030-01-22 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-22 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 277.82 | 0 | 0 | No
2030-01-22 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 214.92 | -22.18 | 0 | 0 | No
2030-01-22 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -22.99 | -86.1 | 0 | 0 | No
2030-01-22 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 277.01 | 0 | 0 | 0 | No
2030-01-22 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 204.93 | 510 | 65.92 | 0 | 0 | No
2030-01-22 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 151.42 | 510 | 136.37 | 0 | 0 | No
2030-01-22 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 47.85 | 0 | 0 | No
2030-01-22 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 435.62 | 0 | 0 | 0 | No
2030-01-22 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 52.31 | 0 | 0 | No
2030-01-22 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 265.39 | 390 | 88.75 | 0 | 0 | No
2030-01-22 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 0 | 0 | 0 | No
2030-01-22 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | -248.08 | 0 | 0 | No
2030-01-22 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-22 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-22 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-22 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-01-22 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 19.04 | 90 | 90 | 0 | 0 | No
2030-01-22 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 180.13 | 328.95 | 210 | 0 | 0 | No
2030-01-22 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 480.13 | 510 | 510 | 0 | 0 | No
2030-01-23 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-23 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 318.99 | 0 | 0 | No
2030-01-23 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 331.13 | 0 | 0 | No
2030-01-23 06:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 300 | 479.27 | 77.97 | 0 | 0 | No
2030-01-23 07:00 | 2030 33% ECP + 1.3 GW Offshore | -11.48 | 0 | 179.27 | -222.03 | 0 | 0 | No
2030-01-23 08:00 | 2030 33% ECP + 1.3 GW Offshore | 408.52 | 0 | 420.53 | 0 | 0 | 0 | No
2030-01-23 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 29.93 | 510 | 0 | 0 | 0 | No
2030-01-23 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 58.3 | 510 | 0 | 0 | 0 | No
2030-01-23 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 210 | 0 | 0 | 0 | No
2030-01-23 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-23 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-01-23 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 34.27 | 0 | 0 | 0 | No
2030-01-23 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 27.94 | 334.27 | 0 | 0 | 0 | No
2030-01-23 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 34.27 | -52.27 | 0 | 0 | No
2030-01-23 17:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -300 | -265.73 | -352.27 | 0 | 0 | No
2030-01-23 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -454.36 | -510 | 0 | 0 | No
2030-01-23 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -154.36 | -247.72 | 0 | 0 | No
2030-01-23 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 145.64 | 0 | 0 | 0 | No
2030-01-23 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 217.08 | 445.64 | 0 | 0 | 0 | No
2030-01-23 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 166.55 | 510 | 3.38 | 0 | 0 | No
2030-01-23 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 345.62 | 510 | 303.38 | 0 | 0 | No
2030-01-24 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-24 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 485 | 0 | 0 | No
2030-01-24 06:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | 368.01 | 510 | 185 | 0 | 0 | No
2030-01-24 07:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 68.01 | 234 | -102.43 | 0 | 0 | No
2030-01-24 08:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 290.45 | -154.69 | 0 | 0 | No
2030-01-24 09:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 51.92 | 510 | -50.05 | 0 | 0 | No
2030-01-24 10:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 359.07 | -18.94 | 0 | 0 | No
2030-01-24 11:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 125.8 | -218.28 | 0 | 0 | No
2030-01-24 12:00 | 2030 33% ECP + 1.3 GW Offshore | 396.16 | 287.97 | 300 | 0 | 0 | 0 | No
2030-01-24 13:00 | 2030 33% ECP + 1.3 GW Offshore | -23.84 | 0 | 0 | -300 | 0 | 0 | No
2030-01-24 14:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -300 | -328.99 | 0 | 0 | No
2030-01-24 15:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -226 | -274.63 | -210 | 0 | 0 | No
2030-01-24 16:00 | 2030 33% ECP + 1.3 GW Offshore | 253.89 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 17:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 18:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 19:00 | 2030 33% ECP + 1.3 GW Offshore | 169.96 | -526 | -510 | -510 | 0 | 0 | No
2030-01-24 20:00 | 2030 33% ECP + 1.3 GW Offshore | 589.96 | -258.9 | -300 | -415.93 | 0 | 0 | No
2030-01-24 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 41.1 | 0 | -115.93 | 0 | 0 | No
2030-01-24 22:00 | 2030 33% ECP + 1.3 GW Offshore | 473.77 | 0 | -300 | -26.37 | 0 | 0 | No
2030-01-24 23:00 | 2030 33% ECP + 1.3 GW Offshore | 53.77 | 0 | 0 | 0 | 0 | 0 | No
2030-01-25 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -300 | 0 | 0 | 0 | No
2030-01-25 01:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -510 | -258.08 | 0 | 0 | No
2030-01-25 02:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -510 | -6.91 | 0 | 0 | No
2030-01-25 03:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | -506.05 | -120.32 | 0 | 0 | No
2030-01-25 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -376.05 | -122.96 | 0 | 0 | No
2030-01-25 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -510 | -273.31 | 0 | 0 | No
2030-01-25 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -510 | -325.92 | 0 | 0 | No
2030-01-25 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -451.57 | -278.63 | 0 | 0 | No
2030-01-25 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -151.57 | 0 | 0 | 0 | No
2030-01-25 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -71.15 | 0 | 0 | 0 | No
2030-01-25 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 210.99 | 18.45 | 0 | 0 | No
2030-01-25 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -89.01 | 0 | 0 | 0 | No
2030-01-25 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -389.01 | -15.7 | 0 | 0 | No
2030-01-25 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -510 | -315.7 | 0 | 0 | No
2030-01-25 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -510 | -89.51 | 0 | 0 | No
2030-01-25 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -225.87 | 0 | 0 | 0 | No
2030-01-25 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -210 | -98.08 | 0 | 0 | No
2030-01-25 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -300 | -510 | -398.08 | 0 | 0 | No
2030-01-25 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-25 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-01-25 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -493.11 | -210 | 0 | 0 | No
2030-01-25 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -18.41 | 0 | 0 | No
2030-01-25 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -34.67 | 0 | 0 | No
2030-01-25 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -91.51 | 0 | 0 | Yes
2030-01-26 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 208.49 | 0 | 0 | Yes
2030-01-26 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 508.49 | 0 | 0 | Yes
2030-01-26 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-26 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-26 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-01-26 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 90 | 510 | 0 | 0 | Yes
2030-01-26 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -210 | 412.4 | 0 | 0 | Yes
2030-01-26 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -395 | -510 | 112.4 | 0 | 0 | No
2030-01-26 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -210 | 53.18 | 0 | 0 | No
2030-01-26 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -29.87 | 350.71 | 0 | 0 | No
2030-01-26 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -55.53 | 181.13 | 0 | 0 | No
2030-01-26 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -61.06 | 0 | 0 | 0 | No
2030-01-26 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 59.76 | 0 | 0 | 0 | No
2030-01-26 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 208.57 | 176.13 | 0 | 0 | No
2030-01-26 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 233.81 | 141.01 | 0 | 0 | No
2030-01-26 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 8.21 | 320.62 | 0 | 0 | No
2030-01-26 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 347.17 | 0 | 0 | No
2030-01-26 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 47.17 | 0 | 0 | No
2030-01-26 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -11.86 | 0 | 0 | No
2030-01-26 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -152.94 | 0 | 0 | No
2030-01-26 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 147.06 | 0 | 0 | No
2030-01-26 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -300.36 | 144.86 | 0 | 0 | No
2030-01-26 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -14.27 | 0 | 0 | No
2030-01-26 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -314.27 | 0 | 0 | No
2030-01-27 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -14.27 | 0 | 0 | No
2030-01-27 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -90 | 0 | 0 | No
2030-01-27 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 210 | 0 | 0 | No
2030-01-27 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | No
2030-01-27 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-27 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 287.77 | 510 | 0 | 0 | No
2030-01-27 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | -12.23 | 218.06 | 0 | 0 | No
2030-01-27 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -312.23 | -81.94 | 0 | 0 | No
2030-01-27 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -146.52 | 0 | 0 | No
2030-01-27 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 9.58 | 0 | 0 | No
2030-01-27 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -290.42 | 0 | 0 | No
2030-01-27 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 9.58 | 0 | 0 | No
2030-01-27 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -410.21 | -510 | -290.42 | 0 | 0 | No
2030-01-27 14:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -110.21 | -210 | 9.58 | 0 | 0 | No
2030-01-27 15:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -77.96 | 133.84 | 0 | 0 | No
2030-01-27 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | 0 | 375.51 | 0 | 0 | No
2030-01-27 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -300 | 224.24 | 0 | 0 | No
2030-01-27 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -231.36 | -300 | 210 | 0 | 0 | No
2030-01-27 19:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | 0 | 510 | 0 | 0 | No
2030-01-27 20:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 0 | 204.02 | 510 | 0 | 0 | No
2030-01-27 21:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 0 | 35.01 | 430.53 | 0 | 0 | No
2030-01-27 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -92.12 | 135.59 | 0 | 0 | No
2030-01-27 23:00 | 2030 33% ECP + 1.3 GW Offshore | 677.63 | -300 | -392.12 | 187.63 | 0 | 0 | No
2030-01-28 | 2030 33% ECP + 1.3 GW Offshore | 297.16 | -95 | -436.98 | 109.93 | 0 | 0 | No
2030-01-28 01:00 | 2030 33% ECP + 1.3 GW Offshore | -122.84 | -395 | -390 | -20.35 | 0 | 0 | No
2030-01-28 02:00 | 2030 33% ECP + 1.3 GW Offshore | -4.94 | -95 | -90 | 243.76 | 0 | 0 | No
2030-01-28 03:00 | 2030 33% ECP + 1.3 GW Offshore | 415.06 | 205 | 210 | 210 | 0 | 0 | No
2030-01-28 04:00 | 2030 33% ECP + 1.3 GW Offshore | 191.96 | 505 | 510 | 510 | 0 | 0 | No
2030-01-28 05:00 | 2030 33% ECP + 1.3 GW Offshore | -228.04 | 505 | 510 | 510 | 0 | 0 | No
2030-01-28 06:00 | 2030 33% ECP + 1.3 GW Offshore | -648.04 | 425.71 | 390 | 510 | 0 | 0 | No
2030-01-28 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 125.71 | 90 | 210 | 0 | 0 | No
2030-01-28 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -174.29 | -210 | 404.9 | 0 | 0 | No
2030-01-28 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -474.29 | -510 | 104.9 | 0 | 0 | No
2030-01-28 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 404.9 | 0 | 0 | No
2030-01-28 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 106.99 | 0 | 0 | No
2030-01-28 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 110.28 | 0 | 0 | No
2030-01-28 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 410.28 | 0 | 0 | No
2030-01-28 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 448.44 | 0 | 0 | No
2030-01-28 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 336.23 | 0 | 0 | No
2030-01-28 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 250.59 | 0 | 0 | No
2030-01-28 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 190.82 | 0 | 0 | No
2030-01-28 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 490.82 | 0 | 0 | No
2030-01-28 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 193.36 | 0 | 0 | No
2030-01-28 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -300 | -328.32 | 493.36 | 0 | 0 | No
2030-01-28 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -28.32 | 510 | 0 | 0 | No
2030-01-28 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 271.68 | 510 | 0 | 0 | No
2030-01-28 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-29 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 210 | 249.42 | 0 | 0 | No
2030-01-29 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -52.23 | -90 | 337.66 | 0 | 0 | No
2030-01-29 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -59.72 | -390 | 510 | 0 | 0 | No
2030-01-29 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -245.98 | -510 | 510 | 0 | 0 | No
2030-01-29 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 425.62 | 0 | 0 | No
2030-01-29 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 125.62 | 0 | 0 | No
2030-01-29 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -174.38 | 0 | 0 | No
2030-01-29 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -358.63 | 0 | 0 | No
2030-01-29 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -237.35 | -510 | -500.01 | 0 | 0 | No
2030-01-29 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -510 | -510 | 0 | 0 | No
2030-01-29 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -510 | -395.5 | 0 | 0 | No
2030-01-29 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -510 | -95.5 | 0 | 0 | No
2030-01-29 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -390 | 204.5 | 0 | 0 | No
2030-01-29 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -90 | 504.5 | 0 | 0 | No
2030-01-29 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 210 | 493.1 | 0 | 0 | No
2030-01-29 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-29 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 460.37 | 510 | 0 | 0 | No
2030-01-30 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 160.37 | 210 | 0 | 0 | No
2030-01-30 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -139.63 | -89.36 | 0 | 0 | No
2030-01-30 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -395 | -439.63 | 165.71 | 0 | 0 | No
2030-01-30 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 382.24 | 0 | 0 | No
2030-01-30 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 139.31 | 0 | 0 | No
2030-01-30 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -297.74 | -300 | 169.08 | 0 | 0 | No
2030-01-30 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 2.26 | 0 | 403.19 | 0 | 0 | No
2030-01-30 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 302.26 | 300 | 510 | 0 | 0 | No
2030-01-30 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 406.91 | 300 | 0 | 0 | No
2030-01-30 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 106.91 | 0 | 0 | 0 | No
2030-01-30 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 374.81 | 210 | 0 | 0 | No
2030-01-30 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 510 | 510 | 0 | 0 | No
2030-01-30 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 129.58 | 510 | 510 | 0 | 0 | No
2030-01-30 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 429.58 | 510 | 510 | 0 | 0 | No
2030-01-30 21:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 313.87 | 510 | 510 | 0 | 0 | No
2030-01-30 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-01-30 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-01-31 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 457.49 | 210 | 510 | 0 | 0 | Yes
2030-01-31 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 157.49 | -90 | 510 | 0 | 0 | Yes
2030-01-31 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -142.51 | -390 | 324.41 | 0 | 0 | No
2030-01-31 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -300 | -391.26 | 24.41 | 0 | 0 | No
2030-01-31 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -91.26 | 324.41 | 0 | 0 | No
2030-01-31 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 10.43 | 208.74 | 510 | 0 | 0 | Yes
2030-01-31 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 310.43 | 508.74 | 510 | 0 | 0 | Yes
2030-01-31 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-31 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-01-31 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-01-31 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 267.5 | 0 | 0 | No
2030-01-31 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-01-31 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-01-31 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 118.95 | 0 | 0 | No
2030-01-31 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 418.95 | 0 | 0 | Yes
2030-01-31 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-01-31 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-01-31 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-01 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 510 | 510 | 0 | 0 | Yes
2030-02-01 16:00 | 2030 33% ECP + 1.3 GW Offshore | -495.55 | 0 | 210 | 210 | 0 | 0 | No
2030-02-01 17:00 | 2030 33% ECP + 1.3 GW Offshore | -75.55 | 93.7 | 510 | 510 | 0 | 0 | No
2030-02-01 18:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 393.7 | 510 | 510 | 0 | 0 | No
2030-02-01 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-01 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 459.45 | 510 | 510 | 0 | 0 | No
2030-02-01 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 159.45 | 510 | 510 | 0 | 0 | No
2030-02-01 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 210 | 510 | 0 | 0 | No
2030-02-01 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -201.43 | -90 | 457.93 | 0 | 0 | No
2030-02-02 | 2030 33% ECP + 1.3 GW Offshore | 700 | -230.73 | -390 | 293.85 | 0 | 0 | No
2030-02-02 01:00 | 2030 33% ECP + 1.3 GW Offshore | 416.6 | -300 | -324.78 | 305.98 | 0 | 0 | No
2030-02-02 02:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 0 | -24.78 | 237.62 | 0 | 0 | No
2030-02-02 03:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -168.83 | -305.11 | 117.51 | 0 | 0 | No
2030-02-02 04:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -468.83 | -510 | 138.64 | 0 | 0 | No
2030-02-02 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 141.04 | 0 | 0 | No
2030-02-02 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 14.42 | 0 | 0 | No
2030-02-02 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 190.9 | 0 | 0 | No
2030-02-02 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 220.01 | 0 | 0 | No
2030-02-02 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 149.26 | 0 | 0 | No
2030-02-02 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 215.01 | 0 | 0 | No
2030-02-02 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 268.16 | 0 | 0 | Yes
2030-02-02 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 300.12 | 0 | 0 | Yes
2030-02-02 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 253.54 | 0 | 0 | Yes
2030-02-02 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 117.52 | 0 | 0 | Yes
2030-02-02 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 63.58 | 0 | 0 | Yes
2030-02-02 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 55.05 | 0 | 0 | Yes
2030-02-02 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 355.05 | 0 | 0 | Yes
2030-02-02 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 391.48 | 0 | 0 | No
2030-02-02 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 91.48 | 0 | 0 | No
2030-02-02 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 108.38 | 0 | 0 | No
2030-02-02 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 221.45 | 0 | 0 | No
2030-02-02 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-02-02 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-02-03 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 233.27 | 0 | 0 | Yes
2030-02-03 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 112.55 | 0 | 0 | Yes
2030-02-03 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 159.47 | 0 | 0 | Yes
2030-02-03 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 201.16 | 0 | 0 | Yes
2030-02-03 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 127.16 | 0 | 0 | Yes
2030-02-03 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 170.54 | 0 | 0 | Yes
2030-02-03 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 255.17 | 0 | 0 | Yes
2030-02-03 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 272.15 | 0 | 0 | Yes
2030-02-03 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 242.94 | 0 | 0 | Yes
2030-02-03 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 488.31 | 0 | 0 | Yes
2030-02-03 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 457.74 | 0 | 0 | Yes
2030-02-03 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 413.28 | 0 | 0 | Yes
2030-02-03 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 455.78 | 0 | 0 | Yes
2030-02-03 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-03 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 488.99 | 0 | 0 | Yes
2030-02-04 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 188.99 | 0 | 0 | Yes
2030-02-04 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-02-04 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-02-04 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-02-04 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 185.66 | 0 | 0 | Yes
2030-02-04 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 386.86 | 0 | 0 | Yes
2030-02-04 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 14:00 | 2030 33% ECP + 1.3 GW Offshore | -417.07 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-04 15:00 | 2030 33% ECP + 1.3 GW Offshore | 2.93 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 16:00 | 2030 33% ECP + 1.3 GW Offshore | 422.93 | 205 | 283.49 | 210 | 0 | 0 | No
2030-02-04 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-02-04 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 98.8 | 510 | 510 | 0 | 0 | No
2030-02-04 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 398.8 | 510 | 510 | 0 | 0 | No
2030-02-04 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 398.8 | 510 | 510 | 0 | 0 | No
2030-02-04 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-04 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 447.98 | 510 | 510 | 0 | 0 | No
2030-02-04 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 147.98 | 510 | 510 | 0 | 0 | No
2030-02-05 | 2030 33% ECP + 1.3 GW Offshore | 700 | 447.98 | 510 | 510 | 0 | 0 | No
2030-02-05 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 05:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-05 06:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | 205 | 210 | 210 | 0 | 0 | No
2030-02-05 07:00 | 2030 33% ECP + 1.3 GW Offshore | -347.69 | 0 | 0 | 0 | 0 | 0 | No
2030-02-05 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -300 | -54.62 | 0 | 0 | No
2030-02-05 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | 0 | 35.71 | 0 | 0 | No
2030-02-05 10:00 | 2030 33% ECP + 1.3 GW Offshore | -418.34 | -300 | -300 | 0 | 0 | 0 | No
2030-02-05 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -300 | -510 | 47.31 | 0 | 0 | No
2030-02-05 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -210 | 28.11 | 0 | 0 | No
2030-02-05 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 52.85 | 0 | 0 | No
2030-02-05 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 12.09 | 54.32 | 0 | 0 | No
2030-02-05 15:00 | 2030 33% ECP + 1.3 GW Offshore | -626.99 | 0 | 0 | 84.66 | 0 | 0 | No
2030-02-05 16:00 | 2030 33% ECP + 1.3 GW Offshore | -206.99 | 0 | -84.03 | 0 | 0 | 0 | No
2030-02-05 17:00 | 2030 33% ECP + 1.3 GW Offshore | -626.99 | 0 | -210 | -99.46 | 0 | 0 | No
2030-02-05 18:00 | 2030 33% ECP + 1.3 GW Offshore | -206.99 | -300 | -510 | -399.46 | 0 | 0 | No
2030-02-05 19:00 | 2030 33% ECP + 1.3 GW Offshore | 213.01 | 0 | -210 | -99.46 | 0 | 0 | No
2030-02-05 20:00 | 2030 33% ECP + 1.3 GW Offshore | 633.01 | 300 | 90 | 200.54 | 0 | 0 | No
2030-02-05 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 180.29 | 19.35 | 0 | 0 | No
2030-02-05 22:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | 24.47 | 0 | 0 | 0 | No
2030-02-05 23:00 | 2030 33% ECP + 1.3 GW Offshore | 190.83 | 0 | 188.38 | 147.08 | 0 | 0 | No
2030-02-06 | 2030 33% ECP + 1.3 GW Offshore | 140 | 233.44 | 488.38 | 447.08 | 0 | 0 | No
2030-02-06 01:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 233.44 | 510 | 510 | 0 | 0 | No
2030-02-06 02:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 138.49 | 510 | 510 | 0 | 0 | No
2030-02-06 03:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | 510 | 510 | 0 | 0 | No
2030-02-06 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 439.02 | 300 | 0 | 0 | No
2030-02-06 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 139.02 | 0 | 0 | 0 | No
2030-02-06 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -300 | -160.98 | -300 | 0 | 0 | No
2030-02-06 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -225.56 | -210 | -210 | 0 | 0 | No
2030-02-06 08:00 | 2030 33% ECP + 1.3 GW Offshore | -653.35 | -525.56 | -510 | -510 | 0 | 0 | No
2030-02-06 09:00 | 2030 33% ECP + 1.3 GW Offshore | -233.35 | -225.56 | -210 | -210 | 0 | 0 | No
2030-02-06 10:00 | 2030 33% ECP + 1.3 GW Offshore | 186.65 | 0 | -363.6 | 0 | 0 | 0 | No
2030-02-06 11:00 | 2030 33% ECP + 1.3 GW Offshore | -3.28 | -300 | -510 | -147.57 | 0 | 0 | No
2030-02-06 12:00 | 2030 33% ECP + 1.3 GW Offshore | -291.38 | -526 | -510 | -186.91 | 0 | 0 | No
2030-02-06 13:00 | 2030 33% ECP + 1.3 GW Offshore | -495.9 | -526 | -510 | -85.12 | 0 | 0 | No
2030-02-06 14:00 | 2030 33% ECP + 1.3 GW Offshore | -75.9 | -526 | -510 | -182.95 | 0 | 0 | No
2030-02-06 15:00 | 2030 33% ECP + 1.3 GW Offshore | -315.42 | -526 | -510 | -210 | 0 | 0 | No
2030-02-06 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 19:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 20:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -418.09 | -510 | -503.89 | 0 | 0 | No
2030-02-06 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-06 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -271.71 | 0 | 0 | No
2030-02-06 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -403.59 | 0 | 0 | No
2030-02-07 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -112.15 | 0 | 0 | No
2030-02-07 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -61.02 | 0 | 0 | No
2030-02-07 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -50.64 | 0 | 0 | No
2030-02-07 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -350.64 | 0 | 0 | No
2030-02-07 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -228.41 | 0 | 0 | No
2030-02-07 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -102.03 | 0 | 0 | No
2030-02-07 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 67.9 | 0 | 0 | No
2030-02-07 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -108.55 | 0 | 0 | No
2030-02-07 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -272.84 | 0 | 0 | No
2030-02-07 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -309.03 | 0 | 0 | No
2030-02-07 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -20.54 | 0 | 0 | No
2030-02-07 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -108.81 | 0 | 0 | No
2030-02-07 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -102.94 | 0 | 0 | No
2030-02-07 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 197.06 | 0 | 0 | No
2030-02-07 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -496.92 | -510 | 497.06 | 0 | 0 | No
2030-02-07 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 254.26 | 0 | 0 | No
2030-02-07 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -45.74 | 0 | 0 | No
2030-02-07 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -345.74 | 0 | 0 | No
2030-02-07 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-07 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -500.77 | 0 | 0 | No
2030-02-07 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -200.77 | 0 | 0 | No
2030-02-07 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 99.23 | 0 | 0 | Yes
2030-02-07 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 399.23 | 0 | 0 | Yes
2030-02-07 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 381.87 | 210 | 0 | 0 | Yes
2030-02-08 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 296.42 | 410.35 | 0 | 0 | Yes
2030-02-08 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -3.58 | 110.35 | 0 | 0 | Yes
2030-02-08 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 172.77 | 210 | 410.35 | 0 | 0 | No
2030-02-08 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 472.77 | 510 | 510 | 0 | 0 | Yes
2030-02-08 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-08 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-02-09 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-02-09 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-02-09 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -510 | -452.18 | 0 | 0 | Yes
2030-02-09 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-02-09 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-09 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-02-09 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-02-09 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-02-09 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-09 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 446.31 | 0 | 0 | Yes
2030-02-10 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 217.86 | 0 | 0 | Yes
2030-02-10 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 225.3 | 0 | 0 | Yes
2030-02-10 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 385.52 | 0 | 0 | Yes
2030-02-10 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 368.81 | 0 | 0 | Yes
2030-02-10 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 98.22 | 0 | 0 | Yes
2030-02-10 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 64.87 | 0 | 0 | Yes
2030-02-10 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 246.57 | 0 | 0 | Yes
2030-02-10 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 396.63 | 0 | 0 | Yes
2030-02-10 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 200.21 | 0 | 0 | Yes
2030-02-10 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 361.04 | 0 | 0 | Yes
2030-02-10 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 296.63 | 0 | 0 | Yes
2030-02-10 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 263.82 | 0 | 0 | Yes
2030-02-10 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 458.49 | 0 | 0 | Yes
2030-02-10 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 346.4 | 0 | 0 | Yes
2030-02-10 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 466.83 | 0 | 0 | Yes
2030-02-10 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-10 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 460.29 | 0 | 0 | Yes
2030-02-10 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 318.94 | 0 | 0 | Yes
2030-02-11 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 250.54 | 0 | 0 | Yes
2030-02-11 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 210.43 | 0 | 0 | Yes
2030-02-11 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 215.82 | 0 | 0 | Yes
2030-02-11 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 153.82 | 0 | 0 | Yes
2030-02-11 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 203.87 | 0 | 0 | Yes
2030-02-11 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 120.42 | 0 | 0 | Yes
2030-02-11 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 157.32 | 0 | 0 | Yes
2030-02-11 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 457.32 | 0 | 0 | Yes
2030-02-11 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-11 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-11 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 01:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 02:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 03:00 | 2030 33% ECP + 1.3 GW Offshore | -49.13 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 04:00 | 2030 33% ECP + 1.3 GW Offshore | -469.13 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-12 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 13:00 | 2030 33% ECP + 1.3 GW Offshore | -504.44 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 14:00 | 2030 33% ECP + 1.3 GW Offshore | -84.44 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 15:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-02-12 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 205 | 210 | 510 | 0 | 0 | No
2030-02-12 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -6.64 | -90 | 510 | 0 | 0 | No
2030-02-12 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -306.64 | -390 | 510 | 0 | 0 | No
2030-02-12 19:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-02-12 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-02-12 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 371.63 | 0 | 0 | No
2030-02-12 22:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 71.63 | 0 | 0 | No
2030-02-12 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 371.63 | 0 | 0 | Yes
2030-02-13 | 2030 33% ECP + 1.3 GW Offshore | -280 | 74 | 90 | 510 | 0 | 0 | Yes
2030-02-13 01:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-13 02:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 505 | 510 | 235.26 | 0 | 0 | Yes
2030-02-13 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 374.98 | 0 | 0 | Yes
2030-02-13 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 464.68 | 0 | 0 | Yes
2030-02-13 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 374.41 | 0 | 0 | Yes
2030-02-13 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-13 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 348.73 | 390 | 277.27 | 0 | 0 | No
2030-02-13 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 48.73 | 90 | -22.73 | 0 | 0 | No
2030-02-13 10:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -251.27 | -210 | 277.27 | 0 | 0 | No
2030-02-13 11:00 | 2030 33% ECP + 1.3 GW Offshore | 235.53 | -526 | -510 | 333.78 | 0 | 0 | No
2030-02-13 12:00 | 2030 33% ECP + 1.3 GW Offshore | 257.49 | -526 | -510 | 33.78 | 0 | 0 | No
2030-02-13 13:00 | 2030 33% ECP + 1.3 GW Offshore | -162.51 | -526 | -510 | -237.12 | 0 | 0 | No
2030-02-13 14:00 | 2030 33% ECP + 1.3 GW Offshore | 123.56 | -526 | -510 | 62.88 | 0 | 0 | No
2030-02-13 15:00 | 2030 33% ECP + 1.3 GW Offshore | 543.56 | -512.75 | -510 | 324.74 | 0 | 0 | No
2030-02-13 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -212.75 | -210 | 510 | 0 | 0 | No
2030-02-13 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 87.25 | 90 | 510 | 0 | 0 | No
2030-02-13 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 34.51 | 355.62 | 0 | 0 | No
2030-02-13 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 449.18 | 0 | 0 | No
2030-02-13 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-13 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 390 | 510 | 0 | 0 | No
2030-02-13 22:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | 90 | 400 | 0 | 0 | No
2030-02-13 23:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -300 | -210 | 100 | 0 | 0 | No
2030-02-14 | 2030 33% ECP + 1.3 GW Offshore | -311.98 | -526 | -510 | -192.58 | 0 | 0 | No
2030-02-14 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -10.86 | 0 | 0 | No
2030-02-14 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -118.45 | 0 | 0 | Yes
2030-02-14 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -162.76 | 0 | 0 | Yes
2030-02-14 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -122.62 | 0 | 0 | Yes
2030-02-14 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -362.78 | 0 | 0 | Yes
2030-02-14 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-14 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-14 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -405.12 | 0 | 0 | Yes
2030-02-14 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -105.12 | 0 | 0 | Yes
2030-02-14 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 194.88 | 0 | 0 | Yes
2030-02-14 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 494.88 | 0 | 0 | Yes
2030-02-14 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-14 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 300 | 362.07 | 0 | 0 | Yes
2030-02-14 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 62.07 | 0 | 0 | No
2030-02-14 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 362.07 | 0 | 0 | No
2030-02-14 19:00 | 2030 33% ECP + 1.3 GW Offshore | -357.4 | 0 | 0 | 510 | 0 | 0 | No
2030-02-14 20:00 | 2030 33% ECP + 1.3 GW Offshore | 62.6 | 0 | 0 | 510 | 0 | 0 | No
2030-02-14 21:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | -231.05 | 467.39 | 0 | 0 | No
2030-02-14 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -6.23 | 484.32 | 0 | 0 | No
2030-02-14 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 293.77 | 510 | 0 | 0 | Yes
2030-02-15 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-15 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 269.51 | 210 | 510 | 0 | 0 | Yes
2030-02-15 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -30.49 | -90 | 510 | 0 | 0 | Yes
2030-02-15 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -330.49 | -390 | 344.11 | 0 | 0 | Yes
2030-02-15 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 175.5 | 0 | 0 | Yes
2030-02-15 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -124.5 | 0 | 0 | Yes
2030-02-15 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 175.5 | 0 | 0 | No
2030-02-15 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 100.71 | 0 | 0 | No
2030-02-15 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 400.71 | 0 | 0 | No
2030-02-15 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 310.7 | 0 | 0 | No
2030-02-15 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-02-15 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-02-15 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-16 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 351.31 | 0 | 0 | Yes
2030-02-16 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 150.4 | 0 | 0 | Yes
2030-02-16 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 450.4 | 0 | 0 | Yes
2030-02-16 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 342.29 | 0 | 0 | Yes
2030-02-16 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 97.66 | 0 | 0 | Yes
2030-02-16 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 292.12 | 0 | 0 | Yes
2030-02-16 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 488.69 | 0 | 0 | Yes
2030-02-16 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 484.39 | 0 | 0 | Yes
2030-02-16 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-16 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 473.4 | 0 | 0 | Yes
2030-02-16 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 421.47 | 0 | 0 | Yes
2030-02-16 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 416.15 | 0 | 0 | Yes
2030-02-16 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 395.41 | 0 | 0 | Yes
2030-02-16 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 406.88 | 0 | 0 | Yes
2030-02-16 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 411.44 | 0 | 0 | Yes
2030-02-16 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 429.98 | 309.18 | 0 | 0 | Yes
2030-02-16 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 129.98 | 90 | 0 | 0 | Yes
2030-02-16 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -170.02 | -210 | 0 | 0 | Yes
2030-02-16 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -395 | -470.02 | -510 | 0 | 0 | Yes
2030-02-16 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -170.02 | -210 | 0 | 0 | Yes
2030-02-16 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 129.98 | 90 | 0 | 0 | Yes
2030-02-16 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 429.98 | 390 | 0 | 0 | Yes
2030-02-16 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 323.13 | 0 | 0 | Yes
2030-02-16 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 230.01 | 0 | 0 | Yes
2030-02-17 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 97.48 | 0 | 0 | Yes
2030-02-17 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 91.15 | 0 | 0 | Yes
2030-02-17 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 83.46 | 0 | 0 | Yes
2030-02-17 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 67.44 | 0 | 0 | Yes
2030-02-17 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 142.1 | 0 | 0 | Yes
2030-02-17 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 442.1 | 0 | 0 | Yes
2030-02-17 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 440.05 | 0 | 0 | Yes
2030-02-17 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 454.34 | 0 | 0 | Yes
2030-02-17 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 504.7 | 0 | 0 | Yes
2030-02-17 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 464.05 | 0 | 0 | Yes
2030-02-17 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 399.94 | 0 | 0 | Yes
2030-02-17 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-17 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 359.96 | 0 | 0 | Yes
2030-02-18 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-18 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 436.64 | 510 | 0 | 0 | No
2030-02-18 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-18 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 01:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 02:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 03:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 04:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-02-19 05:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 425.78 | 390 | 510 | 0 | 0 | No
2030-02-19 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 125.78 | 90 | 510 | 0 | 0 | No
2030-02-19 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -174.22 | -210 | 510 | 0 | 0 | No
2030-02-19 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -474.22 | -510 | 301.65 | 0 | 0 | No
2030-02-19 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 323.25 | 0 | 0 | No
2030-02-19 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-02-19 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-02-19 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-19 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-19 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-19 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-02-19 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-02-19 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 308.04 | 0 | 0 | No
2030-02-19 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 48.58 | 0 | 0 | No
2030-02-19 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 348.58 | 0 | 0 | No
2030-02-19 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -339.46 | 510 | 0 | 0 | No
2030-02-19 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | -39.46 | 510 | 0 | 0 | No
2030-02-19 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 260.54 | 510 | 0 | 0 | No
2030-02-19 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-20 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 272.97 | 210 | 300.93 | 0 | 0 | Yes
2030-02-20 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -27.03 | -90 | 0.93 | 0 | 0 | No
2030-02-20 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 272.97 | 210 | 300.93 | 0 | 0 | Yes
2030-02-20 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-20 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-20 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 441.5 | 0 | 0 | Yes
2030-02-20 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 141.5 | 0 | 0 | No
2030-02-20 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -158.5 | 0 | 0 | No
2030-02-20 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 141.5 | 0 | 0 | No
2030-02-20 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -252.03 | 441.5 | 0 | 0 | No
2030-02-20 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 47.97 | 510 | 0 | 0 | No
2030-02-20 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 347.97 | 510 | 0 | 0 | Yes
2030-02-20 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-21 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-02-21 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 245.41 | 0 | 0 | Yes
2030-02-21 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -54.59 | 0 | 0 | Yes
2030-02-21 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -354.59 | 0 | 0 | No
2030-02-21 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -453.5 | 0 | 0 | No
2030-02-21 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -153.5 | 0 | 0 | No
2030-02-21 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 146.5 | 0 | 0 | Yes
2030-02-21 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 446.5 | 0 | 0 | Yes
2030-02-21 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 370.59 | 0 | 0 | Yes
2030-02-22 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 224.24 | 0 | 0 | Yes
2030-02-22 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 251.64 | 0 | 0 | Yes
2030-02-22 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 503.15 | 0 | 0 | Yes
2030-02-22 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 387.69 | 0 | 0 | Yes
2030-02-22 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 135.49 | 0 | 0 | Yes
2030-02-22 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 280.54 | 0 | 0 | Yes
2030-02-22 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-22 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 466.99 | 510 | 0 | 0 | Yes
2030-02-22 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 166.99 | 394.36 | 0 | 0 | Yes
2030-02-22 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -133.01 | 94.36 | 0 | 0 | Yes
2030-02-22 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -395 | -433.01 | -205.64 | 0 | 0 | No
2030-02-22 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -133.01 | 94.36 | 0 | 0 | No
2030-02-22 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 166.99 | 394.36 | 0 | 0 | No
2030-02-22 21:00 | 2030 33% ECP + 1.3 GW Offshore | -387.77 | 505 | 466.99 | 510 | 0 | 0 | No
2030-02-22 22:00 | 2030 33% ECP + 1.3 GW Offshore | 32.23 | 505 | 510 | 510 | 0 | 0 | No
2030-02-22 23:00 | 2030 33% ECP + 1.3 GW Offshore | -387.77 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 | 2030 33% ECP + 1.3 GW Offshore | 32.23 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 01:00 | 2030 33% ECP + 1.3 GW Offshore | 452.23 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 03:00 | 2030 33% ECP + 1.3 GW Offshore | 584.21 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 04:00 | 2030 33% ECP + 1.3 GW Offshore | 164.21 | 505 | 510 | 510 | 0 | 0 | No
2030-02-23 05:00 | 2030 33% ECP + 1.3 GW Offshore | -255.79 | 205 | 210 | 510 | 0 | 0 | No
2030-02-23 06:00 | 2030 33% ECP + 1.3 GW Offshore | -675.79 | -95 | -90 | 346.74 | 0 | 0 | No
2030-02-23 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -395 | -390 | 291.82 | 0 | 0 | No
2030-02-23 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-02-23 09:00 | 2030 33% ECP + 1.3 GW Offshore | -489.56 | -226 | -289.99 | 0 | 0 | 0 | No
2030-02-23 10:00 | 2030 33% ECP + 1.3 GW Offshore | -329.32 | 74 | 10.01 | 300 | 0 | 0 | No
2030-02-23 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 310.01 | 396.78 | 0 | 0 | Yes
2030-02-23 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-23 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-23 14:00 | 2030 33% ECP + 1.3 GW Offshore | -683.92 | 505 | 510 | 510 | 0 | 0 | Yes
2030-02-23 15:00 | 2030 33% ECP + 1.3 GW Offshore | -263.92 | 505 | 510 | 409.19 | 0 | 0 | Yes
2030-02-23 16:00 | 2030 33% ECP + 1.3 GW Offshore | 156.08 | 205 | 396.59 | 109.19 | 0 | 0 | No
2030-02-23 17:00 | 2030 33% ECP + 1.3 GW Offshore | 576.08 | 412.31 | 510 | 245.15 | 0 | 0 | No
2030-02-23 18:00 | 2030 33% ECP + 1.3 GW Offshore | 642 | 412.31 | 510 | 510 | 0 | 0 | No
2030-02-23 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-02-23 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-02-23 21:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | 300 | 510 | 0 | 0 | No
2030-02-23 22:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | 0 | 0 | 510 | 0 | 0 | No
2030-02-23 23:00 | 2030 33% ECP + 1.3 GW Offshore | -290.25 | -300 | -300 | 461.98 | 0 | 0 | No
2030-02-24 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 161.98 | 0 | 0 | No
2030-02-24 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -138.02 | 0 | 0 | No
2030-02-24 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -227.04 | 0 | 0 | Yes
2030-02-24 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-24 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-24 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-24 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-02-24 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-02-24 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 98.77 | 390 | 0 | 0 | Yes
2030-02-24 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -201.23 | 399.08 | 0 | 0 | Yes
2030-02-24 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -300 | -501.23 | 510 | 0 | 0 | Yes
2030-02-24 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-02-24 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 440.33 | 0 | 0 | Yes
2030-02-24 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 349.38 | 0 | 0 | Yes
2030-02-24 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 49.38 | 0 | 0 | Yes
2030-02-24 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -250.62 | 0 | 0 | Yes
2030-02-24 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-02-24 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-24 18:00 | 2030 33% ECP + 1.3 GW Offshore | -686.56 | -526 | -510 | -210 | 0 | 0 | No
2030-02-24 19:00 | 2030 33% ECP + 1.3 GW Offshore | -613.47 | -395 | -390 | 90 | 0 | 0 | No
2030-02-24 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -90 | 45.92 | 0 | 0 | No
2030-02-24 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 210 | 250.17 | 0 | 0 | No
2030-02-24 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-24 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 01:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 02:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 03:00 | 2030 33% ECP + 1.3 GW Offshore | 228.66 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 04:00 | 2030 33% ECP + 1.3 GW Offshore | -191.34 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 05:00 | 2030 33% ECP + 1.3 GW Offshore | -611.34 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-25 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 210 | 220.2 | 0 | 0 | No
2030-02-25 08:00 | 2030 33% ECP + 1.3 GW Offshore | -492.06 | -95 | -90 | 64.53 | 0 | 0 | No
2030-02-25 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -395 | -390 | 340.98 | 0 | 0 | No
2030-02-25 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 64.18 | 0 | 0 | No
2030-02-25 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 187.58 | 0 | 0 | No
2030-02-25 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 176.17 | 0 | 0 | No
2030-02-25 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-02-25 14:00 | 2030 33% ECP + 1.3 GW Offshore | -539.24 | -526 | -510 | -154.45 | 0 | 0 | No
2030-02-25 15:00 | 2030 33% ECP + 1.3 GW Offshore | -119.24 | -526 | -510 | 79.19 | 0 | 0 | No
2030-02-25 16:00 | 2030 33% ECP + 1.3 GW Offshore | -539.24 | -526 | -510 | 244.06 | 0 | 0 | No
2030-02-25 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -55.94 | 0 | 0 | No
2030-02-25 18:00 | 2030 33% ECP + 1.3 GW Offshore | -630.6 | -526 | -510 | 157.87 | 0 | 0 | No
2030-02-25 19:00 | 2030 33% ECP + 1.3 GW Offshore | -414.77 | -526 | -510 | 403.69 | 0 | 0 | No
2030-02-25 20:00 | 2030 33% ECP + 1.3 GW Offshore | -288.02 | -526 | -510 | 403.69 | 0 | 0 | No
2030-02-25 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 394.81 | 0 | 0 | No
2030-02-25 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 291.58 | 0 | 0 | No
2030-02-25 23:00 | 2030 33% ECP + 1.3 GW Offshore | -387.54 | -526 | -510 | 433.52 | 0 | 0 | No
2030-02-26 | 2030 33% ECP + 1.3 GW Offshore | 0 | -226 | -510 | 496.31 | 0 | 0 | No
2030-02-26 01:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -214.99 | 496.31 | 0 | 0 | No
2030-02-26 02:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 85.01 | 510 | 0 | 0 | No
2030-02-26 03:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 385.01 | 510 | 0 | 0 | No
2030-02-26 04:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 74 | 90 | 258.05 | 0 | 0 | No
2030-02-26 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -41.95 | 0 | 0 | No
2030-02-26 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -341.95 | 0 | 0 | No
2030-02-26 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -41.95 | 0 | 0 | No
2030-02-26 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -391.16 | -510 | 258.05 | 0 | 0 | No
2030-02-26 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 224.62 | 0 | 0 | No
2030-02-26 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 61.6 | 0 | 0 | No
2030-02-26 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 13.35 | 0 | 0 | No
2030-02-26 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -173.58 | 0 | 0 | No
2030-02-26 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -266.3 | 0 | 0 | No
2030-02-26 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -220.3 | 0 | 0 | No
2030-02-26 15:00 | 2030 33% ECP + 1.3 GW Offshore | -305.63 | -300 | -300 | -118.27 | 0 | 0 | No
2030-02-26 16:00 | 2030 33% ECP + 1.3 GW Offshore | -260.81 | 0 | 0 | 181.73 | 0 | 0 | No
2030-02-26 17:00 | 2030 33% ECP + 1.3 GW Offshore | -581.01 | 300 | 300 | 481.73 | 0 | 0 | No
2030-02-26 18:00 | 2030 33% ECP + 1.3 GW Offshore | -161.01 | 0 | 0 | 181.73 | 0 | 0 | No
2030-02-26 19:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -300 | -291.33 | -118.27 | 0 | 0 | No
2030-02-26 20:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 8.67 | 181.73 | 0 | 0 | No
2030-02-26 21:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 300 | 308.67 | 481.73 | 0 | 0 | No
2030-02-26 22:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 418.6 | 510 | 510 | 0 | 0 | No
2030-02-26 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 118.6 | 510 | 290.8 | 0 | 0 | No
2030-02-27 | 2030 33% ECP + 1.3 GW Offshore | 700 | 203.53 | 510 | 495.16 | 0 | 0 | No
2030-02-27 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 16.02 | 510 | 366.75 | 0 | 0 | No
2030-02-27 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 210 | 66.75 | 0 | 0 | No
2030-02-27 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 57.01 | 0 | 0 | 0 | No
2030-02-27 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -131.44 | -242.99 | -300 | 0 | 0 | No
2030-02-27 05:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -68.83 | -510 | -238.09 | 0 | 0 | No
2030-02-27 06:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -510 | -236.04 | 0 | 0 | No
2030-02-27 07:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -353.81 | 0 | 0 | 0 | No
2030-02-27 08:00 | 2030 33% ECP + 1.3 GW Offshore | 366.97 | 0 | -210 | 211.47 | 0 | 0 | No
2030-02-27 09:00 | 2030 33% ECP + 1.3 GW Offshore | 51.34 | -300 | -510 | 108.4 | 0 | 0 | No
2030-02-27 10:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -479.67 | -510 | -69.88 | 0 | 0 | No
2030-02-27 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -395 | -390 | -38.04 | 0 | 0 | No
2030-02-27 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -90 | -90 | 0 | 0 | No
2030-02-27 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-02-27 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-02-27 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 210 | 210 | 0 | 0 | No
2030-02-27 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | 34.94 | 0 | 0 | 0 | No
2030-02-27 17:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 300 | 334.94 | 300 | 0 | 0 | No
2030-02-27 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 210 | 200.01 | 0 | 0 | No
2030-02-27 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -195.21 | -90 | -90 | 0 | 0 | No
2030-02-27 20:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 104.79 | 210 | 210 | 0 | 0 | No
2030-02-27 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 404.79 | 510 | 510 | 0 | 0 | No
2030-02-27 22:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 145.92 | 210 | 300 | 0 | 0 | No
2030-02-27 23:00 | 2030 33% ECP + 1.3 GW Offshore | -31.86 | -154.08 | -90 | 0 | 0 | 0 | No
2030-02-28 | 2030 33% ECP + 1.3 GW Offshore | -68.97 | -454.08 | -390 | -72.59 | 0 | 0 | No
2030-02-28 01:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -421.11 | 227.41 | 0 | 0 | No
2030-02-28 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 181.09 | 0 | 0 | No
2030-02-28 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 125.74 | 0 | 0 | No
2030-02-28 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 206.45 | 0 | 0 | No
2030-02-28 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 71.53 | 0 | 0 | No
2030-02-28 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -178.69 | 0 | 0 | No
2030-02-28 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-02-28 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -300 | 0 | 0 | No
2030-02-28 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-02-28 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-02-28 11:00 | 2030 33% ECP + 1.3 GW Offshore | -684.99 | -300 | -510 | 90 | 0 | 0 | No
2030-02-28 12:00 | 2030 33% ECP + 1.3 GW Offshore | -264.99 | 0 | -210 | 390 | 0 | 0 | No
2030-02-28 13:00 | 2030 33% ECP + 1.3 GW Offshore | 105.06 | 300 | 90 | 510 | 0 | 0 | No
2030-02-28 14:00 | 2030 33% ECP + 1.3 GW Offshore | 525.06 | 455.82 | 390 | 510 | 0 | 0 | No
2030-02-28 15:00 | 2030 33% ECP + 1.3 GW Offshore | 561.85 | 155.82 | 90 | 510 | 0 | 0 | No
2030-02-28 16:00 | 2030 33% ECP + 1.3 GW Offshore | 141.85 | -144.18 | -210 | 306.78 | 0 | 0 | No
2030-02-28 17:00 | 2030 33% ECP + 1.3 GW Offshore | -186.84 | -444.18 | -510 | 398.89 | 0 | 0 | No
2030-02-28 18:00 | 2030 33% ECP + 1.3 GW Offshore | -606.84 | -526 | -510 | 510 | 0 | 0 | No
2030-02-28 19:00 | 2030 33% ECP + 1.3 GW Offshore | -687.3 | -526 | -510 | 510 | 0 | 0 | No
2030-02-28 20:00 | 2030 33% ECP + 1.3 GW Offshore | -267.3 | -526 | -510 | 510 | 0 | 0 | No
2030-02-28 21:00 | 2030 33% ECP + 1.3 GW Offshore | 146.98 | -526 | -510 | 510 | 0 | 0 | No
2030-02-28 22:00 | 2030 33% ECP + 1.3 GW Offshore | -273.02 | -226 | -210 | 307.32 | 0 | 0 | No
2030-02-28 23:00 | 2030 33% ECP + 1.3 GW Offshore | -693.02 | 74 | 90 | 316.02 | 0 | 0 | Yes
2030-03-01 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 202.51 | 0 | 0 | Yes
2030-03-01 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 436.99 | 0 | 0 | Yes
2030-03-01 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 348.35 | 0 | 0 | Yes
2030-03-01 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 74.92 | 0 | 0 | Yes
2030-03-01 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 18.44 | 0 | 0 | Yes
2030-03-01 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 118.9 | 0 | 0 | Yes
2030-03-01 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 339.67 | 0 | 0 | Yes
2030-03-01 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 291.32 | 0 | 0 | Yes
2030-03-01 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 422.67 | 0 | 0 | Yes
2030-03-01 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-01 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 510 | 510 | 0 | 0 | Yes
2030-03-01 17:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | 510 | 510 | 0 | 0 | No
2030-03-01 18:00 | 2030 33% ECP + 1.3 GW Offshore | -313.38 | 0 | 510 | 504.54 | 0 | 0 | No
2030-03-01 19:00 | 2030 33% ECP + 1.3 GW Offshore | 106.62 | 0 | 510 | 510 | 0 | 0 | No
2030-03-01 20:00 | 2030 33% ECP + 1.3 GW Offshore | 526.62 | 0 | 510 | 510 | 0 | 0 | No
2030-03-01 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 210 | 0 | 0 | No
2030-03-01 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 286.04 | 210 | 0 | 0 | No
2030-03-01 23:00 | 2030 33% ECP + 1.3 GW Offshore | 675.74 | 205 | 210 | 510 | 0 | 0 | No
2030-03-02 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-02 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-02 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-02 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 405.25 | 510 | 0 | 0 | No
2030-03-02 04:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 205 | 105.25 | 232.29 | 0 | 0 | No
2030-03-02 05:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -95 | -194.75 | 45.48 | 0 | 0 | No
2030-03-02 06:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | -185.56 | -494.75 | -21.19 | 0 | 0 | No
2030-03-02 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -236.96 | -510 | -299.27 | 0 | 0 | No
2030-03-02 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -195.08 | 0 | 0 | No
2030-03-02 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 104.92 | 0 | 0 | No
2030-03-02 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 188.43 | 0 | 0 | No
2030-03-02 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -111.57 | 0 | 0 | No
2030-03-02 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -411.57 | 0 | 0 | Yes
2030-03-02 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -403.89 | 0 | 0 | Yes
2030-03-02 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -217.3 | 0 | 0 | Yes
2030-03-02 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -340.02 | 0 | 0 | No
2030-03-02 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -40.02 | 0 | 0 | No
2030-03-02 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 194.25 | 0 | 0 | No
2030-03-02 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -51.82 | 0 | 0 | No
2030-03-02 19:00 | 2030 33% ECP + 1.3 GW Offshore | -604.84 | -526 | -510 | 248.18 | 0 | 0 | No
2030-03-02 20:00 | 2030 33% ECP + 1.3 GW Offshore | -184.84 | -526 | -510 | 343.92 | 0 | 0 | No
2030-03-02 21:00 | 2030 33% ECP + 1.3 GW Offshore | -138.34 | -526 | -510 | 439.46 | 0 | 0 | No
2030-03-02 22:00 | 2030 33% ECP + 1.3 GW Offshore | -558.34 | -526 | -510 | 405.95 | 0 | 0 | No
2030-03-02 23:00 | 2030 33% ECP + 1.3 GW Offshore | -597.11 | -526 | -510 | 217.81 | 0 | 0 | No
2030-03-03 | 2030 33% ECP + 1.3 GW Offshore | -260.65 | -300 | -429.17 | 187.2 | 0 | 0 | No
2030-03-03 01:00 | 2030 33% ECP + 1.3 GW Offshore | 159.35 | 0 | -129.17 | 487.2 | 0 | 0 | No
2030-03-03 02:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 278.07 | 0 | 510 | 0 | 0 | No
2030-03-03 03:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | -21.93 | -300 | 210 | 0 | 0 | No
2030-03-03 04:00 | 2030 33% ECP + 1.3 GW Offshore | -664.42 | -206.14 | -510 | -17.45 | 0 | 0 | No
2030-03-03 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -305.25 | -510 | -317.45 | 0 | 0 | No
2030-03-03 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -335.05 | 0 | 0 | No
2030-03-03 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -382.8 | 0 | 0 | No
2030-03-03 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-03 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-03-03 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -424.92 | 0 | 0 | No
2030-03-03 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-03 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-03 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -456.78 | 0 | 0 | No
2030-03-03 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -456.78 | 0 | 0 | No
2030-03-03 15:00 | 2030 33% ECP + 1.3 GW Offshore | -478.55 | -526 | -510 | -156.78 | 0 | 0 | No
2030-03-03 16:00 | 2030 33% ECP + 1.3 GW Offshore | -58.55 | -226 | -248.31 | 0 | 0 | 0 | No
2030-03-03 17:00 | 2030 33% ECP + 1.3 GW Offshore | 361.45 | 0 | -43.16 | 0 | 0 | 0 | No
2030-03-03 18:00 | 2030 33% ECP + 1.3 GW Offshore | -58.55 | -300 | -343.16 | -300 | 0 | 0 | No
2030-03-03 19:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -95 | -90 | -90 | 0 | 0 | No
2030-03-03 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-03-03 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-03 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 510 | 509.14 | 0 | 0 | No
2030-03-03 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 506.66 | 209.14 | 0 | 0 | No
2030-03-04 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 510 | 509.14 | 0 | 0 | No
2030-03-04 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-04 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 458.46 | 510 | 510 | 0 | 0 | No
2030-03-04 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-04 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-04 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-04 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-03-04 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 510 | 510 | 0 | 0 | No
2030-03-04 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-03-04 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 339.23 | 331.88 | 0 | 0 | No
2030-03-04 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 56.94 | 39.23 | 299.64 | 0 | 0 | No
2030-03-04 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -243.06 | -260.77 | -0.36 | 0 | 0 | No
2030-03-04 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -300.36 | 0 | 0 | No
2030-03-04 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -462.53 | -510 | -303 | 0 | 0 | No
2030-03-04 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -246.73 | -510 | -308.94 | 0 | 0 | No
2030-03-04 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -300 | -288.13 | 0 | 0 | No
2030-03-04 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 3.14 | 0 | 0 | 0 | 0 | No
2030-03-04 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -296.86 | -300 | -300 | 0 | 0 | No
2030-03-04 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-04 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -481.73 | -510 | 0 | 0 | No
2030-03-04 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -181.73 | -210 | 0 | 0 | No
2030-03-04 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 118.27 | 90 | 0 | 0 | No
2030-03-04 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 489.8 | 418.27 | 0 | 0 | 0 | No
2030-03-04 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 291.4 | 510 | 0 | 0 | 0 | No
2030-03-05 | 2030 33% ECP + 1.3 GW Offshore | 700 | 504.56 | 510 | 0 | 0 | 0 | No
2030-03-05 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 278 | 14.28 | 0 | 0 | No
2030-03-05 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 314.28 | 0 | 0 | No
2030-03-05 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-05 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 348.74 | 0 | 0 | No
2030-03-05 05:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 300 | 327.88 | 48.74 | 0 | 0 | No
2030-03-05 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 27.88 | -49.71 | 0 | 0 | No
2030-03-05 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | -15.29 | 0 | 0 | No
2030-03-05 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-03-05 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -194.25 | 0 | 0 | 0 | No
2030-03-05 10:00 | 2030 33% ECP + 1.3 GW Offshore | 345.72 | 0 | 0 | 0 | 0 | 0 | No
2030-03-05 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 300 | 300 | 0 | 0 | No
2030-03-05 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 472.86 | 510 | 510 | 0 | 0 | No
2030-03-05 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 285.87 | 510 | 510 | 0 | 0 | No
2030-03-05 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-05 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 390 | 390 | 0 | 0 | No
2030-03-05 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 101.5 | 90 | 90 | 0 | 0 | No
2030-03-05 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -198.5 | -210 | -210 | 0 | 0 | No
2030-03-05 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -498.5 | -510 | -510 | 0 | 0 | No
2030-03-05 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-05 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-03-05 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 2.04 | 90 | 71.1 | 0 | 0 | No
2030-03-05 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95.72 | -210 | -228.9 | 0 | 0 | No
2030-03-05 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 74.87 | 0 | 0 | 0 | No
2030-03-06 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 169.9 | 102.1 | 0 | 0 | No
2030-03-06 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -35.1 | 72.08 | 0 | 0 | No
2030-03-06 02:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -104.27 | -335.1 | 0 | 0 | 0 | No
2030-03-06 03:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 0 | -72.45 | 0 | 0 | 0 | No
2030-03-06 04:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | -349.18 | 0 | 0 | 0 | No
2030-03-06 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -384.33 | -186.31 | 0 | 0 | No
2030-03-06 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -486.31 | 0 | 0 | No
2030-03-06 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -420.13 | 0 | 0 | No
2030-03-06 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -275.57 | 0 | 0 | No
2030-03-06 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -321.33 | 0 | 0 | No
2030-03-06 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -228.72 | 0 | 0 | No
2030-03-06 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -228.72 | 0 | 0 | No
2030-03-06 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -232.09 | 0 | 0 | No
2030-03-06 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 67.91 | 0 | 0 | No
2030-03-06 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -74.95 | 0 | 0 | No
2030-03-06 16:00 | 2030 33% ECP + 1.3 GW Offshore | -302.72 | -526 | -510 | -374.95 | 0 | 0 | No
2030-03-06 17:00 | 2030 33% ECP + 1.3 GW Offshore | 117.28 | -226 | -210 | -210 | 0 | 0 | No
2030-03-06 18:00 | 2030 33% ECP + 1.3 GW Offshore | 5.59 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 19:00 | 2030 33% ECP + 1.3 GW Offshore | 425.59 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-06 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-03-06 22:00 | 2030 33% ECP + 1.3 GW Offshore | 468.44 | 0 | -510 | -291.79 | 0 | 0 | No
2030-03-06 23:00 | 2030 33% ECP + 1.3 GW Offshore | 443.93 | -105.63 | -210 | 8.21 | 0 | 0 | No
2030-03-07 | 2030 33% ECP + 1.3 GW Offshore | 23.93 | -405.63 | -510 | -275.21 | 0 | 0 | No
2030-03-07 01:00 | 2030 33% ECP + 1.3 GW Offshore | -250.51 | -395.94 | -510 | -88.34 | 0 | 0 | No
2030-03-07 02:00 | 2030 33% ECP + 1.3 GW Offshore | -670.51 | -526 | -510 | 11.74 | 0 | 0 | No
2030-03-07 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -25.81 | 0 | 0 | No
2030-03-07 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -197.11 | 0 | 0 | No
2030-03-07 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 102.89 | 0 | 0 | No
2030-03-07 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 16.6 | 0 | 0 | No
2030-03-07 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -12.83 | 0 | 0 | No
2030-03-07 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 6.39 | 0 | 0 | No
2030-03-07 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -129.86 | 0 | 0 | No
2030-03-07 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -429.86 | 0 | 0 | Yes
2030-03-07 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -129.86 | 0 | 0 | Yes
2030-03-07 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 170.14 | 0 | 0 | Yes
2030-03-07 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 470.14 | 0 | 0 | Yes
2030-03-07 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-07 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-03-07 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-03-07 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-03-07 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-07 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-07 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-07 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-03-07 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-03-07 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-03-08 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-08 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-08 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-08 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-08 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-08 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-08 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-08 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-03-08 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-03-08 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 170.04 | 0 | 0 | No
2030-03-08 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 470.04 | 0 | 0 | Yes
2030-03-08 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-08 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-08 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-08 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-08 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-03-08 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 219.31 | 0 | 0 | Yes
2030-03-08 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-08 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-08 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-08 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-08 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-08 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 455.16 | 0 | 0 | No
2030-03-08 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 272.9 | 0 | 0 | Yes
2030-03-09 | 2030 33% ECP + 1.3 GW Offshore | -458.55 | 0 | 0 | 52.07 | 0 | 0 | No
2030-03-09 01:00 | 2030 33% ECP + 1.3 GW Offshore | -458.55 | 0 | 0 | 324.91 | 0 | 0 | No
2030-03-09 02:00 | 2030 33% ECP + 1.3 GW Offshore | -38.55 | 205 | 300 | 471.64 | 0 | 0 | No
2030-03-09 03:00 | 2030 33% ECP + 1.3 GW Offshore | -458.55 | 505 | 510 | 510 | 0 | 0 | No
2030-03-09 04:00 | 2030 33% ECP + 1.3 GW Offshore | -458.55 | 374 | 367.03 | 510 | 0 | 0 | No
2030-03-09 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 67.03 | 210 | 0 | 0 | No
2030-03-09 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -232.97 | -90 | 0 | 0 | No
2030-03-09 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 175.61 | 0 | 0 | No
2030-03-09 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 80.13 | 0 | 0 | No
2030-03-09 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 380.13 | 0 | 0 | No
2030-03-09 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 90 | 0 | 0 | No
2030-03-09 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-03-09 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-09 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -290.39 | 0 | 0 | Yes
2030-03-09 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -460.83 | -510 | 9.61 | 0 | 0 | Yes
2030-03-09 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 276.04 | 0 | 0 | Yes
2030-03-09 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 276.04 | 0 | 0 | Yes
2030-03-09 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 372.04 | 0 | 0 | Yes
2030-03-09 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 72.04 | 0 | 0 | Yes
2030-03-09 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -18.99 | 0 | 0 | No
2030-03-09 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -318.99 | 0 | 0 | No
2030-03-09 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -18.99 | 0 | 0 | Yes
2030-03-09 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 281.01 | 0 | 0 | Yes
2030-03-09 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 393.06 | 0 | 0 | Yes
2030-03-10 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 509.92 | 0 | 0 | Yes
2030-03-10 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 317.83 | 0 | 0 | Yes
2030-03-10 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 402.29 | 0 | 0 | Yes
2030-03-10 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 455.02 | 0 | 0 | Yes
2030-03-10 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 189.24 | 0 | 0 | Yes
2030-03-10 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-03-10 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-03-10 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 69.16 | 0 | 0 | Yes
2030-03-10 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 155.65 | 0 | 0 | Yes
2030-03-10 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 455.65 | 0 | 0 | Yes
2030-03-10 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 239.4 | 0 | 0 | Yes
2030-03-10 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-10 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 18:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 381.06 | 510 | 510 | 0 | 0 | No
2030-03-10 19:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 20:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 21:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 22:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-10 23:00 | 2030 33% ECP + 1.3 GW Offshore | -358.86 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-11 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-11 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-11 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-11 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-03-11 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-03-11 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 281.24 | 0 | 0 | No
2030-03-11 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -311.49 | -390 | 510 | 0 | 0 | No
2030-03-11 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -11.49 | -90 | 510 | 0 | 0 | No
2030-03-11 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 288.51 | 210 | 510 | 0 | 0 | Yes
2030-03-11 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-12 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-03-12 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-03-12 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-03-12 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-12 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-12 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-12 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | No
2030-03-12 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | No
2030-03-12 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-03-13 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 01:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 02:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 04:00 | 2030 33% ECP + 1.3 GW Offshore | 376.89 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 05:00 | 2030 33% ECP + 1.3 GW Offshore | -43.11 | 505 | 510 | 510 | 0 | 0 | No
2030-03-13 06:00 | 2030 33% ECP + 1.3 GW Offshore | -463.11 | 205 | 210 | 210 | 0 | 0 | No
2030-03-13 07:00 | 2030 33% ECP + 1.3 GW Offshore | -43.11 | 0 | 510 | 0 | 0 | 0 | No
2030-03-13 08:00 | 2030 33% ECP + 1.3 GW Offshore | -315.4 | 0 | 299.6 | 0 | 0 | 0 | No
2030-03-13 09:00 | 2030 33% ECP + 1.3 GW Offshore | 104.6 | 0 | 0 | 0 | 0 | 0 | No
2030-03-13 10:00 | 2030 33% ECP + 1.3 GW Offshore | -66.1 | -226 | -210 | -126.04 | 0 | 0 | No
2030-03-13 11:00 | 2030 33% ECP + 1.3 GW Offshore | -486.1 | -526 | -510 | -426.04 | 0 | 0 | No
2030-03-13 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 15:00 | 2030 33% ECP + 1.3 GW Offshore | -630.45 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 16:00 | 2030 33% ECP + 1.3 GW Offshore | -620.03 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 20:00 | 2030 33% ECP + 1.3 GW Offshore | -556.12 | -526 | -510 | -510 | 0 | 0 | No
2030-03-13 21:00 | 2030 33% ECP + 1.3 GW Offshore | -136.12 | -226 | -210 | -210 | 0 | 0 | No
2030-03-13 22:00 | 2030 33% ECP + 1.3 GW Offshore | 283.88 | 0 | 37.28 | 0 | 0 | 0 | No
2030-03-13 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -262.72 | -122.08 | 0 | 0 | No
2030-03-14 | 2030 33% ECP + 1.3 GW Offshore | 437.52 | -124.17 | -90 | -90 | 0 | 0 | No
2030-03-14 01:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 175.83 | 210 | 210 | 0 | 0 | No
2030-03-14 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 475.83 | 510 | 510 | 0 | 0 | No
2030-03-14 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-14 04:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-03-14 05:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 418.66 | 390 | 510 | 0 | 0 | No
2030-03-14 06:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 118.66 | 90 | 230.78 | 0 | 0 | No
2030-03-14 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -181.34 | -210 | 0 | 0 | 0 | No
2030-03-14 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -481.34 | -510 | 210 | 0 | 0 | No
2030-03-14 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-03-14 10:00 | 2030 33% ECP + 1.3 GW Offshore | -634.29 | -526 | -510 | 243.67 | 0 | 0 | No
2030-03-14 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -305.73 | -510 | 355.58 | 0 | 0 | Yes
2030-03-14 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -5.73 | -210 | 510 | 0 | 0 | Yes
2030-03-14 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 294.27 | 90 | 510 | 0 | 0 | Yes
2030-03-14 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 482.48 | 0 | 0 | Yes
2030-03-14 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 182.48 | 0 | 0 | Yes
2030-03-14 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -117.52 | 0 | 0 | Yes
2030-03-14 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -417.52 | 0 | 0 | No
2030-03-14 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -178.74 | 0 | 0 | No
2030-03-14 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 121.26 | 0 | 0 | No
2030-03-14 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 421.26 | 0 | 0 | No
2030-03-14 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-03-14 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-14 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-15 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-15 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-03-15 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-03-15 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-03-15 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-15 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -300 | -346.37 | -210 | 0 | 0 | No
2030-03-15 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -46.37 | 90 | 0 | 0 | No
2030-03-15 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 210 | 143.85 | 0 | 0 | No
2030-03-15 20:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | 510 | 443.85 | 0 | 0 | No
2030-03-15 21:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 0 | 510 | 510 | 0 | 0 | No
2030-03-15 22:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 0 | 510 | 510 | 0 | 0 | No
2030-03-15 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-16 | 2030 33% ECP + 1.3 GW Offshore | 700 | 16.67 | 510 | 510 | 0 | 0 | No
2030-03-16 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-03-16 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 424.14 | 510 | 0 | 0 | No
2030-03-16 03:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 101.66 | 193.82 | 510 | 0 | 0 | No
2030-03-16 04:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | 0 | -106.18 | 233.66 | 0 | 0 | No
2030-03-16 05:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | -300 | -406.18 | -66.34 | 0 | 0 | No
2030-03-16 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -366.34 | 0 | 0 | No
2030-03-16 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-16 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-16 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -276.39 | 0 | 0 | Yes
2030-03-16 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -371.54 | 0 | 0 | Yes
2030-03-16 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -210 | 0 | 0 | Yes
2030-03-16 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-03-16 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -418.51 | 0 | 0 | Yes
2030-03-16 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -236.22 | 0 | 0 | Yes
2030-03-16 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -46.67 | 0 | 0 | No
2030-03-16 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 253.33 | 0 | 0 | No
2030-03-16 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-03-16 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-16 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-17 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-17 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 210 | 510 | 0 | 0 | Yes
2030-03-17 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -90 | 339.79 | 0 | 0 | No
2030-03-17 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 210 | 510 | 0 | 0 | No
2030-03-17 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 21:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 22:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | 505 | 510 | 510 | 0 | 0 | No
2030-03-17 23:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 06:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 07:00 | 2030 33% ECP + 1.3 GW Offshore | 407.07 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-18 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 374 | 499.63 | 510 | 0 | 0 | No
2030-03-18 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 74 | 199.63 | 510 | 0 | 0 | No
2030-03-18 11:00 | 2030 33% ECP + 1.3 GW Offshore | 480.36 | -226 | -100.37 | 313.34 | 0 | 0 | No
2030-03-18 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -400.37 | 86.51 | 0 | 0 | No
2030-03-18 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -362.2 | -510 | 155.32 | 0 | 0 | No
2030-03-18 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -92.92 | -390 | 78.14 | 0 | 0 | No
2030-03-18 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -280.85 | -90 | 0 | 0 | 0 | No
2030-03-18 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 210 | 300 | 0 | 0 | No
2030-03-18 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-18 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-18 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 142.4 | 510 | 510 | 0 | 0 | No
2030-03-18 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 442.4 | 510 | 510 | 0 | 0 | No
2030-03-18 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 423.09 | 510 | 510 | 0 | 0 | No
2030-03-18 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 123.09 | 510 | 510 | 0 | 0 | No
2030-03-18 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-03-19 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-03-19 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 408.25 | 510 | 510 | 0 | 0 | No
2030-03-19 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 108.25 | 510 | 510 | 0 | 0 | No
2030-03-19 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 408.25 | 510 | 510 | 0 | 0 | No
2030-03-19 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 408.25 | 510 | 510 | 0 | 0 | No
2030-03-19 05:00 | 2030 33% ECP + 1.3 GW Offshore | 445.71 | 108.25 | 390 | 501.55 | 0 | 0 | No
2030-03-19 06:00 | 2030 33% ECP + 1.3 GW Offshore | 25.71 | 0 | 90 | 201.55 | 0 | 0 | No
2030-03-19 07:00 | 2030 33% ECP + 1.3 GW Offshore | -394.29 | -300 | -210 | -98.45 | 0 | 0 | No
2030-03-19 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -203.86 | 0 | 0 | No
2030-03-19 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -168.42 | 0 | 0 | No
2030-03-19 10:00 | 2030 33% ECP + 1.3 GW Offshore | -284.31 | -526 | -510 | -432.98 | 0 | 0 | No
2030-03-19 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -303.3 | 0 | 0 | No
2030-03-19 12:00 | 2030 33% ECP + 1.3 GW Offshore | -467.45 | -526 | -510 | -510 | 0 | 0 | No
2030-03-19 13:00 | 2030 33% ECP + 1.3 GW Offshore | -87.13 | -526 | -510 | -432.95 | 0 | 0 | No
2030-03-19 14:00 | 2030 33% ECP + 1.3 GW Offshore | -98.23 | -526 | -510 | -466.32 | 0 | 0 | No
2030-03-19 15:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-03-19 16:00 | 2030 33% ECP + 1.3 GW Offshore | 174.94 | -526 | -510 | -510 | 0 | 0 | No
2030-03-19 17:00 | 2030 33% ECP + 1.3 GW Offshore | -194.59 | -526 | -510 | -413.63 | 0 | 0 | No
2030-03-19 18:00 | 2030 33% ECP + 1.3 GW Offshore | -261.84 | -526 | -510 | -113.63 | 0 | 0 | No
2030-03-19 19:00 | 2030 33% ECP + 1.3 GW Offshore | 158.16 | -526 | -510 | -82.96 | 0 | 0 | No
2030-03-19 20:00 | 2030 33% ECP + 1.3 GW Offshore | 578.16 | -526 | -510 | -57.13 | 0 | 0 | No
2030-03-19 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -426.82 | 110.63 | 0 | 0 | No
2030-03-19 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -113.53 | -510 | -131.23 | 0 | 0 | No
2030-03-19 23:00 | 2030 33% ECP + 1.3 GW Offshore | 591.09 | -413.53 | -510 | -21.44 | 0 | 0 | No
2030-03-20 | 2030 33% ECP + 1.3 GW Offshore | 459.83 | -526 | -510 | -232.97 | 0 | 0 | No
2030-03-20 01:00 | 2030 33% ECP + 1.3 GW Offshore | 653.76 | -526 | -510 | -214.96 | 0 | 0 | No
2030-03-20 02:00 | 2030 33% ECP + 1.3 GW Offshore | 691.64 | -526 | -510 | -204.57 | 0 | 0 | No
2030-03-20 03:00 | 2030 33% ECP + 1.3 GW Offshore | 454.35 | -526 | -510 | -70.91 | 0 | 0 | No
2030-03-20 04:00 | 2030 33% ECP + 1.3 GW Offshore | 322.59 | -526 | -510 | -65.99 | 0 | 0 | No
2030-03-20 05:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -143.97 | 0 | 0 | No
2030-03-20 06:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -55.98 | 0 | 0 | No
2030-03-20 07:00 | 2030 33% ECP + 1.3 GW Offshore | 131.12 | -502.15 | -510 | 51.39 | 0 | 0 | No
2030-03-20 08:00 | 2030 33% ECP + 1.3 GW Offshore | -288.88 | -526 | -510 | 139.96 | 0 | 0 | No
2030-03-20 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 66.14 | 0 | 0 | No
2030-03-20 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 46.67 | 0 | 0 | No
2030-03-20 11:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -69.75 | 0 | 0 | No
2030-03-20 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -24.66 | 0 | 0 | No
2030-03-20 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -99.44 | 0 | 0 | No
2030-03-20 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -94.07 | 0 | 0 | No
2030-03-20 15:00 | 2030 33% ECP + 1.3 GW Offshore | -315.68 | -526 | -510 | -33.16 | 0 | 0 | No
2030-03-20 16:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 199.85 | 0 | 0 | No
2030-03-20 17:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | 256.25 | 0 | 0 | No
2030-03-20 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -499.99 | -510 | 407.49 | 0 | 0 | No
2030-03-20 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 269.68 | 0 | 0 | No
2030-03-20 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -510.14 | -510 | 69.99 | 0 | 0 | No
2030-03-20 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -520.62 | -510 | -30.71 | 0 | 0 | No
2030-03-20 22:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -300 | -510 | -123.54 | 0 | 0 | No
2030-03-20 23:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | 0 | -290.38 | 0 | 0 | 0 | No
2030-03-21 | 2030 33% ECP + 1.3 GW Offshore | -560 | 0 | -441.97 | 0 | 0 | 0 | No
2030-03-21 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -425.76 | -90 | 0 | 0 | No
2030-03-21 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | -125.76 | 210 | 0 | 0 | No
2030-03-21 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 174.24 | 510 | 0 | 0 | No
2030-03-21 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 90 | 252.07 | 0 | 0 | No
2030-03-21 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | -210 | -47.93 | 0 | 0 | No
2030-03-21 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -510 | -347.93 | 0 | 0 | No
2030-03-21 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-21 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-03-21 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-03-21 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 21.12 | 0 | 0 | 0 | Yes
2030-03-21 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 321.12 | 300 | 0 | 0 | Yes
2030-03-21 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-21 15:00 | 2030 33% ECP + 1.3 GW Offshore | -297.07 | 300 | 510 | 266.02 | 0 | 0 | No
2030-03-21 16:00 | 2030 33% ECP + 1.3 GW Offshore | 122.93 | 0 | 210 | -33.98 | 0 | 0 | No
2030-03-21 17:00 | 2030 33% ECP + 1.3 GW Offshore | 542.93 | 0 | 246.1 | 23.38 | 0 | 0 | No
2030-03-21 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 405.83 | 323.38 | 0 | 0 | No
2030-03-21 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 405.83 | 465.71 | 0 | 0 | No
2030-03-21 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 405.83 | 435.92 | 0 | 0 | No
2030-03-21 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 232.01 | 510 | 510 | 0 | 0 | No
2030-03-21 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 459.63 | 483.56 | 0 | 0 | No
2030-03-21 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 05:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 205 | 210 | 265.01 | 0 | 0 | No
2030-03-22 06:00 | 2030 33% ECP + 1.3 GW Offshore | 109.45 | -95 | -90 | 424.27 | 0 | 0 | No
2030-03-22 07:00 | 2030 33% ECP + 1.3 GW Offshore | 529.45 | -395 | -390 | 438.49 | 0 | 0 | No
2030-03-22 08:00 | 2030 33% ECP + 1.3 GW Offshore | 384.74 | -526 | -510 | 420.54 | 0 | 0 | No
2030-03-22 09:00 | 2030 33% ECP + 1.3 GW Offshore | 533.79 | -526 | -510 | 425.58 | 0 | 0 | No
2030-03-22 10:00 | 2030 33% ECP + 1.3 GW Offshore | 113.79 | -526 | -510 | 362.07 | 0 | 0 | No
2030-03-22 11:00 | 2030 33% ECP + 1.3 GW Offshore | -306.21 | -526 | -510 | 243.59 | 0 | 0 | No
2030-03-22 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 83.19 | 0 | 0 | No
2030-03-22 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 24.27 | 0 | 0 | No
2030-03-22 14:00 | 2030 33% ECP + 1.3 GW Offshore | -368.44 | -526 | -510 | -55.98 | 0 | 0 | No
2030-03-22 15:00 | 2030 33% ECP + 1.3 GW Offshore | 51.56 | -526 | -510 | -216.48 | 0 | 0 | No
2030-03-22 16:00 | 2030 33% ECP + 1.3 GW Offshore | 471.56 | -526 | -510 | -49.85 | 0 | 0 | No
2030-03-22 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -71.27 | 0 | 0 | No
2030-03-22 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -257.61 | -510 | 228.73 | 0 | 0 | No
2030-03-22 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -390 | 405.89 | 0 | 0 | No
2030-03-22 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -90 | 346.09 | 0 | 0 | No
2030-03-22 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-03-22 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-22 23:00 | 2030 33% ECP + 1.3 GW Offshore | 379.93 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 02:00 | 2030 33% ECP + 1.3 GW Offshore | 612.52 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 03:00 | 2030 33% ECP + 1.3 GW Offshore | 192.52 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 04:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 05:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-03-23 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 248.69 | 210 | 210 | 0 | 0 | No
2030-03-23 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -51.31 | -90 | -90 | 0 | 0 | No
2030-03-23 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -351.31 | -390 | -390 | 0 | 0 | No
2030-03-23 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -51.31 | -90 | -90 | 0 | 0 | No
2030-03-23 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 248.69 | 210 | 210 | 0 | 0 | Yes
2030-03-23 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-23 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-23 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-23 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-03-23 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 90 | 450.61 | 0 | 0 | Yes
2030-03-23 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -210 | 150.61 | 0 | 0 | Yes
2030-03-23 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -247.38 | -510 | 0 | 0 | 0 | No
2030-03-23 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -42.11 | 0 | 0 | No
2030-03-23 19:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -8.03 | 0 | 0 | No
2030-03-23 20:00 | 2030 33% ECP + 1.3 GW Offshore | -98.97 | -300 | -300 | 184.09 | 0 | 0 | No
2030-03-23 21:00 | 2030 33% ECP + 1.3 GW Offshore | 7.63 | 0 | 0 | 484.09 | 0 | 0 | No
2030-03-23 22:00 | 2030 33% ECP + 1.3 GW Offshore | -412.37 | 205 | 297.87 | 210 | 0 | 0 | No
2030-03-23 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 420.86 | 0 | 0 | Yes
2030-03-24 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 324.54 | 272.69 | 0 | 0 | Yes
2030-03-24 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 24.54 | -27.31 | 0 | 0 | Yes
2030-03-24 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -275.46 | -312.87 | 0 | 0 | No
2030-03-24 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 24.54 | -12.87 | 0 | 0 | No
2030-03-24 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 324.54 | 287.13 | 0 | 0 | Yes
2030-03-24 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-24 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-25 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 01:00 | 2030 33% ECP + 1.3 GW Offshore | -508.65 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 03:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 04:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-03-25 05:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 300 | 252.91 | 510 | 0 | 0 | No
2030-03-25 06:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | -47.09 | 210 | 0 | 0 | No
2030-03-25 07:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -300 | -347.09 | -62.36 | 0 | 0 | No
2030-03-25 08:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -41.85 | 0 | 0 | No
2030-03-25 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 227.4 | 0 | 0 | No
2030-03-25 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 135.61 | 0 | 0 | No
2030-03-25 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -148.77 | 0 | 0 | No
2030-03-25 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -192.38 | 0 | 0 | No
2030-03-25 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -101.99 | 0 | 0 | No
2030-03-25 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 6.11 | 0 | 0 | No
2030-03-25 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 64.86 | 0 | 0 | No
2030-03-25 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -503 | -510 | 149.86 | 0 | 0 | No
2030-03-25 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -150.14 | 0 | 0 | No
2030-03-25 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -412.89 | -504.49 | -371.51 | 0 | 0 | No
2030-03-25 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -112.89 | -204.49 | -71.51 | 0 | 0 | No
2030-03-25 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 187.11 | 95.51 | 210 | 0 | 0 | No
2030-03-25 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 487.11 | 395.51 | 510 | 0 | 0 | No
2030-03-25 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 187.11 | 510 | 510 | 0 | 0 | No
2030-03-25 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 361.81 | 0 | 0 | No
2030-03-26 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 192.85 | 0 | 0 | No
2030-03-26 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-03-26 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 217.37 | 0 | 0 | 0 | No
2030-03-26 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 356.67 | 0 | 0 | 0 | No
2030-03-26 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 56.67 | 0 | 0 | 0 | No
2030-03-26 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-03-26 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -201.11 | 0 | 0 | 0 | No
2030-03-26 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -501.11 | -204.86 | 0 | 0 | No
2030-03-26 08:00 | 2030 33% ECP + 1.3 GW Offshore | 664.47 | -526 | -510 | -313.72 | 0 | 0 | No
2030-03-26 09:00 | 2030 33% ECP + 1.3 GW Offshore | 244.47 | -526 | -510 | -13.72 | 0 | 0 | No
2030-03-26 10:00 | 2030 33% ECP + 1.3 GW Offshore | -6.66 | -526 | -510 | 0 | 0 | 0 | No
2030-03-26 11:00 | 2030 33% ECP + 1.3 GW Offshore | 413.34 | -526 | -510 | 0 | 0 | 0 | No
2030-03-26 12:00 | 2030 33% ECP + 1.3 GW Offshore | 413.34 | -526 | -510 | 0 | 0 | 0 | No
2030-03-26 13:00 | 2030 33% ECP + 1.3 GW Offshore | -6.66 | -526 | -510 | 3.24 | 0 | 0 | No
2030-03-26 14:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-03-26 15:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | 0 | 0 | 0 | No
2030-03-26 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 66.86 | 0 | 0 | No
2030-03-26 17:00 | 2030 33% ECP + 1.3 GW Offshore | 673.73 | -526 | -510 | -167.06 | 0 | 0 | No
2030-03-26 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -216.41 | 0 | 0 | No
2030-03-26 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -358.07 | -510 | 0 | 0 | 0 | No
2030-03-26 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -85.71 | 0 | 0 | No
2030-03-26 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -293.11 | -377.82 | -65.49 | 0 | 0 | No
2030-03-26 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -77.82 | 75.2 | 0 | 0 | No
2030-03-26 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -142.13 | 0 | 0 | 0 | No
2030-03-27 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -329.52 | 0 | 0 | 0 | No
2030-03-27 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -51.2 | -510 | -184.32 | 0 | 0 | No
2030-03-27 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -184.21 | 0 | 0 | No
2030-03-27 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -9.6 | -510 | -231.96 | 0 | 0 | No
2030-03-27 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -77.45 | -510 | -260.54 | 0 | 0 | No
2030-03-27 05:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | 0 | -510 | -381.38 | 0 | 0 | No
2030-03-27 06:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -510 | -130.53 | 0 | 0 | No
2030-03-27 07:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -510 | -51.76 | 0 | 0 | No
2030-03-27 08:00 | 2030 33% ECP + 1.3 GW Offshore | -176.12 | -226 | -292.23 | 0 | 0 | 0 | No
2030-03-27 09:00 | 2030 33% ECP + 1.3 GW Offshore | -596.12 | -526 | -510 | -7.75 | 0 | 0 | No
2030-03-27 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -48.58 | 0 | 0 | No
2030-03-27 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -73.95 | 0 | 0 | No
2030-03-27 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -207.51 | 0 | 0 | No
2030-03-27 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -187.39 | 0 | 0 | No
2030-03-27 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -221.79 | 0 | 0 | No
2030-03-27 15:00 | 2030 33% ECP + 1.3 GW Offshore | -504.3 | -526 | -510 | -146.08 | 0 | 0 | No
2030-03-27 16:00 | 2030 33% ECP + 1.3 GW Offshore | -84.3 | -526 | -510 | -35.02 | 0 | 0 | No
2030-03-27 17:00 | 2030 33% ECP + 1.3 GW Offshore | 151.03 | -526 | -510 | 62.85 | 0 | 0 | No
2030-03-27 18:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -26.11 | 0 | 0 | No
2030-03-27 19:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -117.58 | 0 | 0 | No
2030-03-27 20:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | 90 | 0 | 0 | No
2030-03-27 21:00 | 2030 33% ECP + 1.3 GW Offshore | 628.31 | -417.91 | -510 | -210 | 0 | 0 | No
2030-03-27 22:00 | 2030 33% ECP + 1.3 GW Offshore | 208.31 | -117.91 | -210 | -510 | 0 | 0 | No
2030-03-27 23:00 | 2030 33% ECP + 1.3 GW Offshore | 628.31 | 182.09 | 90 | -331.22 | 0 | 0 | No
2030-03-28 | 2030 33% ECP + 1.3 GW Offshore | 208.31 | 374.92 | 390 | -90 | 0 | 0 | No
2030-03-28 01:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 274.34 | 510 | 210 | 0 | 0 | No
2030-03-28 02:00 | 2030 33% ECP + 1.3 GW Offshore | -368.14 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 03:00 | 2030 33% ECP + 1.3 GW Offshore | -74.22 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 04:00 | 2030 33% ECP + 1.3 GW Offshore | -472.62 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-28 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 346.19 | 510 | 0 | 0 | No
2030-03-28 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 46.19 | 210 | 0 | 0 | No
2030-03-28 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -186.1 | -253.81 | 510 | 0 | 0 | No
2030-03-28 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 113.9 | 46.19 | 510 | 0 | 0 | Yes
2030-03-28 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 413.9 | 346.19 | 510 | 0 | 0 | Yes
2030-03-28 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-28 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-28 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-28 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 258.4 | 0 | 0 | Yes
2030-03-28 18:00 | 2030 33% ECP + 1.3 GW Offshore | -447.54 | -526 | -510 | -41.6 | 0 | 0 | No
2030-03-28 19:00 | 2030 33% ECP + 1.3 GW Offshore | -226.01 | -395 | -510 | -14.74 | 0 | 0 | No
2030-03-28 20:00 | 2030 33% ECP + 1.3 GW Offshore | -226.01 | -95 | -210 | 162.88 | 0 | 0 | No
2030-03-28 21:00 | 2030 33% ECP + 1.3 GW Offshore | -646.01 | 205 | 90 | 462.88 | 0 | 0 | No
2030-03-28 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 390 | 510 | 0 | 0 | No
2030-03-28 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-29 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 320.84 | 510 | 0 | 0 | Yes
2030-03-29 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-03-29 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-03-29 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-03-29 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -210 | 510 | 0 | 0 | Yes
2030-03-29 17:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 210 | 0 | 0 | No
2030-03-29 18:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -226 | -368.74 | 510 | 0 | 0 | No
2030-03-29 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -91.99 | 428.3 | 0 | 0 | No
2030-03-29 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 428.3 | 0 | 0 | No
2030-03-29 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 97.78 | 162.56 | 0 | 0 | No
2030-03-29 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 462.56 | 0 | 0 | No
2030-03-29 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 05:00 | 2030 33% ECP + 1.3 GW Offshore | 616.43 | 505 | 510 | 346.42 | 0 | 0 | No
2030-03-30 06:00 | 2030 33% ECP + 1.3 GW Offshore | 280.55 | 505 | 510 | 46.42 | 0 | 0 | No
2030-03-30 07:00 | 2030 33% ECP + 1.3 GW Offshore | -87.67 | 300 | 300 | -253.58 | 0 | 0 | No
2030-03-30 08:00 | 2030 33% ECP + 1.3 GW Offshore | -507.67 | 0 | 0 | -510 | 0 | 0 | No
2030-03-30 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -233.72 | -210 | 0 | 0 | Yes
2030-03-30 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -361.48 | 90 | 0 | 0 | Yes
2030-03-30 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -185.91 | 0 | 0 | Yes
2030-03-30 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -485.91 | 0 | 0 | Yes
2030-03-30 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -445.37 | 0 | 0 | Yes
2030-03-30 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -145.37 | 0 | 0 | Yes
2030-03-30 15:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | -526 | -510 | 154.63 | 0 | 0 | Yes
2030-03-30 16:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | 166.64 | 0 | 0 | Yes
2030-03-30 17:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 264.14 | 0 | 0 | No
2030-03-30 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 264.14 | 0 | 0 | No
2030-03-30 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -395 | -390 | 510 | 0 | 0 | No
2030-03-30 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -90 | 510 | 0 | 0 | No
2030-03-30 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 300.71 | 0 | 0 | No
2030-03-30 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-03-30 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 336.04 | 390 | 510 | 0 | 0 | No
2030-03-31 | 2030 33% ECP + 1.3 GW Offshore | 700 | 36.04 | 90 | 210 | 0 | 0 | No
2030-03-31 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -210 | 0 | 0 | 0 | No
2030-03-31 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -365.3 | 0 | 0 | 0 | No
2030-03-31 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -235.86 | 0 | 0 | 0 | No
2030-03-31 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -235.86 | 75.58 | 0 | 0 | No
2030-03-31 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 55.6 | 0 | 0 | No
2030-03-31 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-03-31 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-03-31 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 63.13 | 0 | 0 | No
2030-03-31 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-03-31 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 165.09 | 0 | 0 | No
2030-03-31 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 291 | 0 | 0 | No
2030-03-31 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 291.46 | 0 | 0 | No
2030-03-31 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 269.97 | 0 | 0 | No
2030-03-31 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 221.1 | 0 | 0 | No
2030-03-31 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 21.09 | 0 | 0 | No
2030-03-31 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 165.69 | 0 | 0 | No
2030-03-31 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -408.97 | -82.4 | 0 | 0 | No
2030-03-31 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -108.97 | 207.05 | 0 | 0 | No
2030-03-31 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 191.03 | 254.61 | 0 | 0 | No
2030-03-31 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 254.61 | 0 | 0 | No
2030-03-31 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 510 | 0 | 0 | No
2030-03-31 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 359.93 | 0 | 0 | No
2030-03-31 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 367.08 | 0 | 0 | No
2030-04-01 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 304.62 | 0 | 0 | No
2030-04-01 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 211.24 | 0 | 0 | No
2030-04-01 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 255.33 | 0 | 0 | No
2030-04-01 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 171.89 | 0 | 0 | No
2030-04-01 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -1.28 | 247 | 0 | 0 | No
2030-04-01 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -297.64 | 142.31 | 0 | 0 | No
2030-04-01 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -49.5 | 226.29 | 0 | 0 | No
2030-04-01 07:00 | 2030 33% ECP + 1.3 GW Offshore | 689.46 | 3.34 | 210 | 461.59 | 0 | 0 | No
2030-04-01 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 303.34 | 510 | 510 | 0 | 0 | No
2030-04-01 09:00 | 2030 33% ECP + 1.3 GW Offshore | 420.85 | 3.34 | 210 | 475.17 | 0 | 0 | No
2030-04-01 10:00 | 2030 33% ECP + 1.3 GW Offshore | 0.85 | 0 | 0 | 315.7 | 0 | 0 | No
2030-04-01 11:00 | 2030 33% ECP + 1.3 GW Offshore | -419.15 | 0 | 0 | 165.82 | 0 | 0 | No
2030-04-01 12:00 | 2030 33% ECP + 1.3 GW Offshore | -541.64 | 0 | 0 | 165.82 | 0 | 0 | No
2030-04-01 13:00 | 2030 33% ECP + 1.3 GW Offshore | -161.29 | 0 | 0 | 210 | 0 | 0 | No
2030-04-01 14:00 | 2030 33% ECP + 1.3 GW Offshore | -12.53 | 134.59 | 300 | 510 | 0 | 0 | No
2030-04-01 15:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 157.1 | 0 | 510 | 0 | 0 | No
2030-04-01 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -142.9 | -300 | 210 | 0 | 0 | No
2030-04-01 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -302.78 | -510 | 510 | 0 | 0 | No
2030-04-01 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -2.78 | -510 | 300 | 0 | 0 | No
2030-04-01 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -302.78 | -510 | 0 | 0 | 0 | No
2030-04-01 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -302.78 | -390 | 0 | 0 | 0 | No
2030-04-01 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -2.78 | -90 | 271.71 | 0 | 0 | No
2030-04-01 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 457.06 | 0 | 0 | No
2030-04-01 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 | 2030 33% ECP + 1.3 GW Offshore | 474.97 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 01:00 | 2030 33% ECP + 1.3 GW Offshore | 54.97 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 02:00 | 2030 33% ECP + 1.3 GW Offshore | -266.63 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 03:00 | 2030 33% ECP + 1.3 GW Offshore | -541.58 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-02 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-02 17:00 | 2030 33% ECP + 1.3 GW Offshore | -570.12 | 300 | 300 | 510 | 0 | 0 | No
2030-04-02 18:00 | 2030 33% ECP + 1.3 GW Offshore | -445.05 | 0 | 0 | 229.93 | 0 | 0 | No
2030-04-02 19:00 | 2030 33% ECP + 1.3 GW Offshore | -25.05 | -300 | -300 | 482.08 | 0 | 0 | No
2030-04-02 20:00 | 2030 33% ECP + 1.3 GW Offshore | 338.02 | -526 | -510 | 482.08 | 0 | 0 | No
2030-04-02 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -377.05 | -510 | 482.08 | 0 | 0 | No
2030-04-02 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -77.05 | -300 | 431.66 | 0 | 0 | No
2030-04-02 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 222.95 | 0 | 510 | 0 | 0 | No
2030-04-03 | 2030 33% ECP + 1.3 GW Offshore | 526.29 | 0 | 0 | 291.78 | 0 | 0 | No
2030-04-03 01:00 | 2030 33% ECP + 1.3 GW Offshore | 616.8 | 0 | 0 | 0 | 0 | 0 | No
2030-04-03 02:00 | 2030 33% ECP + 1.3 GW Offshore | 233.11 | 0 | 0 | 50.88 | 0 | 0 | No
2030-04-03 03:00 | 2030 33% ECP + 1.3 GW Offshore | 316.21 | 0 | -32.64 | 0 | 0 | 0 | No
2030-04-03 04:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -127.13 | -332.64 | 0 | 0 | 0 | No
2030-04-03 05:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -32.64 | 67.35 | 0 | 0 | No
2030-04-03 06:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | 0 | 267.36 | 210 | 0 | 0 | No
2030-04-03 07:00 | 2030 33% ECP + 1.3 GW Offshore | -446.63 | 0 | 90 | 510 | 0 | 0 | No
2030-04-03 08:00 | 2030 33% ECP + 1.3 GW Offshore | -26.63 | -226 | -210 | 510 | 0 | 0 | No
2030-04-03 09:00 | 2030 33% ECP + 1.3 GW Offshore | -446.63 | -526 | -510 | 329.98 | 0 | 0 | No
2030-04-03 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 305.06 | 0 | 0 | No
2030-04-03 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 283.45 | 0 | 0 | No
2030-04-03 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 107.48 | 0 | 0 | No
2030-04-03 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 120.24 | 0 | 0 | No
2030-04-03 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-03 15:00 | 2030 33% ECP + 1.3 GW Offshore | -626.49 | -526 | -510 | 0 | 0 | 0 | No
2030-04-03 16:00 | 2030 33% ECP + 1.3 GW Offshore | -206.49 | -287.33 | -510 | 166.58 | 0 | 0 | No
2030-04-03 17:00 | 2030 33% ECP + 1.3 GW Offshore | 213.51 | 0 | -210 | 239.04 | 0 | 0 | No
2030-04-03 18:00 | 2030 33% ECP + 1.3 GW Offshore | -101.11 | -300 | -510 | -60.96 | 0 | 0 | No
2030-04-03 19:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -300 | -210 | -240.22 | 0 | 0 | No
2030-04-03 20:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | 90 | 59.78 | 0 | 0 | No
2030-04-03 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 390 | 359.78 | 0 | 0 | No
2030-04-03 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 405.23 | 482.72 | 0 | 0 | No
2030-04-03 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 105.23 | 193.7 | 0 | 0 | No
2030-04-04 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -194.77 | 19.71 | 0 | 0 | No
2030-04-04 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -454.71 | 107.22 | 0 | 0 | No
2030-04-04 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -358.78 | 86.41 | 0 | 0 | No
2030-04-04 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -358.78 | 70.15 | 0 | 0 | No
2030-04-04 04:00 | 2030 33% ECP + 1.3 GW Offshore | 404.86 | 0 | -510 | 0 | 0 | 0 | No
2030-04-04 05:00 | 2030 33% ECP + 1.3 GW Offshore | -15.14 | 0 | -510 | 46.05 | 0 | 0 | No
2030-04-04 06:00 | 2030 33% ECP + 1.3 GW Offshore | -435.14 | 0 | -510 | 169.39 | 0 | 0 | No
2030-04-04 07:00 | 2030 33% ECP + 1.3 GW Offshore | -99.3 | -226 | -510 | 350.72 | 0 | 0 | No
2030-04-04 08:00 | 2030 33% ECP + 1.3 GW Offshore | -519.3 | -526 | -510 | 468.01 | 0 | 0 | No
2030-04-04 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 232.68 | 0 | 0 | No
2030-04-04 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -67.32 | 0 | 0 | Yes
2030-04-04 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 210 | 0 | 0 | Yes
2030-04-04 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-04-04 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-04 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -225.46 | 510 | 0 | 0 | Yes
2030-04-04 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 360.87 | 0 | 0 | Yes
2030-04-04 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 234.09 | 0 | 0 | Yes
2030-04-04 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 242.37 | 0 | 0 | Yes
2030-04-04 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 242.37 | 0 | 0 | No
2030-04-04 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 250.39 | 0 | 0 | No
2030-04-04 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 250.39 | 0 | 0 | No
2030-04-04 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-04-04 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-04-04 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-04-05 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 485.67 | 0 | 0 | Yes
2030-04-05 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 185.67 | 0 | 0 | Yes
2030-04-05 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 161.93 | 0 | 0 | Yes
2030-04-05 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 236.76 | 0 | 0 | Yes
2030-04-05 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-05 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 482.93 | 0 | 0 | Yes
2030-04-05 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 269.83 | 0 | 0 | Yes
2030-04-05 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 208.61 | 0 | 0 | Yes
2030-04-05 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 227.31 | 0 | 0 | Yes
2030-04-05 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 318.24 | 0 | 0 | Yes
2030-04-05 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 361.59 | 0 | 0 | Yes
2030-04-05 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 336.08 | 0 | 0 | Yes
2030-04-05 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 299.2 | 0 | 0 | Yes
2030-04-05 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 310.88 | 0 | 0 | Yes
2030-04-05 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 299.13 | 0 | 0 | Yes
2030-04-05 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 221.64 | 0 | 0 | Yes
2030-04-05 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 157.88 | 0 | 0 | Yes
2030-04-06 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 457.88 | 0 | 0 | Yes
2030-04-06 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-06 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-04-06 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-04-06 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-04-06 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 227.59 | 0 | 0 | No
2030-04-06 17:00 | 2030 33% ECP + 1.3 GW Offshore | -473.36 | -526 | -510 | 352.48 | 0 | 0 | No
2030-04-06 18:00 | 2030 33% ECP + 1.3 GW Offshore | -53.36 | -226 | -210 | 510 | 0 | 0 | No
2030-04-06 19:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | 0 | 497.32 | 0 | 0 | No
2030-04-06 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 496.36 | 0 | 0 | No
2030-04-06 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-04-06 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 466.57 | 0 | 0 | No
2030-04-06 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -1.8 | 510 | 0 | 0 | No
2030-04-07 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -81.07 | 456.54 | 0 | 0 | No
2030-04-07 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -148.65 | 510 | 0 | 0 | No
2030-04-07 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -116.46 | 510 | 0 | 0 | No
2030-04-07 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -210 | 445.79 | 0 | 0 | No
2030-04-07 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 393.74 | 0 | 0 | No
2030-04-07 05:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 0 | -510 | 403.52 | 0 | 0 | No
2030-04-07 06:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 0 | -210 | 390 | 0 | 0 | No
2030-04-07 07:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -236.07 | -510 | 474.99 | 0 | 0 | No
2030-04-07 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 271.85 | 0 | 0 | No
2030-04-07 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 219.29 | 0 | 0 | Yes
2030-04-07 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -80.71 | 0 | 0 | Yes
2030-04-07 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -218.62 | 0 | 0 | Yes
2030-04-07 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 81.38 | 0 | 0 | Yes
2030-04-07 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 176.66 | 0 | 0 | Yes
2030-04-07 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 8.55 | 0 | 0 | Yes
2030-04-07 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -291.94 | -510 | 230.83 | 0 | 0 | Yes
2030-04-07 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -69.17 | 0 | 0 | Yes
2030-04-07 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 210 | 0 | 0 | No
2030-04-07 18:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -487.48 | -510 | 510 | 0 | 0 | No
2030-04-07 19:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -187.48 | -510 | 510 | 0 | 0 | No
2030-04-07 20:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -187.48 | -510 | 510 | 0 | 0 | No
2030-04-07 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -487.48 | -510 | 483.97 | 0 | 0 | No
2030-04-07 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -487.48 | -510 | 369 | 0 | 0 | No
2030-04-07 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 69 | 0 | 0 | No
2030-04-08 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | -231 | 0 | 0 | No
2030-04-08 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -50.07 | -510 | -260.81 | 0 | 0 | No
2030-04-08 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -307.29 | 0 | 0 | No
2030-04-08 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -141.94 | -510 | -297.18 | 0 | 0 | No
2030-04-08 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -205.87 | -510 | -356.52 | 0 | 0 | No
2030-04-08 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -205.87 | -510 | -56.52 | 0 | 0 | No
2030-04-08 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -59.93 | -510 | -269.65 | 0 | 0 | No
2030-04-08 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -314.96 | -510 | -123.06 | 0 | 0 | No
2030-04-08 08:00 | 2030 33% ECP + 1.3 GW Offshore | 530.32 | -526 | -510 | 68.28 | 0 | 0 | No
2030-04-08 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 107.64 | 0 | 0 | No
2030-04-08 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 81.52 | 0 | 0 | No
2030-04-08 11:00 | 2030 33% ECP + 1.3 GW Offshore | 596.61 | -526 | -510 | 59.14 | 0 | 0 | No
2030-04-08 12:00 | 2030 33% ECP + 1.3 GW Offshore | 543.06 | -526 | -510 | 40.02 | 0 | 0 | No
2030-04-08 13:00 | 2030 33% ECP + 1.3 GW Offshore | 543.06 | -526 | -510 | 30.5 | 0 | 0 | No
2030-04-08 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 18.18 | 0 | 0 | No
2030-04-08 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 5.91 | 0 | 0 | No
2030-04-08 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 181.84 | 0 | 0 | No
2030-04-08 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -402.55 | 280.65 | 0 | 0 | No
2030-04-08 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -19.35 | 0 | 0 | No
2030-04-08 19:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | -510 | -256.77 | 0 | 0 | No
2030-04-08 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -358.81 | -281.75 | 0 | 0 | No
2030-04-08 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -58.81 | 0 | 0 | 0 | No
2030-04-08 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 202.3 | 241.19 | 300 | 0 | 0 | No
2030-04-08 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 223.68 | 0 | 0 | 0 | No
2030-04-09 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-04-09 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 49.07 | 0 | 0 | No
2030-04-09 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-04-09 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 390 | 0 | 0 | 0 | No
2030-04-09 04:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 0 | 90 | 0 | 0 | 0 | No
2030-04-09 05:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 0 | -210 | -210 | 0 | 0 | No
2030-04-09 06:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -300 | -510 | -510 | 0 | 0 | No
2030-04-09 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 08:00 | 2030 33% ECP + 1.3 GW Offshore | -499.01 | -526 | -510 | -407.15 | 0 | 0 | No
2030-04-09 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -362.7 | 0 | 0 | No
2030-04-09 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -396.02 | 0 | 0 | No
2030-04-09 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 16:00 | 2030 33% ECP + 1.3 GW Offshore | -675.22 | -526 | -510 | -439.07 | 0 | 0 | No
2030-04-09 17:00 | 2030 33% ECP + 1.3 GW Offshore | -255.22 | -226 | -210 | -210 | 0 | 0 | No
2030-04-09 18:00 | 2030 33% ECP + 1.3 GW Offshore | -675.22 | -526 | -510 | -510 | 0 | 0 | No
2030-04-09 19:00 | 2030 33% ECP + 1.3 GW Offshore | -255.22 | -300 | -510 | -500.79 | 0 | 0 | No
2030-04-09 20:00 | 2030 33% ECP + 1.3 GW Offshore | 164.78 | 0 | -210 | -200.79 | 0 | 0 | No
2030-04-09 21:00 | 2030 33% ECP + 1.3 GW Offshore | 584.78 | 0 | 90 | 93.37 | 0 | 0 | No
2030-04-09 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -85.08 | 0 | 0 | 0 | No
2030-04-09 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -233.22 | 0 | 0 | 0 | No
2030-04-10 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 66.78 | 0 | 0 | 0 | No
2030-04-10 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 275.64 | 0 | 0 | 0 | No
2030-04-10 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 38.72 | 0 | 0 | 0 | No
2030-04-10 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-10 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 38.84 | 0 | 0 | 0 | No
2030-04-10 05:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | 0 | 0.1 | 0 | 0 | 0 | No
2030-04-10 06:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -72.48 | 69.72 | 0 | 0 | No
2030-04-10 07:00 | 2030 33% ECP + 1.3 GW Offshore | -265.8 | -300 | -372.48 | -226.01 | 0 | 0 | No
2030-04-10 08:00 | 2030 33% ECP + 1.3 GW Offshore | 154.2 | 0 | -210 | 73.99 | 0 | 0 | No
2030-04-10 09:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -300 | -510 | 78.7 | 0 | 0 | No
2030-04-10 10:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 11:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 12:00 | 2030 33% ECP + 1.3 GW Offshore | 134.6 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 13:00 | 2030 33% ECP + 1.3 GW Offshore | 554.6 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 14:00 | 2030 33% ECP + 1.3 GW Offshore | 300.95 | -526 | -510 | 0 | 0 | 0 | No
2030-04-10 15:00 | 2030 33% ECP + 1.3 GW Offshore | 578.84 | -358.83 | -510 | 0 | 0 | 0 | No
2030-04-10 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -58.83 | -510 | 39.11 | 0 | 0 | No
2030-04-10 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -260.89 | 0 | 0 | No
2030-04-10 18:00 | 2030 33% ECP + 1.3 GW Offshore | 444.65 | 0 | -390 | -390 | 0 | 0 | No
2030-04-10 19:00 | 2030 33% ECP + 1.3 GW Offshore | 24.65 | 0 | -90 | -90 | 0 | 0 | No
2030-04-10 20:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 142.48 | 210 | 210 | 0 | 0 | No
2030-04-10 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 442.48 | 510 | 510 | 0 | 0 | No
2030-04-10 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 142.48 | 510 | 338.43 | 0 | 0 | No
2030-04-10 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 225.37 | 38.43 | 0 | 0 | No
2030-04-11 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 03:00 | 2030 33% ECP + 1.3 GW Offshore | 632.18 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 04:00 | 2030 33% ECP + 1.3 GW Offshore | 212.18 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 05:00 | 2030 33% ECP + 1.3 GW Offshore | -207.82 | 0 | 0 | 0 | 0 | 0 | No
2030-04-11 06:00 | 2030 33% ECP + 1.3 GW Offshore | -627.82 | 0 | -118.08 | 0 | 0 | 0 | No
2030-04-11 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 21.23 | 0 | 0 | 0 | No
2030-04-11 08:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -278.77 | 0 | 0 | 0 | No
2030-04-11 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -300 | 0 | 0 | No
2030-04-11 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-11 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-11 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-11 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -106.45 | 0 | 0 | No
2030-04-11 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-11 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -204.96 | 0 | 0 | No
2030-04-11 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-11 17:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -321.48 | -510 | -188.77 | 0 | 0 | No
2030-04-11 18:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | -526 | -510 | -488.77 | 0 | 0 | No
2030-04-11 19:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -300 | -510 | -408.19 | 0 | 0 | No
2030-04-11 20:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | -210 | -108.19 | 0 | 0 | No
2030-04-11 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 90 | 191.81 | 0 | 0 | No
2030-04-11 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 379.89 | 195.72 | 0 | 0 | No
2030-04-11 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 79.89 | 0 | 0 | 0 | No
2030-04-12 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 379.89 | 300 | 0 | 0 | No
2030-04-12 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-12 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-12 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 410.27 | 390 | 510 | 0 | 0 | No
2030-04-12 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 110.27 | 90 | 210 | 0 | 0 | No
2030-04-12 05:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -189.73 | -210 | -90 | 0 | 0 | No
2030-04-12 06:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -489.73 | -510 | -390 | 0 | 0 | No
2030-04-12 07:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-04-12 08:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -394.39 | 0 | 0 | No
2030-04-12 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-12 10:00 | 2030 33% ECP + 1.3 GW Offshore | 349.71 | -226 | -510 | -437.35 | 0 | 0 | No
2030-04-12 11:00 | 2030 33% ECP + 1.3 GW Offshore | -70.29 | -526 | -510 | -259.94 | 0 | 0 | No
2030-04-12 12:00 | 2030 33% ECP + 1.3 GW Offshore | -416.46 | -526 | -510 | -243.62 | 0 | 0 | No
2030-04-12 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -155.23 | 0 | 0 | No
2030-04-12 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -337.62 | 0 | 0 | No
2030-04-12 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -199.88 | 0 | 0 | No
2030-04-12 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -59.26 | 0 | 0 | No
2030-04-12 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 84.98 | 0 | 0 | No
2030-04-12 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -16.06 | 0 | 0 | No
2030-04-12 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 76.31 | 0 | 0 | No
2030-04-12 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -299.51 | -510 | 71.78 | 0 | 0 | No
2030-04-12 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0.49 | -210 | 252.51 | 0 | 0 | Yes
2030-04-12 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300.49 | 90 | 64.86 | 0 | 0 | Yes
2030-04-12 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 390 | 0 | 0 | 0 | Yes
2030-04-13 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-04-13 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-13 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-13 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 407.31 | 0 | 0 | Yes
2030-04-13 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 107.31 | 0 | 0 | Yes
2030-04-13 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -192.69 | 0 | 0 | No
2030-04-13 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -492.69 | 0 | 0 | No
2030-04-13 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -265.05 | 0 | 0 | No
2030-04-13 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 34.95 | 0 | 0 | Yes
2030-04-13 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 334.95 | 0 | 0 | Yes
2030-04-13 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-04-13 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 324.04 | 0 | 0 | Yes
2030-04-13 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 426.03 | 0 | 0 | Yes
2030-04-13 17:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 510 | 0 | 0 | No
2030-04-13 18:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -226 | -428.82 | 510 | 0 | 0 | No
2030-04-13 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -210 | 510 | 0 | 0 | No
2030-04-13 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-04-13 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -366.76 | 510 | 0 | 0 | No
2030-04-13 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -66.76 | 510 | 0 | 0 | No
2030-04-13 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -366.76 | 450.92 | 0 | 0 | No
2030-04-14 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 150.92 | 0 | 0 | No
2030-04-14 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 169.69 | 0 | 0 | No
2030-04-14 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -253.67 | 181.32 | 0 | 0 | No
2030-04-14 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -377.76 | 91.24 | 0 | 0 | No
2030-04-14 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -377.76 | 86.36 | 0 | 0 | No
2030-04-14 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -248.88 | 90.87 | 0 | 0 | No
2030-04-14 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 166 | 0 | 0 | No
2030-04-14 07:00 | 2030 33% ECP + 1.3 GW Offshore | 615.57 | -287.68 | -510 | 196.15 | 0 | 0 | No
2030-04-14 08:00 | 2030 33% ECP + 1.3 GW Offshore | 195.57 | -526 | -510 | 140.05 | 0 | 0 | No
2030-04-14 09:00 | 2030 33% ECP + 1.3 GW Offshore | -224.43 | -526 | -510 | 82.21 | 0 | 0 | Yes
2030-04-14 10:00 | 2030 33% ECP + 1.3 GW Offshore | -644.43 | -526 | -510 | 99.34 | 0 | 0 | Yes
2030-04-14 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 62.86 | 0 | 0 | Yes
2030-04-14 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 115.22 | 0 | 0 | Yes
2030-04-14 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 57 | 0 | 0 | Yes
2030-04-14 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 90.32 | 0 | 0 | Yes
2030-04-14 15:00 | 2030 33% ECP + 1.3 GW Offshore | -350.27 | -526 | -510 | 94.72 | 0 | 0 | Yes
2030-04-14 16:00 | 2030 33% ECP + 1.3 GW Offshore | 69.73 | -526 | -510 | 187.3 | 0 | 0 | No
2030-04-14 17:00 | 2030 33% ECP + 1.3 GW Offshore | 489.73 | -526 | -510 | 270.08 | 0 | 0 | No
2030-04-14 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -330.2 | 331.96 | 0 | 0 | No
2030-04-14 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -30.2 | 397.42 | 0 | 0 | No
2030-04-14 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 367.2 | 0 | 0 | No
2030-04-14 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 359.7 | 0 | 0 | No
2030-04-14 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 252.41 | 0 | 0 | No
2030-04-14 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -66.8 | 147.65 | 0 | 0 | No
2030-04-15 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 102.06 | 88.91 | 0 | 0 | No
2030-04-15 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 51.05 | 83.85 | 0 | 0 | No
2030-04-15 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 180.9 | 89.69 | 0 | 0 | No
2030-04-15 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 480.9 | 79.94 | 0 | 0 | No
2030-04-15 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 233.01 | 53.62 | 0 | 0 | No
2030-04-15 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 70.04 | 0 | 0 | No
2030-04-15 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 154.6 | 0 | 0 | No
2030-04-15 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 249.36 | 0 | 0 | No
2030-04-15 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 272.29 | 0 | 0 | No
2030-04-15 09:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 242.45 | 0 | 0 | No
2030-04-15 10:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | 207.98 | 0 | 0 | No
2030-04-15 11:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | -526 | -510 | 203.13 | 0 | 0 | No
2030-04-15 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 207.77 | 0 | 0 | No
2030-04-15 13:00 | 2030 33% ECP + 1.3 GW Offshore | -640.71 | -526 | -510 | 175.3 | 0 | 0 | No
2030-04-15 14:00 | 2030 33% ECP + 1.3 GW Offshore | -220.71 | -526 | -510 | 151.87 | 0 | 0 | No
2030-04-15 15:00 | 2030 33% ECP + 1.3 GW Offshore | 199.29 | -526 | -510 | 178.35 | 0 | 0 | No
2030-04-15 16:00 | 2030 33% ECP + 1.3 GW Offshore | 619.29 | -526 | -510 | 279.41 | 0 | 0 | No
2030-04-15 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 426.04 | 0 | 0 | No
2030-04-15 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 402.94 | 0 | 0 | No
2030-04-15 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 351.76 | 0 | 0 | No
2030-04-15 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 310.4 | 0 | 0 | No
2030-04-15 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 374.15 | 0 | 0 | No
2030-04-15 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 266.82 | 0 | 0 | No
2030-04-15 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -40.92 | 41.37 | 0 | 0 | No
2030-04-16 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -324.78 | 0 | 0 | 0 | No
2030-04-16 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -112.61 | 0 | 0 | No
2030-04-16 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -127.22 | 0 | 0 | No
2030-04-16 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -191.93 | -510 | -53.71 | 0 | 0 | No
2030-04-16 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -360.06 | -510 | -37.23 | 0 | 0 | No
2030-04-16 05:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -232.5 | -510 | -73.94 | 0 | 0 | No
2030-04-16 06:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 0 | -510 | -72.54 | 0 | 0 | No
2030-04-16 07:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -262.4 | -510 | 141.79 | 0 | 0 | No
2030-04-16 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 226.34 | 0 | 0 | No
2030-04-16 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 187.14 | 0 | 0 | No
2030-04-16 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 97.7 | 0 | 0 | No
2030-04-16 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -40.79 | 0 | 0 | No
2030-04-16 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -253.41 | 0 | 0 | No
2030-04-16 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -371.53 | 0 | 0 | No
2030-04-16 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -371.89 | 0 | 0 | No
2030-04-16 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -359.43 | 0 | 0 | No
2030-04-16 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -59.43 | 0 | 0 | No
2030-04-16 17:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 240.57 | 0 | 0 | No
2030-04-16 18:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -269.86 | -510 | 308.78 | 0 | 0 | No
2030-04-16 19:00 | 2030 33% ECP + 1.3 GW Offshore | -147.37 | -411.3 | -510 | 181.06 | 0 | 0 | No
2030-04-16 20:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -411.3 | -510 | -118.94 | 0 | 0 | No
2030-04-16 21:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -111.3 | -510 | -418.94 | 0 | 0 | No
2030-04-16 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -351.84 | -510 | -510 | 0 | 0 | No
2030-04-16 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -490.14 | 0 | 0 | No
2030-04-17 | 2030 33% ECP + 1.3 GW Offshore | 700 | -380.1 | -510 | -190.14 | 0 | 0 | No
2030-04-17 01:00 | 2030 33% ECP + 1.3 GW Offshore | 564.68 | -526 | -510 | -490.14 | 0 | 0 | No
2030-04-17 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -275 | 0 | 0 | No
2030-04-17 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -343.65 | 0 | 0 | No
2030-04-17 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-17 05:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -437.64 | -510 | -510 | 0 | 0 | No
2030-04-17 06:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -137.64 | -510 | -398.89 | 0 | 0 | No
2030-04-17 07:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -241.26 | -510 | -406.46 | 0 | 0 | No
2030-04-17 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -350.16 | 0 | 0 | No
2030-04-17 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -171.31 | 0 | 0 | No
2030-04-17 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 83.72 | 0 | 0 | Yes
2030-04-17 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -216.28 | 0 | 0 | No
2030-04-17 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -260.89 | 0 | 0 | Yes
2030-04-17 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -375.01 | 0 | 0 | No
2030-04-17 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -229.83 | 0 | 0 | No
2030-04-17 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 29.45 | 0 | 0 | Yes
2030-04-17 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 83.08 | 0 | 0 | No
2030-04-17 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 311.35 | 0 | 0 | No
2030-04-17 18:00 | 2030 33% ECP + 1.3 GW Offshore | -587.61 | -526 | -510 | 92.03 | 0 | 0 | Yes
2030-04-17 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 392.03 | 0 | 0 | No
2030-04-17 20:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 408.86 | 0 | 0 | No
2030-04-17 21:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 108.86 | 0 | 0 | No
2030-04-17 22:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -191.14 | 0 | 0 | No
2030-04-17 23:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | -526 | -510 | -227.64 | 0 | 0 | No
2030-04-18 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -503.49 | 0 | 0 | No
2030-04-18 01:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -220.87 | 0 | 0 | No
2030-04-18 02:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -220.87 | 0 | 0 | No
2030-04-18 03:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -118.31 | 0 | 0 | No
2030-04-18 04:00 | 2030 33% ECP + 1.3 GW Offshore | -133.29 | -526 | -510 | -48.81 | 0 | 0 | No
2030-04-18 05:00 | 2030 33% ECP + 1.3 GW Offshore | -22.87 | -526 | -510 | -48.81 | 0 | 0 | No
2030-04-18 06:00 | 2030 33% ECP + 1.3 GW Offshore | -26.02 | -526 | -510 | -348.81 | 0 | 0 | No
2030-04-18 07:00 | 2030 33% ECP + 1.3 GW Offshore | -304.35 | -526 | -510 | -73.45 | 0 | 0 | No
2030-04-18 08:00 | 2030 33% ECP + 1.3 GW Offshore | -696.95 | -526 | -510 | -54.39 | 0 | 0 | No
2030-04-18 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -131.7 | 0 | 0 | No
2030-04-18 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -128.89 | 0 | 0 | No
2030-04-18 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-18 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -221.86 | 0 | 0 | No
2030-04-18 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -324.3 | 0 | 0 | No
2030-04-18 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -74.45 | 0 | 0 | No
2030-04-18 15:00 | 2030 33% ECP + 1.3 GW Offshore | -598 | -526 | -510 | 19.82 | 0 | 0 | No
2030-04-18 16:00 | 2030 33% ECP + 1.3 GW Offshore | -228.16 | -526 | -510 | 180.44 | 0 | 0 | No
2030-04-18 17:00 | 2030 33% ECP + 1.3 GW Offshore | 191.84 | -245.94 | -510 | -119.56 | 0 | 0 | No
2030-04-18 18:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -477.55 | -510 | -419.56 | 0 | 0 | No
2030-04-18 19:00 | 2030 33% ECP + 1.3 GW Offshore | 34.3 | -526 | -510 | -510 | 0 | 0 | No
2030-04-18 20:00 | 2030 33% ECP + 1.3 GW Offshore | 454.3 | -526 | -510 | -345.56 | 0 | 0 | No
2030-04-18 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | -300 | 0 | 0 | No
2030-04-18 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -407.81 | 0 | 0 | 0 | No
2030-04-18 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -254.3 | -510 | -62.46 | 0 | 0 | No
2030-04-19 | 2030 33% ECP + 1.3 GW Offshore | 700 | -503.89 | -510 | -362.46 | 0 | 0 | No
2030-04-19 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -471.92 | -510 | -328 | 0 | 0 | No
2030-04-19 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -471.92 | -510 | -334.05 | 0 | 0 | No
2030-04-19 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -390.46 | -510 | -129.55 | 0 | 0 | No
2030-04-19 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -508.94 | -510 | -429.55 | 0 | 0 | No
2030-04-19 05:00 | 2030 33% ECP + 1.3 GW Offshore | 483.75 | -526 | -510 | -274.9 | 0 | 0 | No
2030-04-19 06:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | -162.33 | 0 | 0 | Yes
2030-04-19 07:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -293.14 | 0 | 0 | No
2030-04-19 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 6.86 | 0 | 0 | No
2030-04-19 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -293.14 | 0 | 0 | No
2030-04-19 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -489.9 | 0 | 0 | No
2030-04-19 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -419.61 | 0 | 0 | No
2030-04-19 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-04-19 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-19 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -353.65 | 0 | 0 | No
2030-04-19 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -105.77 | 0 | 0 | No
2030-04-19 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -53.72 | 0 | 0 | No
2030-04-19 17:00 | 2030 33% ECP + 1.3 GW Offshore | -457.33 | -526 | -510 | 82.31 | 0 | 0 | No
2030-04-19 18:00 | 2030 33% ECP + 1.3 GW Offshore | -37.33 | -526 | -510 | 233.96 | 0 | 0 | No
2030-04-19 19:00 | 2030 33% ECP + 1.3 GW Offshore | 382.67 | -521.2 | -510 | 185.95 | 0 | 0 | No
2030-04-19 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -277.32 | -510 | -114.05 | 0 | 0 | No
2030-04-19 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -491.99 | -0.33 | 0 | 0 | No
2030-04-19 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -191.99 | 60.33 | 0 | 0 | No
2030-04-19 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 108.01 | 360.33 | 0 | 0 | No
2030-04-20 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 408.01 | 510 | 0 | 0 | No
2030-04-20 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 02:00 | 2030 33% ECP + 1.3 GW Offshore | 535.83 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 03:00 | 2030 33% ECP + 1.3 GW Offshore | 141.36 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 04:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 374 | 390 | 423.28 | 0 | 0 | No
2030-04-20 05:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 74 | 90 | 123.28 | 0 | 0 | No
2030-04-20 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -176.72 | 0 | 0 | No
2030-04-20 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -476.72 | 0 | 0 | No
2030-04-20 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-04-20 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -323.53 | 0 | 0 | Yes
2030-04-20 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -23.53 | 0 | 0 | Yes
2030-04-20 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 276.47 | 0 | 0 | Yes
2030-04-20 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-04-20 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-20 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-20 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-04-20 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-04-20 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-04-20 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 300 | 0 | 0 | No
2030-04-20 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -300 | -315.61 | 0 | 0 | 0 | No
2030-04-20 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -15.61 | 255.56 | 0 | 0 | No
2030-04-20 21:00 | 2030 33% ECP + 1.3 GW Offshore | -283.49 | 300 | 284.39 | 510 | 0 | 0 | No
2030-04-20 22:00 | 2030 33% ECP + 1.3 GW Offshore | -130.76 | 505 | 510 | 510 | 0 | 0 | No
2030-04-20 23:00 | 2030 33% ECP + 1.3 GW Offshore | -353.36 | 505 | 510 | 510 | 0 | 0 | No
2030-04-21 | 2030 33% ECP + 1.3 GW Offshore | -619.03 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 01:00 | 2030 33% ECP + 1.3 GW Offshore | -312.35 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 02:00 | 2030 33% ECP + 1.3 GW Offshore | -226.17 | 505 | 510 | 245.66 | 0 | 0 | Yes
2030-04-21 03:00 | 2030 33% ECP + 1.3 GW Offshore | -201.9 | 505 | 510 | -36.56 | 0 | 0 | Yes
2030-04-21 04:00 | 2030 33% ECP + 1.3 GW Offshore | -621.9 | 505 | 510 | 214.44 | 0 | 0 | Yes
2030-04-21 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 361.61 | 0 | 0 | Yes
2030-04-21 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-04-21 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 47.08 | 0 | 0 | Yes
2030-04-21 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 347.08 | 0 | 0 | Yes
2030-04-21 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 451.34 | 0 | 0 | Yes
2030-04-21 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 18:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 300 | 477.62 | 300 | 0 | 0 | No
2030-04-21 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 177.62 | 0 | 0 | 0 | No
2030-04-21 20:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 300 | 477.62 | 300 | 0 | 0 | No
2030-04-21 21:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-21 22:00 | 2030 33% ECP + 1.3 GW Offshore | 422.81 | 505 | 510 | 284.91 | 0 | 0 | Yes
2030-04-21 23:00 | 2030 33% ECP + 1.3 GW Offshore | 192.56 | 505 | 510 | 245.41 | 0 | 0 | Yes
2030-04-22 | 2030 33% ECP + 1.3 GW Offshore | 190.14 | 505 | 510 | 510 | 0 | 0 | Yes
2030-04-22 01:00 | 2030 33% ECP + 1.3 GW Offshore | 146.25 | 505 | 510 | 214.55 | 0 | 0 | Yes
2030-04-22 02:00 | 2030 33% ECP + 1.3 GW Offshore | 20.47 | 505 | 510 | 249.46 | 0 | 0 | Yes
2030-04-22 03:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 252.79 | 0 | 0 | Yes
2030-04-22 04:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 222.3 | 0 | 0 | Yes
2030-04-22 05:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | -77.7 | 0 | 0 | No
2030-04-22 06:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 0 | 0 | 0 | No
2030-04-22 07:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 283.99 | 210 | 0 | 0 | 0 | No
2030-04-22 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -16.01 | -90 | -226.46 | 0 | 0 | No
2030-04-22 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -316.01 | -390 | -298.75 | 0 | 0 | No
2030-04-22 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -16.01 | -317.11 | 0 | 0 | 0 | Yes
2030-04-22 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -41.2 | 0 | 0 | 0 | Yes
2030-04-22 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 258.8 | 300 | 0 | 0 | Yes
2030-04-22 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 390 | 320.19 | 0 | 0 | Yes
2030-04-22 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | No
2030-04-22 15:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -210 | 438.19 | 0 | 0 | No
2030-04-22 16:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 315.71 | 0 | 0 | No
2030-04-22 17:00 | 2030 33% ECP + 1.3 GW Offshore | 130.91 | -526 | -510 | 128.27 | 0 | 0 | No
2030-04-22 18:00 | 2030 33% ECP + 1.3 GW Offshore | 550.91 | -526 | -510 | 0 | 0 | 0 | No
2030-04-22 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -269.1 | -510 | -300 | 0 | 0 | No
2030-04-22 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -145.32 | -510 | -73.64 | 0 | 0 | No
2030-04-22 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -358.53 | -510 | 204.73 | 0 | 0 | No
2030-04-22 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -358.53 | -510 | 171.81 | 0 | 0 | No
2030-04-22 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 13.56 | 0 | 0 | No
2030-04-23 | 2030 33% ECP + 1.3 GW Offshore | 700 | -246.79 | -510 | 0 | 0 | 0 | No
2030-04-23 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -246.79 | -510 | -133.51 | 0 | 0 | No
2030-04-23 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -246.79 | -510 | -133.97 | 0 | 0 | No
2030-04-23 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -246.79 | -510 | -78.11 | 0 | 0 | No
2030-04-23 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -78.11 | 0 | 0 | No
2030-04-23 05:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | 0 | -510 | -162.66 | 0 | 0 | No
2030-04-23 06:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -510 | -218.28 | 0 | 0 | No
2030-04-23 07:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -177.75 | -510 | -273.55 | 0 | 0 | No
2030-04-23 08:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -477.75 | -510 | -283.07 | 0 | 0 | No
2030-04-23 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -352.89 | 0 | 0 | No
2030-04-23 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -307.2 | 0 | 0 | No
2030-04-23 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -191.17 | 0 | 0 | No
2030-04-23 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -224.39 | 0 | 0 | No
2030-04-23 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -230.75 | 0 | 0 | No
2030-04-23 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -184.45 | 0 | 0 | No
2030-04-23 15:00 | 2030 33% ECP + 1.3 GW Offshore | -297.05 | -526 | -510 | -154.45 | 0 | 0 | No
2030-04-23 16:00 | 2030 33% ECP + 1.3 GW Offshore | 122.95 | -526 | -510 | -43.11 | 0 | 0 | No
2030-04-23 17:00 | 2030 33% ECP + 1.3 GW Offshore | 542.95 | -526 | -510 | -252.45 | 0 | 0 | No
2030-04-23 18:00 | 2030 33% ECP + 1.3 GW Offshore | 266.33 | -226 | -510 | -510 | 0 | 0 | No
2030-04-23 19:00 | 2030 33% ECP + 1.3 GW Offshore | 266.33 | 0 | -510 | -302.06 | 0 | 0 | No
2030-04-23 20:00 | 2030 33% ECP + 1.3 GW Offshore | 406.61 | 0 | -510 | -425.38 | 0 | 0 | No
2030-04-23 21:00 | 2030 33% ECP + 1.3 GW Offshore | 385.69 | 0 | -300 | -218.41 | 0 | 0 | No
2030-04-23 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 1.54 | 0 | 0 | No
2030-04-23 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -300 | 0 | 0 | 0 | No
2030-04-24 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 300 | 0 | 0 | No
2030-04-24 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 510 | 0 | 0 | No
2030-04-24 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-04-24 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 390 | 510 | 0 | 0 | No
2030-04-24 04:00 | 2030 33% ECP + 1.3 GW Offshore | 450.09 | 0 | 90 | 210 | 0 | 0 | No
2030-04-24 05:00 | 2030 33% ECP + 1.3 GW Offshore | 30.09 | -226 | -210 | -90 | 0 | 0 | No
2030-04-24 06:00 | 2030 33% ECP + 1.3 GW Offshore | -389.91 | -526 | -510 | -381.06 | 0 | 0 | No
2030-04-24 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -157.85 | 0 | 0 | No
2030-04-24 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -29.07 | 0 | 0 | No
2030-04-24 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-24 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 112.64 | 0 | 0 | No
2030-04-24 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 412.64 | 0 | 0 | No
2030-04-24 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-24 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-24 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 300 | 0 | 0 | No
2030-04-24 15:00 | 2030 33% ECP + 1.3 GW Offshore | -286.91 | -526 | -510 | 0 | 0 | 0 | No
2030-04-24 16:00 | 2030 33% ECP + 1.3 GW Offshore | 133.09 | -526 | -510 | 105.54 | 0 | 0 | No
2030-04-24 17:00 | 2030 33% ECP + 1.3 GW Offshore | 553.09 | -526 | -510 | 243.26 | 0 | 0 | No
2030-04-24 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -490.69 | -56.74 | 0 | 0 | No
2030-04-24 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -356.74 | 0 | 0 | No
2030-04-24 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -289.31 | -56.74 | 0 | 0 | No
2030-04-24 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 229.88 | 0 | 0 | No
2030-04-24 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 141.64 | 0 | 0 | No
2030-04-24 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 72.29 | 300 | 441.64 | 0 | 0 | No
2030-04-25 | 2030 33% ECP + 1.3 GW Offshore | 700 | 372.29 | 510 | 510 | 0 | 0 | No
2030-04-25 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-25 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-25 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 486.8 | 390 | 510 | 0 | 0 | No
2030-04-25 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 186.8 | 90 | 292.87 | 0 | 0 | No
2030-04-25 05:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -113.2 | -210 | -7.13 | 0 | 0 | No
2030-04-25 06:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -413.2 | -510 | -23.2 | 0 | 0 | No
2030-04-25 07:00 | 2030 33% ECP + 1.3 GW Offshore | -158.27 | -526 | -510 | -257.75 | 0 | 0 | No
2030-04-25 08:00 | 2030 33% ECP + 1.3 GW Offshore | -578.27 | -526 | -510 | -204.38 | 0 | 0 | No
2030-04-25 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -176.01 | 0 | 0 | No
2030-04-25 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 123.99 | 0 | 0 | No
2030-04-25 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 338.69 | 0 | 0 | No
2030-04-25 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-25 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 318.29 | 0 | 0 | No
2030-04-25 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-04-25 15:00 | 2030 33% ECP + 1.3 GW Offshore | -365.8 | -526 | -510 | 396.09 | 0 | 0 | No
2030-04-25 16:00 | 2030 33% ECP + 1.3 GW Offshore | 54.2 | -526 | -510 | 96.09 | 0 | 0 | No
2030-04-25 17:00 | 2030 33% ECP + 1.3 GW Offshore | 474.2 | -526 | -510 | 205.67 | 0 | 0 | No
2030-04-25 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 122.84 | 0 | 0 | No
2030-04-25 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -177.16 | 0 | 0 | No
2030-04-25 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -524.51 | -510 | -246.35 | 0 | 0 | No
2030-04-25 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -224.51 | -210 | 53.65 | 0 | 0 | No
2030-04-25 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 353.65 | 0 | 0 | No
2030-04-25 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 60.91 | 53.65 | 0 | 0 | No
2030-04-26 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 360.91 | 353.65 | 0 | 0 | No
2030-04-26 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-26 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-26 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 374 | 390 | 390 | 0 | 0 | No
2030-04-26 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 74 | 90 | 90 | 0 | 0 | No
2030-04-26 05:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -226 | -210 | -210 | 0 | 0 | No
2030-04-26 06:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | -510 | 0 | 0 | No
2030-04-26 07:00 | 2030 33% ECP + 1.3 GW Offshore | -354.85 | -526 | -510 | -510 | 0 | 0 | No
2030-04-26 08:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-04-26 09:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | -325.77 | 0 | 0 | No
2030-04-26 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -185.3 | 0 | 0 | No
2030-04-26 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -400.75 | 0 | 0 | No
2030-04-26 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | -271.07 | 0 | 0 | No
2030-04-26 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -33.42 | -510 | -391.37 | 0 | 0 | No
2030-04-26 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -333.42 | -510 | -322.88 | 0 | 0 | No
2030-04-26 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -33.42 | -510 | -314.28 | 0 | 0 | No
2030-04-26 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -14.28 | 0 | 0 | No
2030-04-26 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -210 | -70.39 | 0 | 0 | No
2030-04-26 18:00 | 2030 33% ECP + 1.3 GW Offshore | 660.17 | -300 | -510 | -370.39 | 0 | 0 | No
2030-04-26 19:00 | 2030 33% ECP + 1.3 GW Offshore | 240.17 | -126.3 | -510 | -510 | 0 | 0 | Yes
2030-04-26 20:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -376.95 | -510 | -510 | 0 | 0 | No
2030-04-26 21:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -76.95 | -300 | -300 | 0 | 0 | No
2030-04-26 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 223.05 | 0 | 0 | 0 | 0 | No
2030-04-26 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -77.71 | 0 | 0 | 0 | No
2030-04-27 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 04:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 0 | 0 | 0 | 0 | 0 | No
2030-04-27 05:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -192.28 | -210 | -210 | 0 | 0 | No
2030-04-27 06:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -492.28 | -510 | -510 | 0 | 0 | No
2030-04-27 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-27 08:00 | 2030 33% ECP + 1.3 GW Offshore | -375.96 | -526 | -510 | -334.66 | 0 | 0 | No
2030-04-27 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -67 | 0 | 0 | No
2030-04-27 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -309.24 | 0 | 0 | No
2030-04-27 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -135.22 | 0 | 0 | No
2030-04-27 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -257.94 | 0 | 0 | No
2030-04-27 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -355.13 | 0 | 0 | No
2030-04-27 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -387.36 | 0 | 0 | No
2030-04-27 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -302.98 | 0 | 0 | No
2030-04-27 16:00 | 2030 33% ECP + 1.3 GW Offshore | -486.06 | -526 | -510 | -29.53 | 0 | 0 | No
2030-04-27 17:00 | 2030 33% ECP + 1.3 GW Offshore | -66.06 | -226 | -267.73 | -210 | 0 | 0 | No
2030-04-27 18:00 | 2030 33% ECP + 1.3 GW Offshore | 353.94 | -526 | -510 | -510 | 0 | 0 | No
2030-04-27 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-27 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-04-27 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-04-27 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 60.31 | 0 | 0 | No
2030-04-27 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 12.59 | 0 | 0 | 0 | No
2030-04-28 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -182.77 | 0 | 0 | 0 | No
2030-04-28 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -13.3 | 0 | 0 | 0 | No
2030-04-28 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-28 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -218.43 | 0 | 0 | 0 | No
2030-04-28 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-04-28 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -191.57 | 0 | 0 | 0 | No
2030-04-28 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -414.47 | 0 | 0 | 0 | No
2030-04-28 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -246.62 | -510 | -111.1 | 0 | 0 | No
2030-04-28 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -157.71 | 0 | 0 | No
2030-04-28 09:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -218.43 | 0 | 0 | No
2030-04-28 10:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -272.87 | 0 | 0 | No
2030-04-28 11:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -226.25 | 0 | 0 | No
2030-04-28 12:00 | 2030 33% ECP + 1.3 GW Offshore | -53.77 | -526 | -510 | -241.25 | 0 | 0 | No
2030-04-28 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -207.73 | 0 | 0 | No
2030-04-28 14:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | -302.37 | 0 | 0 | No
2030-04-28 15:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -153.43 | 0 | 0 | No
2030-04-28 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -139.23 | 0 | 0 | No
2030-04-28 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -8.88 | 0 | 0 | No
2030-04-28 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -263.4 | -510 | 35.28 | 0 | 0 | No
2030-04-28 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 62.37 | 0 | 0 | No
2030-04-28 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 151.73 | 0 | 0 | No
2030-04-28 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 136.7 | 0 | 0 | No
2030-04-28 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 60.43 | 0 | 0 | No
2030-04-28 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -510 | -95.26 | 0 | 0 | No
2030-04-29 | 2030 33% ECP + 1.3 GW Offshore | 700 | -260.62 | -510 | -101.23 | 0 | 0 | No
2030-04-29 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -144.22 | 0 | 0 | No
2030-04-29 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -108.97 | 0 | 0 | No
2030-04-29 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 49.37 | 0 | 0 | No
2030-04-29 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -187.91 | 0 | 0 | No
2030-04-29 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -107.2 | 0 | 0 | No
2030-04-29 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -64.96 | 0 | 0 | No
2030-04-29 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-04-29 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -300 | 0 | 0 | No
2030-04-29 09:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -252.02 | 0 | 0 | No
2030-04-29 10:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -405.78 | 0 | 0 | No
2030-04-29 11:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -105.78 | 0 | 0 | No
2030-04-29 12:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -226 | -256.42 | 194.22 | 0 | 0 | No
2030-04-29 13:00 | 2030 33% ECP + 1.3 GW Offshore | -214.09 | 74 | 43.58 | 494.22 | 0 | 0 | No
2030-04-29 14:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | 374 | 343.58 | 510 | 0 | 0 | No
2030-04-29 15:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-04-29 16:00 | 2030 33% ECP + 1.3 GW Offshore | 290.62 | 505 | 510 | 510 | 0 | 0 | No
2030-04-29 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 222.5 | 510 | 510 | 0 | 0 | No
2030-04-29 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 454.38 | 510 | 510 | 0 | 0 | No
2030-04-29 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 154.38 | 210 | 510 | 0 | 0 | Yes
2030-04-29 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -145.62 | -90 | 510 | 0 | 0 | No
2030-04-29 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 154.38 | 210 | 510 | 0 | 0 | No
2030-04-29 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 454.38 | 510 | 510 | 0 | 0 | No
2030-04-29 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-04-30 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 510 | 510 | 0 | 0 | No
2030-04-30 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 210 | 210 | 0 | 0 | No
2030-04-30 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -90 | -38.5 | 0 | 0 | No
2030-04-30 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 210 | 261.5 | 0 | 0 | No
2030-04-30 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 243.55 | 510 | 510 | 0 | 0 | No
2030-04-30 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 504.55 | 510 | 0 | 0 | No
2030-04-30 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 504.55 | 510 | 0 | 0 | No
2030-04-30 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 504.55 | 510 | 0 | 0 | No
2030-04-30 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 204.55 | 510 | 0 | 0 | No
2030-04-30 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-04-30 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 380.19 | 0 | 0 | No
2030-04-30 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 80.19 | 0 | 0 | No
2030-04-30 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 189.67 | 0 | 0 | No
2030-04-30 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -510 | 0 | 0 | 0 | No
2030-04-30 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 180.25 | 0 | 0 | No
2030-04-30 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 480.25 | 0 | 0 | No
2030-04-30 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -214.77 | -510 | 510 | 0 | 0 | No
2030-04-30 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -336.36 | 462.98 | 0 | 0 | No
2030-04-30 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -36.36 | 349.63 | 0 | 0 | No
2030-05-01 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 263.64 | 510 | 0 | 0 | No
2030-05-01 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 398.36 | 510 | 510 | 0 | 0 | No
2030-05-01 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-01 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-01 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 380.62 | 390 | 510 | 0 | 0 | No
2030-05-01 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 80.62 | 90 | 510 | 0 | 0 | No
2030-05-01 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -219.38 | -210 | 510 | 0 | 0 | No
2030-05-01 07:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -439.56 | -510 | 510 | 0 | 0 | No
2030-05-01 08:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 510 | 0 | 0 | No
2030-05-01 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-01 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 475.94 | 0 | 0 | Yes
2030-05-01 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 175.94 | 0 | 0 | Yes
2030-05-01 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -124.06 | 0 | 0 | Yes
2030-05-01 17:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | -128.68 | 0 | 0 | No
2030-05-01 18:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | 162.18 | 0 | 0 | No
2030-05-01 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 462.18 | 0 | 0 | No
2030-05-01 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-01 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-01 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-01 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 369.91 | 0 | 0 | No
2030-05-02 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -284.73 | 69.91 | 0 | 0 | No
2030-05-02 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 15.27 | 210 | 0 | 0 | No
2030-05-02 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 315.27 | 510 | 0 | 0 | No
2030-05-02 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-02 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 408.02 | 390 | 510 | 0 | 0 | No
2030-05-02 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 108.02 | 90 | 210 | 0 | 0 | No
2030-05-02 06:00 | 2030 33% ECP + 1.3 GW Offshore | 307.78 | -191.98 | -210 | -90 | 0 | 0 | No
2030-05-02 07:00 | 2030 33% ECP + 1.3 GW Offshore | 199.61 | -491.98 | -510 | -79.1 | 0 | 0 | No
2030-05-02 08:00 | 2030 33% ECP + 1.3 GW Offshore | -220.39 | -526 | -510 | -262.97 | 0 | 0 | No
2030-05-02 09:00 | 2030 33% ECP + 1.3 GW Offshore | 185.51 | -526 | -510 | -88.99 | 0 | 0 | No
2030-05-02 10:00 | 2030 33% ECP + 1.3 GW Offshore | -234.49 | -526 | -510 | 211.01 | 0 | 0 | No
2030-05-02 11:00 | 2030 33% ECP + 1.3 GW Offshore | -654.49 | -526 | -510 | 286.75 | 0 | 0 | No
2030-05-02 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 227.77 | 0 | 0 | No
2030-05-02 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 185.42 | 0 | 0 | No
2030-05-02 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 219.23 | 0 | 0 | No
2030-05-02 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 338.37 | 0 | 0 | No
2030-05-02 16:00 | 2030 33% ECP + 1.3 GW Offshore | -539.19 | -526 | -510 | 425.92 | 0 | 0 | No
2030-05-02 17:00 | 2030 33% ECP + 1.3 GW Offshore | -119.19 | -226 | -210 | 145.83 | 0 | 0 | No
2030-05-02 18:00 | 2030 33% ECP + 1.3 GW Offshore | 300.81 | -226 | -431.03 | 0 | 0 | 0 | No
2030-05-02 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -300 | 0 | 0 | No
2030-05-02 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -198.99 | 0 | 0 | No
2030-05-02 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 101.01 | 0 | 0 | No
2030-05-02 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 146.04 | 0 | 0 | No
2030-05-02 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 11.54 | 0 | 0 | No
2030-05-03 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 267.56 | 0 | 0 | 0 | No
2030-05-03 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 58.81 | 9.35 | 0 | 0 | No
2030-05-03 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -85.2 | 9.35 | 0 | 0 | No
2030-05-03 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -264.73 | 0 | 0 | 0 | No
2030-05-03 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -316.56 | 0 | 0 | 0 | No
2030-05-03 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -447.41 | 0 | 0 | 0 | No
2030-05-03 06:00 | 2030 33% ECP + 1.3 GW Offshore | 353.42 | 0 | -147.41 | 12.51 | 0 | 0 | No
2030-05-03 07:00 | 2030 33% ECP + 1.3 GW Offshore | -66.58 | -226 | -210 | 154.35 | 0 | 0 | No
2030-05-03 08:00 | 2030 33% ECP + 1.3 GW Offshore | -486.58 | -526 | -510 | 251.39 | 0 | 0 | No
2030-05-03 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 76.04 | 0 | 0 | No
2030-05-03 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 11.84 | 0 | 0 | No
2030-05-03 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 23.2 | 0 | 0 | No
2030-05-03 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 12.88 | 0 | 0 | No
2030-05-03 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-03 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-03 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-03 16:00 | 2030 33% ECP + 1.3 GW Offshore | -385.5 | -526 | -510 | 7.24 | 0 | 0 | No
2030-05-03 17:00 | 2030 33% ECP + 1.3 GW Offshore | 34.5 | -526 | -510 | -125.93 | 0 | 0 | No
2030-05-03 18:00 | 2030 33% ECP + 1.3 GW Offshore | 454.5 | -526 | -510 | -425.93 | 0 | 0 | No
2030-05-03 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-05-03 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -330.95 | 0 | 0 | No
2030-05-03 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | -30.95 | 0 | 0 | No
2030-05-03 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 206.08 | 0 | 0 | No
2030-05-03 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -94.12 | 0 | 0 | 0 | No
2030-05-04 | 2030 33% ECP + 1.3 GW Offshore | 700 | -135.8 | -394.12 | -300 | 0 | 0 | No
2030-05-04 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -93.48 | -510 | -430.83 | 0 | 0 | No
2030-05-04 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -111.84 | -510 | -298.74 | 0 | 0 | No
2030-05-04 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -312.32 | -510 | -247.64 | 0 | 0 | No
2030-05-04 04:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | -234.11 | 0 | 0 | No
2030-05-04 05:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -286.61 | 0 | 0 | No
2030-05-04 06:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | -526 | -510 | -155.74 | 0 | 0 | No
2030-05-04 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 144.26 | 0 | 0 | No
2030-05-04 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 40.12 | 0 | 0 | No
2030-05-04 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -75.5 | 0 | 0 | Yes
2030-05-04 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -214.04 | 0 | 0 | Yes
2030-05-04 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -194.42 | 0 | 0 | Yes
2030-05-04 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 18.43 | 0 | 0 | Yes
2030-05-04 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -34.85 | 0 | 0 | Yes
2030-05-04 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -275.08 | 0 | 0 | Yes
2030-05-04 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -300.08 | 0 | 0 | Yes
2030-05-04 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -260.7 | 0 | 0 | Yes
2030-05-04 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -309.52 | 0 | 0 | Yes
2030-05-04 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -246.84 | 0 | 0 | No
2030-05-04 19:00 | 2030 33% ECP + 1.3 GW Offshore | -555.7 | -526 | -510 | -220.64 | 0 | 0 | No
2030-05-04 20:00 | 2030 33% ECP + 1.3 GW Offshore | -135.7 | -526 | -510 | -196.3 | 0 | 0 | No
2030-05-04 21:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -172.62 | 0 | 0 | No
2030-05-04 22:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -409.38 | 0 | 0 | No
2030-05-04 23:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | -526 | -510 | -257.31 | 0 | 0 | No
2030-05-05 | 2030 33% ECP + 1.3 GW Offshore | -378.3 | -526 | -510 | 42.69 | 0 | 0 | No
2030-05-05 01:00 | 2030 33% ECP + 1.3 GW Offshore | -660.74 | -526 | -510 | 221.7 | 0 | 0 | No
2030-05-05 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 19.76 | 0 | 0 | Yes
2030-05-05 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -9.21 | 0 | 0 | No
2030-05-05 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -9.21 | 0 | 0 | No
2030-05-05 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-05 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -276.06 | 0 | 0 | Yes
2030-05-05 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -381.9 | 0 | 0 | Yes
2030-05-05 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -446.19 | 0 | 0 | Yes
2030-05-05 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -356.46 | 0 | 0 | Yes
2030-05-05 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -82.01 | 0 | 0 | Yes
2030-05-05 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -49.23 | 0 | 0 | Yes
2030-05-05 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -349.23 | 0 | 0 | Yes
2030-05-05 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -349.4 | 0 | 0 | Yes
2030-05-05 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -402.97 | 0 | 0 | Yes
2030-05-05 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -418.77 | 0 | 0 | Yes
2030-05-05 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -192.55 | 0 | 0 | Yes
2030-05-05 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 76.68 | 0 | 0 | Yes
2030-05-05 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 210.66 | 0 | 0 | No
2030-05-05 19:00 | 2030 33% ECP + 1.3 GW Offshore | -552.93 | -526 | -510 | 0 | 0 | 0 | No
2030-05-05 20:00 | 2030 33% ECP + 1.3 GW Offshore | -218.12 | -526 | -510 | 0 | 0 | 0 | No
2030-05-05 21:00 | 2030 33% ECP + 1.3 GW Offshore | -638.12 | -526 | -510 | 49.69 | 0 | 0 | No
2030-05-05 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-05 23:00 | 2030 33% ECP + 1.3 GW Offshore | -698.66 | -526 | -510 | 164.76 | 0 | 0 | No
2030-05-06 | 2030 33% ECP + 1.3 GW Offshore | -524.15 | -526 | -510 | 111.11 | 0 | 0 | No
2030-05-06 01:00 | 2030 33% ECP + 1.3 GW Offshore | -104.15 | -526 | -510 | -66.89 | 0 | 0 | No
2030-05-06 02:00 | 2030 33% ECP + 1.3 GW Offshore | -104.15 | -526 | -510 | -25.73 | 0 | 0 | No
2030-05-06 03:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -13.84 | 0 | 0 | No
2030-05-06 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -91.76 | 0 | 0 | No
2030-05-06 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -161.88 | 0 | 0 | No
2030-05-06 06:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | 83.43 | 0 | 0 | No
2030-05-06 07:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -21.37 | 0 | 0 | No
2030-05-06 08:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | -526 | -510 | 6.4 | 0 | 0 | Yes
2030-05-06 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 43.12 | 0 | 0 | Yes
2030-05-06 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -66.4 | 0 | 0 | Yes
2030-05-06 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -65.22 | 0 | 0 | Yes
2030-05-06 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -43.31 | 0 | 0 | Yes
2030-05-06 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -28.11 | 0 | 0 | Yes
2030-05-06 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -27.19 | 0 | 0 | Yes
2030-05-06 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -56.92 | 0 | 0 | Yes
2030-05-06 16:00 | 2030 33% ECP + 1.3 GW Offshore | -641.57 | -526 | -510 | 94.71 | 0 | 0 | Yes
2030-05-06 17:00 | 2030 33% ECP + 1.3 GW Offshore | -221.57 | -526 | -510 | 394.71 | 0 | 0 | No
2030-05-06 18:00 | 2030 33% ECP + 1.3 GW Offshore | 198.43 | -526 | -510 | 468.79 | 0 | 0 | No
2030-05-06 19:00 | 2030 33% ECP + 1.3 GW Offshore | -221.57 | -526 | -510 | 510 | 0 | 0 | No
2030-05-06 20:00 | 2030 33% ECP + 1.3 GW Offshore | -269.84 | -526 | -510 | 481.91 | 0 | 0 | No
2030-05-06 21:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | 510 | 0 | 0 | No
2030-05-06 22:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 510 | 0 | 0 | No
2030-05-06 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 431.39 | 0 | 0 | No
2030-05-07 | 2030 33% ECP + 1.3 GW Offshore | 291.54 | -526 | -510 | 228.74 | 0 | 0 | No
2030-05-07 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 234.25 | 0 | 0 | No
2030-05-07 02:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 175.51 | 0 | 0 | No
2030-05-07 03:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 162.38 | 0 | 0 | No
2030-05-07 04:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 173.69 | 0 | 0 | No
2030-05-07 05:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 182.17 | 0 | 0 | No
2030-05-07 06:00 | 2030 33% ECP + 1.3 GW Offshore | -163.52 | -526 | -510 | 208.09 | 0 | 0 | No
2030-05-07 07:00 | 2030 33% ECP + 1.3 GW Offshore | -146.11 | -526 | -510 | 334.52 | 0 | 0 | No
2030-05-07 08:00 | 2030 33% ECP + 1.3 GW Offshore | 273.89 | -526 | -510 | 407.03 | 0 | 0 | No
2030-05-07 09:00 | 2030 33% ECP + 1.3 GW Offshore | -146.11 | -526 | -510 | 311.95 | 0 | 0 | No
2030-05-07 10:00 | 2030 33% ECP + 1.3 GW Offshore | -566.11 | -526 | -510 | 292.16 | 0 | 0 | No
2030-05-07 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 234.29 | 0 | 0 | No
2030-05-07 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 105.28 | 0 | 0 | No
2030-05-07 13:00 | 2030 33% ECP + 1.3 GW Offshore | -597.36 | -526 | -510 | 65.74 | 0 | 0 | No
2030-05-07 14:00 | 2030 33% ECP + 1.3 GW Offshore | -177.36 | -526 | -510 | -3.91 | 0 | 0 | No
2030-05-07 15:00 | 2030 33% ECP + 1.3 GW Offshore | 242.64 | -526 | -510 | -30.8 | 0 | 0 | No
2030-05-07 16:00 | 2030 33% ECP + 1.3 GW Offshore | 662.64 | -526 | -510 | 190.3 | 0 | 0 | No
2030-05-07 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 359.12 | 0 | 0 | No
2030-05-07 18:00 | 2030 33% ECP + 1.3 GW Offshore | 391.08 | -300 | -510 | 322.65 | 0 | 0 | No
2030-05-07 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 402.7 | 0 | 0 | No
2030-05-07 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -81.71 | -510 | 417.54 | 0 | 0 | No
2030-05-07 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -380.66 | 488.3 | 0 | 0 | No
2030-05-07 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -80.66 | 499.8 | 0 | 0 | No
2030-05-07 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -380.66 | 291.9 | 0 | 0 | No
2030-05-08 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 58.12 | 0 | 0 | No
2030-05-08 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0.9 | 0 | 0 | No
2030-05-08 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -215.31 | 0.9 | 0 | 0 | No
2030-05-08 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -90.49 | 0 | 0 | 0 | No
2030-05-08 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -216.16 | 0 | 0 | 0 | No
2030-05-08 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -374.78 | 0 | 0 | 0 | No
2030-05-08 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-05-08 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 96.37 | 0 | 0 | No
2030-05-08 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 87.09 | 0 | 0 | No
2030-05-08 09:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 87.09 | 0 | 0 | No
2030-05-08 10:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 14.73 | 0 | 0 | No
2030-05-08 11:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 12:00 | 2030 33% ECP + 1.3 GW Offshore | -416.19 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 14:00 | 2030 33% ECP + 1.3 GW Offshore | -59.06 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 15:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 75.54 | 0 | 0 | No
2030-05-08 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -224.46 | 0 | 0 | No
2030-05-08 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -243.62 | 0 | 0 | No
2030-05-08 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-08 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -209.39 | 0 | 0 | No
2030-05-08 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -437.07 | -510 | 90.61 | 0 | 0 | No
2030-05-08 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -137.07 | -210 | 390.61 | 0 | 0 | No
2030-05-08 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 50.61 | 90.61 | 0 | 0 | No
2030-05-09 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -45.21 | 0 | 0 | 0 | No
2030-05-09 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -154.7 | 0 | 0 | 0 | No
2030-05-09 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -230.36 | 0 | 0 | 0 | No
2030-05-09 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -301.38 | 0 | 0 | 0 | No
2030-05-09 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -430.5 | 0 | 0 | 0 | No
2030-05-09 05:00 | 2030 33% ECP + 1.3 GW Offshore | 576.65 | 0 | -195 | 0 | 0 | 0 | No
2030-05-09 06:00 | 2030 33% ECP + 1.3 GW Offshore | 156.65 | -226 | -103.19 | 0 | 0 | 0 | No
2030-05-09 07:00 | 2030 33% ECP + 1.3 GW Offshore | -263.35 | -526 | 0 | -186.89 | 0 | 0 | No
2030-05-09 08:00 | 2030 33% ECP + 1.3 GW Offshore | -683.35 | -526 | 0 | 104.48 | 0 | 0 | No
2030-05-09 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | 87.38 | 0 | 0 | No
2030-05-09 10:00 | 2030 33% ECP + 1.3 GW Offshore | -334.67 | -526 | 0 | 52.09 | 0 | 0 | No
2030-05-09 11:00 | 2030 33% ECP + 1.3 GW Offshore | -109.36 | -526 | 0 | 69.33 | 0 | 0 | No
2030-05-09 12:00 | 2030 33% ECP + 1.3 GW Offshore | -109.36 | -526 | 0 | 80.43 | 0 | 0 | No
2030-05-09 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | 0 | 50.64 | 0 | 0 | No
2030-05-09 14:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | 0 | 38.79 | 0 | 0 | No
2030-05-09 15:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | 0 | 92.74 | 0 | 0 | No
2030-05-09 16:00 | 2030 33% ECP + 1.3 GW Offshore | 44.41 | -526 | 0 | 204.95 | 0 | 0 | No
2030-05-09 17:00 | 2030 33% ECP + 1.3 GW Offshore | 390.17 | -526 | 0 | 161.95 | 0 | 0 | No
2030-05-09 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | 0 | -74.79 | 0 | 0 | No
2030-05-09 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | 0 | 10.05 | 0 | 0 | No
2030-05-09 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 126.91 | 0 | 0 | No
2030-05-09 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 33.23 | 0 | 0 | No
2030-05-09 22:00 | 2030 33% ECP + 1.3 GW Offshore | 592.17 | -22.53 | 0 | -111.21 | 0 | 0 | No
2030-05-09 23:00 | 2030 33% ECP + 1.3 GW Offshore | 172.17 | -322.53 | 0 | -209.31 | 0 | 0 | No
2030-05-10 | 2030 33% ECP + 1.3 GW Offshore | -247.83 | -395 | 0 | -306.37 | 0 | 0 | No
2030-05-10 01:00 | 2030 33% ECP + 1.3 GW Offshore | -665.65 | -95 | 0 | -6.37 | 0 | 0 | No
2030-05-10 02:00 | 2030 33% ECP + 1.3 GW Offshore | -245.65 | 205 | 0 | 210 | 0 | 0 | No
2030-05-10 03:00 | 2030 33% ECP + 1.3 GW Offshore | -217.95 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 04:00 | 2030 33% ECP + 1.3 GW Offshore | -637.95 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 354.33 | 0 | 0 | Yes
2030-05-10 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 134.18 | 0 | 0 | Yes
2030-05-10 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 394.42 | 0 | 0 | Yes
2030-05-10 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 314.62 | 0 | 0 | Yes
2030-05-10 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 275.35 | 0 | 0 | Yes
2030-05-10 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 458.76 | 0 | 0 | Yes
2030-05-10 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-05-10 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-10 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 03:00 | 2030 33% ECP + 1.3 GW Offshore | -696.12 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 04:00 | 2030 33% ECP + 1.3 GW Offshore | -366.45 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | No
2030-05-11 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 300 | 510 | 0 | 0 | Yes
2030-05-11 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-11 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-05-11 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-05-11 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 327.67 | 0 | 0 | Yes
2030-05-11 17:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 27.67 | 0 | 0 | Yes
2030-05-11 18:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 0 | 0 | 0 | No
2030-05-11 19:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -226 | -510 | 0 | 0 | 0 | No
2030-05-11 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -385.54 | 232.54 | 0 | 0 | No
2030-05-11 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -85.54 | 280.7 | 0 | 0 | No
2030-05-11 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -56.34 | 0 | 0 | 0 | No
2030-05-11 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 300 | 0 | 0 | No
2030-05-12 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-12 06:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 300 | 300 | 510 | 0 | 0 | No
2030-05-12 07:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 0 | 0 | 510 | 0 | 0 | No
2030-05-12 08:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -300 | -300 | 224.84 | 0 | 0 | Yes
2030-05-12 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-12 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -201.59 | 0 | 0 | Yes
2030-05-12 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -51.87 | 0 | 0 | Yes
2030-05-12 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -351.87 | 0 | 0 | Yes
2030-05-12 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -84.47 | 0 | 0 | Yes
2030-05-12 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-05-12 15:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-05-12 16:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | -380.63 | 0 | 0 | No
2030-05-12 17:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | -428.39 | 0 | 0 | No
2030-05-12 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -304.57 | -510 | -224.08 | 0 | 0 | No
2030-05-12 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -4.57 | -510 | -43.31 | 0 | 0 | No
2030-05-12 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -4.57 | -510 | 0 | 0 | 0 | No
2030-05-12 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -26 | 0 | 0 | No
2030-05-12 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -210 | -16.76 | 0 | 0 | No
2030-05-12 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 202.62 | 90 | 210 | 0 | 0 | No
2030-05-13 | 2030 33% ECP + 1.3 GW Offshore | 700 | 502.62 | 390 | 510 | 0 | 0 | No
2030-05-13 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-13 06:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 374 | 390 | 510 | 0 | 0 | No
2030-05-13 07:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 74 | 90 | 510 | 0 | 0 | No
2030-05-13 08:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -210 | 510 | 0 | 0 | Yes
2030-05-13 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -431.34 | -510 | 510 | 0 | 0 | Yes
2030-05-13 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -322.41 | -510 | 510 | 0 | 0 | Yes
2030-05-13 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-13 17:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 510 | 0 | 0 | No
2030-05-13 18:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | 503.34 | 0 | 0 | No
2030-05-13 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 414.95 | 0 | 0 | No
2030-05-13 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -31.14 | -510 | 510 | 0 | 0 | No
2030-05-13 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -31.14 | -510 | 469.29 | 0 | 0 | No
2030-05-13 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -48.8 | -510 | 469.29 | 0 | 0 | No
2030-05-13 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -48.8 | -510 | 469.29 | 0 | 0 | No
2030-05-14 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 169.29 | 0 | 0 | No
2030-05-14 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 115.47 | 0 | 0 | No
2030-05-14 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 93.9 | 0 | 0 | No
2030-05-14 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 102.78 | 0 | 0 | No
2030-05-14 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -482.2 | 102.56 | 0 | 0 | No
2030-05-14 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 98.81 | 0 | 0 | No
2030-05-14 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 304.37 | 0 | 0 | No
2030-05-14 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 387.45 | 0 | 0 | No
2030-05-14 08:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 306.1 | 0 | 0 | No
2030-05-14 09:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | 312.87 | 0 | 0 | No
2030-05-14 10:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | -526 | -510 | 69.31 | 0 | 0 | No
2030-05-14 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 64.09 | 0 | 0 | No
2030-05-14 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -62.7 | 0 | 0 | No
2030-05-14 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -130.59 | 0 | 0 | No
2030-05-14 14:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 49.68 | 0 | 0 | No
2030-05-14 15:00 | 2030 33% ECP + 1.3 GW Offshore | -133.65 | -526 | -510 | -53.32 | 0 | 0 | No
2030-05-14 16:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -219.72 | 0 | 0 | No
2030-05-14 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 68.38 | 0 | 0 | No
2030-05-14 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-14 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -222.48 | 0 | 0 | 0 | No
2030-05-14 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 130.51 | 0 | 0 | No
2030-05-14 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -39.22 | 257.59 | 0 | 0 | No
2030-05-14 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -339.22 | 280.58 | 0 | 0 | No
2030-05-14 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -39.22 | 149.54 | 0 | 0 | No
2030-05-15 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -16.82 | 81.54 | 0 | 0 | No
2030-05-15 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-05-15 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 125.13 | 0 | 0 | No
2030-05-15 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 113.79 | 0 | 0 | No
2030-05-15 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 81.1 | 0 | 0 | No
2030-05-15 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 87.92 | 0 | 0 | No
2030-05-15 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 0 | 0 | 0 | No
2030-05-15 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 123.88 | 0 | 0 | No
2030-05-15 08:00 | 2030 33% ECP + 1.3 GW Offshore | 442.07 | -526 | -510 | 173.4 | 0 | 0 | No
2030-05-15 09:00 | 2030 33% ECP + 1.3 GW Offshore | 22.07 | -526 | -510 | -60.14 | 0 | 0 | No
2030-05-15 10:00 | 2030 33% ECP + 1.3 GW Offshore | -373 | -526 | -510 | -139.13 | 0 | 0 | No
2030-05-15 11:00 | 2030 33% ECP + 1.3 GW Offshore | -373 | -526 | -510 | -215.91 | 0 | 0 | No
2030-05-15 12:00 | 2030 33% ECP + 1.3 GW Offshore | -243.36 | -526 | -510 | -302.67 | 0 | 0 | No
2030-05-15 13:00 | 2030 33% ECP + 1.3 GW Offshore | -26.72 | -526 | -510 | -208.06 | 0 | 0 | No
2030-05-15 14:00 | 2030 33% ECP + 1.3 GW Offshore | 55.46 | -526 | -510 | -291.2 | 0 | 0 | No
2030-05-15 15:00 | 2030 33% ECP + 1.3 GW Offshore | 475.46 | -526 | -510 | -80.64 | 0 | 0 | No
2030-05-15 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 41.44 | 0 | 0 | No
2030-05-15 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -505.07 | -510 | 174.56 | 0 | 0 | No
2030-05-15 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -205.07 | -210 | 360.68 | 0 | 0 | No
2030-05-15 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 32.46 | 412.51 | 0 | 0 | No
2030-05-15 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 32.46 | 404.36 | 0 | 0 | No
2030-05-15 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 332.46 | 418.21 | 0 | 0 | No
2030-05-15 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 81.95 | 252.11 | 0 | 0 | No
2030-05-15 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 81.95 | 165.95 | 0 | 0 | No
2030-05-16 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 76.87 | 2.61 | 0 | 0 | No
2030-05-16 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 210 | 0 | 0 | 0 | No
2030-05-16 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 96.07 | 0 | 0 | No
2030-05-16 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 259.18 | 0 | 0 | No
2030-05-16 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 390 | 76.65 | 0 | 0 | No
2030-05-16 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 0 | 0 | 0 | No
2030-05-16 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -210 | 0 | 0 | 0 | No
2030-05-16 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -237.76 | -510 | 138.98 | 0 | 0 | No
2030-05-16 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 290.64 | 0 | 0 | No
2030-05-16 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 240.84 | 0 | 0 | No
2030-05-16 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -305.92 | -510 | 510 | 0 | 0 | No
2030-05-16 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -525.73 | -510 | 510 | 0 | 0 | No
2030-05-16 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 340.62 | 0 | 0 | No
2030-05-16 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 79.16 | 0 | 0 | No
2030-05-16 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 50.88 | 0 | 0 | No
2030-05-16 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 281.02 | 0 | 0 | No
2030-05-16 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -493.51 | 395.8 | 0 | 0 | No
2030-05-16 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -193.51 | 465.73 | 0 | 0 | No
2030-05-16 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -489.74 | 444.63 | 0 | 0 | No
2030-05-16 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -189.74 | 255.62 | 0 | 0 | No
2030-05-16 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -12.58 | 344.61 | 0 | 0 | No
2030-05-16 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -12.58 | 388.66 | 0 | 0 | No
2030-05-16 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -12.58 | 340.05 | 0 | 0 | No
2030-05-16 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -312.58 | 219.54 | 0 | 0 | No
2030-05-17 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -214.52 | 30.68 | 0 | 0 | No
2030-05-17 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -503.43 | 150.68 | 0 | 0 | No
2030-05-17 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -282.64 | -510 | 145.62 | 0 | 0 | No
2030-05-17 03:00 | 2030 33% ECP + 1.3 GW Offshore | 628.5 | -190.85 | -510 | 130.43 | 0 | 0 | No
2030-05-17 04:00 | 2030 33% ECP + 1.3 GW Offshore | 224.72 | -442.43 | -510 | 118.28 | 0 | 0 | No
2030-05-17 05:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 51.25 | 0 | 0 | No
2030-05-17 06:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 180.62 | 0 | 0 | No
2030-05-17 07:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 336.06 | 0 | 0 | No
2030-05-17 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 439.71 | 0 | 0 | No
2030-05-17 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 471.06 | 0 | 0 | No
2030-05-17 10:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -300 | -510 | 510 | 0 | 0 | No
2030-05-17 11:00 | 2030 33% ECP + 1.3 GW Offshore | 12.51 | 0 | -210 | 510 | 0 | 0 | No
2030-05-17 12:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 58.57 | 510 | 0 | 0 | No
2030-05-17 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 198.93 | 136.46 | 510 | 0 | 0 | No
2030-05-17 14:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 498.93 | 390 | 510 | 0 | 0 | No
2030-05-17 15:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 198.93 | 90 | 510 | 0 | 0 | No
2030-05-17 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -101.07 | -210 | 428.08 | 0 | 0 | No
2030-05-17 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -401.07 | -510 | 298.06 | 0 | 0 | No
2030-05-17 18:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 0 | 0 | 0 | No
2030-05-17 19:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | 0 | 0 | 0 | No
2030-05-17 20:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | 101.23 | 0 | 0 | No
2030-05-17 21:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | -526 | -510 | 317.17 | 0 | 0 | No
2030-05-17 22:00 | 2030 33% ECP + 1.3 GW Offshore | -315.43 | -526 | -510 | 395.18 | 0 | 0 | No
2030-05-17 23:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -300 | -328.32 | 278.7 | 0 | 0 | No
2030-05-18 | 2030 33% ECP + 1.3 GW Offshore | 420 | 0 | -28.32 | 510 | 0 | 0 | No
2030-05-18 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 271.68 | 510 | 0 | 0 | No
2030-05-18 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 05:00 | 2030 33% ECP + 1.3 GW Offshore | 442.59 | 205 | 210 | 510 | 0 | 0 | No
2030-05-18 06:00 | 2030 33% ECP + 1.3 GW Offshore | 22.59 | -95 | -90 | 243.13 | 0 | 0 | No
2030-05-18 07:00 | 2030 33% ECP + 1.3 GW Offshore | 442.59 | 205 | 210 | 479.31 | 0 | 0 | No
2030-05-18 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-18 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 357.59 | 510 | 0 | 0 | No
2030-05-18 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 57.59 | 281.1 | 0 | 0 | No
2030-05-18 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -242.41 | 510 | 0 | 0 | No
2030-05-18 18:00 | 2030 33% ECP + 1.3 GW Offshore | 537.14 | -526 | -510 | 510 | 0 | 0 | No
2030-05-18 19:00 | 2030 33% ECP + 1.3 GW Offshore | 117.14 | -526 | -510 | 510 | 0 | 0 | No
2030-05-18 20:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 510 | 0 | 0 | No
2030-05-18 21:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 366.54 | 0 | 0 | No
2030-05-18 22:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 130.01 | 0 | 0 | No
2030-05-18 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 130.01 | 0 | 0 | No
2030-05-19 | 2030 33% ECP + 1.3 GW Offshore | 584.37 | -300 | -448.25 | 192.24 | 0 | 0 | No
2030-05-19 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -148.25 | 492.24 | 0 | 0 | No
2030-05-19 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 151.75 | 510 | 0 | 0 | No
2030-05-19 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 293.64 | 90 | 510 | 0 | 0 | No
2030-05-19 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -6.36 | -210 | 484.35 | 0 | 0 | No
2030-05-19 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -306.36 | -510 | 184.35 | 0 | 0 | No
2030-05-19 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-05-19 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -36.82 | 0 | 0 | No
2030-05-19 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -1.32 | 0 | 0 | No
2030-05-19 09:00 | 2030 33% ECP + 1.3 GW Offshore | 332.37 | -526 | -510 | 0 | 0 | 0 | No
2030-05-19 10:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -47.95 | 0 | 0 | No
2030-05-19 11:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 9.68 | 0 | 0 | No
2030-05-19 12:00 | 2030 33% ECP + 1.3 GW Offshore | -260.69 | -526 | -510 | 0 | 0 | 0 | No
2030-05-19 13:00 | 2030 33% ECP + 1.3 GW Offshore | -405.14 | -526 | -510 | 158.21 | 0 | 0 | No
2030-05-19 14:00 | 2030 33% ECP + 1.3 GW Offshore | -12.92 | -526 | -510 | 333 | 0 | 0 | No
2030-05-19 15:00 | 2030 33% ECP + 1.3 GW Offshore | 11.52 | -526 | -510 | 268.44 | 0 | 0 | No
2030-05-19 16:00 | 2030 33% ECP + 1.3 GW Offshore | 431.52 | -526 | -510 | 331.11 | 0 | 0 | No
2030-05-19 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 418.03 | 0 | 0 | No
2030-05-19 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 418.03 | 0 | 0 | No
2030-05-19 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 249.77 | 0 | 0 | No
2030-05-19 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 211.32 | 0 | 0 | No
2030-05-19 21:00 | 2030 33% ECP + 1.3 GW Offshore | 570.99 | -526 | -510 | 184.85 | 0 | 0 | No
2030-05-19 22:00 | 2030 33% ECP + 1.3 GW Offshore | 426.74 | -526 | -510 | 0 | 0 | 0 | No
2030-05-19 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -115.68 | 0 | 0 | No
2030-05-20 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -25.42 | 0 | 0 | No
2030-05-20 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -487.52 | -510 | -14.67 | 0 | 0 | No
2030-05-20 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -57.84 | 0 | 0 | No
2030-05-20 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -57.84 | 0 | 0 | No
2030-05-20 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -143.23 | 0 | 0 | No
2030-05-20 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -48.59 | 0 | 0 | No
2030-05-20 06:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | -13.96 | 0 | 0 | No
2030-05-20 07:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -17.89 | 0 | 0 | No
2030-05-20 08:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | -526 | -510 | -79.1 | 0 | 0 | Yes
2030-05-20 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -81.61 | 0 | 0 | Yes
2030-05-20 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 158.42 | 0 | 0 | Yes
2030-05-20 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -62.67 | 0 | 0 | Yes
2030-05-20 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 237.33 | 0 | 0 | Yes
2030-05-20 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-20 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-20 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-20 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 439.87 | 0 | 0 | Yes
2030-05-20 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-20 18:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -472.43 | 510 | 0 | 0 | No
2030-05-20 19:00 | 2030 33% ECP + 1.3 GW Offshore | -318.89 | -526 | -510 | 510 | 0 | 0 | No
2030-05-20 20:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -300 | -389.23 | 497.42 | 0 | 0 | No
2030-05-20 21:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | -89.23 | 497.42 | 0 | 0 | No
2030-05-20 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 210.77 | 510 | 0 | 0 | No
2030-05-20 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-21 | 2030 33% ECP + 1.3 GW Offshore | 700 | 317.98 | 510 | 510 | 0 | 0 | No
2030-05-21 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-21 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-05-21 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 339.99 | 390 | 510 | 0 | 0 | No
2030-05-21 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 39.99 | 90 | 319.25 | 0 | 0 | No
2030-05-21 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -69.4 | -210 | 214.66 | 0 | 0 | No
2030-05-21 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -69.4 | -510 | 483.01 | 0 | 0 | No
2030-05-21 07:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -369.4 | -510 | 510 | 0 | 0 | No
2030-05-21 08:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 510 | 0 | 0 | No
2030-05-21 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-21 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 455.1 | 0 | 0 | Yes
2030-05-21 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 465.7 | 0 | 0 | Yes
2030-05-21 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 477.03 | 0 | 0 | Yes
2030-05-21 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 350.87 | 0 | 0 | Yes
2030-05-21 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 62.22 | 0 | 0 | Yes
2030-05-21 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -237.78 | 0 | 0 | Yes
2030-05-21 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -95.47 | 0 | 0 | Yes
2030-05-21 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 64.26 | 0 | 0 | No
2030-05-21 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -235.74 | 0 | 0 | No
2030-05-21 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 64.26 | 0 | 0 | No
2030-05-21 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 217.22 | 0 | 0 | No
2030-05-21 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -82.78 | 0 | 0 | No
2030-05-21 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -403.91 | -510 | -382.78 | 0 | 0 | Yes
2030-05-21 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -103.91 | -210 | -82.78 | 0 | 0 | Yes
2030-05-22 | 2030 33% ECP + 1.3 GW Offshore | -700 | 196.09 | 90 | 217.22 | 0 | 0 | Yes
2030-05-22 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 496.09 | 390 | 47.41 | 0 | 0 | Yes
2030-05-22 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 18.69 | 0 | 0 | Yes
2030-05-22 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 165.32 | 0 | 0 | Yes
2030-05-22 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 334.76 | 0 | 0 | Yes
2030-05-22 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 209.12 | 0 | 0 | Yes
2030-05-22 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 133.59 | 0 | 0 | Yes
2030-05-22 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 226.15 | 0 | 0 | Yes
2030-05-22 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 308.24 | 0 | 0 | Yes
2030-05-22 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 288.52 | 0 | 0 | Yes
2030-05-22 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 207.73 | 0 | 0 | Yes
2030-05-22 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 156.11 | 0 | 0 | Yes
2030-05-22 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 146.94 | 0 | 0 | Yes
2030-05-22 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 124.47 | 0 | 0 | Yes
2030-05-22 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 102.01 | 0 | 0 | Yes
2030-05-22 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 112.27 | 0 | 0 | Yes
2030-05-22 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 221.95 | 0 | 0 | Yes
2030-05-22 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 303.07 | 0 | 0 | Yes
2030-05-22 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 331.54 | 0 | 0 | Yes
2030-05-22 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 329.4 | 0 | 0 | Yes
2030-05-22 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 293.18 | 0 | 0 | Yes
2030-05-22 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 505.1 | 0 | 0 | Yes
2030-05-22 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 456.95 | 0 | 0 | Yes
2030-05-22 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 246.33 | 0 | 0 | Yes
2030-05-23 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 247.13 | 0 | 0 | Yes
2030-05-23 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 274.51 | 0 | 0 | Yes
2030-05-23 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 30.27 | 0 | 0 | Yes
2030-05-23 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -59.6 | 0 | 0 | Yes
2030-05-23 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 9.99 | 0 | 0 | Yes
2030-05-23 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -103.5 | 0 | 0 | Yes
2030-05-23 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -24 | 0 | 0 | Yes
2030-05-23 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 139.82 | 0 | 0 | Yes
2030-05-23 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 264.98 | 0 | 0 | Yes
2030-05-23 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 304.71 | 0 | 0 | Yes
2030-05-23 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 281.55 | 0 | 0 | Yes
2030-05-23 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 289.41 | 0 | 0 | Yes
2030-05-23 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 290.56 | 0 | 0 | Yes
2030-05-23 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 246.25 | 0 | 0 | Yes
2030-05-23 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 196.51 | 0 | 0 | Yes
2030-05-23 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 280.58 | 0 | 0 | Yes
2030-05-23 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 316.91 | 0 | 0 | Yes
2030-05-23 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 462.77 | 0 | 0 | Yes
2030-05-23 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 486.4 | 0 | 0 | Yes
2030-05-23 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-23 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-23 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-23 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-23 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-05-24 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-05-24 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-05-24 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-05-24 17:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 484.48 | 0 | 0 | No
2030-05-24 18:00 | 2030 33% ECP + 1.3 GW Offshore | -275.73 | -526 | -510 | 510 | 0 | 0 | No
2030-05-24 19:00 | 2030 33% ECP + 1.3 GW Offshore | 144.27 | -351.03 | -510 | 510 | 0 | 0 | No
2030-05-24 20:00 | 2030 33% ECP + 1.3 GW Offshore | 564.27 | -51.03 | -510 | 510 | 0 | 0 | No
2030-05-24 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-05-24 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-05-24 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -38.94 | -510 | 510 | 0 | 0 | No
2030-05-25 | 2030 33% ECP + 1.3 GW Offshore | 280 | -338.94 | -510 | 210 | 0 | 0 | No
2030-05-25 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 402.35 | 0 | 0 | No
2030-05-25 02:00 | 2030 33% ECP + 1.3 GW Offshore | 345.01 | -526 | 0 | 393.75 | 0 | 0 | No
2030-05-25 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 236.29 | 0 | 0 | No
2030-05-25 04:00 | 2030 33% ECP + 1.3 GW Offshore | 383.07 | -526 | 0 | 310.11 | 0 | 0 | No
2030-05-25 05:00 | 2030 33% ECP + 1.3 GW Offshore | -36.93 | -526 | 0 | 312.87 | 0 | 0 | No
2030-05-25 06:00 | 2030 33% ECP + 1.3 GW Offshore | -456.93 | -526 | 0 | 345.16 | 0 | 0 | No
2030-05-25 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | 264.79 | 0 | 0 | Yes
2030-05-25 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | -31.74 | 0 | 0 | Yes
2030-05-25 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | 0 | 0 | 0 | Yes
2030-05-25 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | -131.96 | 0 | 0 | Yes
2030-05-25 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | -360.86 | 0 | 0 | Yes
2030-05-25 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | -180.15 | 0 | 0 | Yes
2030-05-25 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | -36.59 | 0 | 0 | Yes
2030-05-25 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | -93.91 | 0 | 0 | Yes
2030-05-25 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | 167.39 | 0 | 0 | Yes
2030-05-25 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | 0 | 272.18 | 0 | 0 | Yes
2030-05-25 17:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | 0 | 0 | 0 | 0 | No
2030-05-25 18:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | 0 | 32.28 | 0 | 0 | No
2030-05-25 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 332.28 | 0 | 0 | No
2030-05-25 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 287.81 | 0 | 0 | No
2030-05-25 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | 0 | -12.19 | 0 | 0 | No
2030-05-25 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -304.39 | 0 | 287.81 | 0 | 0 | No
2030-05-25 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -4.39 | 0 | 350.13 | 0 | 0 | No
2030-05-26 | 2030 33% ECP + 1.3 GW Offshore | 700 | -151.27 | 0 | 50.13 | 0 | 0 | No
2030-05-26 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -151.27 | 0 | -45.6 | 0 | 0 | No
2030-05-26 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -279.52 | 0 | -68.86 | 0 | 0 | No
2030-05-26 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -279.52 | 0 | -87.93 | 0 | 0 | No
2030-05-26 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -279.52 | 0 | -191.33 | 0 | 0 | No
2030-05-26 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -378.72 | 0 | -70.33 | 0 | 0 | Yes
2030-05-26 06:00 | 2030 33% ECP + 1.3 GW Offshore | 593.45 | -226 | 0 | 10.21 | 0 | 0 | No
2030-05-26 07:00 | 2030 33% ECP + 1.3 GW Offshore | 173.45 | -526 | 0 | 25.46 | 0 | 0 | No
2030-05-26 08:00 | 2030 33% ECP + 1.3 GW Offshore | -246.55 | -526 | 0 | 25.73 | 0 | 0 | No
2030-05-26 09:00 | 2030 33% ECP + 1.3 GW Offshore | -666.55 | -526 | 0 | 0.65 | 0 | 0 | Yes
2030-05-26 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | -146.48 | 0 | 0 | Yes
2030-05-26 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | -85.34 | 0 | 0 | No
2030-05-26 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | -64.69 | 0 | 0 | Yes
2030-05-26 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | -82.74 | 0 | 0 | No
2030-05-26 14:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | -526 | 0 | 54.01 | 0 | 0 | No
2030-05-26 15:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | 0 | 91.87 | 0 | 0 | No
2030-05-26 16:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | 0 | 163.66 | 0 | 0 | No
2030-05-26 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 291.36 | 0 | 0 | No
2030-05-26 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 303.92 | 0 | 0 | No
2030-05-26 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -439.39 | 0 | 132.03 | 0 | 0 | No
2030-05-26 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -168.12 | 0 | 146.38 | 0 | 0 | No
2030-05-26 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 201.18 | 0 | 0 | No
2030-05-26 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 201.18 | 0 | 0 | No
2030-05-26 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 130.43 | 0 | 0 | No
2030-05-27 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 60.56 | 0 | 0 | No
2030-05-27 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 50.43 | 0 | 0 | No
2030-05-27 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 48.41 | 0 | 0 | No
2030-05-27 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 33.22 | 0 | 0 | No
2030-05-27 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 19.04 | 0 | 0 | No
2030-05-27 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -4.36 | 0 | 0 | No
2030-05-27 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -145.92 | -510 | 44.04 | 0 | 0 | No
2030-05-27 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -435.45 | -510 | 121.48 | 0 | 0 | No
2030-05-27 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 158.32 | 0 | 0 | No
2030-05-27 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 136.35 | 0 | 0 | No
2030-05-27 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 16.13 | 0 | 0 | No
2030-05-27 11:00 | 2030 33% ECP + 1.3 GW Offshore | 477.62 | -526 | -510 | -6.4 | 0 | 0 | No
2030-05-27 12:00 | 2030 33% ECP + 1.3 GW Offshore | 57.62 | -526 | -510 | -104.04 | 0 | 0 | No
2030-05-27 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -150.23 | 0 | 0 | No
2030-05-27 14:00 | 2030 33% ECP + 1.3 GW Offshore | 216.66 | -526 | -510 | -138.25 | 0 | 0 | No
2030-05-27 15:00 | 2030 33% ECP + 1.3 GW Offshore | 551.1 | -526 | -510 | -126.37 | 0 | 0 | No
2030-05-27 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 18.65 | 0 | 0 | No
2030-05-27 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 130.39 | 0 | 0 | No
2030-05-27 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -494.59 | -510 | 100.39 | 0 | 0 | No
2030-05-27 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -194.59 | -510 | 86.69 | 0 | 0 | No
2030-05-27 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 17.41 | 0 | 0 | No
2030-05-27 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 201.36 | 0 | 0 | No
2030-05-27 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 177.45 | 0 | 0 | No
2030-05-27 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -510 | 101.47 | 0 | 0 | No
2030-05-28 | 2030 33% ECP + 1.3 GW Offshore | 700 | -235.66 | -510 | 108.19 | 0 | 0 | No
2030-05-28 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -302.56 | -510 | 125.21 | 0 | 0 | No
2030-05-28 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -388.54 | -510 | 125.93 | 0 | 0 | No
2030-05-28 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 110.43 | 0 | 0 | No
2030-05-28 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 84.75 | 0 | 0 | No
2030-05-28 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 59.83 | 0 | 0 | No
2030-05-28 06:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | 119.19 | 0 | 0 | No
2030-05-28 07:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 171.14 | 0 | 0 | No
2030-05-28 08:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 255.38 | 0 | 0 | Yes
2030-05-28 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 194.46 | 0 | 0 | Yes
2030-05-28 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 147.69 | 0 | 0 | Yes
2030-05-28 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 130.79 | 0 | 0 | Yes
2030-05-28 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 67.47 | 0 | 0 | Yes
2030-05-28 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -30.48 | 0 | 0 | Yes
2030-05-28 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -73.21 | 0 | 0 | Yes
2030-05-28 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 9.46 | 0 | 0 | Yes
2030-05-28 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 79.09 | 0 | 0 | Yes
2030-05-28 17:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 176.48 | 0 | 0 | Yes
2030-05-28 18:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 166.98 | 0 | 0 | No
2030-05-28 19:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | 160.03 | 0 | 0 | No
2030-05-28 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 196.13 | 0 | 0 | No
2030-05-28 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 232.43 | 0 | 0 | No
2030-05-28 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 170.26 | 0 | 0 | No
2030-05-28 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 56.53 | 0 | 0 | No
2030-05-29 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -51.65 | 0 | 0 | No
2030-05-29 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 31.14 | 0 | 0 | No
2030-05-29 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -37.19 | 0 | 0 | No
2030-05-29 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 3.85 | 0 | 0 | No
2030-05-29 04:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | -76.14 | 0 | 0 | No
2030-05-29 05:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | -96.02 | 0 | 0 | No
2030-05-29 06:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -137.74 | 0 | 0 | Yes
2030-05-29 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -25.62 | 0 | 0 | Yes
2030-05-29 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -125.72 | 0 | 0 | Yes
2030-05-29 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -349.48 | 0 | 0 | Yes
2030-05-29 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -487.89 | 0 | 0 | Yes
2030-05-29 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -404.46 | 0 | 0 | Yes
2030-05-29 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-05-29 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -304.8 | 0 | 0 | Yes
2030-05-29 17:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -111.93 | 0 | 0 | Yes
2030-05-29 18:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 0 | 0 | 0 | No
2030-05-29 19:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | 299.18 | 0 | 0 | No
2030-05-29 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 344.28 | 0 | 0 | No
2030-05-29 21:00 | 2030 33% ECP + 1.3 GW Offshore | 583.1 | -526 | -510 | 333.77 | 0 | 0 | No
2030-05-29 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-29 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 475.06 | 0 | 0 | No
2030-05-30 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 247.17 | 0 | 0 | No
2030-05-30 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 361.4 | 0 | 0 | No
2030-05-30 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 327.07 | 0 | 0 | No
2030-05-30 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 470.72 | 0 | 0 | No
2030-05-30 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -426 | -510 | 382.6 | 0 | 0 | No
2030-05-30 05:00 | 2030 33% ECP + 1.3 GW Offshore | 633.76 | -526 | -510 | 331.19 | 0 | 0 | No
2030-05-30 06:00 | 2030 33% ECP + 1.3 GW Offshore | 213.76 | -526 | -510 | 33.6 | 0 | 0 | No
2030-05-30 07:00 | 2030 33% ECP + 1.3 GW Offshore | -206.24 | -526 | -510 | 333.6 | 0 | 0 | No
2030-05-30 08:00 | 2030 33% ECP + 1.3 GW Offshore | -626.24 | -526 | -510 | 393.25 | 0 | 0 | Yes
2030-05-30 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 275.63 | 0 | 0 | Yes
2030-05-30 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 268.82 | 0 | 0 | Yes
2030-05-30 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -474.11 | 510 | 0 | 0 | Yes
2030-05-30 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | Yes
2030-05-30 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 452.17 | 0 | 0 | Yes
2030-05-30 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 152.17 | 0 | 0 | Yes
2030-05-30 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-30 16:00 | 2030 33% ECP + 1.3 GW Offshore | -493.51 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-30 17:00 | 2030 33% ECP + 1.3 GW Offshore | -73.51 | -526 | -510 | 14.09 | 0 | 0 | No
2030-05-30 18:00 | 2030 33% ECP + 1.3 GW Offshore | 346.49 | -526 | -510 | 314.09 | 0 | 0 | No
2030-05-30 19:00 | 2030 33% ECP + 1.3 GW Offshore | 278.23 | -491.94 | -510 | 213.7 | 0 | 0 | No
2030-05-30 20:00 | 2030 33% ECP + 1.3 GW Offshore | 698.23 | -191.94 | -210 | 489.2 | 0 | 0 | Yes
2030-05-30 21:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 108.06 | 90 | 363.68 | 0 | 0 | No
2030-05-30 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 408.06 | 390 | 510 | 0 | 0 | No
2030-05-30 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 283.97 | 0 | 0 | No
2030-05-31 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 380.8 | 0 | 0 | No
2030-05-31 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 80.8 | 0 | 0 | No
2030-05-31 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 206.93 | 0 | 0 | No
2030-05-31 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 206.93 | 0 | 0 | No
2030-05-31 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 374 | 390 | 506.48 | 0 | 0 | No
2030-05-31 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 74 | 90 | 206.48 | 0 | 0 | No
2030-05-31 06:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -226 | -210 | -91.68 | 0 | 0 | No
2030-05-31 07:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | -391.68 | 0 | 0 | No
2030-05-31 08:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -237.19 | 0 | 0 | No
2030-05-31 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -58.71 | 0 | 0 | Yes
2030-05-31 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -252.69 | 0 | 0 | Yes
2030-05-31 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -144.36 | 0 | 0 | Yes
2030-05-31 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-31 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | Yes
2030-05-31 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 149.16 | 0 | 0 | Yes
2030-05-31 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 59.42 | 0 | 0 | Yes
2030-05-31 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 201.65 | 0 | 0 | No
2030-05-31 17:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 483.79 | 0 | 0 | No
2030-05-31 18:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | 483.79 | 0 | 0 | No
2030-05-31 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 483.79 | 0 | 0 | No
2030-05-31 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-31 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-31 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-05-31 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -519.44 | -510 | 442.01 | 0 | 0 | No
2030-06-01 | 2030 33% ECP + 1.3 GW Offshore | 700 | -219.44 | -210 | 382.83 | 0 | 0 | No
2030-06-01 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -45.02 | 126.32 | 0 | 0 | No
2030-06-01 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -66.92 | -345.02 | -150.63 | 0 | 0 | No
2030-06-01 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | -168.35 | 0 | 0 | No
2030-06-01 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -70.57 | 0 | 0 | No
2030-06-01 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -70.86 | 0 | 0 | No
2030-06-01 06:00 | 2030 33% ECP + 1.3 GW Offshore | 666.9 | -526 | -510 | -84.98 | 0 | 0 | No
2030-06-01 07:00 | 2030 33% ECP + 1.3 GW Offshore | 246.9 | -526 | -510 | -28.6 | 0 | 0 | No
2030-06-01 08:00 | 2030 33% ECP + 1.3 GW Offshore | -173.1 | -526 | -510 | -40.28 | 0 | 0 | No
2030-06-01 09:00 | 2030 33% ECP + 1.3 GW Offshore | -593.1 | -526 | -510 | -40.68 | 0 | 0 | No
2030-06-01 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -58.91 | 0 | 0 | No
2030-06-01 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -23.35 | 0 | 0 | No
2030-06-01 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -21.22 | 0 | 0 | No
2030-06-01 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -67.54 | 0 | 0 | No
2030-06-01 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -65.13 | 0 | 0 | No
2030-06-01 15:00 | 2030 33% ECP + 1.3 GW Offshore | -381.9 | -526 | -510 | -47.67 | 0 | 0 | No
2030-06-01 16:00 | 2030 33% ECP + 1.3 GW Offshore | 38.1 | -526 | -510 | 45.43 | 0 | 0 | No
2030-06-01 17:00 | 2030 33% ECP + 1.3 GW Offshore | 458.1 | -526 | -510 | 129.46 | 0 | 0 | No
2030-06-01 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 162.22 | 0 | 0 | No
2030-06-01 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -462.31 | 238.07 | 0 | 0 | No
2030-06-01 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -162.31 | 261.91 | 0 | 0 | No
2030-06-01 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -300 | 270.18 | 0 | 0 | No
2030-06-01 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 257.62 | 0 | 0 | No
2030-06-01 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -300 | 217.34 | 0 | 0 | No
2030-06-02 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 113.75 | 0 | 0 | No
2030-06-02 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -274.73 | 163.78 | 0 | 0 | No
2030-06-02 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -334.7 | 150.68 | 0 | 0 | No
2030-06-02 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -34.7 | 122.88 | 0 | 0 | No
2030-06-02 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -330.31 | 19.97 | 0 | 0 | No
2030-06-02 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -91.98 | -510 | 56.12 | 0 | 0 | No
2030-06-02 06:00 | 2030 33% ECP + 1.3 GW Offshore | 577.38 | -391.98 | -510 | 55.7 | 0 | 0 | No
2030-06-02 07:00 | 2030 33% ECP + 1.3 GW Offshore | 157.38 | -526 | -510 | 33.25 | 0 | 0 | No
2030-06-02 08:00 | 2030 33% ECP + 1.3 GW Offshore | -262.62 | -526 | -510 | -32.44 | 0 | 0 | No
2030-06-02 09:00 | 2030 33% ECP + 1.3 GW Offshore | -682.62 | -526 | -510 | -84.24 | 0 | 0 | No
2030-06-02 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -61.65 | 0 | 0 | Yes
2030-06-02 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -31.48 | 0 | 0 | Yes
2030-06-02 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -25.11 | 0 | 0 | Yes
2030-06-02 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -16.99 | 0 | 0 | Yes
2030-06-02 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -22.05 | 0 | 0 | No
2030-06-02 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -71.06 | 0 | 0 | No
2030-06-02 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -9.06 | 0 | 0 | No
2030-06-02 17:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | -210 | 0 | 0 | No
2030-06-02 18:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | -510 | 0 | 0 | No
2030-06-02 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -370.23 | 0 | 0 | No
2030-06-02 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -265.34 | 0 | 0 | No
2030-06-02 21:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 0 | 0 | 0 | No
2030-06-02 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 161.38 | 0 | 0 | No
2030-06-02 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 43.95 | 0 | 0 | No
2030-06-03 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 18.17 | 0 | 0 | No
2030-06-03 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -34.9 | 0 | 0 | No
2030-06-03 02:00 | 2030 33% ECP + 1.3 GW Offshore | 350.33 | -226 | -300 | 12.68 | 0 | 0 | No
2030-06-03 03:00 | 2030 33% ECP + 1.3 GW Offshore | -69.67 | 74 | 0 | 234.94 | 0 | 0 | No
2030-06-03 04:00 | 2030 33% ECP + 1.3 GW Offshore | -489.67 | 205 | 300 | 241.09 | 0 | 0 | Yes
2030-06-03 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-03 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 224.45 | 300 | 0 | 0 | Yes
2030-06-03 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | -75.55 | 0 | 0 | 0 | Yes
2030-06-03 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -375.55 | -300 | 0 | 0 | Yes
2030-06-03 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -468.16 | 0 | 0 | Yes
2030-06-03 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-03 19:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -210 | -210 | 0 | 0 | No
2030-06-03 20:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 74 | 90 | 90 | 0 | 0 | No
2030-06-03 21:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 374 | 390 | 390 | 0 | 0 | No
2030-06-03 22:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 74 | 510 | 312.62 | 0 | 0 | No
2030-06-03 23:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 374 | 510 | 116.99 | 0 | 0 | No
2030-06-04 | 2030 33% ECP + 1.3 GW Offshore | 420 | 505 | 510 | 416.99 | 0 | 0 | No
2030-06-04 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-04 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-04 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-04 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-04 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 220.39 | 210 | 510 | 0 | 0 | No
2030-06-04 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -79.61 | -90 | 275.76 | 0 | 0 | No
2030-06-04 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -379.61 | -390 | 279.05 | 0 | 0 | No
2030-06-04 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 449.11 | 0 | 0 | No
2030-06-04 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 311.54 | 0 | 0 | No
2030-06-04 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 59.59 | 0 | 0 | No
2030-06-04 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-04 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-04 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-04 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -171.74 | 0 | 0 | No
2030-06-04 15:00 | 2030 33% ECP + 1.3 GW Offshore | 644.29 | -526 | -510 | -294.04 | 0 | 0 | No
2030-06-04 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -110.84 | 0 | 0 | No
2030-06-04 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -95.71 | 0 | 0 | No
2030-06-04 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -63.07 | 0 | 0 | No
2030-06-04 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -363.07 | 0 | 0 | No
2030-06-04 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -124.97 | 0 | 0 | No
2030-06-04 21:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -193.1 | 0 | 0 | No
2030-06-04 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -149.42 | 0 | 0 | No
2030-06-04 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -13.26 | 0 | 0 | No
2030-06-05 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -344.56 | 0 | 0 | 0 | No
2030-06-05 01:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | -44.56 | 210 | 0 | 0 | No
2030-06-05 02:00 | 2030 33% ECP + 1.3 GW Offshore | 71.31 | 300 | 255.44 | 510 | 0 | 0 | No
2030-06-05 03:00 | 2030 33% ECP + 1.3 GW Offshore | -348.69 | 505 | 510 | 510 | 0 | 0 | No
2030-06-05 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-05 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 408.66 | 510 | 483.28 | 0 | 0 | No
2030-06-05 06:00 | 2030 33% ECP + 1.3 GW Offshore | -659.89 | 108.66 | 210 | 183.28 | 0 | 0 | No
2030-06-05 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -90 | -72.61 | 0 | 0 | No
2030-06-05 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 210 | 227.39 | 0 | 0 | Yes
2030-06-05 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 252.61 | 0 | 0 | Yes
2030-06-05 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 166.56 | 0 | 0 | Yes
2030-06-05 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 68.8 | 0 | 0 | Yes
2030-06-05 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 200.94 | 0 | 0 | Yes
2030-06-05 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 92.58 | 0 | 0 | Yes
2030-06-05 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 60.03 | 0 | 0 | Yes
2030-06-05 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 55.08 | 0 | 0 | Yes
2030-06-05 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 165.85 | 0 | 0 | Yes
2030-06-05 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 306.05 | 0 | 0 | Yes
2030-06-05 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 232.62 | 0 | 0 | Yes
2030-06-05 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 201.76 | 0 | 0 | Yes
2030-06-05 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 209.57 | 0 | 0 | Yes
2030-06-05 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 197.35 | 0 | 0 | Yes
2030-06-05 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 60.01 | 0 | 0 | Yes
2030-06-05 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -13.7 | 0 | 0 | Yes
2030-06-06 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 15.18 | 0 | 0 | Yes
2030-06-06 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-06 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 151.75 | 0 | 0 | Yes
2030-06-06 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 80.47 | 0 | 0 | Yes
2030-06-06 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-06 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-06 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 146.51 | 0 | 0 | Yes
2030-06-06 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 146.51 | 0 | 0 | Yes
2030-06-06 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 343.63 | 0 | 0 | Yes
2030-06-06 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 343.63 | 0 | 0 | Yes
2030-06-06 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 356.58 | 0 | 0 | Yes
2030-06-06 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 356.58 | 0 | 0 | Yes
2030-06-06 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-06 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-06 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-06 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 296.52 | 510 | 0 | 0 | Yes
2030-06-06 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | -3.48 | 510 | 0 | 0 | Yes
2030-06-06 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -303.48 | 292.09 | 0 | 0 | Yes
2030-06-06 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -7.91 | 0 | 0 | No
2030-06-06 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -307.91 | 0 | 0 | No
2030-06-06 20:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-06-06 21:00 | 2030 33% ECP + 1.3 GW Offshore | -98.45 | -526 | -510 | -510 | 0 | 0 | No
2030-06-06 22:00 | 2030 33% ECP + 1.3 GW Offshore | -518.45 | -226 | -210 | -362.58 | 0 | 0 | No
2030-06-06 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | -62.58 | 0 | 0 | No
2030-06-07 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 168.3 | 0 | 0 | Yes
2030-06-07 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 371.36 | 0 | 0 | Yes
2030-06-07 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 71.36 | 0 | 0 | Yes
2030-06-07 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 371.36 | 0 | 0 | Yes
2030-06-07 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 90 | 0 | 0 | Yes
2030-06-07 05:00 | 2030 33% ECP + 1.3 GW Offshore | -499.18 | 205 | 210 | -210 | 0 | 0 | No
2030-06-07 06:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -95 | -90 | -510 | 0 | 0 | No
2030-06-07 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -395 | -390 | -510 | 0 | 0 | No
2030-06-07 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-07 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-07 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-07 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -322.78 | -510 | -510 | 0 | 0 | Yes
2030-06-07 15:00 | 2030 33% ECP + 1.3 GW Offshore | -512.48 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-07 16:00 | 2030 33% ECP + 1.3 GW Offshore | -92.48 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 17:00 | 2030 33% ECP + 1.3 GW Offshore | 327.52 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 18:00 | 2030 33% ECP + 1.3 GW Offshore | -92.48 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 19:00 | 2030 33% ECP + 1.3 GW Offshore | 327.52 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-07 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -210 | 0 | 0 | No
2030-06-07 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -445.67 | 0 | 0 | No
2030-06-07 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -510 | -145.67 | 0 | 0 | No
2030-06-08 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -149.32 | 0 | 0 | No
2030-06-08 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -116.77 | 0 | 0 | No
2030-06-08 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -74.11 | 0 | 0 | No
2030-06-08 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -241.94 | 0 | 0 | 0 | No
2030-06-08 04:00 | 2030 33% ECP + 1.3 GW Offshore | 563.96 | 0 | -510 | -139.91 | 0 | 0 | No
2030-06-08 05:00 | 2030 33% ECP + 1.3 GW Offshore | 143.96 | 0 | -510 | -132.92 | 0 | 0 | No
2030-06-08 06:00 | 2030 33% ECP + 1.3 GW Offshore | -276.04 | -226 | -510 | -116.99 | 0 | 0 | No
2030-06-08 07:00 | 2030 33% ECP + 1.3 GW Offshore | -696.04 | -526 | -510 | -56.16 | 0 | 0 | No
2030-06-08 08:00 | 2030 33% ECP + 1.3 GW Offshore | -553.32 | -526 | -510 | -70.01 | 0 | 0 | No
2030-06-08 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -59.08 | 0 | 0 | No
2030-06-08 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -12.25 | 0 | 0 | No
2030-06-08 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 5.14 | 0 | 0 | No
2030-06-08 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -15.12 | 0 | 0 | No
2030-06-08 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -21.27 | 0 | 0 | No
2030-06-08 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -78.73 | 0 | 0 | No
2030-06-08 15:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | -526 | -510 | -95.75 | 0 | 0 | No
2030-06-08 16:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | -27.16 | 0 | 0 | No
2030-06-08 17:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 71.85 | 0 | 0 | No
2030-06-08 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -228.15 | 0 | 0 | No
2030-06-08 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-08 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-08 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -211.73 | 0 | 0 | No
2030-06-08 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 88.27 | 0 | 0 | No
2030-06-08 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 4.56 | 0 | 0 | No
2030-06-09 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 0 | 0 | 0 | No
2030-06-09 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 81.09 | 20.12 | 0 | 0 | No
2030-06-09 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 41.45 | 0 | 0 | No
2030-06-09 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 270.67 | 19 | 0 | 0 | No
2030-06-09 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 208.25 | 0 | 0 | 0 | No
2030-06-09 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 139.43 | 0 | 0 | 0 | No
2030-06-09 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -21.29 | 0 | 0 | 0 | No
2030-06-09 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -258.16 | 0 | 0 | 0 | No
2030-06-09 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -28.3 | 0 | 0 | No
2030-06-09 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -9.51 | 0 | 0 | No
2030-06-09 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 5.51 | 0 | 0 | No
2030-06-09 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 47.35 | 0 | 0 | No
2030-06-09 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 72.32 | 0 | 0 | No
2030-06-09 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 79.39 | 0 | 0 | No
2030-06-09 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 51.19 | 0 | 0 | No
2030-06-09 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 103.2 | 0 | 0 | No
2030-06-09 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 162.83 | 0 | 0 | No
2030-06-09 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -503.63 | -510 | 188.16 | 0 | 0 | No
2030-06-09 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -203.63 | -510 | 121.55 | 0 | 0 | No
2030-06-09 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 69.44 | 0 | 0 | No
2030-06-09 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 15.12 | 0 | 0 | No
2030-06-09 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 62.88 | 0 | 0 | No
2030-06-09 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 20.13 | 0 | 0 | No
2030-06-09 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -30.42 | 0 | 0 | No
2030-06-10 | 2030 33% ECP + 1.3 GW Offshore | 700 | -38.01 | -510 | 24.24 | 0 | 0 | No
2030-06-10 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 19.52 | 0 | 0 | No
2030-06-10 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -138.73 | 0 | 0 | No
2030-06-10 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -194.04 | 0 | 0 | No
2030-06-10 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -216.41 | 0 | 0 | No
2030-06-10 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -22.82 | -510 | -17.82 | 0 | 0 | No
2030-06-10 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -322.82 | -510 | 73.58 | 0 | 0 | No
2030-06-10 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 195.23 | 0 | 0 | No
2030-06-10 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 272.21 | 0 | 0 | No
2030-06-10 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 186.24 | 0 | 0 | No
2030-06-10 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 252.31 | 0 | 0 | No
2030-06-10 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 257.87 | 0 | 0 | No
2030-06-10 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 155.94 | 0 | 0 | No
2030-06-10 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 170.76 | 0 | 0 | No
2030-06-10 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 210.94 | 0 | 0 | No
2030-06-10 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 228.79 | 0 | 0 | No
2030-06-10 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 300.58 | 0 | 0 | No
2030-06-10 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 253.05 | 0 | 0 | No
2030-06-10 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 95.94 | 0 | 0 | No
2030-06-10 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -11.79 | 0 | 0 | No
2030-06-10 20:00 | 2030 33% ECP + 1.3 GW Offshore | 453.84 | -395 | -510 | -42.1 | 0 | 0 | No
2030-06-10 21:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -95 | -298.08 | -142 | 0 | 0 | No
2030-06-10 22:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 205 | 1.92 | -89.53 | 0 | 0 | No
2030-06-10 23:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | 505 | 301.92 | 181.94 | 0 | 0 | Yes
2030-06-11 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 4.7 | 0 | 0 | Yes
2030-06-11 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 151.1 | 0 | 0 | Yes
2030-06-11 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-11 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-06-11 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -41.11 | 0 | 0 | Yes
2030-06-11 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -82.3 | 0 | 0 | Yes
2030-06-11 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 78.85 | 0 | 0 | Yes
2030-06-11 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 120.41 | 0 | 0 | Yes
2030-06-11 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 269.21 | 0 | 0 | Yes
2030-06-11 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 88.67 | 0 | 0 | Yes
2030-06-11 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 54.93 | 0 | 0 | Yes
2030-06-11 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 67.07 | 0 | 0 | Yes
2030-06-11 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 280.95 | 0 | 0 | Yes
2030-06-11 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 300.57 | 0 | 0 | Yes
2030-06-11 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 422.74 | 0 | 0 | Yes
2030-06-11 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 351.26 | 510 | 0 | 0 | Yes
2030-06-11 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 51.26 | 422.1 | 0 | 0 | Yes
2030-06-11 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 351.26 | 510 | 0 | 0 | Yes
2030-06-11 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 415.22 | 0 | 0 | Yes
2030-06-11 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-11 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 437.56 | 0 | 0 | Yes
2030-06-12 | 2030 33% ECP + 1.3 GW Offshore | -572.37 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-12 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 290.88 | 0 | 0 | Yes
2030-06-12 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 61.21 | 0 | 0 | Yes
2030-06-12 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 99.24 | 0 | 0 | Yes
2030-06-12 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 33.94 | 0 | 0 | Yes
2030-06-12 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 173.5 | 0 | 0 | Yes
2030-06-12 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 52.77 | 0 | 0 | Yes
2030-06-12 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 209.64 | 0 | 0 | Yes
2030-06-12 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 510 | 166 | 0 | 0 | Yes
2030-06-12 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 367.68 | 0 | 0 | Yes
2030-06-12 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 344.05 | 0 | 0 | Yes
2030-06-12 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-12 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-12 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 479.84 | 390 | 390 | 0 | 0 | Yes
2030-06-12 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 179.84 | 90 | 90 | 0 | 0 | Yes
2030-06-12 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -120.16 | -210 | -210 | 0 | 0 | Yes
2030-06-12 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -420.16 | -510 | -510 | 0 | 0 | Yes
2030-06-12 17:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -226 | -510 | -409.24 | 0 | 0 | No
2030-06-12 18:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | -381.31 | 0 | 0 | No
2030-06-12 19:00 | 2030 33% ECP + 1.3 GW Offshore | 512.35 | -526 | -510 | -510 | 0 | 0 | No
2030-06-12 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-12 21:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -427.98 | 0 | 0 | No
2030-06-12 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -300 | -246.73 | 0 | 0 | No
2030-06-12 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 53.27 | 0 | 0 | No
2030-06-13 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 346.12 | 0 | 0 | No
2030-06-13 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 33.36 | 0 | 376.8 | 0 | 0 | No
2030-06-13 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -266.64 | -300 | 76.8 | 0 | 0 | No
2030-06-13 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -364.42 | 253.36 | 0 | 0 | No
2030-06-13 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 187.98 | 0 | 0 | No
2030-06-13 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -64.63 | 0 | 0 | No
2030-06-13 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -41.48 | 0 | 0 | No
2030-06-13 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -186.95 | 0 | 0 | No
2030-06-13 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -2.14 | 0 | 0 | No
2030-06-13 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 96.5 | 0 | 0 | No
2030-06-13 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 396.5 | 0 | 0 | No
2030-06-13 11:00 | 2030 33% ECP + 1.3 GW Offshore | 658.18 | -526 | -510 | 124.55 | 0 | 0 | No
2030-06-13 12:00 | 2030 33% ECP + 1.3 GW Offshore | 658.18 | -526 | -510 | 106.03 | 0 | 0 | No
2030-06-13 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 184.98 | 0 | 0 | No
2030-06-13 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -115.02 | 0 | 0 | No
2030-06-13 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 5.41 | 0 | 0 | No
2030-06-13 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -59.96 | 0 | 0 | No
2030-06-13 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 173.39 | 0 | 0 | No
2030-06-13 18:00 | 2030 33% ECP + 1.3 GW Offshore | 531.6 | -526 | -510 | 85.59 | 0 | 0 | No
2030-06-13 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 0 | 0 | 0 | No
2030-06-13 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -300 | 0 | 0 | No
2030-06-13 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-13 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 243.33 | 0 | 0 | No
2030-06-13 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -56.67 | 0 | 0 | No
2030-06-14 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -300 | 0 | 0 | No
2030-06-14 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-14 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -28.27 | 0 | 0 | No
2030-06-14 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-14 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-14 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -146.73 | -510 | -118.12 | 0 | 0 | No
2030-06-14 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -446.73 | -510 | -418.12 | 0 | 0 | No
2030-06-14 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -249.89 | 0 | 0 | No
2030-06-14 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 43.15 | 0 | 0 | No
2030-06-14 09:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 0 | 0 | 0 | No
2030-06-14 10:00 | 2030 33% ECP + 1.3 GW Offshore | 239.31 | -526 | -510 | -267.78 | 0 | 0 | No
2030-06-14 11:00 | 2030 33% ECP + 1.3 GW Offshore | 53.44 | -526 | -510 | -338.75 | 0 | 0 | No
2030-06-14 12:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -345.67 | 0 | 0 | No
2030-06-14 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -177.02 | 0 | 0 | No
2030-06-14 14:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 52.74 | 0 | 0 | No
2030-06-14 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 39.38 | 0 | 0 | No
2030-06-14 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -260.62 | 0 | 0 | No
2030-06-14 17:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -439.66 | 0 | 0 | No
2030-06-14 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-14 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-14 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -273.85 | 0 | 0 | No
2030-06-14 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -259.96 | -169.19 | 0 | 0 | No
2030-06-14 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 74 | 40.04 | 130.81 | 0 | 0 | No
2030-06-14 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 340.04 | 234.88 | 0 | 0 | No
2030-06-15 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 109.21 | 0 | 0 | 0 | No
2030-06-15 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 109.21 | 0 | 0 | 0 | No
2030-06-15 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-15 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -8.56 | 0 | 0 | 0 | No
2030-06-15 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-15 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-15 06:00 | 2030 33% ECP + 1.3 GW Offshore | 517.9 | -226 | -210 | -210 | 0 | 0 | No
2030-06-15 07:00 | 2030 33% ECP + 1.3 GW Offshore | 97.9 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 08:00 | 2030 33% ECP + 1.3 GW Offshore | 166.5 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 09:00 | 2030 33% ECP + 1.3 GW Offshore | -110.08 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 10:00 | 2030 33% ECP + 1.3 GW Offshore | -530.08 | -526 | -510 | -399.1 | 0 | 0 | No
2030-06-15 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -253.73 | 0 | 0 | No
2030-06-15 12:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -81.09 | 0 | 0 | No
2030-06-15 13:00 | 2030 33% ECP + 1.3 GW Offshore | -152.57 | -526 | -510 | -26.06 | 0 | 0 | No
2030-06-15 14:00 | 2030 33% ECP + 1.3 GW Offshore | -152.57 | -526 | -510 | -234.64 | 0 | 0 | No
2030-06-15 15:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -190.87 | 0 | 0 | No
2030-06-15 16:00 | 2030 33% ECP + 1.3 GW Offshore | 372.67 | -526 | -510 | -316.97 | 0 | 0 | No
2030-06-15 17:00 | 2030 33% ECP + 1.3 GW Offshore | -47.33 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 18:00 | 2030 33% ECP + 1.3 GW Offshore | 372.67 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-15 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | -210 | 0 | 0 | No
2030-06-15 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-16 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -238.47 | 0 | 0 | 0 | No
2030-06-16 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -238.47 | 0 | 0 | 0 | No
2030-06-16 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -380.09 | 0 | 0 | 0 | No
2030-06-16 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -359.02 | 0 | 0 | 0 | No
2030-06-16 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -359.02 | 0 | 0 | 0 | No
2030-06-16 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -359.02 | 0 | 0 | 0 | No
2030-06-16 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 0 | 0 | 0 | No
2030-06-16 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 10.1 | 0 | 0 | No
2030-06-16 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -13.29 | 0 | 0 | No
2030-06-16 09:00 | 2030 33% ECP + 1.3 GW Offshore | 673.48 | -526 | -510 | -39.79 | 0 | 0 | No
2030-06-16 10:00 | 2030 33% ECP + 1.3 GW Offshore | 253.48 | -526 | -510 | -42.27 | 0 | 0 | No
2030-06-16 11:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -24.41 | 0 | 0 | No
2030-06-16 12:00 | 2030 33% ECP + 1.3 GW Offshore | 197.13 | -526 | -510 | -2.14 | 0 | 0 | No
2030-06-16 13:00 | 2030 33% ECP + 1.3 GW Offshore | 197.13 | -526 | -510 | 12.2 | 0 | 0 | No
2030-06-16 14:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -35.95 | 0 | 0 | No
2030-06-16 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -81.93 | 0 | 0 | No
2030-06-16 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -40.29 | 0 | 0 | No
2030-06-16 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -72.52 | 0 | 0 | No
2030-06-16 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -510 | 49.47 | 0 | 0 | No
2030-06-16 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 25.39 | 0 | 0 | No
2030-06-16 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -183.59 | 0 | 0 | No
2030-06-16 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -90.79 | -510 | -230.2 | 0 | 0 | No
2030-06-16 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -141.35 | 0 | 0 | No
2030-06-16 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -90.07 | 0 | 0 | No
2030-06-17 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-17 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -507.02 | 0 | 0 | 0 | No
2030-06-17 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -507.02 | 0 | 0 | 0 | No
2030-06-17 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -507.02 | 0 | 0 | 0 | No
2030-06-17 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -507.02 | 0 | 0 | 0 | No
2030-06-17 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -507.02 | 0 | 0 | 0 | No
2030-06-17 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -507.02 | 0 | 0 | 0 | No
2030-06-17 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -507.02 | 100.93 | 0 | 0 | No
2030-06-17 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 260.26 | 0 | 0 | No
2030-06-17 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 305.02 | 0 | 0 | No
2030-06-17 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 291.04 | 0 | 0 | No
2030-06-17 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 329.28 | 0 | 0 | No
2030-06-17 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 298.33 | 0 | 0 | No
2030-06-17 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 222.47 | 0 | 0 | No
2030-06-17 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 254.31 | 0 | 0 | No
2030-06-17 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 261.47 | 0 | 0 | No
2030-06-17 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 319.01 | 0 | 0 | No
2030-06-17 17:00 | 2030 33% ECP + 1.3 GW Offshore | 404.36 | -300 | -471.75 | 405.81 | 0 | 0 | No
2030-06-17 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -171.75 | 429.43 | 0 | 0 | No
2030-06-17 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 128.25 | 314.76 | 0 | 0 | No
2030-06-17 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 312.76 | 0 | 0 | No
2030-06-17 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 69.65 | 295.55 | 0 | 0 | No
2030-06-17 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 241.56 | 0 | 0 | No
2030-06-17 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 120.58 | 0 | 0 | No
2030-06-18 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 206.18 | 86.35 | 0 | 0 | No
2030-06-18 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 91.5 | 0 | 0 | No
2030-06-18 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 98.7 | 0 | 0 | No
2030-06-18 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 88.63 | 0 | 0 | No
2030-06-18 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 56.02 | 0 | 0 | No
2030-06-18 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 32 | 0 | 0 | No
2030-06-18 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 93.41 | 0 | 0 | No
2030-06-18 07:00 | 2030 33% ECP + 1.3 GW Offshore | 318.31 | 0 | 0 | 222.31 | 0 | 0 | No
2030-06-18 08:00 | 2030 33% ECP + 1.3 GW Offshore | -101.69 | -300 | -300 | 248.59 | 0 | 0 | No
2030-06-18 09:00 | 2030 33% ECP + 1.3 GW Offshore | -521.69 | -526 | -510 | 248.77 | 0 | 0 | No
2030-06-18 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 209.93 | 0 | 0 | No
2030-06-18 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 233.04 | 0 | 0 | No
2030-06-18 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 237.37 | 0 | 0 | No
2030-06-18 13:00 | 2030 33% ECP + 1.3 GW Offshore | -566.46 | -526 | -510 | 187.7 | 0 | 0 | No
2030-06-18 14:00 | 2030 33% ECP + 1.3 GW Offshore | -271.74 | -526 | -510 | 192.96 | 0 | 0 | No
2030-06-18 15:00 | 2030 33% ECP + 1.3 GW Offshore | 148.26 | -241.68 | -510 | 185.35 | 0 | 0 | No
2030-06-18 16:00 | 2030 33% ECP + 1.3 GW Offshore | 568.26 | 0 | -274.27 | 227.25 | 0 | 0 | No
2030-06-18 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 25.73 | 182.62 | 0 | 0 | No
2030-06-18 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 235.13 | 0 | 0 | No
2030-06-18 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-18 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-18 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -8.38 | 0 | 0 | 0 | No
2030-06-18 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-18 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 83.38 | 0 | 0 | 0 | No
2030-06-19 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-06-19 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -300 | 0 | 0 | 0 | No
2030-06-19 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -32.35 | 0 | 0 | 0 | No
2030-06-19 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -295.16 | 0 | 0 | 0 | No
2030-06-19 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -406.04 | 0 | 0 | 0 | No
2030-06-19 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -334.22 | 0 | 0 | 0 | No
2030-06-19 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-06-19 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -242.38 | 115.77 | 0 | 0 | No
2030-06-19 08:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 0 | -363.47 | 126.62 | 0 | 0 | No
2030-06-19 09:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -176.34 | -510 | 251.22 | 0 | 0 | No
2030-06-19 10:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -510 | 119.91 | 0 | 0 | No
2030-06-19 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 290.26 | 0 | 0 | No
2030-06-19 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 244.28 | 0 | 0 | No
2030-06-19 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 217.35 | 0 | 0 | No
2030-06-19 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 219.19 | 0 | 0 | No
2030-06-19 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 230.92 | 0 | 0 | No
2030-06-19 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 54.71 | 0 | 0 | No
2030-06-19 17:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -488.33 | 3.35 | 0 | 0 | No
2030-06-19 18:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 0 | -188.33 | 93.26 | 0 | 0 | No
2030-06-19 19:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 0 | -188.33 | 212.49 | 0 | 0 | No
2030-06-19 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -262.25 | 258.03 | 0 | 0 | No
2030-06-19 21:00 | 2030 33% ECP + 1.3 GW Offshore | 510.32 | 0 | -51.03 | 292.25 | 0 | 0 | No
2030-06-19 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -51.03 | 161.77 | 0 | 0 | No
2030-06-19 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -210 | 140.22 | 0 | 0 | No
2030-06-20 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -486.23 | 67.28 | 0 | 0 | No
2030-06-20 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -457.4 | 137.52 | 0 | 0 | No
2030-06-20 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -162.64 | -510 | 127.39 | 0 | 0 | No
2030-06-20 03:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -321.64 | -510 | 78.68 | 0 | 0 | No
2030-06-20 04:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -70.75 | -510 | 62.67 | 0 | 0 | No
2030-06-20 05:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -510 | 0 | 0 | 0 | No
2030-06-20 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 38.76 | 0 | 0 | No
2030-06-20 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 120.76 | 0 | 0 | No
2030-06-20 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 42.02 | 0 | 0 | Yes
2030-06-20 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -121.11 | 0 | 0 | Yes
2030-06-20 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -82.26 | 0 | 0 | Yes
2030-06-20 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -288.57 | 0 | 0 | Yes
2030-06-20 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -501.41 | 0 | 0 | Yes
2030-06-20 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-20 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-06-20 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-06-20 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 44.06 | 0 | 0 | Yes
2030-06-21 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 344.06 | 0 | 0 | Yes
2030-06-21 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-21 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-06-21 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 499.86 | 0 | 0 | Yes
2030-06-21 17:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -210 | 199.86 | 0 | 0 | Yes
2030-06-21 18:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 10.73 | 0 | 0 | No
2030-06-21 19:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | 130.62 | 0 | 0 | No
2030-06-21 20:00 | 2030 33% ECP + 1.3 GW Offshore | 217.26 | -526 | -510 | 412.67 | 0 | 0 | No
2030-06-21 21:00 | 2030 33% ECP + 1.3 GW Offshore | 637.26 | -526 | -510 | 506.8 | 0 | 0 | No
2030-06-21 22:00 | 2030 33% ECP + 1.3 GW Offshore | 683.29 | -526 | -510 | 510 | 0 | 0 | No
2030-06-21 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 379.41 | 0 | 0 | No
2030-06-22 | 2030 33% ECP + 1.3 GW Offshore | 280 | -383.39 | -510 | 291.96 | 0 | 0 | No
2030-06-22 01:00 | 2030 33% ECP + 1.3 GW Offshore | 374.96 | -83.39 | -210 | 370.94 | 0 | 0 | No
2030-06-22 02:00 | 2030 33% ECP + 1.3 GW Offshore | 8.12 | 0 | -210 | 510 | 0 | 0 | No
2030-06-22 03:00 | 2030 33% ECP + 1.3 GW Offshore | -411.88 | -300 | -510 | 349.61 | 0 | 0 | No
2030-06-22 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 49.61 | 0 | 0 | No
2030-06-22 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -250.39 | 0 | 0 | Yes
2030-06-22 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-22 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-22 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-06-22 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-06-22 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-06-22 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-06-22 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 210 | 211.62 | 0 | 0 | Yes
2030-06-22 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -90 | -88.38 | 0 | 0 | Yes
2030-06-22 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 210 | 211.62 | 0 | 0 | Yes
2030-06-22 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-22 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-22 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 01:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 02:00 | 2030 33% ECP + 1.3 GW Offshore | 556.74 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 03:00 | 2030 33% ECP + 1.3 GW Offshore | 683.09 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 04:00 | 2030 33% ECP + 1.3 GW Offshore | 592.86 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 05:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-06-23 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 245.97 | 0 | 0 | No
2030-06-23 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 510 | 0 | 0 | No
2030-06-23 08:00 | 2030 33% ECP + 1.3 GW Offshore | 624.69 | 0 | 0 | 378.07 | 0 | 0 | No
2030-06-23 09:00 | 2030 33% ECP + 1.3 GW Offshore | 278.38 | 0 | 0 | 304.41 | 0 | 0 | No
2030-06-23 10:00 | 2030 33% ECP + 1.3 GW Offshore | 150.19 | 0 | -49.29 | 378.45 | 0 | 0 | No
2030-06-23 11:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -349.29 | 360.24 | 0 | 0 | No
2030-06-23 12:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -510 | 510 | 0 | 0 | No
2030-06-23 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -140.38 | -510 | 491.18 | 0 | 0 | No
2030-06-23 14:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -510 | 250.68 | 0 | 0 | No
2030-06-23 15:00 | 2030 33% ECP + 1.3 GW Offshore | 75.01 | -226 | -504.39 | 389.92 | 0 | 0 | No
2030-06-23 16:00 | 2030 33% ECP + 1.3 GW Offshore | 495.01 | -526 | -510 | 180.65 | 0 | 0 | No
2030-06-23 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 205.79 | 0 | 0 | No
2030-06-23 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-06-23 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 240.63 | 0 | 0 | No
2030-06-23 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 232.21 | 0 | 0 | No
2030-06-23 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -441.54 | -510 | 167.64 | 0 | 0 | No
2030-06-23 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -141.54 | -510 | 236.58 | 0 | 0 | No
2030-06-23 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -141.54 | -510 | 0 | 0 | 0 | No
2030-06-24 | 2030 33% ECP + 1.3 GW Offshore | 700 | -308.13 | -404.35 | 234.15 | 0 | 0 | No
2030-06-24 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -104.35 | 359.99 | 0 | 0 | No
2030-06-24 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 195.65 | 438.54 | 0 | 0 | No
2030-06-24 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 495.65 | 510 | 0 | 0 | No
2030-06-24 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-24 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 312.89 | 0 | 0 | No
2030-06-24 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 276.65 | 462.92 | 0 | 0 | No
2030-06-24 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 207.51 | 510 | 510 | 0 | 0 | No
2030-06-24 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 116.67 | 210 | 510 | 0 | 0 | No
2030-06-24 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -183.33 | -90 | 510 | 0 | 0 | No
2030-06-24 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -483.33 | -390 | 510 | 0 | 0 | No
2030-06-24 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 448.68 | 0 | 0 | No
2030-06-24 12:00 | 2030 33% ECP + 1.3 GW Offshore | 646.25 | -526 | -510 | 419.78 | 0 | 0 | No
2030-06-24 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 397.77 | 0 | 0 | No
2030-06-24 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 453.25 | 0 | 0 | No
2030-06-24 15:00 | 2030 33% ECP + 1.3 GW Offshore | 671.56 | -526 | -510 | 432.53 | 0 | 0 | No
2030-06-24 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 453.73 | 0 | 0 | No
2030-06-24 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 453.73 | 0 | 0 | No
2030-06-24 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -436.33 | -510 | 449.3 | 0 | 0 | No
2030-06-24 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -281.09 | -510 | 421.49 | 0 | 0 | No
2030-06-24 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-06-24 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -259.51 | 505.8 | 0 | 0 | No
2030-06-24 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 40.49 | 505.8 | 0 | 0 | No
2030-06-24 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 340.49 | 510 | 0 | 0 | No
2030-06-25 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 40.49 | 210 | 0 | 0 | No
2030-06-25 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -109.34 | 350.33 | 0 | 0 | No
2030-06-25 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -71.46 | -409.34 | 320.68 | 0 | 0 | No
2030-06-25 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -195.47 | -510 | 422.19 | 0 | 0 | No
2030-06-25 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 461.52 | 0 | 0 | No
2030-06-25 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 461.52 | 0 | 0 | No
2030-06-25 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-06-25 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-06-25 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 447.31 | 0 | 0 | No
2030-06-25 09:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 451.15 | 0 | 0 | No
2030-06-25 10:00 | 2030 33% ECP + 1.3 GW Offshore | 186.25 | -526 | -510 | 346.23 | 0 | 0 | No
2030-06-25 11:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | 405.8 | 0 | 0 | No
2030-06-25 12:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -226 | -210 | 510 | 0 | 0 | No
2030-06-25 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 0 | 510 | 0 | 0 | No
2030-06-25 14:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | 0 | 0 | 510 | 0 | 0 | No
2030-06-25 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -192.35 | 510 | 0 | 0 | No
2030-06-25 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -492.35 | 399.39 | 0 | 0 | No
2030-06-25 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -192.35 | 481.01 | 0 | 0 | No
2030-06-25 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 107.65 | 467.24 | 0 | 0 | No
2030-06-25 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 407.65 | 323.55 | 0 | 0 | No
2030-06-25 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 492.53 | 0 | 0 | No
2030-06-25 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 476.31 | 0 | 0 | No
2030-06-25 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 476.31 | 0 | 0 | No
2030-06-25 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 368.94 | 0 | 0 | No
2030-06-26 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 263.83 | 249.1 | 0 | 0 | No
2030-06-26 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 274.52 | 0 | 0 | No
2030-06-26 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 271.38 | 0 | 0 | No
2030-06-26 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 290.43 | 0 | 0 | No
2030-06-26 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 99.68 | 0 | 0 | No
2030-06-26 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -11.77 | 0 | 0 | 0 | No
2030-06-26 06:00 | 2030 33% ECP + 1.3 GW Offshore | 628.26 | 0 | -311.77 | 0 | 0 | 0 | No
2030-06-26 07:00 | 2030 33% ECP + 1.3 GW Offshore | 208.26 | -254.14 | -510 | 296.39 | 0 | 0 | No
2030-06-26 08:00 | 2030 33% ECP + 1.3 GW Offshore | -211.74 | -526 | -510 | 322.13 | 0 | 0 | No
2030-06-26 09:00 | 2030 33% ECP + 1.3 GW Offshore | 208.26 | -526 | -510 | 264.49 | 0 | 0 | No
2030-06-26 10:00 | 2030 33% ECP + 1.3 GW Offshore | -43.35 | -526 | -510 | 138.01 | 0 | 0 | No
2030-06-26 11:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -226 | -224.27 | 438.01 | 0 | 0 | No
2030-06-26 12:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -160.1 | -210 | 510 | 0 | 0 | No
2030-06-26 13:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | -460.1 | -510 | 338.03 | 0 | 0 | No
2030-06-26 14:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -160.1 | -210 | 510 | 0 | 0 | No
2030-06-26 15:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | 63.61 | 0 | 510 | 0 | 0 | No
2030-06-26 16:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -236.39 | -300 | 275.39 | 0 | 0 | No
2030-06-26 17:00 | 2030 33% ECP + 1.3 GW Offshore | -341.41 | -526 | -510 | 510 | 0 | 0 | No
2030-06-26 18:00 | 2030 33% ECP + 1.3 GW Offshore | -87.28 | -526 | -510 | 510 | 0 | 0 | No
2030-06-26 19:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 510 | 0 | 0 | No
2030-06-26 20:00 | 2030 33% ECP + 1.3 GW Offshore | 135.24 | -526 | -510 | 510 | 0 | 0 | No
2030-06-26 21:00 | 2030 33% ECP + 1.3 GW Offshore | 555.24 | -526 | -510 | 471.87 | 0 | 0 | No
2030-06-26 22:00 | 2030 33% ECP + 1.3 GW Offshore | 217.77 | -434.82 | -510 | 467.5 | 0 | 0 | No
2030-06-26 23:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -134.82 | -210 | 343.22 | 0 | 0 | No
2030-06-27 | 2030 33% ECP + 1.3 GW Offshore | 295.15 | 165.18 | 90 | 354.3 | 0 | 0 | No
2030-06-27 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 465.18 | 390 | 510 | 0 | 0 | No
2030-06-27 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-27 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 452.76 | 0 | 0 | No
2030-06-27 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -90 | 152.76 | 0 | 0 | No
2030-06-27 07:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -183.6 | -390 | 124.66 | 0 | 0 | No
2030-06-27 08:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 0 | -118.4 | 210 | 0 | 0 | No
2030-06-27 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 300 | 181.6 | 510 | 0 | 0 | No
2030-06-27 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 481.6 | 510 | 0 | 0 | Yes
2030-06-27 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 472.75 | 0 | 0 | Yes
2030-06-27 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-27 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 456.38 | 0 | 0 | Yes
2030-06-28 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 434.51 | 0 | 0 | Yes
2030-06-28 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 184.14 | 0 | 0 | Yes
2030-06-28 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 159.99 | 0 | 0 | Yes
2030-06-28 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 242.68 | 0 | 0 | Yes
2030-06-28 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 435.53 | 0 | 0 | Yes
2030-06-28 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 415.38 | 0 | 0 | Yes
2030-06-28 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 341.34 | 0 | 0 | Yes
2030-06-28 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 387.51 | 0 | 0 | Yes
2030-06-28 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 410.68 | 0 | 0 | Yes
2030-06-28 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 423.68 | 0 | 0 | Yes
2030-06-28 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 465.17 | 0 | 0 | Yes
2030-06-28 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-28 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 488.52 | 0 | 0 | Yes
2030-06-29 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-06-29 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 20:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 21:00 | 2030 33% ECP + 1.3 GW Offshore | -159.86 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 22:00 | 2030 33% ECP + 1.3 GW Offshore | 260.14 | 505 | 510 | 510 | 0 | 0 | No
2030-06-29 23:00 | 2030 33% ECP + 1.3 GW Offshore | 680.14 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 381.34 | 510 | 0 | 0 | No
2030-06-30 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-06-30 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 381.39 | 510 | 0 | 0 | No
2030-06-30 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 81.39 | 510 | 0 | 0 | No
2030-06-30 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -218.61 | 510 | 0 | 0 | No
2030-06-30 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-06-30 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-06-30 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 510 | 0 | 0 | No
2030-06-30 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -200.86 | 510 | 0 | 0 | No
2030-06-30 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-06-30 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-06-30 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-06-30 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-06-30 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-07-01 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 210 | 0 | 0 | No
2030-07-01 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 66.05 | 140.2 | 0 | 0 | No
2030-07-01 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 366.05 | 130.81 | 0 | 0 | No
2030-07-01 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 66.05 | 85.05 | 0 | 0 | No
2030-07-01 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 15.47 | 0 | 0 | No
2030-07-01 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-01 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 3.05 | 0 | 0 | No
2030-07-01 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 157.16 | 0 | 0 | No
2030-07-01 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -5.77 | -210 | 248.43 | 0 | 0 | No
2030-07-01 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -305.77 | -510 | 299.23 | 0 | 0 | No
2030-07-01 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 253.06 | 0 | 0 | No
2030-07-01 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 289.3 | 0 | 0 | No
2030-07-01 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 238.75 | 0 | 0 | No
2030-07-01 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 177.86 | 0 | 0 | No
2030-07-01 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 161.53 | 0 | 0 | No
2030-07-01 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 138.39 | 0 | 0 | No
2030-07-01 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 113.17 | 0 | 0 | No
2030-07-01 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -470.28 | -510 | 137.13 | 0 | 0 | No
2030-07-01 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -170.28 | -325.49 | 192.75 | 0 | 0 | No
2030-07-01 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -300 | 181.56 | 0 | 0 | No
2030-07-01 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 156.68 | 0 | 0 | No
2030-07-01 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 182.57 | 0 | 0 | No
2030-07-01 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 218.32 | 0 | 0 | No
2030-07-01 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 172.35 | 0 | 0 | No
2030-07-02 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -20.19 | 112.17 | 0 | 0 | No
2030-07-02 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -320.19 | 111.19 | 0 | 0 | No
2030-07-02 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 95.1 | 0 | 0 | No
2030-07-02 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 85.87 | 0 | 0 | No
2030-07-02 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -107.61 | -510 | 72.71 | 0 | 0 | No
2030-07-02 05:00 | 2030 33% ECP + 1.3 GW Offshore | 679.61 | -263.02 | -510 | 40.8 | 0 | 0 | No
2030-07-02 06:00 | 2030 33% ECP + 1.3 GW Offshore | 259.61 | 0 | -240.57 | 66.43 | 0 | 0 | No
2030-07-02 07:00 | 2030 33% ECP + 1.3 GW Offshore | -160.39 | -226 | -262.69 | 138.1 | 0 | 0 | No
2030-07-02 08:00 | 2030 33% ECP + 1.3 GW Offshore | -580.39 | -526 | -510 | 145.17 | 0 | 0 | No
2030-07-02 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -16.07 | 0 | 0 | No
2030-07-02 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -194.4 | 0 | 0 | No
2030-07-02 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -144.68 | 0 | 0 | No
2030-07-02 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 79.86 | 0 | 0 | No
2030-07-02 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 2.05 | 0 | 0 | No
2030-07-02 14:00 | 2030 33% ECP + 1.3 GW Offshore | -536.65 | -526 | -510 | 51.17 | 0 | 0 | No
2030-07-02 15:00 | 2030 33% ECP + 1.3 GW Offshore | -116.65 | -526 | -510 | 73.32 | 0 | 0 | No
2030-07-02 16:00 | 2030 33% ECP + 1.3 GW Offshore | -536.65 | -526 | -510 | 207.8 | 0 | 0 | No
2030-07-02 17:00 | 2030 33% ECP + 1.3 GW Offshore | -116.65 | -226 | -445.13 | 353.16 | 0 | 0 | No
2030-07-02 18:00 | 2030 33% ECP + 1.3 GW Offshore | 303.35 | 0 | -145.13 | 382.33 | 0 | 0 | No
2030-07-02 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -145.13 | 330.91 | 0 | 0 | No
2030-07-02 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -145.13 | 241.81 | 0 | 0 | No
2030-07-02 21:00 | 2030 33% ECP + 1.3 GW Offshore | 602.56 | 0 | -445.13 | 220.58 | 0 | 0 | No
2030-07-02 22:00 | 2030 33% ECP + 1.3 GW Offshore | 182.56 | -226 | -510 | 273.93 | 0 | 0 | No
2030-07-02 23:00 | 2030 33% ECP + 1.3 GW Offshore | -237.44 | -526 | -510 | 137.5 | 0 | 0 | No
2030-07-03 | 2030 33% ECP + 1.3 GW Offshore | -293.27 | -526 | -510 | -32.46 | 0 | 0 | No
2030-07-03 01:00 | 2030 33% ECP + 1.3 GW Offshore | 61.87 | -526 | -510 | 26.61 | 0 | 0 | No
2030-07-03 02:00 | 2030 33% ECP + 1.3 GW Offshore | -358.13 | -526 | -510 | -168.18 | 0 | 0 | No
2030-07-03 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -432.15 | -510 | 123.01 | 0 | 0 | No
2030-07-03 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 203.64 | 0 | 0 | Yes
2030-07-03 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -96.36 | 0 | 0 | Yes
2030-07-03 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -217.7 | 0 | 0 | Yes
2030-07-03 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 82.3 | 0 | 0 | No
2030-07-03 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 382.3 | 0 | 0 | No
2030-07-03 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-07-03 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-07-03 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-03 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 15:00 | 2030 33% ECP + 1.3 GW Offshore | -514.14 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 16:00 | 2030 33% ECP + 1.3 GW Offshore | -94.14 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 17:00 | 2030 33% ECP + 1.3 GW Offshore | 325.86 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 21:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 205 | 210 | 510 | 0 | 0 | No
2030-07-03 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-03 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-04 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 418.58 | 390 | 510 | 0 | 0 | No
2030-07-04 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 118.58 | 90 | 510 | 0 | 0 | No
2030-07-04 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -181.42 | -210 | 510 | 0 | 0 | No
2030-07-04 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -481.42 | -510 | 510 | 0 | 0 | No
2030-07-04 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -380.53 | 510 | 0 | 0 | No
2030-07-04 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -80.53 | 510 | 0 | 0 | No
2030-07-04 11:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 48.51 | 0 | 510 | 0 | 0 | No
2030-07-04 12:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -221.84 | -300 | 510 | 0 | 0 | No
2030-07-04 13:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | 0 | -248.48 | 510 | 0 | 0 | No
2030-07-04 14:00 | 2030 33% ECP + 1.3 GW Offshore | -432.42 | -226 | -310.07 | 510 | 0 | 0 | No
2030-07-04 15:00 | 2030 33% ECP + 1.3 GW Offshore | -12.42 | -526 | -510 | 510 | 0 | 0 | No
2030-07-04 16:00 | 2030 33% ECP + 1.3 GW Offshore | 210.79 | -526 | -510 | 510 | 0 | 0 | No
2030-07-04 17:00 | 2030 33% ECP + 1.3 GW Offshore | 103.08 | -526 | -510 | 390 | 0 | 0 | No
2030-07-04 18:00 | 2030 33% ECP + 1.3 GW Offshore | -316.92 | -526 | -510 | 90 | 0 | 0 | No
2030-07-04 19:00 | 2030 33% ECP + 1.3 GW Offshore | -560.82 | -526 | -510 | -210 | 0 | 0 | No
2030-07-04 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-07-04 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-07-04 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-07-04 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 208.99 | 0 | 0 | Yes
2030-07-05 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 67.35 | 0 | 0 | Yes
2030-07-05 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 73.48 | 0 | 0 | Yes
2030-07-05 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -23.37 | 0 | 0 | Yes
2030-07-05 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 226.84 | 0 | 0 | Yes
2030-07-05 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 266.02 | 0 | 0 | Yes
2030-07-05 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 479.2 | 0 | 0 | Yes
2030-07-05 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 187.52 | 0 | 0 | Yes
2030-07-05 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 339.7 | 510 | 0 | 0 | 0 | Yes
2030-07-05 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 12.42 | 0 | 0 | Yes
2030-07-05 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 497.37 | 210 | 179.41 | 0 | 0 | Yes
2030-07-05 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 330.15 | 510 | 153.25 | 0 | 0 | Yes
2030-07-05 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 488.82 | 108.58 | 0 | 0 | Yes
2030-07-05 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 265.54 | 0 | 0 | Yes
2030-07-05 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 200.67 | 0 | 0 | Yes
2030-07-05 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 275.32 | 0 | 0 | Yes
2030-07-05 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 446.61 | 0 | 0 | Yes
2030-07-05 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-05 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 363.32 | 0 | 0 | Yes
2030-07-05 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 499.18 | 0 | 0 | Yes
2030-07-06 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 501.15 | 0 | 0 | Yes
2030-07-06 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 278.43 | 0 | 0 | Yes
2030-07-06 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 110.31 | 0 | 0 | Yes
2030-07-06 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 188.49 | 0 | 0 | Yes
2030-07-06 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 488.49 | 0 | 0 | Yes
2030-07-06 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 351.89 | 0 | 0 | Yes
2030-07-06 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 447.87 | 0 | 0 | Yes
2030-07-06 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-06 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-07-06 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-07-06 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 284.44 | 0 | 0 | Yes
2030-07-06 15:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | -526 | -510 | -15.56 | 0 | 0 | No
2030-07-06 16:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | 0 | 0 | 0 | No
2030-07-06 17:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 265.64 | 0 | 0 | No
2030-07-06 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 11.42 | 0 | 0 | No
2030-07-06 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 311.42 | 0 | 0 | No
2030-07-06 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -358.67 | -510 | 282.7 | 0 | 0 | No
2030-07-06 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -358.67 | -510 | 85.41 | 0 | 0 | No
2030-07-06 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -358.67 | -390 | 385.41 | 0 | 0 | No
2030-07-06 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -90 | 88.41 | 0 | 0 | No
2030-07-07 | 2030 33% ECP + 1.3 GW Offshore | 317.44 | 205 | 210 | 347.13 | 0 | 0 | No
2030-07-07 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-07 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-07 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-07 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-07-07 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -90 | 210 | 0 | 0 | No
2030-07-07 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -395 | -390 | -19.39 | 0 | 0 | No
2030-07-07 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-07 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 65.79 | 0 | 0 | No
2030-07-07 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 183.31 | 0 | 0 | No
2030-07-07 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 297.05 | 0 | 0 | No
2030-07-07 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 372 | 0 | 0 | No
2030-07-07 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 329.33 | 0 | 0 | No
2030-07-07 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 482.05 | 0 | 0 | No
2030-07-07 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 442.48 | 0 | 0 | No
2030-07-07 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 307.68 | 0 | 0 | No
2030-07-07 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 307.68 | 0 | 0 | No
2030-07-07 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 418.62 | 0 | 0 | No
2030-07-07 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -286.6 | -510 | 217.02 | 0 | 0 | No
2030-07-07 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 174.66 | 0 | 0 | No
2030-07-07 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 92.82 | 0 | 0 | No
2030-07-07 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -64.87 | 0 | 0 | No
2030-07-07 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-07-07 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-07-08 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 31.04 | 0 | 0 | No
2030-07-08 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 2.59 | 0 | 0 | No
2030-07-08 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-07-08 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -490.24 | 0 | 0 | 0 | No
2030-07-08 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 3.21 | 0 | 0 | No
2030-07-08 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -216.68 | 0 | 0 | 0 | No
2030-07-08 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-07-08 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 127.35 | 0 | 0 | No
2030-07-08 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 163.63 | 0 | 0 | No
2030-07-08 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 174.42 | 0 | 0 | No
2030-07-08 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 174.42 | 0 | 0 | No
2030-07-08 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 198.32 | 0 | 0 | No
2030-07-08 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 227.98 | 0 | 0 | No
2030-07-08 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 207.41 | 0 | 0 | No
2030-07-08 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 227.1 | 0 | 0 | No
2030-07-08 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 243.48 | 0 | 0 | No
2030-07-08 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 303.34 | 0 | 0 | No
2030-07-08 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 389.83 | 0 | 0 | No
2030-07-08 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -362.71 | -510 | 316.21 | 0 | 0 | No
2030-07-08 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -390.06 | -510 | 262.85 | 0 | 0 | No
2030-07-08 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -465.81 | -510 | 150.57 | 0 | 0 | No
2030-07-08 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -165.81 | -510 | -94.92 | 0 | 0 | No
2030-07-08 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 7.67 | 0 | 0 | No
2030-07-08 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -162.84 | -210 | -90 | 0 | 0 | No
2030-07-09 | 2030 33% ECP + 1.3 GW Offshore | 700 | 127.44 | 90 | 210 | 0 | 0 | No
2030-07-09 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 427.44 | 390 | 510 | 0 | 0 | No
2030-07-09 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-09 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-09 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 261.66 | 510 | 0 | 0 | No
2030-07-09 05:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | -38.34 | 231.38 | 0 | 0 | No
2030-07-09 06:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -300 | -338.34 | 141.47 | 0 | 0 | No
2030-07-09 07:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 408.09 | 0 | 0 | No
2030-07-09 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 431.1 | 0 | 0 | No
2030-07-09 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 337.87 | 0 | 0 | No
2030-07-09 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 53.84 | 0 | 0 | No
2030-07-09 11:00 | 2030 33% ECP + 1.3 GW Offshore | 473.65 | -526 | -510 | -212.01 | 0 | 0 | No
2030-07-09 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -347.31 | 0 | 0 | No
2030-07-09 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -263.08 | 0 | 0 | No
2030-07-09 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -269.68 | 0 | 0 | No
2030-07-09 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -158.24 | 0 | 0 | No
2030-07-09 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -263.49 | 0 | 0 | No
2030-07-09 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -137.11 | 0 | 0 | No
2030-07-09 18:00 | 2030 33% ECP + 1.3 GW Offshore | 567.7 | -526 | -510 | -116.31 | 0 | 0 | No
2030-07-09 19:00 | 2030 33% ECP + 1.3 GW Offshore | 147.7 | -526 | -510 | 80.44 | 0 | 0 | No
2030-07-09 20:00 | 2030 33% ECP + 1.3 GW Offshore | -272.3 | -526 | -510 | 59.61 | 0 | 0 | No
2030-07-09 21:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | 359.61 | 0 | 0 | No
2030-07-09 22:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 510 | 0 | 0 | No
2030-07-09 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 357.8 | 0 | 0 | No
2030-07-10 | 2030 33% ECP + 1.3 GW Offshore | 700 | -490.03 | -510 | 248.41 | 0 | 0 | No
2030-07-10 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -453.88 | -510 | 346 | 0 | 0 | No
2030-07-10 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 309.05 | 0 | 0 | No
2030-07-10 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -323 | -510 | 336.08 | 0 | 0 | No
2030-07-10 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -460.06 | -510 | 107.5 | 0 | 0 | No
2030-07-10 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 250.08 | 0 | 0 | No
2030-07-10 06:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -513.77 | -510 | 352.24 | 0 | 0 | No
2030-07-10 07:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 337.68 | 0 | 0 | No
2030-07-10 08:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 286.98 | 0 | 0 | No
2030-07-10 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 34.57 | 0 | 0 | Yes
2030-07-10 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 16.96 | 0 | 0 | Yes
2030-07-10 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -283.04 | 0 | 0 | Yes
2030-07-10 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -192.89 | 0 | 0 | Yes
2030-07-10 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -177.6 | 0 | 0 | Yes
2030-07-10 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -379.6 | 0 | 0 | Yes
2030-07-10 15:00 | 2030 33% ECP + 1.3 GW Offshore | -512.17 | -526 | -510 | -488.85 | 0 | 0 | Yes
2030-07-10 16:00 | 2030 33% ECP + 1.3 GW Offshore | -92.17 | -526 | -510 | -510 | 0 | 0 | No
2030-07-10 17:00 | 2030 33% ECP + 1.3 GW Offshore | 327.83 | -526 | -510 | -210 | 0 | 0 | No
2030-07-10 18:00 | 2030 33% ECP + 1.3 GW Offshore | 164.4 | -526 | -510 | -48.67 | 0 | 0 | No
2030-07-10 19:00 | 2030 33% ECP + 1.3 GW Offshore | 584.4 | -226 | -463.64 | 131.94 | 0 | 0 | No
2030-07-10 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 182.6 | 0 | 0 | No
2030-07-10 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 482.6 | 0 | 0 | No
2030-07-10 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-07-10 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -326.27 | 350 | 0 | 0 | No
2030-07-11 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -318.22 | 50 | 0 | 0 | No
2030-07-11 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -318.22 | 28.52 | 0 | 0 | No
2030-07-11 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -149.92 | 0 | 0 | 0 | No
2030-07-11 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-11 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 3.51 | 0 | 0 | No
2030-07-11 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -300 | 0 | 0 | 0 | No
2030-07-11 06:00 | 2030 33% ECP + 1.3 GW Offshore | 635.7 | -226 | -510 | 0 | 0 | 0 | No
2030-07-11 07:00 | 2030 33% ECP + 1.3 GW Offshore | 215.7 | -526 | -510 | -7.63 | 0 | 0 | No
2030-07-11 08:00 | 2030 33% ECP + 1.3 GW Offshore | 635.7 | -526 | -510 | 21.54 | 0 | 0 | No
2030-07-11 09:00 | 2030 33% ECP + 1.3 GW Offshore | 215.7 | -526 | -510 | 7.8 | 0 | 0 | No
2030-07-11 10:00 | 2030 33% ECP + 1.3 GW Offshore | -157.44 | -526 | -510 | -33.8 | 0 | 0 | No
2030-07-11 11:00 | 2030 33% ECP + 1.3 GW Offshore | -429.34 | -526 | -510 | -6.37 | 0 | 0 | No
2030-07-11 12:00 | 2030 33% ECP + 1.3 GW Offshore | -9.34 | -526 | -510 | 99.27 | 0 | 0 | No
2030-07-11 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 72.88 | 0 | 0 | No
2030-07-11 14:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 56.56 | 0 | 0 | No
2030-07-11 15:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 142.33 | 0 | 0 | No
2030-07-11 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 166.12 | 0 | 0 | No
2030-07-11 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 256.75 | 0 | 0 | No
2030-07-11 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -314.44 | 309.92 | 0 | 0 | No
2030-07-11 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 331.71 | 0 | 0 | No
2030-07-11 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -210 | 319.13 | 0 | 0 | No
2030-07-11 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 306.35 | 0 | 0 | No
2030-07-11 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -210 | 245.28 | 0 | 0 | No
2030-07-11 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 156.03 | 0 | 0 | No
2030-07-12 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 14.35 | 0 | 0 | No
2030-07-12 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -332.78 | 69.15 | 0 | 0 | No
2030-07-12 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -475.44 | 47.68 | 0 | 0 | No
2030-07-12 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -211.07 | -510 | 24.93 | 0 | 0 | No
2030-07-12 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -511.07 | -510 | 9.72 | 0 | 0 | No
2030-07-12 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -27.47 | 0 | 0 | No
2030-07-12 06:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | -20.78 | 0 | 0 | No
2030-07-12 07:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | -20.12 | 0 | 0 | No
2030-07-12 08:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -98.06 | 0 | 0 | No
2030-07-12 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -170.74 | 0 | 0 | Yes
2030-07-12 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -143.62 | 0 | 0 | Yes
2030-07-12 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -210.07 | 0 | 0 | Yes
2030-07-12 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -162.58 | 0 | 0 | Yes
2030-07-12 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -369.7 | 0 | 0 | Yes
2030-07-12 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -329.83 | 0 | 0 | Yes
2030-07-12 15:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -384.15 | 0 | 0 | No
2030-07-12 16:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | -316.06 | 0 | 0 | No
2030-07-12 17:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | -171.9 | 0 | 0 | No
2030-07-12 18:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 19.99 | 0 | 0 | No
2030-07-12 19:00 | 2030 33% ECP + 1.3 GW Offshore | -35.15 | -526 | -510 | 63.24 | 0 | 0 | No
2030-07-12 20:00 | 2030 33% ECP + 1.3 GW Offshore | -455.15 | -526 | -510 | -73.24 | 0 | 0 | No
2030-07-12 21:00 | 2030 33% ECP + 1.3 GW Offshore | -108.82 | -526 | -510 | -2.41 | 0 | 0 | No
2030-07-12 22:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -7.8 | 0 | 0 | No
2030-07-12 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -76.37 | 0 | 0 | No
2030-07-13 | 2030 33% ECP + 1.3 GW Offshore | 437.22 | -226 | -210 | 210 | 0 | 0 | No
2030-07-13 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 74 | 90 | 510 | 0 | 0 | No
2030-07-13 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 374 | 390 | 510 | 0 | 0 | No
2030-07-13 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-13 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 495.09 | 0 | 0 | No
2030-07-13 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -90 | 195.09 | 0 | 0 | No
2030-07-13 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -395 | -390 | -104.91 | 0 | 0 | No
2030-07-13 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -404.91 | 0 | 0 | No
2030-07-13 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -419.32 | 0 | 0 | No
2030-07-13 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -119.32 | 0 | 0 | No
2030-07-13 10:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -226 | -510 | 180.68 | 0 | 0 | No
2030-07-13 11:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -213.88 | 153.2 | 0 | 0 | No
2030-07-13 12:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 86.12 | 210 | 0 | 0 | No
2030-07-13 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 103.81 | 386.12 | 510 | 0 | 0 | No
2030-07-13 14:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 78.06 | 214.04 | 510 | 0 | 0 | No
2030-07-13 15:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | -85.96 | 229.99 | 0 | 0 | No
2030-07-13 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -385.96 | -70.01 | 0 | 0 | No
2030-07-13 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-13 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -371.33 | -510 | 0 | 0 | 0 | No
2030-07-13 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -71.33 | -510 | 0 | 0 | 0 | No
2030-07-13 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -371.33 | -510 | 155.36 | 0 | 0 | No
2030-07-13 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -71.33 | -510 | 72.25 | 0 | 0 | No
2030-07-13 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -371.33 | -510 | 209.55 | 0 | 0 | No
2030-07-13 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -71.33 | -483.5 | 13.06 | 0 | 0 | No
2030-07-14 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -183.5 | 313.06 | 0 | 0 | No
2030-07-14 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 116.5 | 285.53 | 0 | 0 | No
2030-07-14 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 416.5 | 510 | 0 | 0 | No
2030-07-14 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-14 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-14 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 442.97 | 390 | 510 | 0 | 0 | No
2030-07-14 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 142.97 | 90 | 210 | 0 | 0 | No
2030-07-14 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -157.03 | -210 | 268 | 0 | 0 | No
2030-07-14 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -457.03 | -510 | -32 | 0 | 0 | No
2030-07-14 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 237.39 | 0 | 0 | No
2030-07-14 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 31.62 | 0 | 0 | No
2030-07-14 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 180.76 | 0 | 0 | No
2030-07-14 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 177.01 | 0 | 0 | No
2030-07-14 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 259.72 | 0 | 0 | No
2030-07-14 18:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 212.67 | 0 | 0 | No
2030-07-14 19:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 178.18 | 0 | 0 | No
2030-07-14 20:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 226.59 | 0 | 0 | No
2030-07-14 21:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 123.51 | 0 | 0 | No
2030-07-14 22:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-07-14 23:00 | 2030 33% ECP + 1.3 GW Offshore | -62.88 | -526 | -510 | 67.71 | 0 | 0 | No
2030-07-15 | 2030 33% ECP + 1.3 GW Offshore | 14.55 | -526 | -510 | 33.17 | 0 | 0 | No
2030-07-15 01:00 | 2030 33% ECP + 1.3 GW Offshore | 14.55 | -526 | -510 | 159.32 | 0 | 0 | No
2030-07-15 02:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-07-15 03:00 | 2030 33% ECP + 1.3 GW Offshore | 184.15 | -526 | -510 | 54.42 | 0 | 0 | No
2030-07-15 04:00 | 2030 33% ECP + 1.3 GW Offshore | 604.15 | -526 | -510 | -64.39 | 0 | 0 | No
2030-07-15 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 50.27 | 0 | 0 | No
2030-07-15 06:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | -56.32 | 0 | 0 | No
2030-07-15 07:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 57.36 | 0 | 0 | No
2030-07-15 08:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -24.52 | 0 | 0 | No
2030-07-15 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -95.12 | 0 | 0 | Yes
2030-07-15 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -209.49 | 0 | 0 | Yes
2030-07-15 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -136.16 | 0 | 0 | Yes
2030-07-15 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -171.79 | 0 | 0 | Yes
2030-07-15 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -355.39 | 0 | 0 | Yes
2030-07-15 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -190.84 | 0 | 0 | Yes
2030-07-15 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 49.14 | 0 | 0 | Yes
2030-07-15 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -60.73 | 0 | 0 | No
2030-07-15 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-15 18:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -125.38 | 0 | 0 | No
2030-07-15 19:00 | 2030 33% ECP + 1.3 GW Offshore | 12.58 | -526 | -510 | -95.46 | 0 | 0 | No
2030-07-15 20:00 | 2030 33% ECP + 1.3 GW Offshore | 432.58 | -526 | -510 | 182.59 | 0 | 0 | No
2030-07-15 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 169.82 | 0 | 0 | No
2030-07-15 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 40.04 | 0 | 0 | No
2030-07-15 23:00 | 2030 33% ECP + 1.3 GW Offshore | 457.43 | -300 | -397.6 | 43.65 | 0 | 0 | No
2030-07-16 | 2030 33% ECP + 1.3 GW Offshore | 618.15 | 0 | -97.6 | 210 | 0 | 0 | No
2030-07-16 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 202.4 | 510 | 0 | 0 | No
2030-07-16 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 201.62 | 434.36 | 0 | 0 | No
2030-07-16 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 134.36 | 0 | 0 | No
2030-07-16 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -210 | 265.06 | 0 | 0 | No
2030-07-16 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 290.13 | 0 | 0 | No
2030-07-16 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 380.27 | 0 | 0 | No
2030-07-16 07:00 | 2030 33% ECP + 1.3 GW Offshore | 512.95 | 0 | -510 | 510 | 0 | 0 | No
2030-07-16 08:00 | 2030 33% ECP + 1.3 GW Offshore | 92.95 | -292.79 | -510 | 510 | 0 | 0 | No
2030-07-16 09:00 | 2030 33% ECP + 1.3 GW Offshore | -327.05 | -526 | -510 | 510 | 0 | 0 | No
2030-07-16 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 480.4 | 0 | 0 | No
2030-07-16 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 379.68 | 0 | 0 | No
2030-07-16 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 159.19 | 0 | 0 | No
2030-07-16 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 7.14 | 0 | 0 | No
2030-07-16 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -164.14 | 0 | 0 | No
2030-07-16 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -464.14 | 0 | 0 | No
2030-07-16 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -164.14 | 0 | 0 | No
2030-07-16 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 135.86 | 0 | 0 | No
2030-07-16 18:00 | 2030 33% ECP + 1.3 GW Offshore | -374.05 | -526 | -510 | 12.14 | 0 | 0 | No
2030-07-16 19:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 306.74 | 0 | 0 | No
2030-07-16 20:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | 377.85 | 0 | 0 | No
2030-07-16 21:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 323.42 | 0 | 0 | No
2030-07-16 22:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | 401.72 | 0 | 0 | No
2030-07-16 23:00 | 2030 33% ECP + 1.3 GW Offshore | 205.48 | -526 | -510 | 235.39 | 0 | 0 | No
2030-07-17 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 264.38 | 0 | 0 | No
2030-07-17 01:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -307.41 | -510 | 82.03 | 0 | 0 | No
2030-07-17 02:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -7.41 | -510 | 382.03 | 0 | 0 | No
2030-07-17 03:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -182.23 | -510 | 136.47 | 0 | 0 | No
2030-07-17 04:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -226 | -498.46 | 0 | 0 | 0 | No
2030-07-17 05:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -62.22 | 0 | 0 | No
2030-07-17 06:00 | 2030 33% ECP + 1.3 GW Offshore | -90.95 | -526 | -510 | -24.67 | 0 | 0 | No
2030-07-17 07:00 | 2030 33% ECP + 1.3 GW Offshore | -510.95 | -526 | -510 | 184.7 | 0 | 0 | No
2030-07-17 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 473.13 | 0 | 0 | No
2030-07-17 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 484.8 | 0 | 0 | No
2030-07-17 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 460.69 | 0 | 0 | No
2030-07-17 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 473.12 | 0 | 0 | No
2030-07-17 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 17:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-07-17 18:00 | 2030 33% ECP + 1.3 GW Offshore | 103.6 | -526 | -510 | 502.25 | 0 | 0 | No
2030-07-17 19:00 | 2030 33% ECP + 1.3 GW Offshore | 523.6 | -526 | -510 | 506.09 | 0 | 0 | No
2030-07-17 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 498.86 | 0 | 0 | No
2030-07-17 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 484.31 | 0 | 0 | No
2030-07-17 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 444.11 | 0 | 0 | No
2030-07-17 23:00 | 2030 33% ECP + 1.3 GW Offshore | 694.38 | -300 | -510 | 294.74 | 0 | 0 | No
2030-07-18 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -210 | 190.72 | 0 | 0 | No
2030-07-18 01:00 | 2030 33% ECP + 1.3 GW Offshore | 495.27 | 0 | 0 | 253 | 0 | 0 | No
2030-07-18 02:00 | 2030 33% ECP + 1.3 GW Offshore | 108.28 | 0 | -32.46 | 231.31 | 0 | 0 | No
2030-07-18 03:00 | 2030 33% ECP + 1.3 GW Offshore | 528.28 | 0 | -210 | 175.98 | 0 | 0 | No
2030-07-18 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -15.45 | -510 | 143.97 | 0 | 0 | No
2030-07-18 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 39.94 | 0 | 0 | Yes
2030-07-18 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -210.73 | -510 | 117.14 | 0 | 0 | No
2030-07-18 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -485.3 | -510 | 221.82 | 0 | 0 | No
2030-07-18 08:00 | 2030 33% ECP + 1.3 GW Offshore | 431.92 | -526 | -510 | 183.33 | 0 | 0 | No
2030-07-18 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -17.31 | 0 | 0 | No
2030-07-18 10:00 | 2030 33% ECP + 1.3 GW Offshore | 602.1 | -526 | -510 | 215.43 | 0 | 0 | No
2030-07-18 11:00 | 2030 33% ECP + 1.3 GW Offshore | 182.1 | -526 | -510 | 77.34 | 0 | 0 | No
2030-07-18 12:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -215.33 | 0 | 0 | No
2030-07-18 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -180.29 | 0 | 0 | No
2030-07-18 14:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -43.75 | 0 | 0 | No
2030-07-18 15:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -206.21 | 0 | 0 | No
2030-07-18 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 93.79 | 0 | 0 | No
2030-07-18 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 114.83 | 0 | 0 | No
2030-07-18 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -309.63 | -510 | 138.47 | 0 | 0 | No
2030-07-18 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -9.63 | -510 | 313.25 | 0 | 0 | No
2030-07-18 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 193 | 0 | 0 | No
2030-07-18 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 259.71 | 0 | 0 | No
2030-07-18 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 315.44 | 0 | 0 | No
2030-07-18 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 237.96 | 0 | 0 | No
2030-07-19 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -472.58 | 122.09 | 0 | 0 | No
2030-07-19 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -472.58 | 93.73 | 0 | 0 | No
2030-07-19 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -472.58 | 65.55 | 0 | 0 | No
2030-07-19 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -491.61 | 140.43 | 0 | 0 | No
2030-07-19 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -491.61 | 110.93 | 0 | 0 | No
2030-07-19 05:00 | 2030 33% ECP + 1.3 GW Offshore | 485.23 | 0 | -404.15 | 68.24 | 0 | 0 | No
2030-07-19 06:00 | 2030 33% ECP + 1.3 GW Offshore | 65.23 | -226 | -391.31 | 163.42 | 0 | 0 | No
2030-07-19 07:00 | 2030 33% ECP + 1.3 GW Offshore | -354.77 | -526 | -510 | 143.39 | 0 | 0 | No
2030-07-19 08:00 | 2030 33% ECP + 1.3 GW Offshore | 65.23 | -526 | -510 | -156.61 | 0 | 0 | No
2030-07-19 09:00 | 2030 33% ECP + 1.3 GW Offshore | -354.77 | -526 | -510 | -161.48 | 0 | 0 | No
2030-07-19 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 55.48 | 0 | 0 | No
2030-07-19 11:00 | 2030 33% ECP + 1.3 GW Offshore | -401.54 | -526 | -510 | -244.52 | 0 | 0 | No
2030-07-19 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-07-19 13:00 | 2030 33% ECP + 1.3 GW Offshore | -288.7 | -526 | -510 | -510 | 0 | 0 | No
2030-07-19 14:00 | 2030 33% ECP + 1.3 GW Offshore | -288.7 | -526 | -510 | -510 | 0 | 0 | No
2030-07-19 15:00 | 2030 33% ECP + 1.3 GW Offshore | 115.04 | -526 | -510 | -479.8 | 0 | 0 | No
2030-07-19 16:00 | 2030 33% ECP + 1.3 GW Offshore | 535.04 | -526 | -510 | -251.67 | 0 | 0 | No
2030-07-19 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -226.23 | 0 | 0 | No
2030-07-19 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -266.66 | -510 | -199.13 | 0 | 0 | No
2030-07-19 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -310.32 | 100.87 | 0 | 0 | No
2030-07-19 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -10.32 | 244.15 | 0 | 0 | No
2030-07-19 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -310.32 | 292.65 | 0 | 0 | No
2030-07-19 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -10.32 | 108.68 | 0 | 0 | No
2030-07-19 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 71.04 | 0 | 0 | No
2030-07-20 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -300 | 71.04 | 0 | 0 | No
2030-07-20 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 141.26 | 0 | 0 | No
2030-07-20 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -300 | 109.13 | 0 | 0 | No
2030-07-20 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -442.27 | 60.14 | 0 | 0 | No
2030-07-20 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -142.27 | 128.1 | 0 | 0 | No
2030-07-20 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -308.39 | 108.41 | 0 | 0 | No
2030-07-20 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -275.84 | -510 | 0 | 0 | 0 | No
2030-07-20 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 9.31 | 0 | 0 | No
2030-07-20 08:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -92.41 | 0 | 0 | No
2030-07-20 09:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | -117.42 | 0 | 0 | No
2030-07-20 10:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | -526 | -510 | -178.27 | 0 | 0 | No
2030-07-20 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -151.33 | 0 | 0 | No
2030-07-20 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -76.06 | 0 | 0 | No
2030-07-20 13:00 | 2030 33% ECP + 1.3 GW Offshore | -502.44 | -526 | -510 | -54.56 | 0 | 0 | No
2030-07-20 14:00 | 2030 33% ECP + 1.3 GW Offshore | -82.44 | -526 | -510 | -231.22 | 0 | 0 | No
2030-07-20 15:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -194.92 | 0 | 0 | No
2030-07-20 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -30.98 | 0 | 0 | No
2030-07-20 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-20 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -298.23 | 126.16 | 0 | 0 | No
2030-07-20 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 131.32 | 0 | 0 | No
2030-07-20 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 192.63 | 0 | 0 | No
2030-07-20 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 207.8 | 0 | 0 | No
2030-07-20 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 264.8 | 0 | 0 | No
2030-07-20 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -300 | 275.24 | 0 | 0 | No
2030-07-21 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-21 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 2.17 | 0 | 0 | No
2030-07-21 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-07-21 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -81.26 | 0 | 0 | 0 | No
2030-07-21 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -148.47 | 0 | 0 | 0 | No
2030-07-21 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -303.02 | 86.96 | 0 | 0 | No
2030-07-21 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 69.58 | 0 | 0 | No
2030-07-21 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 73.46 | 0 | 0 | No
2030-07-21 08:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 19.7 | 0 | 0 | No
2030-07-21 09:00 | 2030 33% ECP + 1.3 GW Offshore | -103.04 | -526 | -510 | -149.65 | 0 | 0 | No
2030-07-21 10:00 | 2030 33% ECP + 1.3 GW Offshore | -523.04 | -526 | -510 | -114.47 | 0 | 0 | No
2030-07-21 11:00 | 2030 33% ECP + 1.3 GW Offshore | -614.04 | -526 | -510 | -55.52 | 0 | 0 | No
2030-07-21 12:00 | 2030 33% ECP + 1.3 GW Offshore | -614.04 | -526 | -510 | -50.99 | 0 | 0 | No
2030-07-21 13:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | -526 | -510 | -63.85 | 0 | 0 | No
2030-07-21 14:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | 60.88 | 0 | 0 | No
2030-07-21 15:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 60.34 | 0 | 0 | No
2030-07-21 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 177.71 | 0 | 0 | No
2030-07-21 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 230.14 | 0 | 0 | No
2030-07-21 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 111.41 | 0 | 0 | No
2030-07-21 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 124.66 | 0 | 0 | No
2030-07-21 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 103.03 | 0 | 0 | No
2030-07-21 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 44.75 | 0 | 0 | No
2030-07-21 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 32.04 | 0 | 0 | No
2030-07-21 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -48.56 | -510 | -84.18 | 0 | 0 | No
2030-07-22 | 2030 33% ECP + 1.3 GW Offshore | 700 | -348.56 | -510 | -243.27 | 0 | 0 | No
2030-07-22 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -78.72 | 0 | 0 | No
2030-07-22 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -208.9 | 0 | 0 | No
2030-07-22 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -317.18 | 0 | 0 | No
2030-07-22 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -434.23 | 0 | 0 | No
2030-07-22 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-07-22 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-07-22 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -215.01 | 0 | 0 | No
2030-07-22 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -441.68 | 0 | 0 | No
2030-07-22 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -169.74 | 0 | 0 | No
2030-07-22 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 13.26 | 0 | 0 | No
2030-07-22 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 31.7 | 0 | 0 | No
2030-07-22 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -110.88 | 0 | 0 | No
2030-07-22 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 126.35 | 0 | 0 | No
2030-07-22 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -141.96 | 0 | 0 | No
2030-07-22 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -29.53 | 0 | 0 | No
2030-07-22 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 215.87 | 0 | 0 | No
2030-07-22 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 292.53 | 0 | 0 | No
2030-07-22 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 316.76 | 0 | 0 | No
2030-07-22 19:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 130.3 | 0 | 0 | No
2030-07-22 20:00 | 2030 33% ECP + 1.3 GW Offshore | 246.34 | -526 | -510 | 154.72 | 0 | 0 | No
2030-07-22 21:00 | 2030 33% ECP + 1.3 GW Offshore | 246.34 | -526 | -510 | 226.96 | 0 | 0 | No
2030-07-22 22:00 | 2030 33% ECP + 1.3 GW Offshore | 666.34 | -526 | -510 | -23.13 | 0 | 0 | No
2030-07-22 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -42.95 | 0 | 0 | No
2030-07-23 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | -113.42 | 0 | 0 | No
2030-07-23 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -178.55 | 0 | 0 | No
2030-07-23 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -112.66 | 0 | 0 | No
2030-07-23 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -138.43 | 0 | 0 | No
2030-07-23 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -94.82 | 0 | 0 | No
2030-07-23 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -115.73 | 0 | 0 | No
2030-07-23 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 155.15 | 0 | 0 | No
2030-07-23 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 290.97 | 0 | 0 | No
2030-07-23 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 406.82 | 0 | 0 | No
2030-07-23 09:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | 275.25 | 0 | 0 | No
2030-07-23 10:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 269.06 | 0 | 0 | No
2030-07-23 11:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | -526 | -510 | 271.53 | 0 | 0 | No
2030-07-23 12:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | -526 | -510 | 301.32 | 0 | 0 | No
2030-07-23 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 281.04 | 0 | 0 | No
2030-07-23 14:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | 250.9 | 0 | 0 | No
2030-07-23 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 134.75 | 0 | 0 | No
2030-07-23 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 251.68 | 0 | 0 | No
2030-07-23 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -272.86 | -300 | 343.83 | 0 | 0 | No
2030-07-23 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-07-23 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 510 | 0 | 0 | No
2030-07-23 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-23 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-23 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-23 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-24 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-24 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-24 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-24 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-24 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-07-24 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 390 | 510 | 0 | 0 | No
2030-07-24 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 366.16 | 0 | 0 | No
2030-07-24 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -204.09 | -210 | 385.84 | 0 | 0 | No
2030-07-24 08:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -504.09 | -510 | 413.99 | 0 | 0 | No
2030-07-24 09:00 | 2030 33% ECP + 1.3 GW Offshore | 513.59 | -526 | -510 | 402.23 | 0 | 0 | No
2030-07-24 10:00 | 2030 33% ECP + 1.3 GW Offshore | 93.59 | -526 | -510 | 320.59 | 0 | 0 | No
2030-07-24 11:00 | 2030 33% ECP + 1.3 GW Offshore | 262.57 | -526 | -510 | 393.42 | 0 | 0 | No
2030-07-24 12:00 | 2030 33% ECP + 1.3 GW Offshore | -157.43 | -526 | -510 | 287.28 | 0 | 0 | No
2030-07-24 13:00 | 2030 33% ECP + 1.3 GW Offshore | 78.87 | -526 | -510 | 159.93 | 0 | 0 | No
2030-07-24 14:00 | 2030 33% ECP + 1.3 GW Offshore | 498.87 | -526 | -510 | 0 | 0 | 0 | No
2030-07-24 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 162.66 | 0 | 0 | No
2030-07-24 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 295.29 | 0 | 0 | No
2030-07-24 17:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 510 | 0 | 0 | No
2030-07-24 18:00 | 2030 33% ECP + 1.3 GW Offshore | -62.3 | -526 | -510 | 394.28 | 0 | 0 | No
2030-07-24 19:00 | 2030 33% ECP + 1.3 GW Offshore | -192.4 | -526 | -510 | 338.72 | 0 | 0 | No
2030-07-24 20:00 | 2030 33% ECP + 1.3 GW Offshore | -612.4 | -395 | -390 | 38.72 | 0 | 0 | No
2030-07-24 21:00 | 2030 33% ECP + 1.3 GW Offshore | -192.4 | -95 | -90 | -33.96 | 0 | 0 | No
2030-07-24 22:00 | 2030 33% ECP + 1.3 GW Offshore | 190.01 | 205 | 210 | 210 | 0 | 0 | No
2030-07-24 23:00 | 2030 33% ECP + 1.3 GW Offshore | 610.01 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 328.44 | 510 | 510 | 0 | 0 | No
2030-07-25 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 510 | 214.67 | 0 | 0 | No
2030-07-25 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-25 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 444.9 | 510 | 0 | 0 | No
2030-07-25 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 144.9 | 510 | 0 | 0 | No
2030-07-25 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -155.1 | 510 | 0 | 0 | No
2030-07-25 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -395 | -455.1 | 510 | 0 | 0 | No
2030-07-25 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 210 | 0 | 0 | No
2030-07-25 19:00 | 2030 33% ECP + 1.3 GW Offshore | 678.75 | -526 | -510 | 510 | 0 | 0 | No
2030-07-25 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-25 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -395 | -390 | 484.38 | 0 | 0 | No
2030-07-25 22:00 | 2030 33% ECP + 1.3 GW Offshore | 366.49 | -95 | -90 | 464.14 | 0 | 0 | No
2030-07-25 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 388.54 | 0 | 0 | No
2030-07-26 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 03:00 | 2030 33% ECP + 1.3 GW Offshore | 651.52 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-26 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 293.31 | 510 | 510 | 0 | 0 | No
2030-07-26 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 6.64 | 510 | 510 | 0 | 0 | No
2030-07-26 07:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 168.51 | 300 | 510 | 0 | 0 | No
2030-07-26 08:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 0 | 0 | 492.21 | 0 | 0 | No
2030-07-26 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -216.04 | -300 | 510 | 0 | 0 | No
2030-07-26 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -285.19 | 510 | 0 | 0 | No
2030-07-26 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -300 | -473.37 | 510 | 0 | 0 | No
2030-07-26 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -173.37 | 510 | 0 | 0 | No
2030-07-26 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 126.63 | 510 | 0 | 0 | No
2030-07-26 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 358.44 | 390 | 510 | 0 | 0 | No
2030-07-26 15:00 | 2030 33% ECP + 1.3 GW Offshore | -637.52 | 74 | 90 | 510 | 0 | 0 | No
2030-07-26 16:00 | 2030 33% ECP + 1.3 GW Offshore | -217.52 | -226 | -210 | 345.57 | 0 | 0 | No
2030-07-26 17:00 | 2030 33% ECP + 1.3 GW Offshore | 185.4 | -526 | -510 | 510 | 0 | 0 | No
2030-07-26 18:00 | 2030 33% ECP + 1.3 GW Offshore | 605.4 | -431.6 | -510 | 510 | 0 | 0 | No
2030-07-26 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -383.39 | -510 | 497.14 | 0 | 0 | No
2030-07-26 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -83.39 | -390 | 197.14 | 0 | 0 | No
2030-07-26 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -90 | 497.14 | 0 | 0 | No
2030-07-26 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-07-26 23:00 | 2030 33% ECP + 1.3 GW Offshore | 679.99 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 | 2030 33% ECP + 1.3 GW Offshore | 259.99 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 01:00 | 2030 33% ECP + 1.3 GW Offshore | -160.01 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 02:00 | 2030 33% ECP + 1.3 GW Offshore | -535.05 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 03:00 | 2030 33% ECP + 1.3 GW Offshore | -177.73 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 04:00 | 2030 33% ECP + 1.3 GW Offshore | 65.03 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 05:00 | 2030 33% ECP + 1.3 GW Offshore | -197.4 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 06:00 | 2030 33% ECP + 1.3 GW Offshore | -533.26 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 258.09 | 0 | 0 | Yes
2030-07-27 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 107.32 | 0 | 0 | Yes
2030-07-27 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 102.87 | 0 | 0 | Yes
2030-07-27 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 218.76 | 0 | 0 | Yes
2030-07-27 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 382.89 | 0 | 0 | Yes
2030-07-27 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 385.55 | 0 | 0 | Yes
2030-07-27 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 298.37 | 0 | 0 | Yes
2030-07-27 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-27 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-27 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 506.32 | 0 | 0 | Yes
2030-07-27 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 347 | 0 | 0 | Yes
2030-07-28 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 03:00 | 2030 33% ECP + 1.3 GW Offshore | -456.51 | 505 | 510 | 432.75 | 0 | 0 | Yes
2030-07-28 04:00 | 2030 33% ECP + 1.3 GW Offshore | -608.61 | 505 | 510 | 478.81 | 0 | 0 | Yes
2030-07-28 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 391.95 | 0 | 0 | Yes
2030-07-28 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 364.57 | 0 | 0 | Yes
2030-07-28 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 152.01 | 0 | 0 | Yes
2030-07-28 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 61.85 | 0 | 0 | Yes
2030-07-28 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 136.43 | 0 | 0 | Yes
2030-07-28 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-07-28 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 32.15 | 0 | 0 | Yes
2030-07-28 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 276.12 | 0 | 0 | Yes
2030-07-28 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 17:00 | 2030 33% ECP + 1.3 GW Offshore | -494.23 | 505 | 510 | 510 | 0 | 0 | Yes
2030-07-28 18:00 | 2030 33% ECP + 1.3 GW Offshore | -74.23 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 19:00 | 2030 33% ECP + 1.3 GW Offshore | 345.77 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-28 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-29 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-07-29 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -90 | 396.83 | 0 | 0 | No
2030-07-29 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -395 | -390 | 388.5 | 0 | 0 | No
2030-07-29 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 388.5 | 0 | 0 | No
2030-07-29 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 364.72 | 0 | 0 | No
2030-07-29 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 356.42 | 0 | 0 | No
2030-07-29 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 448.83 | 0 | 0 | No
2030-07-29 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 494.49 | 0 | 0 | No
2030-07-29 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-07-29 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 459.82 | 0 | 0 | No
2030-07-29 19:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 494.73 | 0 | 0 | No
2030-07-29 20:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | 217.67 | 0 | 0 | No
2030-07-29 21:00 | 2030 33% ECP + 1.3 GW Offshore | -245.71 | -526 | -510 | 395.6 | 0 | 0 | No
2030-07-29 22:00 | 2030 33% ECP + 1.3 GW Offshore | 174.29 | -526 | -510 | 219.52 | 0 | 0 | No
2030-07-29 23:00 | 2030 33% ECP + 1.3 GW Offshore | 594.29 | -526 | -510 | 175.92 | 0 | 0 | No
2030-07-30 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 52.9 | 0 | 0 | No
2030-07-30 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -7.51 | 0 | 0 | No
2030-07-30 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -112.92 | 0 | 0 | No
2030-07-30 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -104.23 | 0 | 0 | No
2030-07-30 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -129.8 | 0 | 0 | No
2030-07-30 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-07-30 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 98.01 | 0 | 0 | No
2030-07-30 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 163.76 | 0 | 0 | No
2030-07-30 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 229.83 | 0 | 0 | No
2030-07-30 09:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 189.52 | 0 | 0 | No
2030-07-30 10:00 | 2030 33% ECP + 1.3 GW Offshore | -136.72 | -526 | -510 | 153.41 | 0 | 0 | No
2030-07-30 11:00 | 2030 33% ECP + 1.3 GW Offshore | -556.72 | -526 | -510 | 24.3 | 0 | 0 | No
2030-07-30 12:00 | 2030 33% ECP + 1.3 GW Offshore | -676.81 | -526 | -510 | 176.7 | 0 | 0 | No
2030-07-30 13:00 | 2030 33% ECP + 1.3 GW Offshore | -676.81 | -526 | -510 | 148.63 | 0 | 0 | No
2030-07-30 14:00 | 2030 33% ECP + 1.3 GW Offshore | -676.81 | -526 | -510 | 282.27 | 0 | 0 | No
2030-07-30 15:00 | 2030 33% ECP + 1.3 GW Offshore | -436.97 | -526 | -510 | 218.91 | 0 | 0 | No
2030-07-30 16:00 | 2030 33% ECP + 1.3 GW Offshore | -16.97 | -526 | -510 | 100.41 | 0 | 0 | No
2030-07-30 17:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -93.52 | 0 | 0 | No
2030-07-30 18:00 | 2030 33% ECP + 1.3 GW Offshore | 167.38 | -526 | -510 | -276.52 | 0 | 0 | No
2030-07-30 19:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | 23.22 | 0 | 0 | No
2030-07-30 20:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -141.44 | 0 | 0 | No
2030-07-30 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -150.88 | 0 | 0 | No
2030-07-30 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -395 | -510 | 14.7 | 0 | 0 | No
2030-07-30 23:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -95 | -210 | 12.64 | 0 | 0 | No
2030-07-31 | 2030 33% ECP + 1.3 GW Offshore | -123.79 | 205 | 90 | 312.64 | 0 | 0 | No
2030-07-31 01:00 | 2030 33% ECP + 1.3 GW Offshore | -543.79 | 505 | 390 | 510 | 0 | 0 | No
2030-07-31 02:00 | 2030 33% ECP + 1.3 GW Offshore | -695.93 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 03:00 | 2030 33% ECP + 1.3 GW Offshore | -289.23 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 04:00 | 2030 33% ECP + 1.3 GW Offshore | -66.82 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 05:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 331 | 510 | 510 | 0 | 0 | No
2030-07-31 06:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 07:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 258.04 | 510 | 510 | 0 | 0 | No
2030-07-31 08:00 | 2030 33% ECP + 1.3 GW Offshore | -419.23 | 361.85 | 510 | 510 | 0 | 0 | No
2030-07-31 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 15:00 | 2030 33% ECP + 1.3 GW Offshore | -432.17 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 16:00 | 2030 33% ECP + 1.3 GW Offshore | -12.17 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 17:00 | 2030 33% ECP + 1.3 GW Offshore | 407.83 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 460.98 | 510 | 510 | 0 | 0 | No
2030-07-31 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-07-31 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-01 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-08-01 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -90 | 268.22 | 0 | 0 | No
2030-08-01 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -395 | -390 | 363.22 | 0 | 0 | No
2030-08-01 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 309.1 | 0 | 0 | No
2030-08-01 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 384.53 | 0 | 0 | No
2030-08-01 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 364.36 | 0 | 0 | No
2030-08-01 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 411.91 | 0 | 0 | No
2030-08-01 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 412.57 | 0 | 0 | No
2030-08-01 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 343.59 | 0 | 0 | No
2030-08-01 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 463.49 | 0 | 0 | No
2030-08-01 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 435.55 | 0 | 0 | No
2030-08-01 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 254.11 | 0 | 0 | No
2030-08-01 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -445.9 | -510 | 444.93 | 0 | 0 | No
2030-08-01 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -145.9 | -510 | 485.06 | 0 | 0 | No
2030-08-01 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-08-01 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-08-01 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-08-01 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 499.09 | 0 | 0 | No
2030-08-01 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 372.72 | 0 | 0 | No
2030-08-02 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 272.22 | 0 | 0 | No
2030-08-02 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 211.85 | 0 | 0 | No
2030-08-02 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -236.33 | 180.41 | 0 | 0 | No
2030-08-02 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -122.13 | -510 | 179.25 | 0 | 0 | No
2030-08-02 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 139.44 | 0 | 0 | No
2030-08-02 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -180.12 | -510 | 170.93 | 0 | 0 | No
2030-08-02 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 239.85 | 0 | 0 | No
2030-08-02 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 323.88 | 0 | 0 | No
2030-08-02 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 403.07 | 0 | 0 | No
2030-08-02 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 403.07 | 0 | 0 | No
2030-08-02 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 283.79 | 0 | 0 | No
2030-08-02 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 329.91 | 0 | 0 | No
2030-08-02 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 305.21 | 0 | 0 | No
2030-08-02 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 319.05 | 0 | 0 | No
2030-08-02 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 262.6 | 0 | 0 | No
2030-08-02 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 342.84 | 0 | 0 | No
2030-08-02 16:00 | 2030 33% ECP + 1.3 GW Offshore | 653.19 | -526 | -510 | 380.69 | 0 | 0 | No
2030-08-02 17:00 | 2030 33% ECP + 1.3 GW Offshore | 233.19 | -526 | -510 | 350.02 | 0 | 0 | No
2030-08-02 18:00 | 2030 33% ECP + 1.3 GW Offshore | 240.39 | -526 | -510 | 446.19 | 0 | 0 | No
2030-08-02 19:00 | 2030 33% ECP + 1.3 GW Offshore | 660.39 | -226 | -510 | 466.17 | 0 | 0 | No
2030-08-02 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 430.4 | 0 | 0 | No
2030-08-02 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -269.3 | 464.54 | 0 | 0 | No
2030-08-02 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 384.41 | 0 | 0 | No
2030-08-02 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -1.27 | 358.51 | 0 | 0 | No
2030-08-03 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -181.37 | 252.29 | 0 | 0 | No
2030-08-03 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -60.53 | 268.2 | 0 | 0 | No
2030-08-03 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 238.68 | 0 | 0 | No
2030-08-03 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 177.51 | 0 | 0 | No
2030-08-03 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 194.85 | 0 | 0 | No
2030-08-03 05:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 0 | 0 | 195.66 | 0 | 0 | No
2030-08-03 06:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 0 | -78.92 | 200.85 | 0 | 0 | No
2030-08-03 07:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -378.92 | 215.08 | 0 | 0 | No
2030-08-03 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 79.44 | 0 | 0 | No
2030-08-03 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 69.13 | 0 | 0 | No
2030-08-03 10:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 151.44 | 0 | 0 | No
2030-08-03 11:00 | 2030 33% ECP + 1.3 GW Offshore | -176.07 | -526 | -510 | 51.37 | 0 | 0 | No
2030-08-03 12:00 | 2030 33% ECP + 1.3 GW Offshore | 240.97 | -526 | -510 | 165.26 | 0 | 0 | No
2030-08-03 13:00 | 2030 33% ECP + 1.3 GW Offshore | 42.93 | -526 | -510 | 121.33 | 0 | 0 | No
2030-08-03 14:00 | 2030 33% ECP + 1.3 GW Offshore | 462.93 | -526 | -510 | 0 | 0 | 0 | No
2030-08-03 15:00 | 2030 33% ECP + 1.3 GW Offshore | 688.06 | -526 | -510 | 183.38 | 0 | 0 | No
2030-08-03 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 250.52 | 0 | 0 | No
2030-08-03 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 352.34 | 0 | 0 | No
2030-08-03 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 377.21 | 0 | 0 | No
2030-08-03 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 412.55 | 0 | 0 | No
2030-08-03 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 387.65 | 0 | 0 | No
2030-08-03 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -293.46 | 398.88 | 0 | 0 | No
2030-08-03 22:00 | 2030 33% ECP + 1.3 GW Offshore | 615.75 | 0 | -510 | 348.87 | 0 | 0 | No
2030-08-03 23:00 | 2030 33% ECP + 1.3 GW Offshore | 195.75 | -226 | -510 | 213.79 | 0 | 0 | No
2030-08-04 | 2030 33% ECP + 1.3 GW Offshore | 140 | -525.4 | -510 | 84.41 | 0 | 0 | No
2030-08-04 01:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -436.19 | -510 | -2.26 | 0 | 0 | No
2030-08-04 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 43.92 | 0 | 0 | No
2030-08-04 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -16.38 | 0 | 0 | No
2030-08-04 04:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -316.38 | 0 | 0 | No
2030-08-04 05:00 | 2030 33% ECP + 1.3 GW Offshore | -538.03 | -526 | -510 | -510 | 0 | 0 | No
2030-08-04 06:00 | 2030 33% ECP + 1.3 GW Offshore | -538.03 | -526 | -510 | -510 | 0 | 0 | No
2030-08-04 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -419.93 | 0 | 0 | Yes
2030-08-04 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -119.93 | 0 | 0 | Yes
2030-08-04 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 180.07 | 0 | 0 | Yes
2030-08-04 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 292.74 | 0 | 0 | Yes
2030-08-04 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 399.68 | 0 | 0 | Yes
2030-08-04 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 360.1 | 0 | 0 | Yes
2030-08-04 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 371.19 | 0 | 0 | Yes
2030-08-04 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 486.11 | 0 | 0 | Yes
2030-08-04 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 319.1 | 0 | 0 | Yes
2030-08-04 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 304.97 | 0 | 0 | Yes
2030-08-04 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 232.57 | 0 | 0 | Yes
2030-08-04 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 456.01 | 0 | 0 | Yes
2030-08-04 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-08-04 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-04 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-05 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 01:00 | 2030 33% ECP + 1.3 GW Offshore | -483.39 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 04:00 | 2030 33% ECP + 1.3 GW Offshore | -498.48 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 07:00 | 2030 33% ECP + 1.3 GW Offshore | -647.48 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 08:00 | 2030 33% ECP + 1.3 GW Offshore | -687.99 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 09:00 | 2030 33% ECP + 1.3 GW Offshore | -563.91 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 10:00 | 2030 33% ECP + 1.3 GW Offshore | -282.82 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-05 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-05 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-08-05 17:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 300 | 315.96 | 510 | 0 | 0 | No
2030-08-05 18:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 0 | 15.96 | 510 | 0 | 0 | No
2030-08-05 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 508.81 | 0 | 0 | No
2030-08-05 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 443.97 | 0 | 0 | No
2030-08-05 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 471.22 | 0 | 0 | No
2030-08-05 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 471.22 | 0 | 0 | No
2030-08-05 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -284.45 | 370.56 | 0 | 0 | No
2030-08-06 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -8.25 | 213.15 | 0 | 0 | No
2030-08-06 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -8.25 | 262.66 | 0 | 0 | No
2030-08-06 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -47.49 | 239.09 | 0 | 0 | No
2030-08-06 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -347.49 | 215.4 | 0 | 0 | No
2030-08-06 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -255.78 | -510 | 211.94 | 0 | 0 | No
2030-08-06 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -111.95 | -510 | 185.01 | 0 | 0 | No
2030-08-06 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -411.95 | -510 | 161.94 | 0 | 0 | No
2030-08-06 07:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | 116.34 | 0 | 0 | No
2030-08-06 08:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 1.4 | 0 | 0 | No
2030-08-06 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -86.38 | 0 | 0 | No
2030-08-06 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -203.34 | 0 | 0 | No
2030-08-06 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -503.34 | 0 | 0 | No
2030-08-06 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-06 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-06 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -340.17 | 0 | 0 | No
2030-08-06 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -105 | 0 | 0 | No
2030-08-06 16:00 | 2030 33% ECP + 1.3 GW Offshore | -346.34 | -526 | -510 | 195 | 0 | 0 | No
2030-08-06 17:00 | 2030 33% ECP + 1.3 GW Offshore | 73.66 | -526 | -510 | 265.82 | 0 | 0 | No
2030-08-06 18:00 | 2030 33% ECP + 1.3 GW Offshore | -346.34 | -526 | -510 | 434.36 | 0 | 0 | No
2030-08-06 19:00 | 2030 33% ECP + 1.3 GW Offshore | -57.32 | -526 | -510 | 408.47 | 0 | 0 | No
2030-08-06 20:00 | 2030 33% ECP + 1.3 GW Offshore | -57.32 | -526 | -510 | 441.69 | 0 | 0 | No
2030-08-06 21:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 415.83 | 0 | 0 | No
2030-08-06 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 153.55 | 0 | 0 | No
2030-08-06 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 2.64 | 0 | 0 | No
2030-08-07 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 80.97 | 0 | 0 | No
2030-08-07 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 89.71 | 0 | 0 | No
2030-08-07 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -7.52 | 0 | 0 | No
2030-08-07 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -91.5 | 0 | 0 | No
2030-08-07 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -40.88 | 0 | 0 | No
2030-08-07 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -125.5 | 0 | 0 | No
2030-08-07 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -40.56 | 0 | 0 | No
2030-08-07 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -76.41 | 0 | 0 | No
2030-08-07 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 43.05 | 0 | 0 | No
2030-08-07 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -80.8 | 0 | 0 | No
2030-08-07 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -157.84 | 0 | 0 | No
2030-08-07 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 98.17 | 0 | 0 | No
2030-08-07 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 217.2 | 0 | 0 | No
2030-08-07 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -32.96 | 0 | 0 | No
2030-08-07 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-08-07 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 194.67 | 0 | 0 | No
2030-08-07 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 494.67 | 0 | 0 | No
2030-08-07 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -422.7 | 410.35 | 0 | 0 | No
2030-08-07 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -122.7 | 475.58 | 0 | 0 | No
2030-08-07 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 60.06 | 510 | 0 | 0 | No
2030-08-07 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 60.06 | 338.15 | 0 | 0 | No
2030-08-07 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 380.14 | 0 | 0 | No
2030-08-07 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 307.65 | 0 | 0 | No
2030-08-07 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 180.05 | 0 | 0 | No
2030-08-08 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 22.07 | 83.85 | 0 | 0 | No
2030-08-08 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 108.15 | 0 | 0 | No
2030-08-08 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 97.01 | 0 | 0 | No
2030-08-08 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 69.93 | 0 | 0 | No
2030-08-08 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 80.93 | 22.47 | 0 | 0 | No
2030-08-08 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 80.93 | 26.75 | 0 | 0 | No
2030-08-08 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -148.44 | 76.64 | 0 | 0 | No
2030-08-08 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -448.44 | 188.06 | 0 | 0 | No
2030-08-08 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 245.1 | 0 | 0 | No
2030-08-08 09:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 209.03 | 0 | 0 | No
2030-08-08 10:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | 160.06 | 0 | 0 | No
2030-08-08 11:00 | 2030 33% ECP + 1.3 GW Offshore | -447.51 | -526 | -510 | 160.73 | 0 | 0 | No
2030-08-08 12:00 | 2030 33% ECP + 1.3 GW Offshore | -64.53 | -526 | -510 | 151.32 | 0 | 0 | No
2030-08-08 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 98.19 | 0 | 0 | No
2030-08-08 14:00 | 2030 33% ECP + 1.3 GW Offshore | -32.42 | -526 | -510 | 61.46 | 0 | 0 | No
2030-08-08 15:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 50.49 | 0 | 0 | No
2030-08-08 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 152.94 | 0 | 0 | No
2030-08-08 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 227.3 | 0 | 0 | No
2030-08-08 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 302.66 | 0 | 0 | No
2030-08-08 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 1.14 | 254.71 | 0 | 0 | No
2030-08-08 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 145.76 | 224.15 | 0 | 0 | No
2030-08-08 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 24.96 | 187.89 | 0 | 0 | No
2030-08-08 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 6.29 | 0 | 0 | No
2030-08-08 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-09 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 26.15 | 0 | 0 | 0 | No
2030-08-09 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 44.77 | 0 | 0 | 0 | No
2030-08-09 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 25.99 | 344.77 | 216.55 | 0 | 0 | No
2030-08-09 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 325.99 | 510 | 510 | 0 | 0 | No
2030-08-09 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 206.58 | 210 | 210 | 0 | 0 | No
2030-08-09 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -93.42 | -90 | -90 | 0 | 0 | No
2030-08-09 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -194.78 | -390 | -390 | 0 | 0 | No
2030-08-09 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -494.78 | -510 | -249.26 | 0 | 0 | No
2030-08-09 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -65.61 | 0 | 0 | No
2030-08-09 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 145.87 | 0 | 0 | No
2030-08-09 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 295.06 | 0 | 0 | No
2030-08-09 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 234.69 | 0 | 0 | No
2030-08-09 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 226.37 | 0 | 0 | No
2030-08-09 13:00 | 2030 33% ECP + 1.3 GW Offshore | 686.29 | -526 | -510 | 245.08 | 0 | 0 | No
2030-08-09 14:00 | 2030 33% ECP + 1.3 GW Offshore | 686.29 | -526 | -510 | 245.08 | 0 | 0 | No
2030-08-09 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 267.3 | 0 | 0 | No
2030-08-09 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 408.36 | 0 | 0 | No
2030-08-09 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 417.33 | 0 | 0 | No
2030-08-09 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 510 | 0 | 0 | No
2030-08-09 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-08-09 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 390 | 427.14 | 0 | 0 | No
2030-08-09 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 480.98 | 327.62 | 0 | 0 | No
2030-08-09 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 180.98 | 107.77 | 0 | 0 | No
2030-08-09 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 299.91 | 252.77 | 0 | 0 | No
2030-08-10 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-10 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | -16.92 | 0 | 0 | No
2030-08-10 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-10 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-10 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-10 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-10 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-10 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -234.47 | 0 | 0 | 0 | No
2030-08-10 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 253.1 | 0 | 0 | No
2030-08-10 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 294.34 | 0 | 0 | No
2030-08-10 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 231.63 | 0 | 0 | No
2030-08-10 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 318.06 | 0 | 0 | No
2030-08-10 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 375.33 | 0 | 0 | No
2030-08-10 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 295.34 | 0 | 0 | No
2030-08-10 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 296.88 | 0 | 0 | No
2030-08-10 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 318.14 | 0 | 0 | No
2030-08-10 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 364.18 | 0 | 0 | No
2030-08-10 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -282.97 | -510 | 263.02 | 0 | 0 | No
2030-08-10 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 352.21 | 0 | 0 | No
2030-08-10 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -492.43 | 52.21 | 0 | 0 | No
2030-08-10 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -342.31 | 343.23 | 0 | 0 | No
2030-08-10 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 360.73 | 0 | 0 | No
2030-08-10 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -335.02 | 125.97 | 0 | 0 | No
2030-08-10 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 271.08 | 0 | 0 | No
2030-08-11 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 163.52 | 0 | 0 | No
2030-08-11 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -369.42 | 219.65 | 0 | 0 | No
2030-08-11 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 202.02 | 0 | 0 | No
2030-08-11 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -260.25 | 186.11 | 0 | 0 | No
2030-08-11 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 197.92 | 0 | 0 | No
2030-08-11 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -231.82 | 136.92 | 0 | 0 | No
2030-08-11 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 125.8 | 0 | 0 | No
2030-08-11 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 145.19 | 0 | 0 | No
2030-08-11 08:00 | 2030 33% ECP + 1.3 GW Offshore | 617.73 | -526 | -510 | 106 | 0 | 0 | No
2030-08-11 09:00 | 2030 33% ECP + 1.3 GW Offshore | 197.73 | -526 | -510 | 46.18 | 0 | 0 | No
2030-08-11 10:00 | 2030 33% ECP + 1.3 GW Offshore | -222.27 | -526 | -510 | -16.98 | 0 | 0 | No
2030-08-11 11:00 | 2030 33% ECP + 1.3 GW Offshore | -642.27 | -526 | -510 | 1.52 | 0 | 0 | No
2030-08-11 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 34.32 | 0 | 0 | No
2030-08-11 13:00 | 2030 33% ECP + 1.3 GW Offshore | -658.77 | -526 | -510 | 142.99 | 0 | 0 | No
2030-08-11 14:00 | 2030 33% ECP + 1.3 GW Offshore | -238.77 | -526 | -510 | 137.72 | 0 | 0 | No
2030-08-11 15:00 | 2030 33% ECP + 1.3 GW Offshore | 181.23 | -526 | -510 | 138.67 | 0 | 0 | No
2030-08-11 16:00 | 2030 33% ECP + 1.3 GW Offshore | 601.23 | -526 | -510 | 216.75 | 0 | 0 | No
2030-08-11 17:00 | 2030 33% ECP + 1.3 GW Offshore | 474.64 | -300 | -510 | 305.71 | 0 | 0 | No
2030-08-11 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -224.87 | 341.68 | 0 | 0 | No
2030-08-11 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -224.87 | 346.38 | 0 | 0 | No
2030-08-11 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 352.2 | 0 | 0 | No
2030-08-11 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 386.63 | 0 | 0 | No
2030-08-11 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 337.2 | 0 | 0 | No
2030-08-11 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 236.8 | 0 | 0 | No
2030-08-12 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -67.19 | 38.22 | 0 | 0 | No
2030-08-12 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -343.54 | 0 | 0 | 0 | No
2030-08-12 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -435.33 | 0 | 0 | 0 | No
2030-08-12 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -329.78 | 0 | 0 | 0 | No
2030-08-12 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-12 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-12 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -93.31 | -508.78 | 1.04 | 0 | 0 | No
2030-08-12 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -393.31 | -510 | 89.84 | 0 | 0 | No
2030-08-12 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 359.6 | 0 | 0 | No
2030-08-12 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 302.68 | 0 | 0 | No
2030-08-12 10:00 | 2030 33% ECP + 1.3 GW Offshore | 530.69 | -526 | -510 | 148.11 | 0 | 0 | No
2030-08-12 11:00 | 2030 33% ECP + 1.3 GW Offshore | 206.58 | -526 | -510 | 139.38 | 0 | 0 | No
2030-08-12 12:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -59.25 | 0 | 0 | No
2030-08-12 13:00 | 2030 33% ECP + 1.3 GW Offshore | 175.76 | -526 | -510 | -48.12 | 0 | 0 | No
2030-08-12 14:00 | 2030 33% ECP + 1.3 GW Offshore | 178.93 | -526 | -510 | -43.36 | 0 | 0 | No
2030-08-12 15:00 | 2030 33% ECP + 1.3 GW Offshore | 598.93 | -526 | -510 | 97.72 | 0 | 0 | No
2030-08-12 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 261.61 | 0 | 0 | No
2030-08-12 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 305.25 | 0 | 0 | No
2030-08-12 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 169.93 | 0 | 0 | No
2030-08-12 19:00 | 2030 33% ECP + 1.3 GW Offshore | 653.54 | -526 | -510 | -120.48 | 0 | 0 | No
2030-08-12 20:00 | 2030 33% ECP + 1.3 GW Offshore | 233.54 | -526 | -510 | -228.71 | 0 | 0 | No
2030-08-12 21:00 | 2030 33% ECP + 1.3 GW Offshore | 459.53 | -526 | -510 | -108.77 | 0 | 0 | No
2030-08-12 22:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -73.14 | 0 | 0 | No
2030-08-12 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 19.5 | 0 | 0 | No
2030-08-13 | 2030 33% ECP + 1.3 GW Offshore | 700 | -365.41 | -510 | -0.85 | 0 | 0 | No
2030-08-13 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -412.43 | -510 | 14.2 | 0 | 0 | No
2030-08-13 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -357.02 | -510 | 57.52 | 0 | 0 | No
2030-08-13 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -413.86 | -510 | 0.56 | 0 | 0 | No
2030-08-13 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -25.46 | 0 | 0 | No
2030-08-13 05:00 | 2030 33% ECP + 1.3 GW Offshore | 553.78 | -526 | -510 | -219.35 | 0 | 0 | No
2030-08-13 06:00 | 2030 33% ECP + 1.3 GW Offshore | 362.06 | -526 | -510 | -153.44 | 0 | 0 | No
2030-08-13 07:00 | 2030 33% ECP + 1.3 GW Offshore | 698 | -526 | -510 | 146.56 | 0 | 0 | No
2030-08-13 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 205.36 | 0 | 0 | No
2030-08-13 09:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 109.85 | 0 | 0 | No
2030-08-13 10:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | 69.6 | 0 | 0 | No
2030-08-13 11:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | -526 | -510 | 144.18 | 0 | 0 | No
2030-08-13 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 56.6 | 0 | 0 | No
2030-08-13 13:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | -526 | -510 | -56.51 | 0 | 0 | No
2030-08-13 14:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | -188.45 | 0 | 0 | No
2030-08-13 15:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | -324.94 | 0 | 0 | No
2030-08-13 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -144.78 | 0 | 0 | No
2030-08-13 17:00 | 2030 33% ECP + 1.3 GW Offshore | 542.1 | -300 | -510 | 155.22 | 0 | 0 | No
2030-08-13 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -210 | 211.01 | 0 | 0 | No
2030-08-13 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -164.98 | 21.06 | 0 | 0 | No
2030-08-13 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -464.98 | 0 | 0 | 0 | No
2030-08-13 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -363.89 | 0 | 0 | 0 | No
2030-08-13 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -186.86 | 0 | 0 | 0 | No
2030-08-13 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -486.86 | 0 | 0 | 0 | No
2030-08-14 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -428.15 | 0 | 0 | 0 | No
2030-08-14 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -428.15 | 0 | 0 | 0 | No
2030-08-14 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -128.15 | 134.15 | 0 | 0 | No
2030-08-14 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -134.12 | 0 | 0 | 0 | No
2030-08-14 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -31.53 | 102.29 | 0 | 0 | No
2030-08-14 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -31.53 | 0 | 0 | 0 | No
2030-08-14 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -31.53 | 0 | 0 | 0 | No
2030-08-14 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -294.74 | 0 | 0 | 0 | No
2030-08-14 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 125.58 | 0 | 0 | No
2030-08-14 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 233.52 | 0 | 0 | No
2030-08-14 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 168.63 | 0 | 0 | No
2030-08-14 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 166.72 | 0 | 0 | No
2030-08-14 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 145.4 | 0 | 0 | No
2030-08-14 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 104.25 | 0 | 0 | No
2030-08-14 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 115.08 | 0 | 0 | No
2030-08-14 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 155.52 | 0 | 0 | No
2030-08-14 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 235.56 | 0 | 0 | No
2030-08-14 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 413.71 | 0 | 0 | No
2030-08-14 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-08-14 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -240.47 | -300 | 375.27 | 0 | 0 | No
2030-08-14 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -67.94 | -90 | 366.38 | 0 | 0 | No
2030-08-14 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 179.34 | 210 | 510 | 0 | 0 | No
2030-08-14 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 343.89 | 510 | 510 | 0 | 0 | No
2030-08-14 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 43.89 | 510 | 510 | 0 | 0 | No
2030-08-15 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 441.98 | 210 | 0 | 0 | No
2030-08-15 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 473.37 | 0 | 0 | 0 | No
2030-08-15 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 173.37 | 0 | 0 | 0 | No
2030-08-15 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 273.75 | 0 | 0 | 0 | No
2030-08-15 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 273.75 | 0 | 0 | 0 | No
2030-08-15 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 273.75 | 0 | 0 | 0 | No
2030-08-15 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-15 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -26.74 | -210 | 0 | 0 | 0 | No
2030-08-15 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -326.74 | -510 | 0 | 0 | 0 | No
2030-08-15 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 161.32 | 0 | 0 | No
2030-08-15 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 182 | 0 | 0 | No
2030-08-15 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 151.75 | 0 | 0 | No
2030-08-15 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 159.24 | 0 | 0 | No
2030-08-15 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 151.4 | 0 | 0 | No
2030-08-15 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 169.2 | 0 | 0 | No
2030-08-15 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 191.93 | 0 | 0 | No
2030-08-15 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -497.18 | -510 | -108.07 | 0 | 0 | No
2030-08-15 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -408.07 | 0 | 0 | No
2030-08-15 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-15 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -310.91 | -300 | 0 | 0 | No
2030-08-15 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -10.91 | 0 | 0 | 0 | No
2030-08-15 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 289.09 | 300 | 0 | 0 | No
2030-08-15 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 218.85 | 510 | 91.34 | 0 | 0 | No
2030-08-15 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 222.16 | -208.66 | 0 | 0 | No
2030-08-16 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -77.84 | 0 | 0 | 0 | No
2030-08-16 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -78.4 | 0 | 0 | 0 | No
2030-08-16 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-08-16 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -300 | 0 | 0 | 0 | No
2030-08-16 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-16 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -285.79 | 0 | 0 | 0 | No
2030-08-16 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -314.03 | 0 | 0 | 0 | No
2030-08-16 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -506.44 | 0 | 0 | 0 | No
2030-08-16 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-16 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-16 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-16 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-16 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-16 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-08-16 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -222.39 | -52.27 | 0 | 0 | No
2030-08-16 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -254.45 | -510 | -352.27 | 0 | 0 | No
2030-08-16 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -395 | -415.41 | -510 | 0 | 0 | No
2030-08-16 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -115.41 | -210 | 0 | 0 | No
2030-08-16 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 184.59 | 90 | 0 | 0 | No
2030-08-16 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 484.59 | 140.19 | 0 | 0 | No
2030-08-16 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 476.51 | 510 | 323.72 | 0 | 0 | No
2030-08-16 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 217.98 | 510 | 259.47 | 0 | 0 | No
2030-08-17 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-08-17 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 500.26 | -106.15 | 0 | 0 | No
2030-08-17 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 468.56 | -26.41 | 0 | 0 | No
2030-08-17 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | -137.67 | 0 | 0 | No
2030-08-17 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 311.33 | -85.63 | 0 | 0 | No
2030-08-17 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 235.36 | 0 | 0 | 0 | No
2030-08-17 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | -275.5 | 0 | 0 | No
2030-08-17 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 187.48 | 0 | 0 | 0 | No
2030-08-17 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 97.63 | 0 | 0 | 0 | No
2030-08-17 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 128.09 | 89.64 | 0 | 0 | No
2030-08-17 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 64.14 | 0 | 0 | 0 | No
2030-08-17 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -18.05 | 89.55 | 0 | 0 | No
2030-08-17 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 74.52 | 2.84 | 0 | 0 | No
2030-08-17 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -225.48 | -0.62 | 0 | 0 | No
2030-08-17 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -450.44 | 0 | 0 | 0 | No
2030-08-17 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -436.45 | -2.3 | 0 | 0 | No
2030-08-17 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -136.45 | 36.45 | 0 | 0 | No
2030-08-17 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 163.55 | 267.79 | 0 | 0 | No
2030-08-17 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 463.55 | 510 | 0 | 0 | No
2030-08-17 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-08-17 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 210 | 0 | 0 | No
2030-08-17 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 455.5 | 0 | 0 | No
2030-08-17 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 208.3 | 0 | 0 | No
2030-08-17 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 451.06 | 0 | 0 | 0 | No
2030-08-18 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 151.06 | 0 | 0 | 0 | No
2030-08-18 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 451.06 | 0 | 0 | 0 | No
2030-08-18 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 309.11 | 9.29 | 0 | 0 | No
2030-08-18 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 248.52 | 0 | 0 | 0 | No
2030-08-18 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 195.99 | 95.36 | 0 | 0 | No
2030-08-18 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 70.31 | 0 | 0 | No
2030-08-18 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -16.55 | 76.08 | 0 | 0 | No
2030-08-18 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -81.54 | -260.14 | 116.75 | 0 | 0 | No
2030-08-18 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -381.54 | -510 | 108.84 | 0 | 0 | No
2030-08-18 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 149.08 | 0 | 0 | No
2030-08-18 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 163.77 | 0 | 0 | No
2030-08-18 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 187.91 | 0 | 0 | No
2030-08-18 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 300.07 | 0 | 0 | No
2030-08-18 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 271.99 | 0 | 0 | No
2030-08-18 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 258.79 | 0 | 0 | No
2030-08-18 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 245.07 | 0 | 0 | No
2030-08-18 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 275 | 0 | 0 | No
2030-08-18 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -500.39 | 357.06 | 0 | 0 | No
2030-08-18 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -200.39 | 314.98 | 0 | 0 | No
2030-08-18 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 99.61 | 124.32 | 0 | 0 | No
2030-08-18 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 353.76 | 339.91 | 0 | 0 | No
2030-08-18 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 53.76 | 393.78 | 0 | 0 | No
2030-08-18 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 322.71 | 336.85 | 0 | 0 | No
2030-08-18 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 22.71 | 244.36 | 0 | 0 | No
2030-08-19 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 263.14 | 0 | 0 | No
2030-08-19 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 222.28 | 0 | 0 | No
2030-08-19 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 201.71 | 0 | 0 | No
2030-08-19 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 185.37 | 0 | 0 | No
2030-08-19 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 184.82 | 67.2 | 0 | 0 | No
2030-08-19 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 66.24 | 0 | 0 | No
2030-08-19 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -73.45 | 0 | 0 | 0 | No
2030-08-19 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -373.45 | 72.26 | 0 | 0 | No
2030-08-19 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -274.18 | -510 | -21.91 | 0 | 0 | No
2030-08-19 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -8.94 | 0 | 0 | No
2030-08-19 10:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | 115.91 | 0 | 0 | No
2030-08-19 11:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 77.81 | 0 | 0 | No
2030-08-19 12:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -210 | 377.81 | 0 | 0 | No
2030-08-19 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 452.39 | 0 | 0 | Yes
2030-08-19 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 269.45 | 0 | 0 | Yes
2030-08-19 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-19 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 426.32 | 0 | 0 | Yes
2030-08-19 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 342.35 | 0 | 0 | Yes
2030-08-19 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 204.93 | 0 | 0 | Yes
2030-08-19 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 184.99 | 0 | 0 | Yes
2030-08-19 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 147.38 | 0 | 0 | Yes
2030-08-19 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 295.82 | 0 | 0 | Yes
2030-08-19 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-19 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 210 | 0 | 0 | Yes
2030-08-20 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -90 | 0 | 0 | Yes
2030-08-20 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -74.33 | 0 | 0 | Yes
2030-08-20 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -91.36 | 0 | 0 | Yes
2030-08-20 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -125.38 | 0 | 0 | Yes
2030-08-20 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -95.69 | 0 | 0 | Yes
2030-08-20 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 51.19 | 0 | 0 | Yes
2030-08-20 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 57.69 | 0 | 0 | Yes
2030-08-20 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 119.42 | 0 | 0 | Yes
2030-08-20 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 203.33 | 0 | 0 | Yes
2030-08-20 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 200 | 0 | 0 | Yes
2030-08-20 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 151.84 | 0 | 0 | Yes
2030-08-20 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 175.76 | 0 | 0 | Yes
2030-08-20 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 366.62 | 0 | 0 | Yes
2030-08-20 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 416.75 | 0 | 0 | Yes
2030-08-20 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 116.75 | 0 | 0 | Yes
2030-08-20 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 82.39 | 0 | 0 | Yes
2030-08-20 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 248.03 | 0 | 0 | Yes
2030-08-20 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 277.27 | 0 | 0 | Yes
2030-08-20 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 341.54 | 510 | 200.66 | 0 | 0 | Yes
2030-08-20 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 41.54 | 210 | -99.34 | 0 | 0 | Yes
2030-08-20 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 341.54 | 510 | 200.66 | 0 | 0 | Yes
2030-08-20 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 160.66 | 0 | 0 | Yes
2030-08-20 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 57.22 | 0 | 0 | Yes
2030-08-20 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -51.28 | 0 | 0 | Yes
2030-08-21 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 248.72 | 0 | 0 | Yes
2030-08-21 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 183.99 | 0 | 0 | Yes
2030-08-21 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-08-21 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-21 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 300 | 0 | 0 | Yes
2030-08-21 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-21 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-21 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 | 2030 33% ECP + 1.3 GW Offshore | -472.24 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 01:00 | 2030 33% ECP + 1.3 GW Offshore | -575.18 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-22 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-22 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 390 | 510 | 0 | 0 | Yes
2030-08-22 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 212.9 | 90 | 510 | 0 | 0 | Yes
2030-08-22 17:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -87.1 | -210 | 510 | 0 | 0 | No
2030-08-22 18:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -387.1 | -510 | 295.99 | 0 | 0 | No
2030-08-22 19:00 | 2030 33% ECP + 1.3 GW Offshore | 202.85 | -526 | -510 | 103.97 | 0 | 0 | No
2030-08-22 20:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -231.5 | -210 | 106.38 | 0 | 0 | No
2030-08-22 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 68.5 | 90 | 406.38 | 0 | 0 | No
2030-08-22 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 368.5 | 390 | 510 | 0 | 0 | No
2030-08-22 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-23 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 448.86 | 510 | 0 | 0 | No
2030-08-23 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 148.86 | 474.11 | 0 | 0 | No
2030-08-23 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -151.14 | 445.64 | 0 | 0 | No
2030-08-23 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -395 | -451.14 | 349.69 | 0 | 0 | No
2030-08-23 09:00 | 2030 33% ECP + 1.3 GW Offshore | 307.89 | -526 | -510 | 305.11 | 0 | 0 | No
2030-08-23 10:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 459.17 | 0 | 0 | No
2030-08-23 11:00 | 2030 33% ECP + 1.3 GW Offshore | -161.56 | -526 | -510 | 450.48 | 0 | 0 | No
2030-08-23 12:00 | 2030 33% ECP + 1.3 GW Offshore | -581.56 | -526 | -510 | 392.29 | 0 | 0 | No
2030-08-23 13:00 | 2030 33% ECP + 1.3 GW Offshore | -161.56 | -526 | -510 | 461.67 | 0 | 0 | No
2030-08-23 14:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 416.52 | 0 | 0 | No
2030-08-23 15:00 | 2030 33% ECP + 1.3 GW Offshore | 140.21 | -526 | -510 | 421.74 | 0 | 0 | No
2030-08-23 16:00 | 2030 33% ECP + 1.3 GW Offshore | 560.21 | -526 | -510 | 283.93 | 0 | 0 | No
2030-08-23 17:00 | 2030 33% ECP + 1.3 GW Offshore | 140.21 | -526 | -510 | 238.27 | 0 | 0 | No
2030-08-23 18:00 | 2030 33% ECP + 1.3 GW Offshore | 560.21 | -226 | -288.27 | 0 | 0 | 0 | No
2030-08-23 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 8.24 | 274.43 | 0 | 0 | No
2030-08-23 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 247.95 | 264.61 | 0 | 0 | No
2030-08-23 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 406.79 | 0 | 0 | No
2030-08-23 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 210 | 372.75 | 0 | 0 | No
2030-08-23 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 210 | 325.05 | 0 | 0 | No
2030-08-24 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 179.04 | 0 | 0 | No
2030-08-24 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 466.72 | 0 | 0 | No
2030-08-24 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 270.62 | 0 | 0 | No
2030-08-24 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 508.58 | 0 | 0 | No
2030-08-24 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 208.58 | 0 | 0 | No
2030-08-24 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 22.08 | 0 | 0 | No
2030-08-24 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 46.75 | 0 | 0 | No
2030-08-24 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 73.65 | 0 | 0 | No
2030-08-24 08:00 | 2030 33% ECP + 1.3 GW Offshore | 362.31 | -300 | -300 | 53.85 | 0 | 0 | No
2030-08-24 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 38.99 | 0 | 0 | No
2030-08-24 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 16.35 | 0 | 0 | No
2030-08-24 11:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 20.21 | 0 | 0 | No
2030-08-24 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 25.75 | 0 | 0 | No
2030-08-24 13:00 | 2030 33% ECP + 1.3 GW Offshore | 337.95 | -526 | -510 | 0 | 0 | 0 | No
2030-08-24 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 185.04 | 0 | 0 | No
2030-08-24 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-08-24 16:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 48.82 | 0 | 0 | No
2030-08-24 17:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -526 | -510 | -251.18 | 0 | 0 | No
2030-08-24 18:00 | 2030 33% ECP + 1.3 GW Offshore | -184.57 | -526 | -510 | -510 | 0 | 0 | No
2030-08-24 19:00 | 2030 33% ECP + 1.3 GW Offshore | -184.57 | -526 | -510 | -406.91 | 0 | 0 | No
2030-08-24 20:00 | 2030 33% ECP + 1.3 GW Offshore | -184.57 | -526 | -510 | -117.61 | 0 | 0 | No
2030-08-24 21:00 | 2030 33% ECP + 1.3 GW Offshore | -604.57 | -526 | -510 | -272.09 | 0 | 0 | No
2030-08-24 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -260.95 | 0 | 0 | No
2030-08-24 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-25 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-08-25 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-08-25 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-08-25 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 0 | 0 | 0 | Yes
2030-08-25 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -185.85 | 0 | 0 | Yes
2030-08-25 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -183.81 | 0 | 0 | Yes
2030-08-25 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -223.38 | 0 | 0 | Yes
2030-08-25 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | -176.87 | 0 | 0 | Yes
2030-08-25 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 48.39 | 0 | 0 | Yes
2030-08-25 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 0 | 0 | 0 | Yes
2030-08-25 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 186.36 | 0 | 0 | Yes
2030-08-25 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 486.36 | 0 | 0 | Yes
2030-08-25 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-25 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-26 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 01:00 | 2030 33% ECP + 1.3 GW Offshore | -606.59 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 02:00 | 2030 33% ECP + 1.3 GW Offshore | -186.59 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 03:00 | 2030 33% ECP + 1.3 GW Offshore | -260.86 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 04:00 | 2030 33% ECP + 1.3 GW Offshore | -2.3 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 05:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 08:00 | 2030 33% ECP + 1.3 GW Offshore | 383.19 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 09:00 | 2030 33% ECP + 1.3 GW Offshore | -36.81 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 10:00 | 2030 33% ECP + 1.3 GW Offshore | -456.81 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 13:00 | 2030 33% ECP + 1.3 GW Offshore | -560 | 505 | 510 | 510 | 0 | 0 | No
2030-08-26 14:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | 205 | 210 | 510 | 0 | 0 | No
2030-08-26 15:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -95 | -90 | 459.87 | 0 | 0 | No
2030-08-26 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -395 | -390 | 510 | 0 | 0 | No
2030-08-26 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -252.32 | -510 | 510 | 0 | 0 | No
2030-08-26 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -210 | 425.93 | 0 | 0 | No
2030-08-26 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 425.93 | 0 | 0 | No
2030-08-26 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -3.47 | 425.93 | 0 | 0 | No
2030-08-26 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 425.93 | 0 | 0 | No
2030-08-26 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -58.67 | 446.38 | 0 | 0 | No
2030-08-26 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -232.74 | 268.34 | 0 | 0 | No
2030-08-27 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 53.47 | 0 | 0 | No
2030-08-27 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 55.1 | 0 | 0 | No
2030-08-27 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 23.44 | 0 | 0 | No
2030-08-27 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -183.34 | 25.46 | 0 | 0 | No
2030-08-27 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -215.78 | 12.02 | 0 | 0 | No
2030-08-27 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -430.69 | 29.77 | 0 | 0 | No
2030-08-27 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -241.45 | 99.34 | 0 | 0 | No
2030-08-27 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -94.81 | 167.67 | 0 | 0 | No
2030-08-27 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 51.58 | 272.17 | 0 | 0 | No
2030-08-27 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 51.58 | 495.84 | 0 | 0 | No
2030-08-27 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -75.99 | 495.84 | 0 | 0 | No
2030-08-27 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -131.66 | -375.99 | 443.93 | 0 | 0 | No
2030-08-27 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -234.27 | -510 | 444.46 | 0 | 0 | No
2030-08-27 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -494.3 | -510 | 168.56 | 0 | 0 | No
2030-08-27 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 380.81 | 0 | 0 | No
2030-08-27 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -466.73 | -510 | 361.72 | 0 | 0 | No
2030-08-27 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -352.95 | 417.14 | 0 | 0 | No
2030-08-27 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -52.95 | 270.71 | 0 | 0 | No
2030-08-27 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 247.05 | 270.71 | 0 | 0 | No
2030-08-27 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 302.67 | 199.61 | 0 | 0 | No
2030-08-27 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 244.99 | 0 | 0 | No
2030-08-27 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 13.65 | 0 | 0 | No
2030-08-27 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-08-27 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 01:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 381.23 | 510 | 382.24 | 0 | 0 | No
2030-08-28 02:00 | 2030 33% ECP + 1.3 GW Offshore | -95.34 | 505 | 510 | 84.22 | 0 | 0 | Yes
2030-08-28 03:00 | 2030 33% ECP + 1.3 GW Offshore | -132.48 | 505 | 510 | 27.09 | 0 | 0 | Yes
2030-08-28 04:00 | 2030 33% ECP + 1.3 GW Offshore | -424.03 | 505 | 510 | 327.09 | 0 | 0 | Yes
2030-08-28 05:00 | 2030 33% ECP + 1.3 GW Offshore | -672.96 | 505 | 510 | 27.09 | 0 | 0 | Yes
2030-08-28 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 327.09 | 0 | 0 | Yes
2030-08-28 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 436.38 | 0 | 0 | Yes
2030-08-28 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-28 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 510 | 510 | 0 | 0 | Yes
2030-08-28 18:00 | 2030 33% ECP + 1.3 GW Offshore | -456.24 | 0 | 210 | 210 | 0 | 0 | No
2030-08-28 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -0.6 | 0 | 0 | 0 | No
2030-08-28 20:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | 0 | 75.9 | 0 | 0 | No
2030-08-28 21:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 300 | 300 | 375.9 | 0 | 0 | No
2030-08-28 22:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | 505 | 510 | 510 | 0 | 0 | No
2030-08-28 23:00 | 2030 33% ECP + 1.3 GW Offshore | -313.29 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 | 2030 33% ECP + 1.3 GW Offshore | -167.21 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 01:00 | 2030 33% ECP + 1.3 GW Offshore | -587.21 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 02:00 | 2030 33% ECP + 1.3 GW Offshore | -421.66 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 03:00 | 2030 33% ECP + 1.3 GW Offshore | -596.48 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 16:00 | 2030 33% ECP + 1.3 GW Offshore | -533.68 | 505 | 510 | 510 | 0 | 0 | Yes
2030-08-29 17:00 | 2030 33% ECP + 1.3 GW Offshore | -113.68 | 205 | 210 | 477.57 | 0 | 0 | No
2030-08-29 18:00 | 2030 33% ECP + 1.3 GW Offshore | 306.32 | -95 | -90 | 177.57 | 0 | 0 | No
2030-08-29 19:00 | 2030 33% ECP + 1.3 GW Offshore | 138.36 | -395 | -390 | -90 | 0 | 0 | No
2030-08-29 20:00 | 2030 33% ECP + 1.3 GW Offshore | 558.36 | -95 | -90 | 210 | 0 | 0 | No
2030-08-29 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-08-29 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-29 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-08-30 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 263.63 | 399.88 | 0 | 0 | No
2030-08-30 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -36.37 | 262.2 | 0 | 0 | No
2030-08-30 08:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -300 | -336.37 | 262.2 | 0 | 0 | No
2030-08-30 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 201.2 | 0 | 0 | No
2030-08-30 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -98.8 | 0 | 0 | No
2030-08-30 11:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 166.54 | 0 | 0 | No
2030-08-30 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 169.68 | 0 | 0 | No
2030-08-30 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 137.81 | 0 | 0 | No
2030-08-30 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 107.43 | 0 | 0 | No
2030-08-30 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 146.31 | 0 | 0 | No
2030-08-30 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -300 | -11.49 | 0 | 0 | No
2030-08-30 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 74 | 0 | 101.11 | 0 | 0 | No
2030-08-30 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -84.92 | -300 | -198.89 | 0 | 0 | No
2030-08-30 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -244.55 | -425.96 | -473.32 | 0 | 0 | No
2030-08-30 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -125.96 | -173.32 | 0 | 0 | No
2030-08-30 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 174.04 | 126.68 | 0 | 0 | No
2030-08-30 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 305.38 | 474.04 | 426.68 | 0 | 0 | No
2030-08-30 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 140.1 | 510 | 329.29 | 0 | 0 | No
2030-08-31 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 312.15 | 29.29 | 0 | 0 | No
2030-08-31 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 169.5 | 29.98 | 0 | 0 | No
2030-08-31 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -130.5 | 0 | 0 | 0 | No
2030-08-31 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -430.5 | 0 | 0 | 0 | No
2030-08-31 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -159.07 | 0 | 0 | No
2030-08-31 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -286.38 | 0 | 0 | No
2030-08-31 06:00 | 2030 33% ECP + 1.3 GW Offshore | 418.89 | 0 | -510 | -17.98 | 0 | 0 | No
2030-08-31 07:00 | 2030 33% ECP + 1.3 GW Offshore | -1.11 | -226 | -510 | -317.98 | 0 | 0 | No
2030-08-31 08:00 | 2030 33% ECP + 1.3 GW Offshore | -421.11 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-08-31 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-08-31 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 17:00 | 2030 33% ECP + 1.3 GW Offshore | -495.29 | -526 | -510 | -396.94 | 0 | 0 | No
2030-08-31 18:00 | 2030 33% ECP + 1.3 GW Offshore | -75.29 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 19:00 | 2030 33% ECP + 1.3 GW Offshore | 250.89 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 20:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -510 | 0 | 0 | No
2030-08-31 21:00 | 2030 33% ECP + 1.3 GW Offshore | 244.55 | -526 | -510 | -224.64 | 0 | 0 | No
2030-08-31 22:00 | 2030 33% ECP + 1.3 GW Offshore | 506.79 | -526 | -510 | -321.11 | 0 | 0 | No
2030-08-31 23:00 | 2030 33% ECP + 1.3 GW Offshore | 89.66 | -526 | -510 | -75.78 | 0 | 0 | No
2030-09-01 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -109.11 | 0 | 0 | No
2030-09-01 01:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -84 | 0 | 0 | No
2030-09-01 02:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -75.56 | 0 | 0 | No
2030-09-01 03:00 | 2030 33% ECP + 1.3 GW Offshore | 283.17 | -526 | -510 | -92.68 | 0 | 0 | No
2030-09-01 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -139.03 | 0 | 0 | No
2030-09-01 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -319.45 | 0 | 0 | No
2030-09-01 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -135.64 | 0 | 0 | No
2030-09-01 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -216.58 | 0 | 0 | No
2030-09-01 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -24.38 | 0 | 0 | No
2030-09-01 09:00 | 2030 33% ECP + 1.3 GW Offshore | 672.89 | -526 | -510 | -82.33 | 0 | 0 | No
2030-09-01 10:00 | 2030 33% ECP + 1.3 GW Offshore | 252.89 | -526 | -510 | -98.2 | 0 | 0 | No
2030-09-01 11:00 | 2030 33% ECP + 1.3 GW Offshore | 27.46 | -526 | -510 | -165.5 | 0 | 0 | No
2030-09-01 12:00 | 2030 33% ECP + 1.3 GW Offshore | 103.82 | -526 | -510 | -235.3 | 0 | 0 | No
2030-09-01 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -322.47 | 0 | 0 | No
2030-09-01 14:00 | 2030 33% ECP + 1.3 GW Offshore | 205.29 | -526 | -510 | -55.65 | 0 | 0 | No
2030-09-01 15:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -226.01 | 0 | 0 | No
2030-09-01 16:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | -526 | -510 | 48.77 | 0 | 0 | No
2030-09-01 17:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 151.87 | 0 | 0 | No
2030-09-01 18:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 151.87 | 0 | 0 | No
2030-09-01 19:00 | 2030 33% ECP + 1.3 GW Offshore | -132.47 | -526 | -510 | 50.04 | 0 | 0 | No
2030-09-01 20:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | 0 | 0 | 0 | No
2030-09-01 21:00 | 2030 33% ECP + 1.3 GW Offshore | -272.31 | -526 | -510 | -96.24 | 0 | 0 | No
2030-09-01 22:00 | 2030 33% ECP + 1.3 GW Offshore | -272.31 | -526 | -510 | -232.43 | 0 | 0 | No
2030-09-01 23:00 | 2030 33% ECP + 1.3 GW Offshore | -82.57 | -526 | -510 | -245.14 | 0 | 0 | No
2030-09-02 | 2030 33% ECP + 1.3 GW Offshore | -502.57 | -526 | -510 | -387.02 | 0 | 0 | No
2030-09-02 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -260.73 | 0 | 0 | Yes
2030-09-02 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -229.25 | 0 | 0 | Yes
2030-09-02 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -210 | 0 | 0 | No
2030-09-02 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-09-02 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-09-02 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-09-02 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-09-02 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-09-02 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-09-02 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-02 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-02 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 04:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 05:00 | 2030 33% ECP + 1.3 GW Offshore | -560.87 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 06:00 | 2030 33% ECP + 1.3 GW Offshore | -140.87 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 07:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 205 | 510 | 448.51 | 0 | 0 | No
2030-09-03 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-03 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 356.58 | 510 | 0 | 0 | Yes
2030-09-03 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 56.58 | 210 | 0 | 0 | No
2030-09-03 18:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 0 | -243.42 | -90 | 0 | 0 | No
2030-09-03 19:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -300 | -366.58 | -300 | 0 | 0 | No
2030-09-03 20:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -66.58 | 0 | 0 | 0 | No
2030-09-03 21:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 300 | 233.42 | 300 | 0 | 0 | No
2030-09-03 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-03 23:00 | 2030 33% ECP + 1.3 GW Offshore | 379.89 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 04:00 | 2030 33% ECP + 1.3 GW Offshore | 682.7 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 05:00 | 2030 33% ECP + 1.3 GW Offshore | 262.7 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 06:00 | 2030 33% ECP + 1.3 GW Offshore | -157.3 | 205 | 210 | 210 | 0 | 0 | No
2030-09-04 07:00 | 2030 33% ECP + 1.3 GW Offshore | -577.3 | 0 | 0 | 0 | 0 | 0 | No
2030-09-04 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 0 | 124.7 | 0 | 0 | No
2030-09-04 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 3.89 | 300 | 424.7 | 0 | 0 | No
2030-09-04 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 150.82 | 510 | 319.31 | 0 | 0 | Yes
2030-09-04 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | 210 | 19.31 | 0 | 0 | Yes
2030-09-04 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 510 | 319.31 | 0 | 0 | Yes
2030-09-04 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-04 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 210 | 347.55 | 0 | 0 | Yes
2030-09-04 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | -90 | 47.55 | 0 | 0 | Yes
2030-09-04 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -390 | -252.45 | 0 | 0 | No
2030-09-04 18:00 | 2030 33% ECP + 1.3 GW Offshore | -424.24 | -526 | -510 | -505.5 | 0 | 0 | No
2030-09-04 19:00 | 2030 33% ECP + 1.3 GW Offshore | -198.65 | -395 | -390 | -244.51 | 0 | 0 | No
2030-09-04 20:00 | 2030 33% ECP + 1.3 GW Offshore | -209.19 | -95 | -90 | -90 | 0 | 0 | No
2030-09-04 21:00 | 2030 33% ECP + 1.3 GW Offshore | -209.19 | 205 | 210 | 210 | 0 | 0 | No
2030-09-04 22:00 | 2030 33% ECP + 1.3 GW Offshore | 210.81 | 505 | 510 | 510 | 0 | 0 | No
2030-09-04 23:00 | 2030 33% ECP + 1.3 GW Offshore | -209.19 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 01:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 02:00 | 2030 33% ECP + 1.3 GW Offshore | 115.22 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 03:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 04:00 | 2030 33% ECP + 1.3 GW Offshore | 104.12 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 05:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 06:00 | 2030 33% ECP + 1.3 GW Offshore | 109.08 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 07:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 205 | 313.92 | 210 | 0 | 0 | No
2030-09-05 08:00 | 2030 33% ECP + 1.3 GW Offshore | -282.05 | 505 | 510 | 510 | 0 | 0 | No
2030-09-05 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-05 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 331.6 | 510 | 0 | 0 | Yes
2030-09-05 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 205 | 31.6 | 496.29 | 0 | 0 | Yes
2030-09-05 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -95 | -268.4 | 196.29 | 0 | 0 | Yes
2030-09-05 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -339.18 | 471.1 | 0 | 0 | Yes
2030-09-05 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | No
2030-09-05 15:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-09-05 16:00 | 2030 33% ECP + 1.3 GW Offshore | 8.01 | -526 | -510 | 510 | 0 | 0 | No
2030-09-05 17:00 | 2030 33% ECP + 1.3 GW Offshore | 428.01 | -226 | -510 | 510 | 0 | 0 | No
2030-09-05 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-09-05 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-09-05 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-09-05 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-09-05 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 510 | 0 | 0 | No
2030-09-05 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -435.53 | 469 | 0 | 0 | No
2030-09-06 | 2030 33% ECP + 1.3 GW Offshore | 280 | 0 | -239.78 | 169 | 0 | 0 | No
2030-09-06 01:00 | 2030 33% ECP + 1.3 GW Offshore | 578.76 | 0 | 0 | 0 | 0 | 0 | No
2030-09-06 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -165.26 | 0 | 0 | 0 | No
2030-09-06 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -465.26 | 0 | 0 | 0 | No
2030-09-06 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -37.84 | 0 | 0 | No
2030-09-06 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -204.67 | -510 | -12.31 | 0 | 0 | No
2030-09-06 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -66.37 | -510 | -144.8 | 0 | 0 | No
2030-09-06 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -9.21 | 0 | 0 | No
2030-09-06 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -42.54 | -437.72 | 0 | 0 | 0 | No
2030-09-06 09:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -342.54 | -510 | -69.8 | 0 | 0 | No
2030-09-06 10:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -137.82 | 0 | 0 | No
2030-09-06 11:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -526 | -510 | -146.98 | 0 | 0 | No
2030-09-06 12:00 | 2030 33% ECP + 1.3 GW Offshore | -185.8 | -526 | -510 | -150.93 | 0 | 0 | No
2030-09-06 13:00 | 2030 33% ECP + 1.3 GW Offshore | -83.62 | -526 | -510 | -238.28 | 0 | 0 | No
2030-09-06 14:00 | 2030 33% ECP + 1.3 GW Offshore | -503.62 | -526 | -510 | -217.58 | 0 | 0 | No
2030-09-06 15:00 | 2030 33% ECP + 1.3 GW Offshore | -83.62 | -526 | -510 | -106.86 | 0 | 0 | No
2030-09-06 16:00 | 2030 33% ECP + 1.3 GW Offshore | 257.71 | -526 | -510 | -298.33 | 0 | 0 | No
2030-09-06 17:00 | 2030 33% ECP + 1.3 GW Offshore | 677.71 | -226 | -510 | -374.25 | 0 | 0 | No
2030-09-06 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -374.25 | 0 | 0 | No
2030-09-06 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -354.72 | 0 | 0 | No
2030-09-06 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -497.29 | 0 | 0 | No
2030-09-06 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -300 | -197.29 | 0 | 0 | No
2030-09-06 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 102.71 | 0 | 0 | No
2030-09-06 23:00 | 2030 33% ECP + 1.3 GW Offshore | 666.44 | -300 | -300 | -197.29 | 0 | 0 | No
2030-09-07 | 2030 33% ECP + 1.3 GW Offshore | 673.6 | -436.85 | -510 | -200.95 | 0 | 0 | No
2030-09-07 01:00 | 2030 33% ECP + 1.3 GW Offshore | 253.6 | -526 | -510 | -158.21 | 0 | 0 | No
2030-09-07 02:00 | 2030 33% ECP + 1.3 GW Offshore | -42.43 | -445.79 | -510 | -49.17 | 0 | 0 | No
2030-09-07 03:00 | 2030 33% ECP + 1.3 GW Offshore | -462.43 | -526 | -510 | -17.2 | 0 | 0 | No
2030-09-07 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -231.36 | 0 | 0 | No
2030-09-07 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -180.36 | 0 | 0 | No
2030-09-07 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -180.85 | 0 | 0 | No
2030-09-07 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 51.17 | 0 | 0 | No
2030-09-07 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 144.58 | 0 | 0 | No
2030-09-07 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 95.38 | 0 | 0 | No
2030-09-07 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 168.3 | 0 | 0 | Yes
2030-09-07 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 468.3 | 0 | 0 | Yes
2030-09-07 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-09-07 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-09-07 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-07 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 300 | 510 | 510 | 0 | 0 | Yes
2030-09-07 16:00 | 2030 33% ECP + 1.3 GW Offshore | -290.23 | 0 | 210 | 381.28 | 0 | 0 | No
2030-09-07 17:00 | 2030 33% ECP + 1.3 GW Offshore | -277.67 | 0 | 0 | 230.75 | 0 | 0 | No
2030-09-07 18:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -300 | -300 | -69.25 | 0 | 0 | No
2030-09-07 19:00 | 2030 33% ECP + 1.3 GW Offshore | -170.46 | -300 | -300 | -90 | 0 | 0 | No
2030-09-07 20:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 0 | 210 | 0 | 0 | No
2030-09-07 21:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 300 | 300 | 510 | 0 | 0 | No
2030-09-07 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-07 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 210 | 0 | 0 | No
2030-09-08 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 269.05 | 210 | 510 | 0 | 0 | No
2030-09-08 09:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -30.95 | -90 | 510 | 0 | 0 | No
2030-09-08 10:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | -330.95 | -390 | 510 | 0 | 0 | No
2030-09-08 11:00 | 2030 33% ECP + 1.3 GW Offshore | -461.46 | -76.58 | -510 | 510 | 0 | 0 | No
2030-09-08 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -145.13 | -510 | 510 | 0 | 0 | No
2030-09-08 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -111.74 | -510 | 510 | 0 | 0 | No
2030-09-08 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -148.27 | -508.51 | 510 | 0 | 0 | No
2030-09-08 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 0 | -208.51 | 357.93 | 0 | 0 | No
2030-09-08 16:00 | 2030 33% ECP + 1.3 GW Offshore | -361.48 | 0 | 0 | 339.11 | 0 | 0 | No
2030-09-08 17:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | 139.4 | 285.22 | 0 | 0 | No
2030-09-08 18:00 | 2030 33% ECP + 1.3 GW Offshore | -40.99 | 0 | 0 | 10.42 | 0 | 0 | No
2030-09-08 19:00 | 2030 33% ECP + 1.3 GW Offshore | -236.03 | 205 | 210 | 303.47 | 0 | 0 | No
2030-09-08 20:00 | 2030 33% ECP + 1.3 GW Offshore | -527.55 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 21:00 | 2030 33% ECP + 1.3 GW Offshore | -107.55 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 22:00 | 2030 33% ECP + 1.3 GW Offshore | 158.62 | 505 | 510 | 510 | 0 | 0 | No
2030-09-08 23:00 | 2030 33% ECP + 1.3 GW Offshore | 102 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 | 2030 33% ECP + 1.3 GW Offshore | 522 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 01:00 | 2030 33% ECP + 1.3 GW Offshore | 597.54 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 02:00 | 2030 33% ECP + 1.3 GW Offshore | 231.45 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 03:00 | 2030 33% ECP + 1.3 GW Offshore | 136.91 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 04:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 05:00 | 2030 33% ECP + 1.3 GW Offshore | 252.25 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 06:00 | 2030 33% ECP + 1.3 GW Offshore | 292.42 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 07:00 | 2030 33% ECP + 1.3 GW Offshore | -20.97 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 08:00 | 2030 33% ECP + 1.3 GW Offshore | -440.97 | 505 | 510 | 510 | 0 | 0 | No
2030-09-09 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 15:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-09 16:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 300 | 248.71 | 510 | 0 | 0 | No
2030-09-09 17:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | 0 | -51.29 | 336.41 | 0 | 0 | No
2030-09-09 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 203.11 | 510 | 0 | 0 | No
2030-09-09 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 413.43 | 510 | 0 | 0 | No
2030-09-09 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-09 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-09 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 210 | 510 | 0 | 0 | No
2030-09-09 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-10 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 256.95 | 0 | 0 | No
2030-09-10 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 332.03 | 229.26 | 0 | 0 | No
2030-09-10 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 380.89 | 190.54 | 0 | 0 | No
2030-09-10 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 171.17 | 0 | 0 | No
2030-09-10 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 183.38 | 0 | 0 | No
2030-09-10 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 264.1 | 225.1 | 0 | 0 | No
2030-09-10 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 324.3 | 0 | 0 | No
2030-09-10 07:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -247.97 | -300 | 350.25 | 0 | 0 | No
2030-09-10 08:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -226 | -210 | 503.4 | 0 | 0 | No
2030-09-10 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 510 | 0 | 0 | No
2030-09-10 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 381 | 0 | 0 | No
2030-09-10 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 355.04 | 0 | 0 | No
2030-09-10 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 166.65 | 0 | 0 | No
2030-09-10 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 176.12 | 0 | 0 | No
2030-09-10 14:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 210.29 | 0 | 0 | No
2030-09-10 15:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 288.87 | 0 | 0 | No
2030-09-10 16:00 | 2030 33% ECP + 1.3 GW Offshore | 279.53 | -526 | -510 | 489.09 | 0 | 0 | No
2030-09-10 17:00 | 2030 33% ECP + 1.3 GW Offshore | 699.53 | -394.26 | -510 | 460.63 | 0 | 0 | No
2030-09-10 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -94.26 | -510 | 510 | 0 | 0 | No
2030-09-10 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -94.26 | -510 | 510 | 0 | 0 | No
2030-09-10 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -394.26 | -510 | 392.03 | 0 | 0 | No
2030-09-10 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -394.26 | -510 | 388.84 | 0 | 0 | No
2030-09-10 22:00 | 2030 33% ECP + 1.3 GW Offshore | 354.06 | -300 | -378.93 | 275.66 | 0 | 0 | No
2030-09-10 23:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | 0 | -78.93 | 93.25 | 0 | 0 | No
2030-09-11 | 2030 33% ECP + 1.3 GW Offshore | 23.23 | 300 | 221.07 | 393.25 | 0 | 0 | No
2030-09-11 01:00 | 2030 33% ECP + 1.3 GW Offshore | -396.77 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-11 16:00 | 2030 33% ECP + 1.3 GW Offshore | -406.88 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 17:00 | 2030 33% ECP + 1.3 GW Offshore | 13.12 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 18:00 | 2030 33% ECP + 1.3 GW Offshore | 239.72 | 205 | 210 | 210 | 0 | 0 | No
2030-09-11 19:00 | 2030 33% ECP + 1.3 GW Offshore | 659.72 | -95 | -90 | 0 | 0 | 0 | No
2030-09-11 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -90 | 109.75 | 0 | 0 | No
2030-09-11 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 390.45 | 0 | 0 | No
2030-09-11 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-11 23:00 | 2030 33% ECP + 1.3 GW Offshore | 410.62 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 01:00 | 2030 33% ECP + 1.3 GW Offshore | -228.3 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 02:00 | 2030 33% ECP + 1.3 GW Offshore | -280.81 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 03:00 | 2030 33% ECP + 1.3 GW Offshore | -457.83 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 04:00 | 2030 33% ECP + 1.3 GW Offshore | -37.83 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 05:00 | 2030 33% ECP + 1.3 GW Offshore | -37.83 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 06:00 | 2030 33% ECP + 1.3 GW Offshore | 119.33 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 07:00 | 2030 33% ECP + 1.3 GW Offshore | -105.06 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 08:00 | 2030 33% ECP + 1.3 GW Offshore | -525.06 | 505 | 510 | 510 | 0 | 0 | No
2030-09-12 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-12 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-12 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-12 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-12 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 510 | 0 | 0 | Yes
2030-09-12 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 510 | 0 | 0 | Yes
2030-09-12 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | 510 | 0 | 0 | Yes
2030-09-12 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 286.01 | 0 | 0 | Yes
2030-09-12 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 84.05 | 0 | 0 | No
2030-09-12 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -92.89 | 0 | 0 | No
2030-09-12 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -304.05 | 0 | 0 | No
2030-09-12 20:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -328.55 | 0 | 0 | No
2030-09-12 21:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -28.55 | 0 | 0 | Yes
2030-09-12 22:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 271.45 | 0 | 0 | Yes
2030-09-12 23:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 377.05 | 0 | 0 | Yes
2030-09-13 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-13 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-13 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 300 | 510 | 0 | 0 | Yes
2030-09-13 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 0 | 510 | 0 | 0 | Yes
2030-09-13 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 0 | 510 | 0 | 0 | Yes
2030-09-13 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 0 | 510 | 0 | 0 | Yes
2030-09-13 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | 0 | 510 | 0 | 0 | Yes
2030-09-13 16:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | 416.46 | 0 | 0 | Yes
2030-09-13 17:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | 248.37 | 0 | 0 | Yes
2030-09-13 18:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | 444.14 | 0 | 0 | No
2030-09-13 19:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | 0 | 510 | 0 | 0 | No
2030-09-13 20:00 | 2030 33% ECP + 1.3 GW Offshore | -675.23 | -526 | 0 | 481.52 | 0 | 0 | No
2030-09-13 21:00 | 2030 33% ECP + 1.3 GW Offshore | -255.23 | -526 | 0 | 510 | 0 | 0 | No
2030-09-13 22:00 | 2030 33% ECP + 1.3 GW Offshore | 164.77 | -526 | 0 | 445.1 | 0 | 0 | No
2030-09-13 23:00 | 2030 33% ECP + 1.3 GW Offshore | 584.77 | -526 | 0 | 269.7 | 0 | 0 | No
2030-09-14 | 2030 33% ECP + 1.3 GW Offshore | 541.2 | -226 | 0 | 279.24 | 0 | 0 | No
2030-09-14 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 74 | 0 | 510 | 0 | 0 | No
2030-09-14 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | 0 | 210 | 0 | 0 | No
2030-09-14 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | -68.32 | 0 | 0 | No
2030-09-14 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | -18.93 | 0 | 0 | No
2030-09-14 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 14.48 | 0 | 0 | No
2030-09-14 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -424.61 | 0 | 45.98 | 0 | 0 | No
2030-09-14 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -377.23 | 0 | 139.71 | 0 | 0 | No
2030-09-14 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 172.33 | 0 | 0 | No
2030-09-14 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 199.85 | 0 | 0 | No
2030-09-14 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 224.28 | 0 | 0 | No
2030-09-14 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 228.23 | 0 | 0 | No
2030-09-14 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 223.7 | 0 | 0 | No
2030-09-14 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 167.81 | 0 | 0 | No
2030-09-14 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 146.61 | 0 | 0 | No
2030-09-14 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 164.2 | 0 | 0 | No
2030-09-14 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | 177.98 | 0 | 0 | No
2030-09-14 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | -118.84 | 0 | 0 | No
2030-09-14 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | -280.11 | 0 | 0 | No
2030-09-14 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | -236.47 | 0 | 0 | No
2030-09-14 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | -6.87 | 0 | 0 | No
2030-09-14 21:00 | 2030 33% ECP + 1.3 GW Offshore | 511.7 | -526 | 0 | 194.18 | 0 | 0 | No
2030-09-14 22:00 | 2030 33% ECP + 1.3 GW Offshore | 636.64 | -526 | 0 | 130.02 | 0 | 0 | No
2030-09-14 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | 0 | -147.56 | 0 | 0 | No
2030-09-15 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | 0 | 0 | 0 | 0 | No
2030-09-15 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-15 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-15 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-15 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-15 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-15 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-15 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -421.47 | 6.78 | 0 | 0 | No
2030-09-15 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -510 | 0 | 0 | 0 | No
2030-09-15 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 23.42 | 0 | 0 | No
2030-09-15 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-09-15 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-09-15 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 36.79 | 0 | 0 | No
2030-09-15 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 57.51 | 0 | 0 | No
2030-09-15 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 68.25 | 0 | 0 | No
2030-09-15 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 91.14 | 0 | 0 | No
2030-09-15 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 164.34 | 0 | 0 | No
2030-09-15 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -319.84 | 300 | 0 | 0 | No
2030-09-15 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-09-15 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 195.01 | 0 | 0 | No
2030-09-15 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 495.01 | 0 | 0 | No
2030-09-15 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 74 | 90 | 510 | 0 | 0 | No
2030-09-15 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 151.53 | 390 | 510 | 0 | 0 | No
2030-09-15 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 239.55 | 0 | 0 | No
2030-09-16 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 352.5 | 0 | 0 | No
2030-09-16 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 172.12 | 0 | 0 | No
2030-09-16 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 387.1 | 149.04 | 0 | 0 | No
2030-09-16 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 495.26 | 109.46 | 0 | 0 | No
2030-09-16 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 232.94 | 109.52 | 0 | 0 | No
2030-09-16 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 354.8 | 140.07 | 0 | 0 | No
2030-09-16 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 484.28 | 249.11 | 0 | 0 | No
2030-09-16 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 378.39 | 347.32 | 0 | 0 | No
2030-09-16 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 210 | 510 | 0 | 0 | No
2030-09-16 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 198.94 | 510 | 510 | 0 | 0 | No
2030-09-16 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 198.94 | 510 | 510 | 0 | 0 | No
2030-09-16 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 137.06 | 510 | 510 | 0 | 0 | No
2030-09-16 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 137.06 | 510 | 510 | 0 | 0 | No
2030-09-16 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 335.66 | 390 | 510 | 0 | 0 | No
2030-09-16 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 190.97 | 90 | 510 | 0 | 0 | No
2030-09-16 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -109.03 | -210 | 510 | 0 | 0 | No
2030-09-16 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -10.12 | -510 | 510 | 0 | 0 | No
2030-09-16 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -265.67 | 510 | 0 | 0 | No
2030-09-16 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-09-16 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -300 | 510 | 0 | 0 | No
2030-09-16 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -177.25 | 510 | 0 | 0 | No
2030-09-16 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 510 | 0 | 0 | No
2030-09-16 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 333.43 | 0 | 0 | No
2030-09-16 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 300 | 406.02 | 0 | 0 | No
2030-09-17 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 67.23 | 190.89 | 0 | 0 | No
2030-09-17 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 178.49 | 249.87 | 0 | 0 | No
2030-09-17 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -26.44 | 159.07 | 0 | 0 | No
2030-09-17 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -4.89 | 0 | 0 | 0 | No
2030-09-17 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-17 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -40.76 | 0 | 0 | 0 | No
2030-09-17 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 0 | 0 | 0 | No
2030-09-17 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -84.82 | 108.17 | 0 | 0 | No
2030-09-17 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -257.77 | -384.82 | 192.86 | 0 | 0 | No
2030-09-17 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 217.77 | 0 | 0 | No
2030-09-17 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 217.77 | 0 | 0 | No
2030-09-17 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 250.22 | 0 | 0 | No
2030-09-17 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 164.07 | 0 | 0 | No
2030-09-17 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 203.83 | 0 | 0 | No
2030-09-17 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 239.8 | 0 | 0 | No
2030-09-17 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 245.17 | 0 | 0 | No
2030-09-17 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -447.73 | -510 | 361.85 | 0 | 0 | No
2030-09-17 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -147.73 | -210 | 473.8 | 0 | 0 | No
2030-09-17 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 389.61 | 0 | 0 | No
2030-09-17 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 336.05 | 0 | 0 | No
2030-09-17 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 485.64 | 0 | 0 | No
2030-09-17 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -242.64 | 485.64 | 0 | 0 | No
2030-09-17 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 271.41 | 0 | 0 | No
2030-09-17 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -229.24 | 399.13 | 0 | 0 | No
2030-09-18 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -188.16 | 469.2 | 0 | 0 | No
2030-09-18 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -432.07 | 461.02 | 0 | 0 | No
2030-09-18 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 162.33 | 0 | 0 | No
2030-09-18 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -323.05 | 0 | 0 | 0 | No
2030-09-18 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 0 | 0 | 0 | No
2030-09-18 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -24.77 | -510 | 14.25 | 0 | 0 | No
2030-09-18 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 200.24 | 0 | 0 | No
2030-09-18 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -368.86 | 336.77 | 0 | 0 | No
2030-09-18 08:00 | 2030 33% ECP + 1.3 GW Offshore | 571.44 | -526 | -510 | 335.41 | 0 | 0 | No
2030-09-18 09:00 | 2030 33% ECP + 1.3 GW Offshore | 151.44 | -526 | -510 | 195.66 | 0 | 0 | No
2030-09-18 10:00 | 2030 33% ECP + 1.3 GW Offshore | -268.56 | -526 | -510 | 242.73 | 0 | 0 | No
2030-09-18 11:00 | 2030 33% ECP + 1.3 GW Offshore | -688.56 | -526 | -510 | 0 | 0 | 0 | No
2030-09-18 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 249.45 | 0 | 0 | No
2030-09-18 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 135.18 | 0 | 0 | No
2030-09-18 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 109.23 | 0 | 0 | No
2030-09-18 15:00 | 2030 33% ECP + 1.3 GW Offshore | -581.54 | -526 | -510 | 195.46 | 0 | 0 | No
2030-09-18 16:00 | 2030 33% ECP + 1.3 GW Offshore | -161.54 | -526 | -510 | 360.73 | 0 | 0 | No
2030-09-18 17:00 | 2030 33% ECP + 1.3 GW Offshore | 128.56 | -526 | -510 | 451.74 | 0 | 0 | No
2030-09-18 18:00 | 2030 33% ECP + 1.3 GW Offshore | 548.56 | -526 | -510 | 364.17 | 0 | 0 | No
2030-09-18 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -395 | -390 | 354.75 | 0 | 0 | No
2030-09-18 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -90 | 217.99 | 0 | 0 | No
2030-09-18 21:00 | 2030 33% ECP + 1.3 GW Offshore | 455.52 | 205 | 210 | 283.14 | 0 | 0 | No
2030-09-18 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-18 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-19 05:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | 205 | 210 | 210 | 0 | 0 | No
2030-09-19 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -90 | 207.45 | 0 | 0 | No
2030-09-19 07:00 | 2030 33% ECP + 1.3 GW Offshore | 467.81 | -289.48 | -390 | 425.86 | 0 | 0 | No
2030-09-19 08:00 | 2030 33% ECP + 1.3 GW Offshore | 47.81 | -526 | -510 | 177.34 | 0 | 0 | No
2030-09-19 09:00 | 2030 33% ECP + 1.3 GW Offshore | -372.19 | -526 | -510 | 320.38 | 0 | 0 | No
2030-09-19 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 416.51 | 0 | 0 | No
2030-09-19 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 369.57 | 0 | 0 | No
2030-09-19 12:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -226 | -496.43 | 510 | 0 | 0 | No
2030-09-19 13:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 0 | -496.43 | 510 | 0 | 0 | No
2030-09-19 14:00 | 2030 33% ECP + 1.3 GW Offshore | -88.13 | -226 | -496.43 | 510 | 0 | 0 | No
2030-09-19 15:00 | 2030 33% ECP + 1.3 GW Offshore | -508.13 | -526 | -510 | 489.09 | 0 | 0 | No
2030-09-19 16:00 | 2030 33% ECP + 1.3 GW Offshore | -224.08 | -526 | -510 | 489.09 | 0 | 0 | No
2030-09-19 17:00 | 2030 33% ECP + 1.3 GW Offshore | 195.92 | -226 | -210 | 489.09 | 0 | 0 | No
2030-09-19 18:00 | 2030 33% ECP + 1.3 GW Offshore | 615.92 | 0 | 28.81 | 425.25 | 0 | 0 | No
2030-09-19 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 28.81 | 394.04 | 0 | 0 | No
2030-09-19 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 175.34 | 0 | 0 | No
2030-09-19 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 277.19 | 0 | 0 | No
2030-09-19 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 104.06 | 317.11 | 0 | 0 | No
2030-09-19 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 404.06 | 179.08 | 0 | 0 | No
2030-09-20 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 421.42 | 179.08 | 0 | 0 | No
2030-09-20 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 55.69 | 0 | 0 | No
2030-09-20 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 356.79 | 264.93 | 0 | 0 | No
2030-09-20 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 43.39 | 510 | 510 | 0 | 0 | No
2030-09-20 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 248.47 | 300 | 510 | 0 | 0 | No
2030-09-20 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 0 | 210 | 0 | 0 | No
2030-09-20 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 100.83 | 127.26 | 0 | 0 | No
2030-09-20 07:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 0 | 179.99 | 424.1 | 0 | 0 | No
2030-09-20 08:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 0 | -120.01 | 510 | 0 | 0 | No
2030-09-20 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -300 | -420.01 | 381.6 | 0 | 0 | No
2030-09-20 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 268.19 | 0 | 0 | No
2030-09-20 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 267.41 | 0 | 0 | No
2030-09-20 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 237.96 | 0 | 0 | No
2030-09-20 13:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 210.07 | 0 | 0 | No
2030-09-20 14:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 198.14 | 0 | 0 | No
2030-09-20 15:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | 224.22 | 0 | 0 | No
2030-09-20 16:00 | 2030 33% ECP + 1.3 GW Offshore | 350.9 | -300 | -478.93 | 314.65 | 0 | 0 | No
2030-09-20 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -178.93 | 344.14 | 0 | 0 | No
2030-09-20 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -478.93 | 44.14 | 0 | 0 | No
2030-09-20 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -95 | -178.93 | 135.31 | 0 | 0 | No
2030-09-20 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 121.07 | 435.31 | 0 | 0 | No
2030-09-20 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 421.07 | 510 | 0 | 0 | No
2030-09-20 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-20 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 227.94 | 510 | 510 | 0 | 0 | No
2030-09-21 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-21 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-21 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-21 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 300 | 0 | 0 | No
2030-09-21 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 0 | 0 | 0 | No
2030-09-21 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 448.19 | 0 | 0 | 0 | No
2030-09-21 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 390 | 265.66 | 0 | 0 | No
2030-09-21 07:00 | 2030 33% ECP + 1.3 GW Offshore | 420 | 0 | 90 | 510 | 0 | 0 | No
2030-09-21 08:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | -226 | -210 | 510 | 0 | 0 | No
2030-09-21 09:00 | 2030 33% ECP + 1.3 GW Offshore | -420 | -526 | -510 | 270.33 | 0 | 0 | No
2030-09-21 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 156.19 | 0 | 0 | No
2030-09-21 11:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | 77.75 | 0 | 0 | No
2030-09-21 12:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | -526 | -510 | 77.75 | 0 | 0 | No
2030-09-21 13:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | -526 | -510 | 0 | 0 | 0 | No
2030-09-21 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-09-21 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 0 | 0 | 0 | No
2030-09-21 16:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 88.75 | 0 | 0 | No
2030-09-21 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -211.25 | 0 | 0 | No
2030-09-21 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -390 | 0 | 0 | No
2030-09-21 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -410.41 | -510 | -90 | 0 | 0 | No
2030-09-21 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -110.41 | -210 | 210 | 0 | 0 | No
2030-09-21 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 189.59 | 90 | 510 | 0 | 0 | No
2030-09-21 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 4.6 | 390 | 510 | 0 | 0 | No
2030-09-21 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 255.4 | 0 | 0 | No
2030-09-22 | 2030 33% ECP + 1.3 GW Offshore | 700 | -31.21 | -210 | -44.6 | 0 | 0 | No
2030-09-22 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | -48.36 | 0 | 0 | No
2030-09-22 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -243.99 | -510 | 69.78 | 0 | 0 | No
2030-09-22 03:00 | 2030 33% ECP + 1.3 GW Offshore | 584.81 | -526 | -510 | -136.11 | 0 | 0 | No
2030-09-22 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -180.83 | 0 | 0 | No
2030-09-22 05:00 | 2030 33% ECP + 1.3 GW Offshore | 633.24 | -526 | -510 | -247.3 | 0 | 0 | No
2030-09-22 06:00 | 2030 33% ECP + 1.3 GW Offshore | 213.24 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 07:00 | 2030 33% ECP + 1.3 GW Offshore | -206.76 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 08:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -526 | -510 | -510 | 0 | 0 | No
2030-09-22 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | -510 | 0 | 0 | Yes
2030-09-22 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -226 | -210 | -210 | 0 | 0 | Yes
2030-09-22 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 74 | 90 | 90 | 0 | 0 | Yes
2030-09-22 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 374 | 390 | 390 | 0 | 0 | Yes
2030-09-22 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-22 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-22 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-22 16:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-22 17:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 18:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-22 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-23 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 510 | 0 | 0 | No
2030-09-23 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 96.3 | 412.73 | 0 | 0 | No
2030-09-23 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 96.3 | 510 | 0 | 0 | No
2030-09-23 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 374.99 | 510 | 0 | 0 | No
2030-09-23 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 74.99 | 510 | 0 | 0 | No
2030-09-23 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -199.43 | 510 | 0 | 0 | No
2030-09-23 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -466.49 | 510 | 0 | 0 | No
2030-09-23 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 472.42 | 0 | 0 | No
2030-09-23 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 361.03 | 0 | 0 | No
2030-09-23 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 383.08 | 0 | 0 | No
2030-09-23 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | 441.68 | 0 | 0 | No
2030-09-23 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 74.07 | 510 | 0 | 0 | No
2030-09-23 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 374.07 | 510 | 0 | 0 | No
2030-09-23 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-23 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-23 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 510 | 510 | 0 | 0 | No
2030-09-23 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 419.39 | 500.41 | 0 | 0 | No
2030-09-23 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 191.24 | 510 | 0 | 0 | No
2030-09-23 23:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 300 | 491.24 | 510 | 0 | 0 | No
2030-09-24 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 01:00 | 2030 33% ECP + 1.3 GW Offshore | 382.15 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 02:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 03:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 04:00 | 2030 33% ECP + 1.3 GW Offshore | 0 | 505 | 510 | 510 | 0 | 0 | No
2030-09-24 05:00 | 2030 33% ECP + 1.3 GW Offshore | 188.36 | 374 | 390 | 510 | 0 | 0 | No
2030-09-24 06:00 | 2030 33% ECP + 1.3 GW Offshore | 608.36 | 74 | 90 | 287.64 | 0 | 0 | No
2030-09-24 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -226 | -210 | -12.36 | 0 | 0 | No
2030-09-24 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -312.36 | 0 | 0 | No
2030-09-24 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | -248.7 | 0 | 0 | No
2030-09-24 10:00 | 2030 33% ECP + 1.3 GW Offshore | 673.33 | -226 | -210 | 51.3 | 0 | 0 | No
2030-09-24 11:00 | 2030 33% ECP + 1.3 GW Offshore | 253.33 | 0 | 0 | 351.3 | 0 | 0 | No
2030-09-24 12:00 | 2030 33% ECP + 1.3 GW Offshore | -149.25 | 0 | -300 | 170.18 | 0 | 0 | No
2030-09-24 13:00 | 2030 33% ECP + 1.3 GW Offshore | -569.25 | -235.19 | -510 | 162.94 | 0 | 0 | No
2030-09-24 14:00 | 2030 33% ECP + 1.3 GW Offshore | -471.36 | -526 | -510 | 0 | 0 | 0 | No
2030-09-24 15:00 | 2030 33% ECP + 1.3 GW Offshore | -51.36 | -526 | -510 | -20.71 | 0 | 0 | No
2030-09-24 16:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -526 | -510 | 181.83 | 0 | 0 | No
2030-09-24 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 481.83 | 0 | 0 | No
2030-09-24 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-24 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-24 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-24 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 510 | 0 | 0 | No
2030-09-24 22:00 | 2030 33% ECP + 1.3 GW Offshore | 280 | -226 | -210 | 510 | 0 | 0 | No
2030-09-24 23:00 | 2030 33% ECP + 1.3 GW Offshore | -140 | 74 | 90 | 510 | 0 | 0 | No
2030-09-25 | 2030 33% ECP + 1.3 GW Offshore | -560 | 374 | 390 | 510 | 0 | 0 | No
2030-09-25 01:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 02:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 03:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 04:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 05:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 06:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 07:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 08:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 09:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 15:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 16:00 | 2030 33% ECP + 1.3 GW Offshore | -575.14 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-25 17:00 | 2030 33% ECP + 1.3 GW Offshore | -155.14 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 18:00 | 2030 33% ECP + 1.3 GW Offshore | 264.86 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 19:00 | 2030 33% ECP + 1.3 GW Offshore | 684.86 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-25 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 07:00 | 2030 33% ECP + 1.3 GW Offshore | 573.55 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 08:00 | 2030 33% ECP + 1.3 GW Offshore | 153.55 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 09:00 | 2030 33% ECP + 1.3 GW Offshore | -266.45 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 10:00 | 2030 33% ECP + 1.3 GW Offshore | -686.45 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-26 11:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-26 12:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-26 13:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 14:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | 505 | 510 | 510 | 0 | 0 | Yes
2030-09-26 15:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 16:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 17:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 434.39 | 0 | 0 | No
2030-09-26 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 307.42 | 0 | 0 | No
2030-09-26 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-26 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 07:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 205 | 210 | 355.42 | 0 | 0 | No
2030-09-27 08:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 354.64 | 510 | 510 | 0 | 0 | No
2030-09-27 09:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 505 | 510 | 510 | 0 | 0 | No
2030-09-27 10:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 300 | 390 | 510 | 0 | 0 | No
2030-09-27 11:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | 90 | 510 | 0 | 0 | No
2030-09-27 12:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -300 | -210 | 361.04 | 0 | 0 | No
2030-09-27 13:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 361.04 | 0 | 0 | No
2030-09-27 14:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 218.96 | 0 | 0 | No
2030-09-27 15:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 397.4 | 0 | 0 | No
2030-09-27 16:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -396.82 | -510 | 477.19 | 0 | 0 | No
2030-09-27 17:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -96.82 | -301.39 | 477.19 | 0 | 0 | No
2030-09-27 18:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -1.39 | 477.19 | 0 | 0 | No
2030-09-27 19:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -1.39 | 477.19 | 0 | 0 | No
2030-09-27 20:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -301.39 | 353.75 | 0 | 0 | No
2030-09-27 21:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 353.75 | 0 | 0 | No
2030-09-27 22:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | 0 | -510 | 353.75 | 0 | 0 | No
2030-09-27 23:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -47.09 | -510 | 201.77 | 0 | 0 | No
2030-09-28 | 2030 33% ECP + 1.3 GW Offshore | 700 | -347.09 | -510 | 100.98 | 0 | 0 | No
2030-09-28 01:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -386.02 | -510 | 83.34 | 0 | 0 | No
2030-09-28 02:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -526 | -510 | 87.38 | 0 | 0 | No
2030-09-28 03:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -228.73 | -510 | 122.04 | 0 | 0 | No
2030-09-28 04:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -56.9 | -510 | 51.35 | 0 | 0 | No
2030-09-28 05:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -15.14 | -510 | 75.25 | 0 | 0 | No
2030-09-28 06:00 | 2030 33% ECP + 1.3 GW Offshore | 700 | -189.23 | -510 | 21.17 | 0 | 0 | No
2030-09-28 07:00 | 2030 33% ECP + 1.3 GW Offshore | 560 | 0 | -490.54 | 158.94 | 0 | 0 | No
2030-09-28 08:00 | 2030 33% ECP + 1.3 GW Offshore | 140 | 0 | -490.54 | 281.71 | 0 | 0 | No
2030-09-28 09:00 | 2030 33% ECP + 1.3 GW Offshore | -280 | -264.78 | -510 | 335.57 | 0 | 0 | No
2030-09-28 10:00 | 2030 33% ECP + 1.3 GW Offshore | -700 | -526 | -510 | 301.52 | 0 | 0 | No