## Cover Sheet
UNIT NAME EON ION FON Checklist
Disclaimer:
This docuyment contains information (and/or attachments) which may be privileged or confidential. All content is intended solely for the use of the individual or entity to whom it is addressed. If you are not the intended recipient please be aware that any disclosure, copying, distribution or use of the contents of this document is prohibited. If you suspect that you have received this document in error please notify EirGrid immediately. Further information can be found at: http://www.eirgridgroup.com/legal/

## Version Control
Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by

## Grid Code
Modification or Equipment Failure following receipt of FON:

## Scope of Works
Scope of Works
Outline the scope of the works required e.g.
New Unit
or
Governor refurbishment
MV switch gear replacement
etc.

## Progress Summary
XX1 Status dd mmm yyyy
|  | %Test procedures agreed | % Performed on Primary Fuel | % Performed on Secondary Fuel | % Closed
| EON Checklist - Technical Data & Parameters | N/A | N/A | N/A | 0%
| ION Checklist - Offload test | 0% | N/A | N/A | 0%
| FON Checklist - Onload tests | 0% | 0% | 0% | 0%
| System Services | 0% | 0% | N/A | 0%
| Update provided | Backfeed of Connection Transformer | Synchronisation of Unit (first export) | Start of High Export | FON Checklist Complete
Current schedule
N-1 schedule
N-2 scheulde
EON | Description | Test Status
1 | Commissioning Plan | Open
2 | Provision of Study Requirements & Templates | Open
3 | Provision of Models | Open
4 | Provision of Studies | Open
5 | Signal List | Open
6 | Modes of Operation | Open
7 | Protection Settings | Open
8 | Governor Data | Open
9 | Excitation System & Generator | Open
10 | Transformer Data | Open
11 | Implemented Protection Settings | Open
12 | Authorisation to Construct | Open
13 | Connection Agreement Pre-requisites to Energisation | Open
14 | Unit Registration | Open
15 | Operational Information | Open
16 | Standard Operating Procedure | Open
17 | Pre-energisation signals & controls check | Open
18 | Declaration of Fitness | Open
19 | Operation Instruction & Energisation Instruction | Open
20 | Itemised Statement of Compliance | Open
ION | Description | Test procedure agreed | Test Status Primary Fuel
21 | Signal Interface | Open | Open
22 | Generator Excitation - Offline Checks | Open | Open
23 | Generator Governor - offline checks | Open | Open
24 | Turbine overspeed test. | Open | Open
25 | Synchroniser Checks | Open | Open
26 | Pre-synchronisation Requirements | Open | Open
27 | Itemised Statement of Compliance | Open | Open
FON | Description | Test procedure Agreed | Testing Completed on Primary Fuel | Testing Completed on Secondary Fuel | Test Status
28 | Block Load | Open | Open | Open | Open
29 | Governor Characteristics | Open | Open | Open | Open
30 | Minimum Load / Generation | Open | Open | Open | Open
31 | Ramp Rates | Open | Open | Open | Open
32 | RfG Trip to House Load | Open | Open | Open | Open
33 | Demonstration of Start Up Times | Open | Open | Open | Open
34 | Demonstration of Shutdown Times | Open | Open | Open | Open
35 | Operation on Primary/Secondary/Mix fuel | Open | Open | Open | Open
36 | Operation on Primary/Secondary/Mix fuel | Open | N/A | Open | Open
37 | Modes of Operation | Open | Open | Open | Open
38 | Verification of Output vs Ambient Conditions | Open | Open | Open | Open
39 | RfG Reactive Power Capability / Excitation Limiters | Open | Open | N/A | Open
40 | Automatic Voltage Regulator Droop | Open | Open | N/A | Open
41 | Online SCADA signals check | Open | N/A | Open | Open
42 | Operation at High and Low Generator Voltages | Open | Open | N/A | Open
43 | RfG Operation at High and Low Frequency | Open | Open | Open | Open
44 | Alerts | Open | Open | N/A | Open
45 | Automatic Generator Control | Open | Open | N/A | Open
46 | Emergency power supplies | Open | Open | N/A | Open
47 | Online PSS and Excitation Controller Testing | Open | Open | N/A | Open
48 | Registered Capacity | Open | Open | Open | Open
49 | Registered Characteristics | Open | Open | Open | Open
50 | Reliability run | Open | Open | Open | Open
51 | Export Adjustment Factors | Open | Open | Open | Open
52 | TSAT Model Validation | Open | Open | Open | Open
53 | EMT Model Validation | Open | Open | Open | Open
54 | Technical Offer Data | N/A | Open | Open | Open
55 | Snags | N/A | N/A | N/A | Open
56 | Special Protection Scheme Testing | Open | Open | N/A | Open
57 | Itemised Statement of Compliance | Open | Open | Open | Open
Phase D | Description | Test procedure Agreed | Testing Completed on Primary Fuel | Testing Completed on Secondary Fuel | Test Status
58 | Black Start | Open | Open | Open | Open
59 | Operating Reserves | Open | Open | Open | Open
60 | Ramping Margins | Open | Open | Open | Open
61 | Fast Post Fault Active Power Recovery & Dynamic Reactive Response | Open | Open | Open | Open
62 | Steady State Reactive Power | Open | Open | Open | Open
63 | Synchronous Inertial Response | Open | Open | Open | Open

## Issues Log
No. | Issue Description | Owner | Action | Decision | Status
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
The Issues Log shall be populated with any items that are identified outside of the prescribed tests, identified following the closure of a prescribed test, or during performance monitoring of the unit, prior to issuance of an Operational Certificate. All items in the Issues Log shall be closed prior to the issuance of an Operational Certificate.

## EON
Test # |  | Test | EirGrid Witness | Grid Code Reference | Description | Comment | Timeline | Path | Status
1 |  | Commissioning Plan |  |  | Provide Target Dates for Commissiong Plan and Capacity Demonstration: |  |  |  | Open
| 1a |  |  |  | Provide the tagret dates for completion of following: a) EON checklist complete b) Energisation of Connection Point c) First fire d) ION Checklist complete e) First sync f) Grid Code Compliance Testing (on load) g) Model Validation h) FON Checklist complete |  | Kickoff Meeting | GeneratorTesting@eirgrid.com | Open
| 1b |  |  |  | Target Date and Deadlines for Capacity Demonstration: a) Connection Agreement: Long Stop Date for Capacity Bond b) Capacity Market Obligation: Target Date for Substantial Completion (Long Stop Date)? c) System Services Gate: Which Services? Target Date? |  |  |  | Open
2 |  | Provision of Study Requirements & Templates | No |  | EirGrid shall provide the customer with following documents and templates, 2a to 2d will be provided by PED Team 2e to 2j will be provided by Genrator Testing Team |  | 18 months before energisation |  | Open
[5 empty] | PED Team will provide following, |  |  | PED@eirgrid.com | Open
| 2a |  |  |  | a) RoCoF assessment pack |  |  |  | Open
| 2b |  |  |  | b) Minimum System Strength Data |  |  |  | Open
| 2c |  |  |  | c) FRT report template https://www.eirgridgroup.com/customer-and-industry/general-customer-information/simulation-studies/ |  |  |  | Open
| 2d |  |  |  | d) Power Quality document https://www.eirgridgroup.com/customer-and-industry/general-customer-information/simulation-studies/ |  |  |  | Open
[5 empty] | Generator Testing Team will provide following, |  |  | GeneratorTesting@eirgrid.com | Open
| 2e |  |  |  | e) Signal List Inputs Template |  |  |  | Open
| 2f |  |  |  | f) Template for incident reports |  |  |  | Open
| 2g |  |  |  | g) Specification for AGC |  |  |  | Open
| 2h |  |  |  | h) EDIL Registration Pack |  |  |  | Open
| 2i |  |  |  | i) Specification and process for system Alerts https://www.eirgridgroup.com/site-files/library/EirGrid/Guidelines-for-Generators-and-Demand-Side-Units-during-System-States-(Oct-2021).pdf |  |  |  | Open
| 2j |  |  |  | j) PC.A4 in Microsoft Word format. This file is to be populated throughout the commissioning of the power station and will be included as an appendix to the FON. https://www.eirgridgroup.com/site-files/library/EirGrid/Registered-Characteristics-Test-Procedure-Template.docx |  |  |  | Open
3 |  | Provision of Models |  | PC.A8 | The unit shall provide the following Nodels in line with "Simulation studies and Modelling requirements" 1. Models to be provided with (i) clear model documentation, and (ii) site specific model parameters. A document register is required to accompany submissions and be maintained. 2. Applicant to confirm data within these models and reports is as provided in application form. Applicant to identify any differences between data used in these submissions and data provided as part of application process. 3. These models are to be validated against testing and a model validation report to be submitted in FON Checklist. Submitted PSSE and TSAT user-defined models should use the same dynamic model parameters, which should be validated against grid code testing results. |  | 12 months before energisation | PED@eirgrid.com & OPTAP@eirgrid.com | Open
| 3a |  |  |  | a) PSSE Model SPGMs are required to provide User Defined models for FRT dynamic analysis in PSSE. The PSSE version used to carry out dynamic analysis and compile model files must be version 34 and above. The Dynamic model must contain all files including vendor specific libraries developed for FRT analysis. Note that a separate Validation Report for the FRT Dynamic model should be provided which includes factory and/or type tests that validate the model’s response. (The validation report is different to that of the customer self-assessment FRT report which must be produced as per the FRT Study Template and Assessment Guide) Models should be accompanied with data sheets and technical specifications of all major equipment in the SPGM plant. More information can be found in the latest version of FRT Study Template and Assessment Guide within Publications https://www.eirgrid.ie/publications?page=1&pageSize=10&keyword=&sortBy=-created&categories=%7B%7D |  |  | Customer to submit via EirGrid PM to PED Team (PED@eirgrid.com) | Open
| 3b |  |  |  | b) TSAT Model SPGMs are required to submit a PowerTech DSA Tools TSAT Version 19 dynamic models for the EirGrid operations model. These can either be generic models (with site-specific parameters) which are directly compatible with TSAT v19, or TSAT user-defined dynamic models (UDMs). Where UDMs have been submitted the User must provide the TSO with the relevant documentation for the model. List of compatible generic models can be requested from WSAT team. |  |  | Customer to submit via EirGrid PM to (wsat_support@Eirgrid.com) | Open
| 3c |  |  |  | c ) EMT Model |  |  | Customer to submit via EirGrid PM to TSPS Team (optap@eirgrid.com) | Open
[5 empty] | Generator to provide EMT Model for the power station. The software tool and version will be included in the EMT Model Specification document provided by EirGrid. |  |  |  | Open
[5 empty] | The EMT model must be accompanied by a completed checklist – see appendix to the EMT Model Specification document. |  |  |  | Open
[5 empty] | Generator to provide a separate guidance document with details on how to use the EMT model. |  |  |  | Open
4 |  | Provision of Studies |  |  | The unit shall provide the following studies in line with "Simulation studies and Modelling requirements" |  |  |  | Open
| 4a |  |  |  | a) Power System Stabiliser study (EirGrid to inform customers of which local oscillation modes to tune out. Customer is responsible for appropriate tuning) |  |  | Customer to submit via EirGrid PM to PED Team (PED@eirgrid.com) | Open
| 4b |  |  |  | b) Voltage Fault Ride Through study |  |  |  | Open
| 4c |  |  |  | c) Rate of Change of Frequency study |  |  |  | Open
| 4d |  |  |  | d) Power Quality Study |  |  |  | Open
| 4e |  |  |  | e) Demostration of transformer tap range is sufficient to allow provision of the full reactive power capability requirements over the full range of system voltages per CC.7.3.6.1 |  |  | GeneratorTesting@eirgrid.com | Open
5 |  | Signal List | No | CC.12 | Signal List requirements |  |  | Customer to submit signal list inputs via EIrGrid PM to GeneratorTesting@Eirgrid.com | Open
| 5a |  |  |  | Customer to provide Signal List Inputs Customer must provide all data required for development of a signal list along with latest SLD. |  | 9 months before energisation |  | Open
| 5b |  |  |  | Eirgrid to issue Signal List for Power Station SCADA to/from NCC. |  | 6 months before energisation |  | Open
6 |  | Modes of Operation | No |  | Where relevant (e.g. combined cycle plant), the unit shall provide a description of different plant configurations (e.g. combustion turbine and steam turbine configurations). Note this will inform the testing required in Phase C (FON). |  | 12 months before energisation | GeneratorTesting@eirgrid.com | Open
7 |  | Protection Settings | No | CC.10.9.1 CC.10.9.2 CC.10.9.4 CC. 10.9.5 CC. 10.9.6 CC. 10.9.7 CC. 10.9.8 CC.7.3.1.1 a-ff | The unit shall agree the following protection settings with EirGrid, via Protection Coordination Study or Protection Summary Report Protection Matrix should inlcude trip to house load if time to sync >15 mins… Trip matrix to be agreed with EirGrid protection. Note: Report shall include the Protection Trip Matrix Generator transformer shall have differential and buchholz protection and the unit transformer shall have overcurrent (HV side preferable), differential and buchholz protection for first energisation All frequency settings must allow for compliance with CC.10.... |  | 3 Months pre-energisation for Protection Study | Submit via EirGrid PM to Protection & Generator Testing (ProtectionSettingsRequest@Eirgrid.com & GeneratorTesting@eirgrid.com) | Open
| 7a |  |  |  | a) Generator |  |  |  | Open
| 7b |  |  |  | b) Generator Transformer(s) |  |  |  | Open
| 7c |  |  |  | c) Unit Transformer(s) |  |  |  | Open
| 7d |  |  |  | d) Balance of Plant |  |  |  | Open
8 |  | Governor Data | No |  | The unit shall provide the following for the Governor System in line with information provided in Test 2 |  | 6 weeks before energisation | Protection & WSAT teams via GeneratorTesting@eirgrid.com | Open
| 8a |  |  |  | a) design sheets For Generators > 250 MW the governor must measure mechanical output rather than electrical output, to prevent oscillations |  |  |  | Open
| 8b |  |  |  | b) settings list |  |  |  | Open
| 8c |  |  |  | c) FAT results |  |  |  | Open
| 8d |  |  |  | d) Conversion charts for plant output for variations with ambient conditions These charts are used to determine Reg Cap during testing and used to determine base load during normal operation. |  |  |  | Open
9 |  | Excitation System & Generator | No | CC 10 CC.7.3.1.1(g) CC. 7.3.8 | The unit shall provide the following data sheets for the Excitation System ensuring it alligns with information provided in Test 2 Note. AVR shall measure voltage on all 3 phases. |  | 6 weeks before energisation | Protection & WSAT teams via GeneratorTesting@eirgrid.com | Open
| 9a |  |  |  | a) Generator data sheets |  |  |  | Open
| 9b |  |  |  | b) Settings list for the Excitation System |  |  |  | Open
| 9c |  |  |  | c) FAT results for the Excitation System |  |  |  | Open
10 |  | Transformer Data | No | CC.7.2.5 | The unit shall provide the following for Grid Connected Tranformer and Unit Transformer, |  | 6 weeks before energisation | Protection, WSAT & EMS teams via GeneratorTesting@eirgrid.com | Open
| 10a |  |  |  | For the Grid Connected Transformer: FAT results including transformer impedance data (positive and zero phase sequence) for top, centre and bottom tap positions. |  |  |  | Open
| 10b |  |  |  | For the Grid Connected Transformer: Legible photograph of transformer Name Plate Rating (if not included in the FAT report) |  |  |  | Open
| 10c |  |  |  | For the Unit Transformer: FAT results including transformer impedance data (positive and zero phase sequence) for top, centre and bottom tap positions. |  |  |  | Open
| 10d |  |  |  | For the Unit Transformer: Legible photograph of transformer Name Plate Rating (if not included in the FAT report) |  |  |  | Open
11 |  | Implemented Protection Settings | Yes | CC 10 | If any of the commissioned protection settings differ from those provided in the Protection Coordination study, provide a list of updated settings. DOF will also be provided in Energisation Instruction, below. Where there is no Energisation Instruction, DOF will be provided per ION Checklist. |  | 2 weeks before energisation | Protection Team via Project Manager | Open
12 |  | Authorisation to Construct |  |  | e-mail licensing@cru.ie (cc to Generator_Testing@eirgrid.com) requesting confirmation of consented MW capacity |  | 2 weeks before energisation | GeneratorTesting@eirgrid.com | Open
13 |  | Connection Agreement Pre-requisites to Energisation |  |  | SPGM shall provide confirmation that they have met all pre-requisites to Energisation under the Connection Agreement (Email from EirGrid C&C team that all items have been addressed) |  | 2 weeks before energisation | GeneratorTesting@eirgrid.com | Open
14 |  | Unit Registration | No |  | The unit shall provide the following for registration in the market and EDIL, |  | Deadline: 60 days before energisation |  | Open
| 14a |  |  |  | The unit must be registered in the market before energistaion. In order to register in the market, the unit must: - submit a fully completed party accession pack - submit a fully completed particpant notification pack |  |  | BalancingMarketRegistration@sem-o.com | Open
| 14b |  |  |  | The unit must be set up in EDIL before energisation. In order to register in the market, the unit must: - submit a completed EDIL registration form EDIL must be run on a dedicated PC, as per Grid Code clause OC.7.2.5.4.1 |  |  | GeneratorTesting@eirgrid.com | Open
| 14c |  |  |  | - Carry out EDIL training |  | 2-3 weeks before first sync | PerformanceMonitor@eirgrid.com | Open
15 |  | Operational Information |  |  | Provide the following to EirGrid Customer Relations Completed Form via e-mail to info@eirgrid.com - 24 hour contacts - Authorised Operators - Authorised DOF givers Form: To get form contact info@eirgrid.com Note. Authorised Operators must be agreed and trained with ESBN for switching to take place. |  | 6-8 week before energisation | info@eirgrid.com | Open
16 |  | Standard Operating Procedure |  |  | SOP: Operator not to reenergise / resynch without express permission from NCC / CHCC. The unit shall provide the Standard Operating Procedure which covers the following scenarios: a) Tripping of generator b) Failure of protection c) Failure of power supplies etc. |  | 2 weeks before energisation | GeneratorTesting@eirgrid.com | Open
17 |  | Pre-energisation signals & controls check | N/A |  | Carried out with ESB Telecoms and EirGrid IPP to request EirGrid Project Manager to schedule this test, giving 15 business days notice for the requested test date. |  | 2 weeks before energisation | GeneratorTesting@eirgrid.com | Open
18 |  | Declaration of Fitness | N/A |  | The unit shall issue Declarations of Fitness as specified in the Energisation Instruction. |  | Before Energisation | N/A | Open
19 |  | Operation Instruction & Energisation Instruction | No |  | Operationing Instruction & Energization Instruction must cover below requirements, |  |  | EITeam@Eirgrid.com via Client Engineer | Open
| 19a |  |  |  | Agree Operation Instruction, including a check to see that the procedures can be safely followed. Written by EirGrid, agreed with ESBN and the unit. Suitable operating personnel are available with call-out procedure that is in line with EirGrid Operating Instruction. |  | Before Energisation |  | Open
| 19b |  |  |  | Agree Energisation Instruction for 1st energisation of the connection point. Written by EirGrid, agreed with ESBN and the unit. |  | Before Energisation |  | Open
20 |  | Itemised Statement of Compliance | N/A | RfG | Unit to provide an itemised statement of compliance to the TSO Document will include: name of person making the statement of compliance, company, date, and a table listing: 1. the relevant clauses 2. brief summary / compliance requirement 3. statement that the unit complies with same (or derogation in place where there's a shortfall in compliance). |  | Before Energisation | GeneratorTesting@eirgrid.com | Open
All EON Checklist tests to be completed to achieve Energisation Operational Notification

## ION
Test # |  | Test | EirGrid Witness | Grid Code Reference | TSO Description | TSO Comment | Test procedure Agreed | Test Status
21 |  | Signal Interface | Yes | CC 7.2.3 CC 10 CC12 | Function check of all Transmission Station trip commands and signals and alarms/recording: - from Transmission Station to Power Station - from Power Station to Transmission Station - from interface/NCC to SCADA system. Check actual tripping of HV CB by emergency trip pushbutton Note that some or all of these tests may already have been completed in Phase A tests. | Functional check of (available) SCADA before first sync (compare to synchroniser and DCS) Functional checks may require ESBTS at site for verification. | Open | Open
22 |  | Generator Excitation - Offline Checks | Yes | CC7.3.1.1 (j) | Open Circuit and Short Circuit testing Functional checks of Excitation control (e.g. AVR stationer and dynamic control checks at no load condition) Data gathered here feeds into PC.A4. Notify EirGrid of any changes to the Excitation System from phase A (applies over the lifetime of the plant) |  | Open | Open
| 22a |  |  |  | 1. Demonstrate AVR / Excitation System has been commissioned successfully, per OEM Commissioning Procedure |  | Open | Open
| 22b |  |  |  | 2. Verification of Subtransient Reactance (Xd) and demonstration that Short Circuit Ratio is in accordance with IEC 60034 |  | Open | Open
23 |  | Generator Governor - offline checks | Yes |  | Testing of Governor system - Functional checks (governor stationer and dynamic control checks at no load condition) Notify EirGrid of any changes to the Governor Control from EON (phase A) applies over the lifetime of the plant |  | Open | Open
24 |  | Turbine overspeed test. | No |  | Demonstrate operation of all turbine overspeed protection. |  | Open | Open
25 |  | Synchroniser Checks | Yes | CC 7.3.3 CC 7.3.4 | Testing of synchroniser - Generator CB and check contact closing time. Test protocols of factory tests to be available. Testing of synchroniser by backfeeding to generator to check VTs and then by testing pulses to blocked generator CB during dummy synchroniser tests using high speed recorder. CC7.3.4 The synchronising facilities in CC7.3.3 shall facilitate synchronising under (a) frequency between 48-52 Hz and voltage between 99 kV-123 kV. IPP must provide evidence that the settings don't prevent compliance with CC7.3.4 |  | Open | Open
26 |  | Pre-synchronisation Requirements | N/A | CC 7.3.3 CC 7.3.4 | Unit to submit declaration as per published template "Pre-synchronisation Declaration Template" which includes the following: - Power Station to issue Declarations of Fitness - Market Registration is completed - Load Profiles for export have been approved by the TSO and SEM https://cms.eirgrid.ie/sites/default/files/publications/Pre-synchronisation-Declaration-Template.docx |  | Open | Open
27 |  | Itemised Statement of Compliance | N/A | RfG | Unit to provide an itemised statement of compliance to the TSO |  | Open | Open
All ION Checklist tests to be completed to achieve Interim Operational Notification

## FON
Test # |  | Test | EirGrid Witness | Grid Code Reference | Description | Comment | Test procedure Agreed | Testing Completed on Primary Fuel | Testing Completed on Secondary Fuel | Test Status
28 |  | Block Load | Yes | CC 7.3.1.1 | Measure initial exported MW following synchronisation, before the unit begins loading up. Applies for Cold, Warm and Hot starts. |  | Open | Open | Open | Open
29 |  | Governor Characteristics | Yes | CC 7.3.1 CC.7.3.7 OC 4.3.4 OC 4.6.3 | Testing by simulation of defined frequency excursions within frequency control software of all connected primary movers, being gas turbine(s) or steam turbine(s). Carried out at mimum and maximum loads. |  | Open | Open | Open | Open
| 29a |  |  |  | Testing of POR, SOR, TOR and ROCOF capability by frequency injection at various loads. |  | Open | Open | Open | Open
| 29b |  | Yes | CC 7.3.1 CC.7.3.7 OC 4.3.4 OC 4.6.3 | Measurement of governor droop characteristic at various loads by simulation of frequency change on turbine governor. |  | Open | Open | Open | Open
| 29c |  | Yes | CC 7.3.1.1 CC 7.5.8 OC 4.3.4 | Measurement of governor deadband characteristic by simulation of a defined frequency change on the governor turbine. |  | Open | Open | Open | Open
30 |  | Minimum Load / Generation | Yes | CC 7.3.1.1 | Demonstrate that MW output and process parameters (e.g. temperatures and vibration levels) remain stable during sustained operation at the defined minimum generation. The Minimum Load value will be determined using meter data. |  | Open | Open | Open | Open
31 |  | Ramp Rates | Yes | CC 7.3.1.1 | Demonstration of capability to ramp up and down between defined load points (rate of change to be Grid Code compliant). The generator should demonstrate stable operation at Registered Capacity for some period following ramp up. |  | Open | Open | Open | Open
32 |  | RfG Trip to House Load | Yes | CC.7.3.2 CC.7.3.3 | Load rejection test at 100% load and resynchronisation across HV CB after 1 hour operating at house load. The unit must remain running at normal frequency, feeding its own auxiliaries while completely disconnected from the grid for the 1 hour up to when resynchronisation takes place. Demonstrate that the process parameters (e.g. temperatures and vibration levels) remain stable during sustained operation at house load. Only applicable for start up >15 minutes. |  | Open | Open | Open | Open
33 |  | Demonstration of Start Up Times | Yes | CC 7.3.1.1 | Following requirements to apply: |  | Open | Open | Open | Open
| 33a |  |  |  | Time to synchronising from cold, warm and hot starts |  | Open | Open | Open | Open
| 33b |  |  |  | Time from synchronising to minimum load on cold, warm and hot starts |  | Open | Open | Open | Open
| 33c |  |  |  | Time to synchronising following turbine and boiler trips. |  | Open | Open | Open | Open
34 |  | Demonstration of Shutdown Times | No | CC 7.3.1.1 | Following requirements to apply: |  | Open | Open | Open | Open
| 34a |  |  |  | a) Demonstration of shutdown time from Minimum Load. |  | Open | Open | Open | Open
| 34b |  |  |  | b) Demonstration of hot and warm cooling boundaries. Note: this not included in the published template. |  | Open | Open | Open | Open
35 |  | Operation on Primary/Secondary/Mix fuel |  | CC 7.3.1 OC 10.2.2 OC 10.4.4 OC 10.5.5 | Following requirements to apply: |  | Open | Open | Open | Open
| 35a |  | Yes |  | Demonstrate fuel changeover time and load point for primary to secondary fuel |  | Open | Open | Open | Open
| 35b |  | Yes |  | Demonstrate fuel changeover time and load point for secondary to primary fuel |  | Open | Open | Open | Open
36 |  | Operation on Primary/Secondary/Mix fuel | Yes | CC 7.3.1 OC 10.2.2 OC 10.4.4 OC 10.5.5 | Also close out of all tests on Sec Fuel. |  | Open | N/A | Open | Open
37 |  | Modes of Operation | Yes |  | Where relevant (e.g. combined cycle plant), demonstration of operation in different plant configurations (e.g combustion turbine and steam turbine configurations) Additional tests to be carried out for multiple modes of operation: 1. Submission of PSS study, FRT study, ROCOF study, dynamic models and laplace diagram 2. Time to synchronise 3. Block Load 4. Time from synch to min load 5. Minimum Load 6. Ramp Rates 7. Reg Cap 8. Operating Reserve 9. Time to desynch from min load 10. Reactive Power Capability? 11. Trip to House Load |  | Open | Open | Open | Open
38 |  | Verification of Output vs Ambient Conditions | No | CC 1.1 | The unit shall validate the conversion charts provided in phase A by converting plant output in the various ambient conditions to Registered Capacity (temperature and pressure as defined in the Grid Code) . |  | Open | Open | Open | Open
39 |  | RfG Reactive Power Capability / Excitation Limiters | Yes | CC 7.2.5 CC 7.3.1.1 CC 7.3.6 CC 7.5 | Demonstration of the stability of the unit at all MW/Mvar settings within the generator stability envelope at rated grid voltage. Measurement of the maximum leading/lagging reactive power capability at various loads and after thermal stabilisation of the generator. This shall also demonstrate the action of automatic limiters (OEL and UEL) to prevent the generator from operating outside its stability envelope. |  | Open | Open | N/A | Open
40 |  | Automatic Voltage Regulator Droop | Yes | CC 7.3.1.1 & CC 7.3.6 | Demonstration of voltage regulator droop characteristic in relation to voltage. Tested by comparing the voltage at the generator terminals before and after a tap change on the Grid Connected Transformer |  | Open | Open | N/A | Open
41 |  | Online SCADA signals check | Yes | CC 7.3.1.1 & CC 7.3.6 | Demonstration of accurate transmission of voltage, current and power signals and all SCADA signals. |  | Open | N/A | Open | Open
42 |  | Operation at High and Low Generator Voltages | Yes | CC 7.3.1.1 CC7.3.6 | Demonstration of generator MW capability at minimum and maximum generator voltages at rated power factor. |  | Open | Open | N/A | Open
43 |  | RfG Operation at High and Low Frequency | Yes | CC 7.3.1.1 CC 7.3.2 OC4.3.4 | Demonstration of operation of plant on house load at high frequency and low frequency limits of operation for 60 minutes. This test is normally carried out in conjunction with the load rejection test. |  | Open | Open | Open | Open
44 |  | Alerts | Yes | OC8.4 OC 9.4 | Demonstration of amber, red and blue alerts. |  | Open | Open | N/A | Open
45 |  | Automatic Generator Control | Yes | CC 7.3.1.1 OC.4.3.6 | Demonstration of direct control from NCC in line with AGC specification provided in phase A and in line with the published test procedure template. |  | Open | Open | N/A | Open
46 |  | Emergency power supplies | Yes | CC 13.1 | Demonstration of capability of diesel generator to supply Power Station emergency loads Procedure for operation in this mode to be provided to EirGrid. This shall include demonstration of secure backup power supply to the associated transmission station, as applicable. The measured result can be extrapolated to cover the full duration. |  | Open | Open | N/A | Open
47 |  | Online PSS and Excitation Controller Testing | Yes | CC 10.9.2 | Demonstration of the PSS performance in response to step changes in AVR reference. This may also include operational switching on the power system. Eirgrid will verify, using PMU data from Point of Connection, that it does not excite very Low Frequency Mode or Electo Mechanical Modes |  | Open | Open | N/A | Open
48 |  | Registered Capacity | Yes |  | Demonstrate stable operation at registered capacity for defined time period. This is the maximum sustained output where the unit can achieve all Grid Code requirements (ramping, min load, reactive power, etc.) and comply with emissions requirements. Registered Capacity will be determined using meter data. To be adjusted for temperature and pressure as specified in the Grid Code. |  | Open | Open | Open | Open
49 |  | Registered Characteristics | No | PC A4 | Provision of generator data following commissioning tests. See Planning Code Appendix of the Grid Code. Updated PC.A information and dynamic models & PSS Parameters/Study based on test report information |  | Open | Open | Open | Open
50 |  | Reliability run | Yes | OC 7.2.4 OC 10.2.2 | EirGrid will review the unit’s reliability run. This will be agreed with RealTime through submission of agreed profiles. Testing tariffs shall apply under this phase. Unit shall be operating in its final configuration following completion of tuning (governor, AVR, PSS, ramp rates, etc.). Unit shall have frequency response ON for the duration of the test. Unit shall evaluate temperatures, vibrations and emissions against allowable limits in the report. If the unit trips or fails to synchronise on time ('fail sync' issued), the reliability run will restart following resolution of the issue that caused the trip or fail sync. If possible, the unit should be run by the operations staff, rather than the commissioning staff. |  | Open | Open | Open | Open
51 |  | Export Adjustment Factors | Yes |  | Measurement of Adjustment Factors at various load levels to convert from generated MW to exported MW: - Fixed Load - Scalar These are needed for EMS (y = mx+c) and needed for EDIL (trafo etc. at full load) Mvar table needed for control centre tools too. Data is gathered during minimum load and Registered Capacity tests. |  | Open | Open | Open | Open
52 |  | TSAT Model Validation | No | Grid Code modification MPID239 | IPP to provide a validation report for dynamic model provided in EON Checklist vs actual performance during testing (https://www.eirgridgroup.com/customer-and-industry/general-customer-information/simulation-studies/) |  | Open | Open | Open | Open
53 |  | EMT Model Validation | No | Grid Code modification MPID239 | IPP to provide a validation report for EMT model provided in EON Checklist vs actual performance during testing (https://www.eirgridgroup.com/customer-and-industry/general-customer-information/simulation-studies/) |  | Open | Open | Open | Open
54 |  | Technical Offer Data | No | N/A | Submission and Validation of Technical Offer Data via Market Participant Interface. |  | N/A | Open | Open | Open
55 |  | Snags | No | N/A | All snags / time limited derogations / performance monitoring issues have been resolved. This includes assessment of Grid Code compliance in response to any system events that may occur before the FON is issued. |  | N/A | N/A | N/A | Open
56 |  | Special Protection Scheme Testing | Yes |  | Where required |  | Open | Open | N/A | Open
57 |  | Itemised Statement of Compliance | N/A | RfG | Unit to provide an itemised statement of compliance to the TSO |  | Open | Open | Open | Open

## System Services
Test # | Test | Grid Code Reference | EirGrid Witness | Comment | Test procedure Agreed | Testing Completed on Primary Fuel | Testing Completed on Secondary Fuel | Test Status | Link to template procedure on website (Update all links!!)
58 | Black Start |  |  | Demonstrate Black Start capability | Open | Open | Open | Open
59 | Operating Reserves |  |  | FFR, POR, SOR, TOR1, TOR2 Tested during Operating Reserve Tests Requires data recording at 20 ms resolution for FFR Unit must assess Inertia Credit the test report. | Open | Open | Open | Open | http://www.eirgridgroup.com/site-files/library/EirGrid/Synchronous-Machine-OR-Test-Report-Template.docx
60 | Ramping Margins |  |  | Replacement Reserve Synchronised, RM1, RM3, RM8 are demonstrated during Ramp Rates test Replacement Reserve Desynchronised may be demonstrated during Hot/Warm/Cold start and ramp to full load | Open | Open | Open | Open | http://www.eirgridgroup.com/site-files/library/EirGrid/Ramping-Margin-Test-Report-Template.docx
61 | Fast Post Fault Active Power Recovery & Dynamic Reactive Response |  |  | Tested through FRT studies | Open | Open | Open | Open
62 | Steady State Reactive Power |  |  | Demonstrated during Reactive Power Capability test | Open | Open | Open | Open | http://www.eirgridgroup.com/site-files/library/EirGrid/Synchronous-SSRP-Test-Report-Template.docx
63 | Synchronous Inertial Response |  |  | Calculation based on unit Registered Characteristics | Open | Open | Open | Open | http://www.eirgridgroup.com/site-files/library/EirGrid/SSC-Synchronous-Inertial-Response.docx