## OACA
220kV FEEDER - AGHADA LONG POINT [Aghada AD2]
TO-24-AD-LPT-1-02 ISO week: 10mo - 10fr Date: 04 Mar - 08 Mar Duration: 5 Days (5 WD) Status: Scheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
| AD |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,GRL100
OPTSF62 | AD~ | - | 901396997 | DO | 1 | 4 | 220kV SF6 Cubicle Operational Test
XLPCI_A | CABLE | - | 901413560 | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
| LPT |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,GRL100
CORRECT | LPT | - | 901240106 | DO | 2 | 3 | Repeat Oil Sampling
CORRECT | LPT | - | 901433727 | DO | 1 | 4 | O1-DE Earth Straps Birdcaging.
GENERATOR TRANSFORMER - AGHADA ST101 [Aghada Battery AD3]
TO-24-AD-ST101-01 ISO week: 17mo - 17fr Date: 22 Apr - 26 Apr Duration: 5 Days (5 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OSSF6110 | AD~ | 110 | 901396366 | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
CORRECT | AD~ | 110 | 901348642 | DO | 4 | 4 | O1-MO for Ordinary Service ST101 Cubicle
CA_110 | AD~ | 110 | 901396292 | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
GENERATOR TRANSFORMER - AGHADA T2011/12 [Aghada AT11; Aghada AT12]
TO-24-AD-T2011/12-02 Window: Sep Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| AD |  |  | DO | 2 |  | P3 Protection maintenance of BOC (M1),RET630,7SA612,RET670,RET630
OS | AD~ | 220 | ESBN TO CONFIRM | DO | 5 | 4 | 220kV SF6 Cubicle Ordinary Service
AMCAB | AD~ | 220 | ESBN TO CONFIRM | DO | 2 | 4 | Annual Insp. 400 & 220 Station OF Cable
FO_CABLE | AD~ | - | 901247447 | DO | 1 | 1 | 2021PM_Monitor oil pressure levels withi
FO_CABLE | AD~ | 220 | 901302176 | DO | 1 | 4 | 2022PM_Replacement of corroded earthing
FO_CABLE | AD~ | 220 | 901302177 | DO | 1 | 4 | 2022PM_Replacement of corroded bolts on
FO_CABLE | AD~ | 220 | 901302178 | DO | 1 | 1 | 2022PM_Replace Low Pressure & Differenti
GENERATOR TRANSFORMER - AGHADA T2014 [Aghada AT14]
TO-24-AD-T2014-02 Window: Sep Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
FO_CABLE | AD~ | - | 901246243 | DO | 5 | 3 | 2021PM_Replace S-Phase differential rela
AMCAB | AD~ | 220 | ESBN TO CONFIRM | DO | 2 | 4 | Annual Insp. 400 & 220 Station OF Cable
OPT | AD~ | 220 | ESBN TO CONFIRM | DO | 1 | 4 | 220kV SF6 Cubicle Operational Test
| AD |  |  | DO | 2 |  | P3 Protection maintenance of BOC (M1),RET630,7SA612,RET650,RATUA
N/A | - | - | N/A |  | 5 | N/A | Total Maintenance Outage Duration Requested
CORRECT | AD~ | 220 | 901344954 | DO | 1 | 4 | O1-Corrosion on CB Mech Box.
GENERATOR TRANSFORMER - ARDNACRUSHA GIS T101 [Ardnacrusha AA1]
TO-24-AA GIS-T101-02 ISO week: 16mo - 16th Date: 15 Apr - 18 Apr Duration: 4 Days (4 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
| AA |  |  | DO | 2 |  | P2 Protection maintenance of 7SA612,BOC(M1),7UT513
AMCAB | AA~ | 110 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
GENERATOR TRANSFORMER - ARDNACRUSHA GIS T102 [Ardnacrusha AA2]
TO-24-AA GIS-T102-01 Window: Jun Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
| AA |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,7UT513
AMCAB | AA~ | 110 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
GENERATOR TRANSFORMER - ARDNACRUSHA GIS T103 [Ardnacrusha AA3]
TO-24-AA GIS-T103-01 Window: Sep Duration: (4 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
| AA |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,7UT513
OPT | AA~ | 110 | ESBN TO CONFIRM | DO | 2 | 4 | 110KV GIS Cubicle Operational Test
AMCAB | AA~ | 110 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
GENERATOR TRANSFORMER - ARDNACRUSHA GIS T104 [Ardnacrusha AA4]
TO-24-AA GIS-T104-01 Window: May Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
| AA |  |  | DO | 2 |  | P2 Protection maintenance of 7SA612,BOC(M1),7UT513
AMCAB | AA~ | 110 | ESBN TO CONFIRM | DO | 3 | 4 | Cable Insp. 110kV XLPE
110kV FEEDER - ATHEA DROMADA [Dromada WF (DR1)]
TO-24-ATE-DRO-1-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - |  | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | ATE | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - ATHEA KNOCKANURE [Athea / Beena&Tob / Dromada WF]
TO-24-ATE-KNR-1-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - |  | DO | 5 | N/A | Total Maintenance Outage Duration Requested
FO_CABLE | - | - | 901423890 | DO | 2 | 4 | 2023CM_Install bridging SVL's at GIS ter
FO_MISC | - | - | 901370202 | DO | 1 | 4 | 2022HP-1[31]Bird Nests
FOSTRHW | - | - | 901503229 | DO | 1 | 4 | 2023HP-1[21]Check Structure (Top Rot)-S2
FOSTRHW | - | - | 901503230 | DO | 1 | 4 | 2023HP-1[26]Check Structure (Top Rot)-S2
FOSTRHW | - | - | 901503231 | DO | 1 | 4 | 2023HP-1[29]Check Structure (Top Rot)-S2
FOSTRHW | - | - | 901503232 | DO | 1 | 4 | 2023HP-1[34]Check Structure (Top Rot)-S2
FOSTRHW | - | - | 901503233 | DO | 1 | 4 | 2023HP-1[35]Check Structure (Top Rot)-S2
AMCAB | ATE | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
OPT | ATE | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
AMCAB | KNR | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
GENERATOR TRANSFORMER - ATHEA T121 [Athea WF (AH1)]
TO-24-ATE-T121-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
OSSF6110 | ATE | 110 | 901396378 | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
CA_110 | ATE | 110 | 901396303 | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
FO_CABLE | ATE | 110 | 901452092 | DO | 2 | 4 | 2023PM_Install BL Shrinks-OD 2 Days
110kV FEEDER - ATHEA TOBERTOREEN [Beenanaspuck & Tobe... WF/Batt]
TO-24-ATE-TOB-1-02 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - |  | DO | 5 | N/A | Total Maintenance Outage Duration Requested
AMCAB | - | cable | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
OS | ATE | - | ESBN TO CONFIRM | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
OPT | ATH | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - AUGHINISH SEALROCK 3 [Sealrock SK3]
TO-24-AUG-SK-3-01 Window: Jun Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - |  | DO | 10 | N/A | Total Maintenance Outage Duration Requested
CORRECT | AUG | - | 901445480 | DO | 8 | 4 | CB spring charge AC supply mod required
CORRECT | AUG | - | 901445481 | DO | 8 | 4 | Replace CB HV flange bolts
CORRECT | AUG | - | 901445482 | DO | 8 | 1 | SF6 densimeter isolation plunger required
| AUG |  |  | DO | 2 |  | P3 Protection maintenance of 7SA511,REL551
AMCAB | AUG | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
| SK |  |  | DO | 2 |  | P3 Protection maintenance of 7SA513,REL551
110kV FEEDER - AUGHINISH SEALROCK 4 [Sealrock SK4]
TO-24-AUG-SK-4-01 Window: Jul - Sep Duration: (44 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - |  | DO | 3 | N/A | Total Maintenance Outage Duration Requested
AMCAB | AUG | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
OPT | AUG | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - BALLYNAHULLA CORDAL [Cordal 1/2 WF (DL1/DL2)]
TO-24-BYH-CDL-1-01 Window: May Duration: (4 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
XLPCI_A | - | - | 901535585 | DO | 4 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
OPT | CDL | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - BALLYVOUSKILL COOMATAGGART [Grousemount WF (GD1)]
TO-24-BVK-COT-1-01 Window: Jul Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - |  | DO | 5 | N/A | Total Maintenance Outage Duration Requested
FO_CABLE | - | - | 901468879 | DO | 5 | 4 | 2023PM_Water ingress in CB link box @ JB33 - raise or relocate.
N/A | - | - | ESBN TO CONFIRM | DO | 5 | 4 | Cable Insp. 110kV XLPE (MID SECTION 1/3)
FO_CABLE | - | - | 901468941 | DO | 2 | 4 | 2023PM_Replace all SVL's in JB33 link box - water logged and poor readings.
| BVK |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,GRL100 702D
OPT | BVK | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
OS | COT | - | ESBN TO CONFIRM | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| CTG |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,GRL100 702D
| COT | - | 901520009 | DO | 3 | 1 | P1 Hotspot on Ballyvouskill DA S phase required immediately
| COT | - | 901520010 | DO | 3 | 3 | P3 Hotspot on Ballyvouskill DL R phase required within the next 12 months
| COT | - | 901534443 | DO | 3 | 2 | P2 Hotspot on Ballyvouskill DA T phase required within the next 3 months
110kV FEEDER - BALLYWATER CRANE [Ballywater WF (BW1)]
TO-24-BWR-CRA-1-02 Status: Unscheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| CRA |  |  | DO | 2 |  | P3 Protection maintenance of 7SD610,7SA513
110kV FEEDER - BARRYMORE tee CAHIR
TO-24-BAR,T-CAH-1-01 Window: Jul - Aug Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - |  | DO | 10 | N/A | Total Maintenance Outage Duration Requested
FO_MISC | - | - | 901170978 | DO | 2 | 3 | 2020HP-1[22-23]Air Craft Sphere Bird Div
FO_INSUL | - | - | 901385039 | DO | 2 | 4 | Insulator off Plumb. Pole No. 227
FO_MISC | - | - | 901368960 | DO | 1 | 4 | 2022HP-1[120]Off Plumb (Re-plumb poles)
FO_MISC | - | - | 901368961 | DO | 1 | 4 | 2022HP-1[121]Off Plumb (Re-plumb poles)
FO_COND | - | - | 901519316 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 22]C/Ph Repl. Deadend 3 Months. Response: 3 Months. Due: 12-Apr-2024
FO_COND | - | - | 901519317 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 22]C/Ph Repl. Deadend 1 Months. Response: 1 Month. Due: 12-Feb-2024
FO_COND | - | - | 901519318 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 22]C/Ph Repl. Jumper 1 Months. Response: 1 Month. Due: 12-Feb-2024
FO_COND | - | - | 901519319 | DO | 1 | 1 | HOTSPOT - 2023IR[23-24]L/Ph Repl Midspan Immediate. Response: Immediately. Due: Immediately
FO_COND | - | - | 901519320 | DO | 1 | 1 | HOTSPOT - 2023IR[53-54]C/Ph Repl Midspan Immediate. Response: Immediately. Due: Immediately
FO_COND | - | - | 901519321 | DO | 1 | 1 | HOTSPOT - 2023IR[62-63]L/Ph Repl. Midspan. Response: 6 Months. Due: 12-Jul-2024
FO_COND | - | - | 901519322 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 63]R/Ph Repl. Deadend. Response: 3 Months. Due: 12-Apr-2024
FO_COND | - | - | 901519323 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 63]L/Ph Repl. Deadend. Response: 1 Month. Due: 12-Feb-2024
FO_COND | - | - | 901519324 | DO | 1 | 1 | HOTSPOT - 2023IR[63-64]R/Ph Repl. Midspan. Response: 3 Months. Due: 12-Apr-2024
FO_COND | - | - | 901519325 | DO | 1 | 1 | HOTSPOT - 2023IR[63-64]C/Ph Repl. Midspan. Response: 3 Months. Due: 12-Apr-2024
FO_COND | - | - | 901519327 | DO | 1 | 1 | HOTSPOT - 2023IR[130-131]C/Ph Repl Midspan. Response: 1 Month. Due: 12-Feb-2024
FO_COND | - | - | 901519328 | DO | 1 | 1 | HOTSPOT - 2023IR[181-182]C/Ph Repl Midspan. Response: 3 Months. Due: 12-Apr-2024
FO_COND | - | - | 901519329 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 181]L/Ph Repl. Deadend. Response: 1 Month. Due: 12-Feb-2024
OSSF6110 | CAH | - | 901300801 | DO | 4 | 3 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| CAH | - | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
| CAH |  |  | DO | 2 |  | P3 Protection maintenance of 7SA511,REL521
FO_MISC | STH | CK | 901500688 | DO | 1 | 4 | 2023HP-1[205]Insulator 1xBroken disc R/P
FO_MISC | STH | CK | 901500689 | DO | 1 | 4 | 2023HP-1[107]off Plumb
FO_COND | STH | CK | 901519326 | DO | 1 | 1 | HOTSPOT - 2023IR[70-71]C/Ph Repl. Midspan. Response: 1 Month. Due: 12-Feb-2024
110kV FEEDER - BARRYMORE tee KNOCKRAHA
TO-24-BAR,T-KRA-1-01 Window: Jul - Aug Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - |  | DO | 10 | N/A | Total Maintenance Outage Duration Requested
FOSTRHW | - | - | 901298981 | DO | 5 | 4 | Replace Pole Set 227- Pole Rot
FOSTRHW | - | - | 901298983 | DO | 5 | 4 | Replace Pole Set 236. -Rotten
FOSTRHW | - | - | 901298990 | DO | 5 | 4 | Replace Pole No. 296. Rotten
FOSTRHW | - | - | 901397306 | DO | 5 | 4 | Replace Pole No. 248. Top Right Pole Rot
FO_TIMB | - | - | 901217145 | DO | 1 | 3 | HAZ CNF 40M (278-279) Tim Cut
FO_MISC | - | - | 901253795 | DO | 1 | 4 | 2021HP-1[332]Off Plumb
FO_COND | - | - | 901519330 | DO | 1 | 2 | 2023IR[AT 287]R/Ph Repl. Deadend 3 Months
FO_COND | - | - | 901519331` | DO | 1 | 1 | 2023IR[AT 287]R/Ph Repl. Deadend Immediat
FO_COND | - | - | 901519332 | DO | 1 | 1 | HOTSPOT - 2023IR[286-287]R/Ph Rep Midspan. Response: Immediately. Due: Immediately
FO_COND | - | - | 901519333 | DO | 1 | 1 | HOTSPOT - 2023IR[286-287]L1/Ph Resistance Midspan. Response: Next Planned Maintenance. Due: Next Planned Maintenance
OSSF6110 | KRA | - | 901396820 | DO | 5 | 1 | 110kV SF6 Cubicle Ordinary Service
CA_110 | KRA | - | 901396433 | DO | 3 | 4 | 110KV CUBICLE CONDITION ASSESSMENT
| KRA |  |  | DO | 2 |  | P3 Protection maintenance of 7SA511,REL521
FOSTRHW | STH | CK | 901503248 | DO | 1 | 4 | 2023HP-1[341]Check Structure (Top Rot)S2
FO_COND | STH | CK | 901519331 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 278]L/Ph Repl Deadend . Response: Immediately. Due: Immediately
110kV FEEDER - BELLACORICK SRAHNAKILLY [Oweninny 1/2 WFs (OY1/OY2)]
TO-24-BK-SKY-1-02 ISO week: 15mo - 17fr Date: 08 Apr - 26 Apr Duration: 19 Days (15 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - |  | DO | 10 | N/A | Total Maintenance Outage Duration Requested
AMCAB | - | cable | ESBN TO CONFIRM | DO | 10 | 4 | Cable Insp. 110kV XLPE
FO_CABLE | - | - | 901238134 | DO | 5 | 3 | 2021PM_Investigation & repair of S-Phase
OS | BK~ | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| BK~ | - | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
OS | SKY | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
SECTIONALISING DISCONNECT - BOGGERAGH 110SA1 [Boggeragh 2 WF (BG2)]
TO-24-BGH-110SA1-01 Window: Aug Duration: (7 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
OS | BGH | 110-SA1 | ESBN TO CONFIRM | DO | 2 | 4 | 110kV Sect / Dist Ordinary Service (including busbar disconnects of all bays that are connected to the busbar section that is on outage)
110kV FEEDER - BOGGERAGH CLASHAVOON [Boggeragh 1/2 WFs (BG1/BG2)]
TO-24-BGH-CLA-1-01 Window: Aug Duration: (7 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - |  | DO | 7 | N/A | Total Maintenance Outage Duration Requested
OS | BGH | - | ESBN TO CONFIRM | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
CORRECT | BGH | - | 901412245 | DO | 2 | 4 | O1-Surge Counter Screen not working S Ph
AMCAB | Cable | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
OS | CLA | - | ESBN TO CONFIRM | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service
| CLA | - | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
CORRECT | CLA | - | 901474431 | DO | 1 | 4 | O1- H3 CB light defect
FO_MISC | LINE | - | 901501297 | DO | 1 | 4 | 2023HP-1[7]Earths-Replace (Pole Top)
FO_MISC | LINE | - | 901501298 | DO | 1 | 4 | 2023HP-1[77]Earths-Replace (Pole Top)
GENERATOR TRANSFORMER - BOGGERAGH T121 [Boggeragh 1 WF (BG1)]
TO-24-BGH-T121-01 Window: Aug Duration: (7 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | BGH | 110 | ESBN TO CONFIRM | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
GENERATOR TRANSFORMER - BOGGERAGH T132 [Boggeragh 2 WF (BG2)]
TO-24-BGH-T132-01 Window: Aug Duration: (7 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| BGH |  |  | DO | 2 |  | P3 Protection maintenance of BOC (M1),7SA612,SPS (M1)
OPT | BGH | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - BOOLTIAGH T121 [Booltiagh 1/2 WF (BT1/BT2)]
TO-24-BOL-T121-01 Window: Aug Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
OPT | BOO | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - CARRIGADROHID T103 [Lee LE3]
TO-24-CD-T103-02 Status: Unscheduled
| CD |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,RET521,7SV512
110kV FEEDER - CARRIGDANGAN DUNMANWAY [Carrigdangan WF (XA1)]
TO-24-CGG-DMY-1-01 ISO week: 12tu - 13mo Date: 19 Mar - 25 Mar Duration: 7 Days (5 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
AIC110D | - | cable | 901535620 | DO | 4 | 2 | Cable Insp. 110kV XLPE
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
OPT | CGG | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV GIS Cubicle Operational Test
OPT | DMY | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - CATHALEENS FALL CLIFF [Erne ER1; Erne ER2]
TO-24-CF-CL-1-02 ISO week: 15we - 15th Date: 10 Apr - 11 Apr Duration: 2 Days (2 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
| CF |  |  | DO | 2 |  | P1 Protection maintenance of 7SA511
FOFAULT | CF~ | - | 901335734 | DO | 2 | 4 | H5 CB densimeter replacement.
OPTSF61 | CF~ | - | 901396673 | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - CATHALEENS FALL T103 [Erne ER3]
TO-24-CF-T103-01 Window: Jun Duration: (7 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 7 | N/A | Total Maintenance Outage Duration Requested
| CF |  |  | DO | 2 |  | P3 Protection maintenance of BOC (M1),7SA612,7UT513
OS | CF~ | 110 | ESBN TO CONFIRM | DO | 4 | 1 | 110KV SF6 Cubicle Ordinary Service
CA_110 | CF~ | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110kV CUBICLE CONDITION ASSESSMENT
GENERATOR TRANSFORMER - CATHALEENS FALL T104 [Erne ER4]
TO-24-CF-T104-01 Window: Sep Duration: (7 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
| CF |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,7UT513
OSSF6110 | CF~ | 110 | 901396849 | DO | 4 | 1 | 110KV SF6 Cubicle Ordinary Service
CA_110 | CF~ | 110 | 901396488 | DO | 3 | 4 | 110KV CUBICLE CONDITION ASSESSMENT
CORRECT | CF~ | 110 | 901332346 | DO | 1 | 1 | T104 SF6 CB Operational Test C Falls
GENERATOR TRANSFORMER - CLAHANE T122 [Clahane 1/2 WFs (CJ1/CJ2)]
TO-24-CLH-T122-01 Window: May Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
OS | CLH | 110 | ESBN TO CONFIRM | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
GENERATOR TRANSFORMER - CLIFF T101 [Erne ER1]
TO-24-CL-T101-03 Status: Unscheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| CL |  |  | DO | 2 |  | P3 Protection maintenance of 7SJ511,7UT513
TO-24-CL-T101-02 ISO week: 15we - 15th Date: 10 Apr - 11 Apr Duration: 2 Days (2 WD) Status: Proposed
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
CORRECT | CL~ | - | 901230085 | DO | 2 | 3 | Repair corrosion issue on CTs
GENERATOR TRANSFORMER - CLIFF T102 [Erne ER2]
TO-24-CL-T102-03 Window: May Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
| CL |  |  | DO | 2 |  | P1 Protection maintenance of 7SJ511,7UT513
CORRECT | CL~ | - | 901314311 | DO | 5 | 3 | Visually Inspect CT's bellow pipework
CORRECT | CL~ | - | 901314313 | DO | 5 | 1 | Replace SF6 Pressure gauge
CORRECT | CL~ | - | 901314314 | DO | 5 | 1 | Measure SF6 gasquality for level of SO2
OPTSF61 | CL~ | 110 | 901432253 | DO | 1 | 4 | 110KV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - CLOGHBOOLA T131 [Cloghboola WF (CL1)]
TO-24-CBA-T131-01 Window: Jul Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| CBL |  |  | DO | 2 |  | P3 Protection maintenance of 7SA611,7SJ804
110kV FEEDER - CLOGHBOOLA TRIEN [Cloghboola WF (CL1)]
TO-24-CBA-TRI-1-01 Window: Jul Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
FO_CABLE | - | - | 901423790 | DO | 5 | 4 | 2023PM_Testing after correctives (LB cha
FO_CABLE | - | - | 901423791 | DO | 5 | 4 | 2023PMWater ingress into link box at JB08
FO_CABLE | - | - | 901423792 | DO | 5 | 4 | 2023PMWater ingress into link box at JB10
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
FO_CABLE | CBA | - | 901155245 | DO | 5 | 1 | Clean CSE stand-off insulators in Cloghb
FO_CABLE | CBA | - | 901155246 | DO | 5 | 1 | Water ingress into link box at JB12 - ra
OPT | CBA | - | ESBN TO CONFIRM | DO | 2 | 4 | 110kV SF6 Cubicle Operational Test
OPT | TRI | - | ESBN TO CONFIRM | DO | 2 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - CLOGHER MULREAVY [Mulreavy 1/2 WFs (MB1/MB2)]
TO-24-CLO-MRY-1-01 ISO week: 17mo - 18mo Date: 22 Apr - 29 Apr Duration: 8 Days (6 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
AICX110S | CABLE | 110 | 901129091 | DO | 4 | 1 | Cable Insp. 110kV XLPE
OSGIS110 | CLO | - | 901300588 | DO | 4 | 3 | 110kV GIS Cubicle Ordinary Service
| CLO |  |  | DO | 2 |  | P2 Protection maintenance of 7SA612,GRL100
| MRY |  |  | DO | 2 |  | P2 Protection maintenance of 7SA612,GRL100
220kV FEEDER - CLONIFFEEN SHANNONBRIDGE [Shannonbridge Batts SI1/SI2]
TO-24-CFN-SH-1-01 Window: Jul Duration: (1 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPTSF62 | SH~ | - | 901397035 | DO | 1 | 4 | 220kV SF6 Cubicle Operational Test
110kV FEEDER - CLONKEEN COOMAGEARLAHY [Coomagearlahy 1/2/3 Glanlee WF]
TO-24-CKN-CGL-1-02 ISO week: 15mo - 17fr Date: 08 Apr - 26 Apr Duration: 19 Days (15 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
FO_COND | - | - | 901495141 | DO | 1 | 4 | 2023LP-1[40] Treat Jumper Bolts
FO_COND | - | - | 901495142 | DO | 1 | 4 | 2023LP-1[44] Treat Jumper Bolts
FO_COND | - | - | 901495143 | DO | 1 | 4 | 2023LP-1[45] Treat Jumper Bolts
FO_MISC | - | - | 901495144 | DO | 1 | 4 | 2023LP-1[14]Vibration Dampers Replace
FO_MISC | - | - | 901495145 | DO | 1 | 4 | 2023LP-1[24]Vibration Dampers Replace
FO_MISC | - | - | 901495146 | DO | 1 | 4 | 2023LP-1[25]Vibration Dampers Replace
FO_MISC | - | - | 901495147 | DO | 1 | 4 | 2023LP-1[28]Vibration Dampers Replace
FO_MISC | - | - | 901495148 | DO | 1 | 4 | 2023LP-1[29]Vibration Dampers Replace
FO_MISC | - | - | 901495149 | DO | 1 | 4 | 2023LP-1[41]Vibration Dampers Replace
FO_STDMG | - | - | 901495157 | DO | 1 | 4 | 2023LP-1[28]Check - Ubolts (S2)
FO_STDMG | - | - | 901495158 | DO | 1 | 4 | 2023LP-1[29]Check -Ubolts (S2)
AMCAB | Cable | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
OPT | CGL | - | ESBN TO CONFIRM | DO | 2 | 4 | 110kV SF6 Cubicle Operational Test
| CKN |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,GRL100
OPT | CKN | - | ESBN TO CONFIRM | DO | 2 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - COOLNANOONAGH KILPADDOGE [Kelwin WF/Bat/Diesel Cap]
TO-24-CNO-KPG-1-02 Status: Unscheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| KPG |  |  | DO | 2 |  | P3 Protection maintenance of 7SA611,BOC,RET670,GRB100,7SJ804
TO-24-CNO-KPG-1-01 Window: Jun Duration: (2 WD) Status: Planned
OPTSF61 | KPG | - | 901396810 | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - COOMAGEARLAHY GLANLEE [Glanlee WF (GLC)]
TO-24-CGL-GAE-1-02 ISO week: 15mo - 17fr Date: 08 Apr - 26 Apr Duration: 19 Days (15 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
OSSF6110 | CGL | - | 901396332 | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| CGL |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,GRL100
AMCAB | CGL | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
GENERATOR TRANSFORMER - COOMAGEARLAHY T121 [Coomagearlahy 3 WF (CG3)]
TO-24-CGL-T121-02 ISO week: 15mo - 15fr Date: 08 Apr - 26 Apr Duration: 19 Days (15 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
CORRECT | CGL | 110 | 901323272 | DO | 3 | 4 | Carry out loss of AC supply mod
| CGL |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,7VK611
SECTIONALISING DISCONNECT - COOMATAGGART 110SA1
TO-24-COT-110SA1-02 Window: Jul Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | COT | 110-SA1 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV Sect / Dist Ordinary Service (including busbar disconnects of all bays that are connected to the busbar section that is on outage)
SECTIONALISING DISCONNECT - COOMATAGGART 110SA2
TO-24-COT-110SA2-02 Window: Jul Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | COT | 110-SA2 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV Sect / Dist Ordinary Service (including busbar disconnects of all bays that are connected to the busbar section that is on outage)
GENERATOR TRANSFORMER - COOMATAGGART T132 [Grousemount WF (GD1)]
TO-24-COT-T132-01 Window: Jul Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
OS | COT | 110 | ESBN TO CONFIRM | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| COT | 110 | 901520011 | DO | 3 | 3 | P3 Hotspot on T132 DT disconnect R phase required within 12 months
| COT | 110 | 901520012 | DO | 3 | 3 | P3 Hotspot on T132 DA disconnect T phase required during next planned maintenance
GENERATOR TRANSFORMER - CORDAL T132 [Cordal 1/2 WF (DL1/DL2)]
TO-24-CDL-T132-01 Window: May Duration: (4 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
FO_CABLE | CDL | 110 | 901469066 | DO | 3 | 4 | 2023PM_Install shrinks to top of bonding leads-water ingress.
110kV FEEDER - CORDERRY GARVAGH [Garvagh 1/2 WFs (GH1/GH2)]
TO-24-CDY-GRV-1-02 Status: Unscheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| GAR |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,GRL100
TO-24-CDY-GRV-1-01 Window: Jul Duration: (1 WD) Status: Planned
FO_CABLE | - | - | 901452521 | DO | 1 | 2 | 2023PM_Inst.LCIM bonding cbl ties;OD1Day
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | CDY | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
OPT | GRV | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV GIS Cubicle Operational Test
220kV FEEDER - CORDUFF HUNTSTOWN [Huntstown HN2]
TO-24-CDU-HN-1-01 Window: Oct Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
AMCAB | CABLE | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 220kV Feeder XLPE
OPT | CDU | - | ESBN TO CONFIRM | DO | 1 | 4 | 220kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - CUNGHILL T121 [Kingsmountain 1/2 WF (KGM/KG2)]
TO-24-CUN-T121-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | CUN | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| CUN | 110 | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
CA_110 | CUN | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
110kV FEEDER - CUSHALING KILCUMBER [Cloncreen WF (OE1)]
TO-24-CUS-KIR-1-01 Window: Jul Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
GENERATOR TRANSFORMER - CUSHALING T101 [Edenderry ED1]
TO-24-CUS-T101-01 Window: Aug Duration: (1 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | CUS | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - CUSHALING T103/5 [Edenderry ED3; Edenderry ED5]
TO-24-CUS-T103/5-01 Window: Jul - Aug Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
| CUS | 110 | ESBN TO CONFIRM | DO | 5 | 1 | O-Ring Replacement to prevent SF6 leaks
OS | CUS | 110 | ESBN TO CONFIRM | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| CUS |  |  | DO | 2 |  | P1 Protection maintenance of 7SA612,SEL551
GENERATOR TRANSFORMER - DERRYCARNEY T132 [Lumcloon Batteries LU1 & LU2]
TO-24-DEY-T132-01 Window: Jul Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | DEY | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV AIS Cubicle Operational Test
GENERATOR TRANSFORMER - DERRYCARNEY T134 [Statkraft]
TO-24-DEY-T134-02 Window: Jun Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
XLPCI_S | DEY | - | 901535601 | DO | 2 | 4 | Cable Insp. 110kV XLPE
N/A | DEY | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV AIS Cubicle Operational Test
GENERATOR TRANSFORMER - DERRYIRON RHODE T1/T2 [Rhode RP1/RP2]
TO-24-DER-T1/T2-04 ISO week: 12mo - 15we Date: 18 Mar - 10 Apr Duration: 24 Days (15 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
FO_TIMB | - | - | 901332399 | DO | 1 | 4 | 60m[1-2]TimCut 110kV(Rural)
OS | DER | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| DER | 110 | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
CA_110 | DER | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
OPTSF61 | DER | 110 | 901396752 | DO | 1 | 4 | 110KV SF6 Cubicle Operational Test
110kV FEEDER - DRUMKEEN MEENTYCAT [Meentycat WF (MCT)]
TO-24-DRM-MEE-1-01 Status: Unscheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| DRM |  |  | DO | 2 |  | P3 Protection maintenance of 7SA513
110kV FEEDER - ENNIS SLIEVECALLAN [Boolinrudda/Knockalassa WF]
TO-24-ENN-SLC-1-02 Window: Jul Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
AICX4/2F | ENN | - | 901212142 | DO | 2 | 1 | Cable Insp. 110kV XLPE
OPT | ENN | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
| SLC |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,GRL100 702D
OPT | SLC | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
220kV FEEDER - FINGLAS HUNTSTOWN [Huntstown HNC]
TO-24-FIN-HN-1-01 ISO week: 17sa - 19we Date: 27 Apr - 08 May Duration: 12 Days (7 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OSSF6220 | FIN | - | 901300960 | DO | 5 | 3 | 220kV SF6 Cubicle Ordinary Service
CORRECT | FIN | - | 901301504 | DO | 1 | 3 | CHECK TORQUE OF MECHANISM DRIVE RODS
GENERATOR TRANSFORMER - GALLANSTOWN T133 [Gallanstown SF (IA01)]
TO-24-GLN-T133-03 ISO week: 7mo - 10we Date: 12 Feb - 06 Mar Duration: 24 Days (18 WD) Status: Scheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | GLN | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
COUPLER/SECTIONALISING CB - GARROW 110SA1-2CB [Coomacheo WF (CZ1)]
TO-24-GRO-110SA1-2CB-01 Window: Jul Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
CA_110 | GRO | - | 901396295 | DO | 5 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
OSSF6110 | GRO | - | 901396370 | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
OSSEC110 | GRO | 110kV-SA2 | 901396211 | DO | 3 | 4 | 110kV Sect / Dist Ordinary Service (including busbar disconnects of all bays that are connected to the busbar section that is on outage)
OSSEC110 | GRO | 110kV-SA1 | 901396212 | DO | 3 | 4 | 110kV Sect / Dist Ordinary Service (including busbar disconnects of all bays that are connected to the busbar section that is on outage)
| GRO | 110SA1-2CB | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
| GRO | 110SA1-2CB | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
GENERATOR TRANSFORMER - GARROW T122 [Coomacheo WF (CZ1)]
TO-24-GRO-T122-01 Window: Jul Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| GRO | 110 | ESBN TO CONFIRM | DO | 5 | 1 | O-Ring Replacement to prevent SF6 leaks
OS | GRO | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
AMCAB | GRO | 110 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
OPTSF61 | GRO | 110 | 901396741 | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - GARVAGH T121 [Garvagh 1/2 WFs (GH1/GH2)]
TO-24-GRV-T121-01 Window: Jul Duration: (7 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 7 | N/A | Total Maintenance Outage Duration Requested
| GAR |  |  | DO | 2 |  | P3 Protection maintenance of BOC (M1),7SA611,RET670,GRB100,7SJ804
OSSF6110 | GRV | 110 | 901396852 | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service
CA_110 | GRV | 110 | 901396493 | DO | 3 | 4 | 110KV CUBICLE CONDITION ASSESSMENT
AMCAB | GRV | 110 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
GENERATOR TRANSFORMER - GLANAGOW T2001 [Whitegate (WG1)]
TO-24-GGO-T2001-01 Window: Sep Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
AMCAB | GGO | 220 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
110kV FEEDER - GLENLARA KNOCKACUMMER [Knockacummer WF (KC1)]
TO-24-GLE-KCR-1-01 Window: Jun Duration: (4 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
AMCAB | CABLE | - | ESBN TO CONFIRM | DO | 5 | 4 | Cable Insp. 110kV XLPE
| GLE |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,GRL100
| KCR |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612, GRL100
GENERATOR TRANSFORMER - GORMAN T122 [Gorman Battery GF1]
TO-24-GOR-T122-01 ISO week: 18tu Date: 30 Apr Duration: 1 Day (1 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
OPTSF61 | GOR | 110 | 901432254 | DO | 1 | 4 | 110KV SF6 Cubicle Operational Test
N/A | GOR | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
GENERATOR TRANSFORMER - GREAT ISLAND GIS T2004 [Great Island GI4 (GI4)]
TO-24-GI GIS-T2004-02 Window: May Duration: (9 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
| GI |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612
OPT | GI~ | 220 | ESBN TO CONFIRM | DO | 1 | 4 | 220kV GIS Cubicle Operational Test
GENERATOR TRANSFORMER - HUNTSTOWN T2002 [Huntstown HN2]
TO-24-HN-T2002-01 Window: Oct Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
CORRECT | HUN | 220-DL/DE | 901385523 | DO | 5 | 1 | Hotspot on R Phase DL/DE disconnect DUE: IMMEDIATE 3 month wait time on parts 12/04/2023
CORRECT | HUN | 220 | 901450455 | DO | 4 | 4 | RE-test CB
AICX4/2F | HUN | - | 901299975 | DO | 2 | 3 | Cable Insp. 400 & 220kV Feeder XLPE
OPT | HUN | 220 | ESBN TO CONFIRM | DO | 1 | 4 | 220kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - HUNTSTOWN T2010/11 [Huntstown HNC]
TO-24-HN-T2010/11-02 Window: May Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
CORRECT | HUN | 220-DL/DE | 901348865 | DO | 3 | 1 | Hotspot- DL/DE disconnect R phase Due- Immediate
OPT | HUN | 220 | ESBN TO CONFIRM | DO | 1 | 4 | 220kV SF6 Cubicle Operational Test
110kV FEEDER - IKERRIN tee SHANNONBRIDGE
TO-24-IKE,T-SH-1-05 Window: Sep Duration: (7 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 7 | N/A | Total Maintenance Outage Duration Requested
FOSTRHW | - | - | 901311071 | DO | 3 | 4 | Poleset replacement @38
FOSTRHW | - | - | 901324409 | DO | 2 | 4 | 1[219]Replace Pole Rot Confirmed (Drone)
FOSTRHW | - | - | 901324406 | DO | 1 | 4 | 1[137]Replace Pole Rot Confirmed (Drone)
FO_MISC | - | - | 901370781 | DO | 1 | 4 | 2022HP-24[261-285]Danger Notices Replace
FO_MISC | - | - | 901504230 | DO | 1 | 1 | 2023HP-1[236]Bird Nests (Remove)
FOSTRHW | - | - | 901504231 | DO | 1 | 4 | 2023HP-1[126]Check Structure (Top Rot)S2
FOSTRHW | - | - | 901504232 | DO | 1 | 4 | 2023HP-1[137]Check Structure (Top Rot)S2
FOSTRHW | - | - | 901504233 | DO | 1 | 4 | 2023HP-1[199]Check Structure (Top Rot)S2
FOSTRHW | - | - | 901504235 | DO | 1 | 4 | 2023HP-1[241]Check Structure (Top Rot)S2
FOSTRHW | - | - | 901504236 | DO | 1 | 4 | 2023HP-1[253]Check Structure (Top Rot)S2
FOSTRHW | - | - | 901504237 | DO | 1 | 4 | 2023HP-1[27]Check Structure (Top Rot)-S2
FOSTRHW | - | - | 901504238 | DO | 1 | 4 | 2023HP-1[37]Check Structure (Top Rot)-S2
FOSTRHW | - | - | 901504239 | DO | 1 | 4 | 2023HP-1[38]Check Structure (Top Rot)-S2
FOSTRHW | - | - | 901504240 | DO | 1 | 4 | 2023HP-1[57]Check Structure (Top Rot)-S2
FOSTRHW | - | - | 901504241 | DO | 1 | 4 | 2023HP-1[9]Check Structure (Top Rot)-S2
FO_MISC | - | - | 901504242 | DO | 1 | 4 | 2023HP-1[17-18]Conflicts Shed underline
FO_MISC | - | - | 901504246 | DO | 1 | 4 | 2023HP-1[117]Stays-Replace (Bog Stays)
FOSTRHW | - | - | 901504252 | DO | 1 | 4 | 2023HP-1[282]Check Structure (Top Rot)S2
CORRECT | SH~ | - | 901365415 | DO | 1 | 4 | Replace bellows on T-phase CTVT
CORRECT | SH~ | - | 901365416 | DO | 1 | 4 | Replace surge counter on R-phase SA
CORRECT | SH~ | - | 901365417 | DO | 1 | 4 | Replace surge counter on T-phase SA
110kV FEEDER - IKERRIN tee THURLES
TO-24-IKE,T-THU-1-05 Window: Sep Duration: (7 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
FO_COND | - | - | 901432133 | DO | 5 | 1 | Take Conductor Samples of 1962 430 ACSR. Take 3 samples at different spans along its route.
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
FO_MISC | - | - | 901126159 | DO | 1 | 2 | 2019LP-1[291]Off Plumb - Pole
OPT | THU | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV MO Cubicle Operational Test
GENERATOR TRANSFORMER - INNISCARRA T101 [Lee LE1; Lee LE2]
TO-24-IA-T101-02 Window: May Duration: (1 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | IA~ | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110KV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - IRISHTOWN T2001 [Dublin Bay DB1]
TO-24-ISH-T2001-01 Window: Aug Duration: (1 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
AIC4/2A | ISH | 220 | 901280821 | DO | 1 | 1 | Cable Insp. 400 & 220kV Feeder XLPE
OPTGIS2 | ISH | 220 | 901300310 | DO | 1 | 3 | 220kV GIS Cubicle Operational Test
GENERATOR TRANSFORMER - KILCUMBER T131 [Cloncreen WF (OE1)]
TO-24-KIR-T131-01 Window: Jul Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
N/A | KIR | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - KILL HILL T131 [Kill Hill WF (KH1)]
TO-24-KHL-T131-01 Window: Jul Duration: (1 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | KHL | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - KILTEEL T131 [Porterstown Battery PN1]
TO-24-KTL-T131-01 Window: May Duration: (1 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
N/A | KTL | 110 | 901397142 | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - KNOCKALOUGH KNOCKRANNY [Knockalough WF (KU1)]
TO-24-KLH-KNY-1-01 Window: Jul Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - |  | DO | 3 | N/A | Total Maintenance Outage Duration Requested
CORRECT | KLH | - | 901343446 | DO | 1 | 4 | Master Sub Remote Switch
CORRECT | KLH | - | 901343450 | DO | 1 | 4 | Surge Arrestor Counter Covers
CORRECT | KLH | - | 901343451 | DO | 1 | 4 | V.T Secondary fuse holders
OPTSF61 | KLH | - | 901396808 | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
| KNY |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,GRL100 702D
OPTSF61 | KNY | - | 901396809 | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - KNOCKRANNY UGGOOL [Seecon/Uggool WF (SO1/UG1)]
TO-24-KNY-UGL-1-01 Window: Jul Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
AMCAB | Cable | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
OPT | KNY | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV GIS Cubicle Operational Test
OPT | UGL | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV GIS Cubicle Operational Test
GENERATOR TRANSFORMER - LISDRUM T131 [Lisdrumdoagh Battery LF1]
TO-24-LIS-T131-01 Window: May Duration: (1 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | LIS | 110 | 901348591 | DO | 1 | 4 | 110KV SF6 Cubicle Operational Test
SECTIONALISING DISCONNECT - LISHEEN 110SA2-4
TO-24-LSN-110SA2-4-03 Window: Aug Duration: (9 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | LSN | SA4 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV Sect / Dist Ordinary Service (including busbar disconnects of all bays that are connected to the busbar section that is on outage)
OS | LSN | SA2 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV Sect / Dist Ordinary Service (including busbar disconnects of all bays that are connected to the busbar section that is on outage)
GENERATOR TRANSFORMER - LISHEEN T122 [Lisheen 1/2 WFs (LS1/LS2)]
TO-24-LSN-T122-03 Window: Aug Duration: (9 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | LSN | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
110kV FEEDER - LISHEEN THURLES [Lisheen 1/2/3 WF (LS1/LS2/LS3)]
TO-24-LSN-THU-1-03 Window: Aug Duration: (9 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 9 | N/A | Total Maintenance Outage Duration Requested
OS | LSN | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
OS | THU | - | ESBN TO CONFIRM | DO | 9 | 1 | 110kV MO Cubicle Ordinary Service (excludes busbar disconnects)
CA_110 | THU | - | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
GENERATOR TRANSFORMER - LONG POINT T2002 [Aghada AD2]
TO-24-LPT-T2002-02 ISO week: 9mo - 15fr Date: 26 Feb - 12 Apr Duration: 47 Days (32 WD) Status: Scheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPTSF62 | LPT | 220 | 901397021 | DO | 1 | 4 | 220kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - MONEYPOINT GIS T121 [Moneypoint WF (MP9)]
TO-24-MP GIS-T121-02 Window: Aug Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
OPT | MP~ | 110 | ESBN TO CONFIRM | DO | 2 | 4 | 110KV GIS Cubicle Operational Test
FO_CABLE | MP~ | 110 | 901452318 | DO | 1 | 1 | 2023PM_Retest follow corr. Work; OD1 Day
FO_CABLE | MP~ | 110 | 901452500 | DO | 1 | 1 | 2023PM_Clean cable SO Ins @ T121; OD1Day
GENERATOR TRANSFORMER - MONEYPOINT GIS T4001 [Moneypoint MP1]
TO-24-MP GIS-T4001-01 Window: May Duration: (7 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 7 | N/A | Total Maintenance Outage Duration Requested
CA_400 | MP~ | - | ESBN TO CONFIRM | DO | 4 | 4 | 400KV CUBICLE CONDITION ASSESSMENT
OS | MP~ | - | ESBN TO CONFIRM | DO | 3 | 4 | 400kV GIS Cubicle Ordinary Service
GENERATOR TRANSFORMER - MONEYPOINT GIS T4002 [Moneypoint MP2]
TO-24-MP GIS-T4002-02 Window: May Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | MP~ | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | MP~ | - | ESBN TO CONFIRM | DO | 3 | 4 | 400kV GIS Cubicle Ordinary Service
AMCAB | MP~ | 400 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
GENERATOR TRANSFORMER - MONEYPOINT GIS T4003 [Moneypoint MP3]
TO-24-MP GIS-T4003-02 Window: Sep Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
AMCAB | MP~ | 400 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
GENERATOR TRANSFORMER - MOUNTLUCAS T121 [Mountlucas WF (MO1)]
TO-24-MLC-T121-02 Status: Unscheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| MLC |  |  | DO | 2 |  | P3 Protection maintenance of BOC (M1),7SA612,SPS (M1)
TO-24-MLC-T121-01 Window: May Duration: (2 WD) Status: Planned
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
| MLC |  |  | DO | 2 |  | P1 Protection maintenance of 7SA612,BOC(M1),SPS(M1)
OPT | MLC | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - NORTH WALL T2004/5 [Northwall TEG(NW8)]
TO-24-NW-T2004/5-01 Window: Jul Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
| NW |  |  | DO | 2 |  | P1 Protection maintenance of 7SA612,RET521
OPT | NW~ | 220 | ESBN TO CONFIRM | DO | 1 | 4 | 220kV GIS Cubicle Operational Test
GENERATOR TRANSFORMER - POLLAPHUCA T101 [Liffey LI1/LI2/LI4]
TO-24-PA-T101-04 Window: May - Jun Duration: (19 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 6 | N/A | Total Maintenance Outage Duration Requested
| PA |  |  | DO | 2 |  | P2 Protection maintenance of 7SA511,7UT513,7SV512
OS | POL | 110 | ESBN TO CONFIRM | DO | 6 | 1 | 110kV MO Cubicle Ordinary Service
GENERATOR TRANSFORMER - RATRUSSAN T121 [Bindoo WF (BD1)]
TO-24-RRU-T121-05 ISO week: 17we - 21we Date: 24 Apr - 22 May Duration: 29 Days (20 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OSSF6110 | RRU | - | 901300859 | DO | 4 | 3 | 110kV SF6 Cubicle Ordinary Service
| RRU | 110 | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
GENERATOR TRANSFORMER - RATRUSSAN T122 [Mountain Lodge WF (ML1)]
TO-24-RRU-T122-05 ISO week: 17we - 21we Date: 24 Apr - 22 May Duration: 29 Days (20 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OSSF6110 | RRU | 110 | 901396364 | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service
| RRU | 110 | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
110kV FEEDER - REAMORE TRALEE
TO-24-REM-TRL-1-01 Window: Aug Duration: (8 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 8 | N/A | Total Maintenance Outage Duration Requested
FO_CABLE | - | - | 901452070 | DO | 3 | 3 | 2023PM_Raise JB15 cham lid 100mm OD:3Day
FO_CABLE | - | - | 901452081 | DO | 3 | 1 | 2023PM_Mntr Leak Current JB1-2 OD:3 Day
FO_CABLE | - | - | 901452082 | DO | 3 | 1 | 2023PM_Mntr Leak Current JB2-3 OD:3 Day
FO_CABLE | - | - | 901452087 | DO | 3 | 1 | 2023PM_Mntr Leak Current JB3-6_OD 3 Days
FO_CABLE | - | - | 901452088 | DO | 3 | 1 | 2023PM_Mntr Leak Current JB6-9_OD 3 Days
FO_CABLE | - | - | 901452089 | DO | 3 | 1 | 2023PM_Mntr Leak Current JB9-12_OD 3 Day
FO_CABLE | - | - | 901452090 | DO | 3 | 1 | 2023PM_Mntr Leak Current JB12-15_OD 3Day
FO_CABLE | - | - | 901452091 | DO | 3 | 4 | 2023PM_Repl.JB18 LB-bad connect.-OD3days
FO_CABLE | - | - | 901452076 | DO | 1 | 3 | 2023PM_Replace JB01 LB bolts x6-OD 1 Day
FO_CABLE | - | - | 901452080 | DO | 1 | 4 | 2023PM_Install all LB # labels-OD 1 Day
CORRECT | REM | - | 901445458 | DO | 5 | 4 | CB overhaul required. Pole radial seals.
CORRECT | REM | - | 901451461 | DO | 3 | 4 | Comms fail alarm - replace relay. Replac
| REM |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,GRL100
FOFAULT | TRL | - | 901450768 | DO | 3 | 4 | Comms fail alarm on diff relay
GENERATOR TRANSFORMER - ROSSPILE T131 [Rosspile SF (R01)]
TO-24-ROP-T131-01 Window: Nov Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
N/A | ROP | 110 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
N/A | ROSS | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - SEALROCK T103 [Sealrock SK3]
TO-24-SK-T103-01 Window: Jun Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
AMCAB | SK | 110 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
OPT | SK | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110KV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - SEALROCK T104 [Sealrock SK4]
TO-24-SK-T104-01 Window: Jul - Sep Duration: (44 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | SK | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110KV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - SHELLYBANKS T2014 [Poolbeg PB14]
TO-24-SHL-T2014-01 Status: Unscheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
OS | SHL | 220-DT | ESBN TO CONFIRM | DO | 5 | 4 | 220kV Sect / Dist Ordinary Service
AMCAB | SHL | cable | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
| SHL |  |  | DO | 2 |  | P1 Protection maintenance of 7SA513
N/A | - | - | N/A |  | 5 | N/A | Total Maintenance Outage Duration Requested
OPTSEC2 | SHL | 220-DL | 901396980 | DO | 1 | 4 | 220kV Sect / Dist Operational Test
GENERATOR TRANSFORMER - SHELLYBANKS T2015 [Poolbeg PB15]
TO-24-SHL-T2015-01 Window: Sep Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OSSEC220 | SHL | 220-DT | 901130137 | DO | 5 | 1 | 220kV Sect / Dist Ordinary Service
| SHL |  |  | DO | 2 |  | P2 Protection maintenance of 7SA513
AIC4/2A | SHL | - | 901281053 | DO | 1 | 1 | Cable Insp. 400 & 220kV Feeder XLPE
GENERATOR TRANSFORMER - SHELLYBANKS T2016 [Poolbeg PB16]
TO-24-SHL-T2016-01 Window: Oct Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OPTSEC2 | SHL | 220-DL | 901042993 | DO | 5 | 1 | 220kV Sect / Dist Operational Test
GENERATOR TRANSFORMER - SLIABH BAWN T132 [Sliabh Bawn WF (SB1)]
TO-24-SLB-T132-02 Status: Unscheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| SLB |  |  | DO | 2 |  | P2 Protection maintenance of BOC (M1),7SA612
GENERATOR TRANSFORMER - SLIEVECALLAN T121 [Knockalassa WF (KD1)]
TO-24-SLC-T121-02 Window: Jul Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| SLC |  |  | DO | 2 |  | P3 Protection maintenance of BOC (M1),7SA611,RET615,7SJ804
GENERATOR TRANSFORMER - SLIEVECALLAN T122 [Boolinrudda WF (RD1)]
TO-24-SLC-T122-02 Window: Jul Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| SLC |  |  | DO | 2 |  | P3 Protection maintenance of BOC (M1),7SA611,RET615,7SJ804
SECTIONALISING DISCONNECT - SRAHNAKILLY 110SA1 [Oweninny WF (OY2)]
TO-24-SKY-110SA1-02 ISO week: 15mo - 17fr Date: 08 Apr - 26 Apr Duration: 19 Days (15 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | SKY | 110-SA1 | ESBN TO CONFIRM | DO | 2 | 4 | 110kV Sect / Dist Ordinary Service (including busbar disconnects of all bays that are connected to the busbar section that is on outage)
SECTIONALISING DISCONNECT - SRAHNAKILLY 110SA2 [Oweninny WF (OY2)]
TO-24-SKY-110SA2-02 ISO week: 15mo - 17fr Date: 08 Apr - 26 Apr Duration: 19 Days (15 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
OS | SKY | 110-SA2 | ESBN TO CONFIRM | DO | 2 | 4 | 110kV Sect / Dist Ordinary Service (including busbar disconnects of all bays that are connected to the busbar section that is on outage)
OSSEC110 | SKY | 110-SA1-2 | 901310005 | DO | 1 | 1 | 110kV Sect / Dist Ordinary Service (including busbar disconnects of all bays that are connected to the busbar section that is on outage)
GENERATOR TRANSFORMER - SRAHNAKILLY T131 [Oweninny WF (OY1)]
TO-24-SKY-T131-03 ISO week: 15mo - 17fr Date: 08 Apr - 26 Apr Duration: 19 Days (15 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | SKY | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service
| SKY |  |  | DO | 2 |  | P3 Protection maintenance of BOC (M1),7SA611,RET630,7SJ804
110kV FEEDER - STRATFORD tee CARLOW [Liffey LI1/LI2/LI4]
TO-24-STR,T-CLW-1-04 Window: May - Jun Duration: (19 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 15 | N/A | Total Maintenance Outage Duration Requested
OPT | CLW | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
FO_COND | EST II | PLS | 901472696 | DO | 2 | 4 | 1[169-170]Conductor Samp R or L Phase
FO_COND | EST II | PLS | 901472697 | DO | 2 | 4 | 1[90-91]Conductor Sampling R or L Phase
FO_COND | EST II | PLS | 901472699 | DO | 2 | 4 | 1[127-128]Conductor Sampling R or L Phas
FO_COND | EST II | PLS | 901472780 | DO | 2 | 4 | 1[153-154]Conductor Sampling R or L Phas
FO_COND | EST II | PLS | 901472781 | DO | 2 | 4 | 1[71-72]Conductor Sampling R or L Phase
FO_COND | EST II | PLS | 901472782 | DO | 2 | 4 | 1[5-6]Conductor Sampling R or L Phase
FOSTRHW | EST II | PLS | 901500728 | DO | 1 | 4 | 2023HP-1[94]Check Structure (Top Rot)S2
FO_MISC | EST II | PLS | 901500732 | DO | 1 | 4 | 2023HP-1[160]Off Plumb (Poles)
110kV FEEDER - STRATFORD tee POLLAPHUCA [Liffey LI1/LI2/LI4]
TO-24-STR,T-PA-1-04 Window: May - Jun Duration: (19 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 20 | N/A | Total Maintenance Outage Duration Requested
FO_MISC | - | - | 901085001 | DO | 2 | 1 | 2019HP-1[13]Off Plumb -plumb poles
FO_STDMG | EST II | PLS | 901454006 | DO | 3 | 4 | 2023LP-1[14]Crossarm Treat/Replace
FO_MISC | EST II | PLS | 901454007 | DO | 1 | 4 | 2023LP-1[11]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454008 | DO | 1 | 4 | 2023LP-1[17]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454009 | DO | 1 | 4 | 2023LP-1[28]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454010 | DO | 1 | 4 | 2023LP-1[34]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454011 | DO | 1 | 4 | 2023LP-1[37]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454012 | DO | 1 | 4 | 2023LP-1[41]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454013 | DO | 1 | 4 | 2023LP-1[43]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454014 | DO | 1 | 4 | 2023LP-1[49]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454015 | DO | 1 | 4 | 2023LP-1[51]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454016 | DO | 1 | 4 | 2023LP-1[57]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454017 | DO | 1 | 4 | 2023LP-1[59]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454018 | DO | 1 | 4 | 2023LP-1[61]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454019 | DO | 1 | 4 | 2023LP-1[64]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901504153 | DO | 1 | 4 | 2023HP-1[49]Repl./Retire pole butts
| PA |  |  | DO | 2 |  | P1 Protection maintenance of 7SA511
OPTMO110 | POL | - | 901300349 | DO | 1 | 3 | 110kV MO Cubicle Operational Test
GENERATOR TRANSFORMER - TAWNAGHMORE T1/T2 [Tawnaghmore TP1]
TO-24-TAW-T1/T2-01 Window: Jul Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
| TAW |  |  | DO | 2 |  | P1 Protection maintenance of 7SA611,BOC(M1)
FO_CABLE | TAW | 110 | 901465088 | DO | 2 | 1 | 2023PM_Clean CSE SO Ins in Stn_OD 1Day
FO_CABLE | TAW | 110 | 901465090 | DO | 2 | 4 | 2023PM_Repl S-Ph SVL @ Trafo End OD 1Day
FO_CABLE | TAW | 110 | 901465089 | DO | 1 | 4 | 2023PM_Clean CSE SO Ins @ Trafo_OD 1 Day
OPT | TAW | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - TAWNAGHMORE T3 [Tawnaghmore TP3]
TO-24-TAW-T3-01 Window: Jul Duration: (1 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | TAW | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - TULLABRACK tee BOOLTIAGH
TO-24-TBK,T-BOL-1-01 Window: Aug Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 8 | N/A | Total Maintenance Outage Duration Requested
| BOL |  |  | DO | 2 |  | P1 Protection maintenance of 7SA612,GRZ100
OPTSF61 | BOL | - | 901396731 | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
CORRECT | BOO | - | 901469811 | DO | 8 | 4 | Booltiagh Moneypoint Tullabrack Pro Main
FOSTRHW | WST | LIM | 901500640 | DO | 1 | 4 | 2023HP-1[75]Check Structure (Top Rot)-S2
FOSTRHW | WST | LIM | 901500641 | DO | 1 | 4 | 2023HP-1[79]Check Structure (Top Rot)-S2
110kV FEEDER - TULLABRACK tee MONEYPOINT GIS
TO-24-TBK,T-MP GIS-1-01 Window: Aug Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
FO_MISC | - | - | 901168382 | DO | 2 | 3 | 2020LP-1[99]Off Plumb (4 Heads off)
FO_MISC | - | - | 901370581 | DO | 2 | 4 | 2022HP-1[125]Off Plumb Plumb IMP Poleset
AMCAB | MP~ | - | ESBN TO CONFIRM | DO | 2 | 4 | Annual Insp. 110kV Feeder XLPE Cable
OPT | MP~ | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV GIS Cubicle Operational Test
| TBK |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612, GRZ100
FOSTRHW | WST | LIM | 901503849 | DO | 1 | 4 | 2023HP-1[118]Check Structure (Top Rot)S2
GENERATOR TRANSFORMER - TURLOUGH HILL T2001/2 [Turlough Hill TH1/TH2]
TO-24-TH-T2001/2-02 ISO week: 10su - 11we Date: 10 Mar - 13 Mar Duration: 4 Days (3 WD) Status: Scheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
AIFFC_S | TH~ | 220 | 901432315 | DO | 2 | 1 | Annual Insp. 400 & 220 Station OF Cable
GENERATOR TRANSFORMER - TURLOUGH HILL T2003/4 [Turlough Hill TH3/TH4]
TO-24-TH-T2003/4-02 ISO week: 9su - 10we Date: 03 Mar - 06 Mar Duration: 4 Days (3 WD) Status: Scheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| TH |  |  | DO | 2 |  | P2 Protection maintenance of S,R1Z23b,RT22b
AIFFC_S | TH~ | 220 | 901432318 | DO | 2 | 1 | Annual Insp. 400 & 220 Station OF Cable
GENERATOR TRANSFORMER - TYNAGH T2001/2 [Tynagh TYC]
TO-24-TY-T2001/2-02 Window: Jun Duration: (1 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | TYN | 220 | ESBN TO CONFIRM | DO | 1 | 4 | 220kV SF6 Cubicle Operational Test
COUPLER/SECTIONALISING CB - UGGOOL 110SA1-2CB [Seecon WF (SO1)]
TO-24-UGL-110SA1-2CB-01 Window: Jul Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | UGL | 110-SA1-2 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV GIS Cubicle Operational Test
GENERATOR TRANSFORMER - UGGOOL T131 [Uggool WF (UG1)]
TO-24-UGL-T131-01 Window: Jul Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
AICX110F | UG | 110 | 901212057 | DO | 2 | 1 | Cable Insp. 110kV XLPE
GENERATOR TRANSFORMER - UGGOOL T132 [Seecon WF (SO1)]
TO-24-UGL-T132-02 Window: Jul Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
AICX110F | UG | 110 | 901212058 | DO | 2 | 1 | Cable Insp. 110kV XLPE
GENERATOR TRANSFORMER - UGGOOL T134 [Seecon WF (SO1)]
TO-24-UGL-T134-01 Window: Jul Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
AICX110F | UG | 110 | 901212059 | DO | 2 | 1 | Cable Insp. 110kV XLPE
GENERATOR TRANSFORMER - WOODHOUSE T122 [Woodhouse WF (WS1)]
TO-24-WOH-T122-01 Window: May Duration: (4 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | WOO | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test