## OACA
110kV FEEDER - AGANNYGAL DERRYBRIEN
TO-25-AGL-DYN-1-01 Window: Jun Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
FO_MISC | - | - | 901371056 | DO | 1 | 3 | 2022HP-1[3]Off Plumb
FOINSHW | - | - | 901371059 | DO | 1 | 3 | 2022HP-1[8]Insulator&HW Check (Aux. HW)
220kV FEEDER - AGHADA HADWELL [Aghada Battery AD4, AD5]
TO-25-AD-HWL-1-01 Window: Sep Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
AMCAB | CABLE | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
220kV FEEDER - AGHADA LONG POINT [Aghada AD2]
TO-25-AD-LPT-1-01 Window: Sep Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
| AD~ | - | ESBN TO CONFIRM | DO | 1 | 4 | Replace flexible current carrying straps
| AD~ | - | ESBN TO CONFIRM | DO | 1 | 4 | Replace flexible current carrying straps
| AD~ | - | ESBN TO CONFIRM | DO | 1 | 4 | Replace upper mechanism drive rods
| AD~ | - | ESBN TO CONFIRM | DO | 1 | 4 | Replace upper mechanism drive rods
| LPT | - | ESBN TO CONFIRM | DO | 1 | 4 | Replace flexible current carrying straps
| LPT | - | ESBN TO CONFIRM | DO | 1 | 4 | Replace flexible current carrying straps
| LPT | - | ESBN TO CONFIRM | DO | 1 | 4 | Replace upper mechanism drive rods
| LPT | - | ESBN TO CONFIRM | DO | 1 | 4 | Replace upper mechanism drive rods
GENERATOR TRANSFORMER - AGHADA ST101 [Aghada Battery AD3]
TO-25-AD-ST101-01 ISO week: 15mo - 16mo Date: 07 Apr - 14 Apr Duration: 8 Days (6 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | AD~ | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - AGHADA T2011/12 [Aghada AT11; Aghada AT12]
TO-25-AD-T2011/12-02 ISO week: 13mo - 14tu Date: 24 Mar - 01 Apr Duration: 9 Days (7 WD) Status: Proposed
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
AMCAB | AD~ | 220 | ESBN TO CONFIRM | DO | 2 | 4 | Annual Insp. 400 & 220 Station OF Cable
FO_CABLE | AD~ | - | 901247447 | DO | 1 | 1 | 2021PM_Monitor oil pressure levels withi
FO_CABLE | AD~ | 220 | 901302176 | DO | 1 | 2 | 2022PM_Replacement of corroded earthing
FO_CABLE | AD~ | 220 | 901302177 | DO | 1 | 2 | 2022PM_Replacement of corroded bolts on
FO_CABLE | AD~ | 220 | 901302178 | DO | 1 | 1 | 2022PM_Replace Low Pressure & Differenti
FM | AD~ | 220 | ESBN TO CONFIRM | DO | 1 | 1 | HV Pressure Vessel Inspection
GENERATOR TRANSFORMER - AGHADA T2014 [Aghada AT14]
TO-25-AD-T2014-02 ISO week: 14tu - 15tu Date: 01 Apr - 08 Apr Duration: 8 Days (6 WD) Status: Proposed
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
| AD |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612
FO_CABLE | AD~ | - | 901246243 | DO | 5 | 1 | 2021PM_Replace S-Phase differential rela
AMCAB | AD~ | 220 | ESBN TO CONFIRM | DO | 2 | 4 | Annual Insp. 400 & 220 Station OF Cable
FO_CABLE | AD~ | - | 901167032 | DO | 1 | 1 | Clean CSE stand-off insulators in Aghada
GENERATOR TRANSFORMER - ARDNACRUSHA GIS T101 [Ardnacrusha AA1]
TO-25-AA GIS-T101-01 Window: Aug Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OSGIS110 | AA~ | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110KV GIS Cubicle Ordinary Service
CA_110 | AA~ | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV CUBICLE CONDITION ASSESSMENT
| AA~ | 110 | 901263781 | DO | 2 | 4 | 2021PM: Repair damaged connection termin
GENERATOR TRANSFORMER - ARDNACRUSHA GIS T102 [Ardnacrusha AA2]
TO-25-AA GIS-T102-01 ISO week: 18mo - 18fr Date: 28 Apr - 02 May Duration: 5 Days (5 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OSGIS110 | AA~ | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110KV GIS Cubicle Ordinary Service
CA_110 | AA~ | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV CUBICLE CONDITION ASSESSMENT
| AA~ | 110 | 901588073 | DO | 2 | 4 | 2024PM_Inves T102 term discharge_OD2Days
GENERATOR TRANSFORMER - ARDNACRUSHA GIS T103 [Ardnacrusha AA3]
TO-25-AA GIS-T103-01 Window: Sep Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OSGIS110 | AA~ | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110KV GIS Cubicle Ordinary Service
CA_110 | AA~ | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV CUBICLE CONDITION ASSESSMENT
GENERATOR TRANSFORMER - ARDNACRUSHA GIS T104 [Ardnacrusha AA4]
TO-25-AA GIS-T104-01 Window: May Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OSGIS110 | AA~ | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110KV GIS Cubicle Ordinary Service
CA_110 | AA~ | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV CUBICLE CONDITION ASSESSMENT
COUPLER/SECTIONALISING CB - ATHEA 110SA1-2CB [Beenanaspuck & Tobe... WF/Batt]
TO-25-ATE-110SA1-2CB-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
| ATE |  |  | DO | 2 |  | P1 Protection maintenance of 7SJ611
OPT | ATE | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - ATHEA DROMADA [Dromada WF (DR1)]
TO-25-ATE-DRO-1-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | ATE | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - ATHEA KNOCKANURE [Athea / Beena&Tob / Dromada WF]
TO-25-ATE-KNR-1-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| - | - | 901576409 | DO | 5 | 1 | 2024CM_R-Phase short to GIS Pot_OD 1Week
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
FO_CABLE | - | - | 901423890 | DO | 2 | 3 | 2023CM_Install bridging SVL's at GIS ter
| - | - | 901578656 | DO | 2 | 4 | Replace Pole 19
| - | - | 901578657 | DO | 2 | 4 | Replace Pole No.21
| - | - | 901579020 | DO | 2 | 4 | Replace Pole No.22
OS | ATE | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
CA_110 | ATE | - | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
OS | KNR | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service
CA_110 | KNR | - | ESBN TO CONFIRM | DO | 3 | 4 | 110KV CUBICLE CONDITION ASSESSMENT
GENERATOR TRANSFORMER - ATHEA T121 [Athea WF (AH1)]
TO-25-ATE-T121-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
FO_CABLE | ATE | 110 | 901452092 | DO | 2 | 3 | 2023PM_Install BL Shrinks-OD 2 Days
110kV FEEDER - ATHEA TOBERTOREEN [Beenanaspuck & Tobe... WF/Batt]
TO-25-ATE-TOB-1-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | ATE | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - AUGHINISH SEALROCK 3 [Sealrock SK3]
TO-25-AUG-SK-3-01 Window: Jul - Aug Duration: (15 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
CORRECT | AUG | - | 901445480 | DO | 8 | 3 | CB spring charge AC supply mod required
CORRECT | AUG | - | 901445481 | DO | 8 | 3 | Replace CB HV flange bolts
CORRECT | AUG | - | 901445482 | DO | 8 | 1 | SF6 densimeter isolation plunger require
OPT | AUG | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
| Cable | - | 901546945 | DO | 2 | 4 | 2024CM_Repl. CSE SO's@Aughinish_OD2 Days
| Cable | - | 901555568 | DO | 2 | 4 | 2024CM_Pepl. CSE SO's@Sealrock_OD 2 Days
110kV FEEDER - AUGHINISH SEALROCK 4 [Sealrock SK4]
TO-25-AUG-SK-4-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OPT | AUG | - | 901542320 | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
| Cable | - | 901650124 | DO | 5 | 4 | 2024PM_Repair Sheath Fault_T Ph_OD1Week
| Cable | - | 901650125 | DO | 5 | 4 | 2024PM_Repair Sheath Fault_S Ph_OD1Week
| Cable | - | 901650126 | DO | 5 | 4 | 2024PM_Repair Sheath Fault_R Ph_OD1Week
110kV FEEDER - BALLYNAHULLA CORDAL [Cordal 1/2 WF (DL1/DL2)]
TO-25-BYH-CDL-1-01 Window: Aug Duration: (15 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 15 | N/A | Total Maintenance Outage Duration Requested
| - | - | 901582022 | DO | 7 | 1 | 2024PM_Repair at JB06_High Leakage_OD1Wk
| - | - | 901582023 | DO | 7 | 1 | 2024PM_Repair_JB04/5_High Leakage_OD1Wk
| - | - | 901581999 | DO | 2 | 1 | 2024PM_Raise JB04 LB Chamber Lid_OD2Days
| - | - | 901582020 | DO | 2 | 1 | 2024PM_Raise JB06 LB Chamber Lid_OD2Days
OS | BYH | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV GIS Cubicle Ordinary Service
CA_110 | BYH | - | ESBN TO CONFIRM | DO | 3 | 4 | 110KV CUBICLE CONDITION ASSESSMENT
OS | CDL | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| CDL | - | 901606273 | DO | 3 | 1 | H2 Sf6 Leak Repair
| CDL | - | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 Leaks, DOF required
CA_110 | CDL | - | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
| CDL | - | 901606272 | DO | 1 | 1 | H2 Sf6 Leak Investigation
110kV FEEDER - BALLYVOUSKILL COOMATAGGART [Grousemount WF (GD1)]
TO-25-BVK-COT-1-01 Window: Jun - Jul Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
FO_CABLE | - | - | 901468879 | DO | 5 | 3 | 2023PM_Water ingress in CB link box @ JB33 - raise or relocate.
FO_CABLE | - | - | 901468941 | DO | 2 | 3 | 2023PM_Replace all SVL's in JB33 link box - water logged and poor readings.
OS | BVK | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service
AMCAB | CABLE | - | ESBN TO CONFIRM | DO | 5 | 4 | Cable Insp. 110kV XLPE (BALLYVOUSKILL SECTION 1/3)
N/A | CABLE | - | ESBN TO CONFIRM | DO | 5 | 4 | Cable Insp. 110kV XLPE (COOMATAGGART SECTION 1/3)
OPT | COT | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - BARRYMORE tee CAHIR
TO-25-BAR,T-CAH-1-01 ISO week: 7mo - 9fr Date: 10 Feb - 28 Feb Duration: 19 Days (15 WD) Status: Scheduled
N/A | - | - | N/A | DO | 12 | N/A | Total Maintenance Outage Duration Requested
FO_MISC | - | - | 901170978 | DO | 2 | 1 | 2020HP-1[22-23]Air Craft Sphere Bird Div
FO_INSUL | - | - | 901385039 | DO | 2 | 3 | Insulator off Plumb. Pole No. 227
FO_MISC | - | - | 901368960 | DO | 1 | 3 | 2022HP-1[120]Off Plumb (Re-plumb poles)
FO_MISC | - | - | 901368961 | DO | 1 | 3 | 2022HP-1[121]Off Plumb (Re-plumb poles)
FO_COND | - | - | 901519316 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 22]C/Ph Repl. Deadend 3 Months. Response: 3 Months. Due: 12-Apr-2024
FO_COND | - | - | 901519317 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 22]C/Ph Repl. Deadend 1 Months. Response: 1 Month. Due: 12-Feb-2024
FO_COND | - | - | 901519318 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 22]C/Ph Repl. Jumper 1 Months. Response: 1 Month. Due: 12-Feb-2024
FO_COND | - | - | 901519319 | DO | 1 | 1 | HOTSPOT - 2023IR[23-24]L/Ph Repl Midspan Immediate. Response: Immediately. Due: Immediately
FO_COND | - | - | 901519320 | DO | 1 | 1 | HOTSPOT - 2023IR[53-54]C/Ph Repl Midspan Immediate. Response: Immediately. Due: Immediately
FO_COND | - | - | 901519321 | DO | 1 | 1 | HOTSPOT - 2023IR[62-63]L/Ph Repl. Midspan. Response: 6 Months. Due: 12-Jul-2024
FO_COND | - | - | 901519322 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 63]R/Ph Repl. Deadend. Response: 3 Months. Due: 12-Apr-2024
FO_COND | - | - | 901519323 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 63]L/Ph Repl. Deadend. Response: 1 Month. Due: 12-Feb-2024
FO_COND | - | - | 901519324 | DO | 1 | 1 | HOTSPOT - 2023IR[63-64]R/Ph Repl. Midspan. Response: 3 Months. Due: 12-Apr-2024
FO_COND | - | - | 901519325 | DO | 1 | 1 | HOTSPOT - 2023IR[63-64]C/Ph Repl. Midspan. Response: 3 Months. Due: 12-Apr-2024
FO_COND | - | - | 901519327 | DO | 1 | 1 | HOTSPOT - 2023IR[130-131]C/Ph Repl Midspan. Response: 1 Month. Due: 12-Feb-2024
FO_COND | - | - | 901519328 | DO | 1 | 1 | HOTSPOT - 2023IR[181-182]C/Ph Repl Midspan. Response: 3 Months. Due: 12-Apr-2024
FO_COND | - | - | 901519329 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 181]L/Ph Repl. Deadend. Response: 1 Month. Due: 12-Feb-2024
OSSF6110 | CAH | - | 901300801 | DO | 4 | 2 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| CAH | - | 901543243 | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
CA_110 | CAH | - | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment
FO_MISC | STH | CK | 901500688 | DO | 1 | 4 | 2023HP-1[205]Insulator 1xBroken disc R/P
FO_COND | STH | CK | 901519326 | DO | 1 | 1 | HOTSPOT - 2023IR[70-71]C/Ph Repl. Midspan. Response: 1 Month. Due: 12-Feb-2024
TO-25-BAR,T-CAH-1-02 ISO week: 7mo - 9fr Date: 10 Feb - 28 Feb Duration: 19 Days (15 WD) Status: Proposed
| BAR |  |  | DO | 2 |  | P3 Protection maintenance of 7SA511,REL521
| CAH |  |  | DO | 2 |  | P3 Protection maintenance of 7SA511, REl521
| STH | CK | 901643064 | DO | 1 | 4 | 2024HP-1[22-23]Air_Craft_Sphere_Bird_Sph
110kV FEEDER - BARRYMORE tee KNOCKRAHA
TO-25-BAR,T-KRA-1-01 ISO week: 9mo - 11fr Date: 24 Feb - 14 Mar Duration: 19 Days (15 WD) Status: Scheduled
N/A | - | - | N/A | DO | 20 | N/A | Total Maintenance Outage Duration Requested
FOSTRHW | - | - | 901298981 | DO | 5 | 2 | Replace Pole Set 227- Pole Rot
FOSTRHW | - | - | 901298983 | DO | 5 | 2 | Replace Pole Set 236. -Rotten
FOSTRHW | - | - | 901298990 | DO | 5 | 2 | Replace Pole No. 296. Rotten
FOSTRHW | - | - | 901397306 | DO | 5 | 3 | Replace Pole No. 248. Top Right Pole Rot
FO_MISC | - | - | 901253795 | DO | 1 | 2 | 2021HP-1[332]Off Plumb
FO_COND | - | - | 901519330 | DO | 1 | 3 | 2023IR[AT 287]R/Ph Repl. Deadend 3 Months
FO_COND | - | - | 901519331` | DO | 1 | 1 | 2023IR[AT 287]R/Ph Repl. Deadend Immediat
FO_COND | - | - | 901519332 | DO | 1 | 1 | HOTSPOT - 2023IR[286-287]R/Ph Rep Midspan. Response: Immediately. Due: Immediately
FO_COND | - | - | 901519333 | DO | 1 | 1 | HOTSPOT - 2023IR[286-287]L1/Ph Resistance Midspan. Response: Next Planned Maintenance. Due: Next Planned Maintenance
| BAR |  |  | DO | 2 |  | P3 Protection maintenance of 7SA511,REl521
OSSF6110 | KRA | - | 901396820 | DO | 5 | 1 | 110kV SF6 Cubicle Ordinary Service
CA_110 | KRA | - | 901396433 | DO | 3 | 3 | 110KV CUBICLE CONDITION ASSESSMENT
| KRA |  |  | DO | 2 |  | P3 Protection maintenance of 7SA511, REl521
FOSTRHW | STH | CK | 901503248 | DO | 1 | 4 | 2023HP-1[341]Check Structure (Top Rot)S2
FO_COND | STH | CK | 901519331 | DO | 1 | 1 | HOTSPOT - 2023IR[AT 278]L/Ph Repl Deadend . Response: Immediately. Due: Immediately
| STH | CK | 901545787 | DO | 1 | 4 | Climb to check Top Rot Pole no.240
| STH | CK | 901545788 | DO | 1 | 4 | Climb to check Top Rot, Pole no.242
| STH | CK | 901545791 | DO | 1 | 4 | Climb to check Top Rot, Pole no.243
| STH | CK | 901545792 | DO | 1 | 4 | Climb to check Top Rot, Pole no.244
| STH | CK | 901545795 | DO | 1 | 4 | Climb to check Top Rot, Pole no.245
| STH | CK | 901545797 | DO | 1 | 4 | OFF Plumb, Pole no.239- 3-4 heads
110kV FEEDER - BELLACORICK SRAHNAKILLY [Oweninny 1/2 WFs (OY1/OY2)]
TO-25-BK-SKY-1-01 Window: May Duration: (11 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 11 | N/A | Total Maintenance Outage Duration Requested
AMCAB | - | cable | ESBN TO CONFIRM | DO | 10 | 4 | Cable Insp. 110kV XLPE
OPT | BK~ | - | ESBN TO CONFIRM | DO | 2 | 4 | 110kV SF6 Cubicle Operational Test
| SKY | - | 901576521 | DO | 2 | 4 | FOMO DL / DE NOT MAINTAINED AS IT IS A P
OPT | SKY | - | ESBN TO CONFIRM | DO | 2 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - BLUNDELSTOWN T131
TO-25-BLU-T131-02 ISO week: 10tu - 10we Date: 04 Mar - 05 Mar Duration: 2 Days (2 WD) Status: Scheduled
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
| BLU | - | ESBN TO CONFIRM | DO | 2 | N/A | Cable Insp. 110kV XLPE
N/A | BLU | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
SECTIONALISING DISCONNECT - BOGGERAGH 110SA1 [Boggeragh 2 WF (BG2)]
TO-25-BGH-110SA1-01 Window: May Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | BGH | 110-SA1 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV Sect / Dist Operational Test
SECTIONALISING DISCONNECT - BOGGERAGH 110SA2 [Boggeragh 2 WF (BG2)]
TO-25-BGH-110SA2-01 Window: May Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | BGH | 110-SA2 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV Sect / Dist Operational Test
110kV FEEDER - BOGGERAGH CLASHAVOON [Boggeragh 1/2 WFs (BG1/BG2)]
TO-25-BGH-CLA-1-01 Window: May Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 6 | N/A | Total Maintenance Outage Duration Requested
| BGH | - | 901609571 | DO | 10 | 1 | Replace CB drive tubes + pole seals
OPT | BGH | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
AMCAB | Cable | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
OS | CLA | - | 901542689 | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service
| CLA | - | 901543250 | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
CORRECT | CLA | - | 901474431 | DO | 1 | 4 | O1- H3 CB light defect
| LINE | - | 901618432 | DO | 1 | 4 | Repair Broken Earth Pole Top No.58
GENERATOR TRANSFORMER - BOGGERAGH T121 [Boggeragh 1 WF (BG1)]
TO-25-BGH-T121-02 Window: May Duration: (10 WD) Status: Planned
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
| BGH | 110 | 901609595 | DO | 10 | 1 | Replace CB drive tubes + pole seals
GENERATOR TRANSFORMER - BOGGERAGH T132 [Boggeragh 2 WF (BG2)]
TO-25-BGH-T132-01 Window: May Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
OS | BGH | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
CA_110 | BGH | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
| BGH |  |  | DO | 2 |  | P1 Protection maintenance of 7SA612
110kV FEEDER - BOGTOWN MOUNTLUCAS
TO-25-BOT-MLC-1-02 Status: Unscheduled
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
N/A | BOT | 110 | ESBN TO CONFIRM | DO | 1 | 4 | Cable Inspection XLPE
N/A | BOT | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
N/A | MLC | 110 | ESBN TO CONFIRM | DO | 1 | 4 | Cable Inspection XLPE
N/A | MLC | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - BOOLTIAGH T121 [Booltiagh 1/2 WF (BT1/BT2)]
TO-25-BOL-T121-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | BOL | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
CA_110 | BOL | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
110kV FEEDER - BUFFY KNOCKRANNY [Ardderroo WF (UF1)]
TO-25-BUF-KNY-1-01 Window: May Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
AMCAB | CABLE | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
OPT | KNY | - | ESBN TO CONFIRM | DO | 2 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - BUFFY T131 [Ardderroo WF (UF1)]
TO-25-BUF-T131-01 Window: May Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
OPT | BUF | - | ESBN TO CONFIRM | DO | 2 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - CARRIGADROHID T103 [Lee LE3]
TO-25-CD-T103-02 ISO week: 17th - 18tu Date: 24 Apr - 29 Apr Duration: 6 Days (4 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
OS | CD~ | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| CD~ | 110 | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 Leaks, DOF required
110kV FEEDER - CARRIGDANGAN DUNMANWAY [Carrigdangan WF (XA1)]
TO-25-CGG-DMY-1-01 Window: May Duration: (7 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 7 | N/A | Total Maintenance Outage Duration Requested
AIC110D | - | cable | 901535620 | DO | 4 | 1 | Cable Insp. 110kV XLPE
OS | CGG | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service
OS | DMY | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| DMY | - | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 Leaks, DOF required
110kV FEEDER - CASTLEDOCKRELL LODGEWOOD [Castledockrell WF (CK1)]
TO-25-CDK-LWD-1-02 Window: Jun Duration: (4 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
| CDK |  |  | DO | 2 |  | P1 Protection maintenance of 7SA612
OS | LWD | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| LWD | - | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 Leaks, DOF required
| LWD |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612
110kV FEEDER - CATHALEENS FALL CLIFF [Erne ER1; Erne ER2]
TO-25-CF-CL-1-02 ISO week: 15mo - 15th Date: 07 Apr - 10 Apr Duration: 4 Days (4 WD) Status: Proposed
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
| CF |  |  | DO | 2 |  | P1 Protection maintenance of 7SA511
FOFAULT | CF~ | - | 901335734 | DO | 2 | 1 | H5 CB densimeter replacement.
OPTSF61 | CF~ | - | 901396673 | DO | 2 | 3 | 110kV SF6 Cubicle Operational Test
| NTH | LET | 901568582 | DO | 2 | 4 | 2024LP-1[31]Reposition Pole
| NTH | LET | 901568583 | DO | 2 | 4 | 2024LP-1[22]Replace Pole
GENERATOR TRANSFORMER - CATHALEENS FALL T103 [Erne ER3]
TO-25-CF-T103-01 Window: Jun - Jul Duration: (9 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 9 | N/A | Total Maintenance Outage Duration Requested
| CF |  |  | DO | 2 |  | P1 Protection maintenance of 7SA612 ,7UT513
OS | CF~ | 110 | 901542716 | DO | 5 | 1 | 110KV SF6 Cubicle Ordinary Service
CA_110 | CF~ | 110 | 901542021 | DO | 3 | 4 | 110kV CUBICLE CONDITION ASSESSMENT
GENERATOR TRANSFORMER - CATHALEENS FALL T104 [Erne ER4]
TO-25-CF-T104-01 ISO week: 17th - 19we Date: 24 Apr - 07 May Duration: 14 Days (9 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 9 | N/A | Total Maintenance Outage Duration Requested
| CF |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612
OSSF6110 | CF~ | 110 | 901396849 | DO | 5 | 1 | 110KV SF6 Cubicle Ordinary Service
CA_110 | CF~ | 110 | 901396488 | DO | 3 | 3 | 110KV CUBICLE CONDITION ASSESSMENT
GENERATOR TRANSFORMER - CLAHANE T122 [Clahane 1/2 WFs (CJ1/CJ2)]
TO-25-CLH-T122-01 Window: May Duration: (1 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
Customer Outage Request - 13 May
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | CLH | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - CLIFF T101 [Erne ER1]
TO-25-CL-T101-02 Window: May Duration: (8 WD) Status: Planned
N/A | - | - | N/A | DO | 8 | N/A | Total Maintenance Outage Duration Requested
OS | CL~ | 110 | ESBN TO CONFIRM | DO | 5 | 1 | 110KV SF6 Cubicle Ordinary Service
CORRECT | CL~ | - | 901230085 | DO | 2 | 1 | Repair corrosion issue on CTs
GENERATOR TRANSFORMER - CLIFF T102 [Erne ER2]
TO-25-CL-T102-01 ISO week: 15mo - 16tu Date: 07 Apr - 15 Apr Duration: 9 Days (7 WD) Status: Proposed
N/A | - | - | N/A | DO | 7 | N/A | Total Maintenance Outage Duration Requested
CORRECT | CL~ | - | 901314311 | DO | 5 | 3 | Visually Inspect CT's bellow pipework
CORRECT | CL~ | - | 901314313 | DO | 5 | 1 | Replace SF6 Pressure gauge
OS | CL~ | 110 | ESBN TO CONFIRM | DO | 5 | 1 | 110KV SF6 Cubicle Ordinary Service
SECTIONALISING DISCONNECT - CLOGHBOOLA 110SA1 [Cloghboola WF (CL1)]
TO-25-CBA-110SA1-01 Window: Jul Duration: (12 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | CBA | SA1 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV Sect / Dist Operational Test
SECTIONALISING DISCONNECT - CLOGHBOOLA 110SA2 [Cloghboola WF (CL1)]
TO-25-CBA-110SA2-01 Window: Jul Duration: (12 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | 110-SA2 | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | CBA | SA2 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV Sect / Dist Operational Test
GENERATOR TRANSFORMER - CLOGHBOOLA T131 [Cloghboola WF (CL1)]
TO-25-CBA-T131-01 Window: Jul Duration: (12 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| CBL |  |  | DO | 2 |  | P1 Protection maintenance of 7SJ804 ,7SA611
110kV FEEDER - CLOGHBOOLA TRIEN [Cloghboola WF (CL1)]
TO-25-CBA-TRI-1-01 Window: Jul Duration: (12 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 12 | N/A | Total Maintenance Outage Duration Requested
FO_CABLE | - | - | 901423790 | DO | 5 | 3 | 2023PM_Testing after correctives (LB cha
FO_CABLE | - | - | 901423791 | DO | 5 | 3 | 2023PMWater ingress into link box at JB08
FO_CABLE | - | - | 901423792 | DO | 5 | 3 | 2023PMWater ingress into link box at JB10
FO_CABLE | CBA | - | 901155245 | DO | 5 | 1 | Clean CSE stand-off insulators in Cloghb
FO_CABLE | CBA | - | 901155246 | DO | 5 | 1 | Water ingress into link box at JB12 - ra
OPT | CBA | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
OPT | TRI | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - CLOGHER MULREAVY [Mulreavy 1/2 WFs (MB1/MB2)]
TO-25-CLO-MRY-1-01 Window: May Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
AICX110S | CABLE | 110 | 901129091 | DO | 4 | 4 | Cable Insp. 110kV XLPE
OSGIS110 | CLO | - | 901300588 | DO | 4 | 2 | 110kV GIS Cubicle Ordinary Service
220kV FEEDER - CLONIFFEEN SHANNONBRIDGE [Shannonbridge Batts SI1/SI2]
TO-25-CFN-SH-1-01 ISO week: 18mo - 18fr Date: 28 Apr - 02 May Duration: 5 Days (5 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
AMCAB | - | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
OS | SH~ | - | ESBN TO CONFIRM | DO | 4 | 4 | 220kV SF6 Cubicle Ordinary Service
110kV FEEDER - CLONKEEN COOMAGEARLAHY [Coomagearlahy 1/2/3 Glanlee WF]
TO-25-CKN-CGL-1-01 Window: Jun Duration: (6 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 6 | N/A | Total Maintenance Outage Duration Requested
| - | - | 901595911 | DO | 1 | 1 | 2024PM_Clean CSE SO Ins_CLKN SS_OD 1Day
| - | - | 901595912 | DO | 1 | 1 | 2024PM_Clean CSE SO Ins_CLK LCIM_OD 1Day
| - | - | 901596113 | DO | 1 | 1 | 2024PM_Clean CSE SO Ins_COM LCIM_OD 1Day
| - | - | 901596164 | DO | 1 | 1 | 2024PM_Clean CSE SO Ins_CLKN STN_OD 1Day
OPT | CGL | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
OS | CKN | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| CKN | - | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 Leaks, DOF required
CA_110 | CKN | - | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
110kV FEEDER - COOLNANOONAGH KILPADDOGE [Kelwin WF/Bat/Diesel Cap]
TO-25-CNO-KPG-1-01 Window: Jun Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
| KPG |  |  | DO | 2 |  | P3 Protection maintenance of 7SA611,7SJ804
AMCAB | KPG | - | ESBN TO CONFIRM | DO | 2 | 4 | Annual Insp. 110kV Feeder XLPE Cable
OPT | KPG | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - COOMAGEARLAHY GLANLEE [Glanlee WF (GLC)]
TO-25-CGL-GAE-1-01 Window: Jun Duration: (6 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | CGL | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - COOMAGEARLAHY T121 [Coomagearlahy 3 WF (CG3)]
TO-25-CGL-T121-01 Window: Jun Duration: (6 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
CORRECT | CGL | 110 | 901323272 | DO | 3 | 2 | Carry out loss of AC supply mod
SECTIONALISING DISCONNECT - COOMATAGGART 110SA1
TO-25-COT-110SA1-01 Window: Jun - Jul Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
N/A | COT | 110-SA1 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV Sect / Dist Operational Test
SECTIONALISING DISCONNECT - COOMATAGGART 110SA2
TO-25-COT-110SA2-01 Window: Jun - Jul Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
N/A | COT | 110-SA2 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV Sect / Dist Operational Test
GENERATOR TRANSFORMER - COOMATAGGART T132 [Grousemount WF (GD1)]
TO-25-COT-T132-01 Window: Jun - Jul Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | COT | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
SECTIONALISING DISCONNECT - CORDAL 110SA1
TO-25-CDL-110SA1-01 Window: Aug Duration: (15 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | CDL | 110-SA1 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV Sect / Dist Operational Test
SECTIONALISING DISCONNECT - CORDAL 110SA2
TO-25-CDL-110SA2-01 Window: Aug Duration: (15 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | CDL | 110-SA2 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV Sect / Dist Operational Test
GENERATOR TRANSFORMER - CORDAL T132 [Cordal 1/2 WF (DL1/DL2)]
TO-25-CDL-T132-01 Window: Aug Duration: (15 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | CDL | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - CORDERRY GARVAGH [Garvagh 1/2 WFs (GH1/GH2)]
TO-25-CDY-GRV-1-01 Window: Jul Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
| - | - | 901646801 | DO | 4 | 4 | 2024HP-1[26]Replace_Pole_Top_Rot
FO_CABLE | - | - | 901452521 | DO | 1 | 3 | 2023PM_Inst.LCIM bonding cbl ties;OD1Day
| - | - | 901646785 | DO | 1 | 4 | 2024HP-1[11]Bird_Nests_(Remove)
| - | - | 901646802 | DO | 1 | 4 | 2024HP-1[5]Replace_Pole_Top_Rot
OPT | CDY | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
220kV FEEDER - CORDUFF HUNTSTOWN [Huntstown HN2]
TO-25-CDU-HN-1-01 Status: Unscheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
AMCAB | CABLE | - | 901542864 | DO | 2 | 4 | Cable Insp. 220kV Feeder XLPE
OS | CDU | - | ESBN TO CONFIRM | DO | 5 | 4 | 220kV SF6 Cubicle Ordinary Service
CA_110 | CDU | - | ESBN TO CONFIRM | DO | 3 | 4 | 220KV CUBICLE CONDITION ASSESSMENT
GENERATOR TRANSFORMER - CORDUFF T102 [Corduff Flexgen (FG2)]
TO-25-CDU-T102-01 Window: Sep Duration: (1 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
N/A | CDU | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV Cubicle Operational Test
GENERATOR TRANSFORMER - CUNGHILL T121 [Kingsmountain 1/2 WF (KGM/KG2)]
TO-25-CUN-T121-02 Window: Jun Duration: (6 WD) Status: Planned
N/A | - | - | N/A | DO | 6 | N/A | Total Maintenance Outage Duration Requested
| CUN | 110 | 901588594 | DO | 5 | 4 | Replace the pipework on the CB.
| CUN | 110 | 901595024 | DO | 5 | 4 | Repair corrosion issues on the drive
| CUN | 110 | 901595029 | DO | 5 | 4 | Replace corroded pole support bolts
OPT | CUN | 110 | ESBN TO CONFIRM | DO | 2 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - CUSHALING KILCUMBER [Cloncreen WF/Bat (OE1/OE2)]
TO-25-CUS-KIR-1-03 Window: Jun Duration: (2 WD) Status: Planned
| - | - | ESBN TO CONFIRM | DO | 2 | 3 | Cable Insp. 110kV XLPE
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
GENERATOR TRANSFORMER - CUSHALING T101 [Edenderry ED1]
TO-25-CUS-T101-03 Window: Jul Duration: (1 WD) Status: Planned
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
OPT | CUS | 110 | 901542471 | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - CUSHALING T103/5 [Edenderry ED3; Edenderry ED5]
TO-25-CUS-T103/5-01 Window: Jul - Aug Duration: (10 WD) Status: Planned
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
OS | CUS | 110 | 901542812 | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| CUS | 110 | 901543361 | DO | 5 | 1 | O-Ring Replacement to prevent SF6 leaks
| CUS |  |  | DO | 2 |  | P1 Protection maintenance of 7SA612
GENERATOR TRANSFORMER - DERRYCARNEY T132 [Lumcloon Batteries LU1 & LU2]
TO-25-DEY-T132-01 Window: Apr Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OSGIS110 | DEY | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV AIS Cubicle Ordinary Service
GENERATOR TRANSFORMER - DERRYIRON RHODE T1/T2 [Rhode RP1/RP2]
TO-25-DER-T1/T2-04 Window: May Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
FO_TIMB | - | - | 901332399 | DO | 1 | 3 | 60m[1-2]TimCut 110kV(Rural)
OPT | DER | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110KV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - DROMADA T121 [Dromada WF (DR1)]
TO-25-DRO-T121-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
OS | DRO | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service
| DRO | 110 | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 Leaks, DOF required
110kV FEEDER - DRUMKEEN MEENTYCAT [Meentycat WF (MCT)]
TO-25-DRM-MEE-1-01 Window: Jun Duration: (9 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 8 | N/A | Total Maintenance Outage Duration Requested
OS | DRM | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| DRM | - | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 Leaks, DOF required
CA_110 | DRM | - | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
| MEE | - | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 Leaks, DOF required
110kV FEEDER - DUNFIRTH tee DUNFIRTH
TO-25-DFR,T-DFR-1-03 Window: Aug Duration: (4 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
OS | DFR | - | 901542754 | DO | 4 | 1 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
110kV FEEDER - DUNFIRTH tee KINNEGAD [HP]
TO-25-DFR,T-KIN-1-03 Window: Nov Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
| DFR |  |  | DO | 2 |  | P1 Protection maintenance of 7SA511
FO_MISC | EST I | DUB | 901504685 | DO | 2 | 4 | O 1 REPLACE STAY DAMAGED {3} 16 HRS
HELI_HV | EST I | DUB | 901519006 | DO | 2 | 1 | HOTSPOT-2023 Replace jumper bolts, span 92/93, centre/ ph clean, within 6 months due 11.06.2023
| EST I | DUB | 901550047 | DO | 2 | 1 | 1[1-10]Earth wire Sampling
FO_COND | EST I | DUB | 901550048 | DO | 2 | 1 | 1[2-3]Conductor Sampling R or L Phase
FO_COND | EST I | DUB | 901550049 | DO | 2 | 1 | 1[50-51]Conductor Sampling R or L Phase
FO_COND | EST I | DUB | 901550050 | DO | 2 | 1 | 1[68-69]Conductor Sampling R or L Phase
FO_COND | EST I | DUB | 901550051 | DO | 2 | 1 | 1[93-94]Conductor Sampling R or L Phase
OS | KIN | - | 901542755 | DO | 4 | 1 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
CA_110 | KIN | - | 901542053 | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
| KIN |  |  | DO | 2 |  | P1 Protection maintenance of 7SA511
110kV FEEDER - DUNFIRTH tee RINAWADE [HP]
TO-25-DFR,T-RNW-1-02 Window: Aug Duration: (7 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 7 | N/A | Total Maintenance Outage Duration Requested
| DFR |  |  | DO | 2 |  | P1 Protection maintenance of 7SA511
FOSTRHW | EST I | DUB | 901430065 | DO | 2 | 3 | 2022LP-1[138]Replace Pole Right
FOSTRHW | EST I | DUB | 901430066 | DO | 2 | 3 | 2022LP-1[201]Replace Pole Right
FOSTRHW | EST I | DUB | 901471689 | DO | 2 | 4 | 2023LCA-1[201]Replace Pole (Top Rot)
FO_COND | EST I | DUB | 901550052 | DO | 2 | 1 | 1[135-136]Conductor Sampling R or L Phas
FO_COND | EST I | DUB | 901550053 | DO | 2 | 1 | 1[160-161]Conductor Sampling R or L Phas
FO_COND | EST I | DUB | 901550054 | DO | 2 | 1 | 1[214-215]Conductor Sampling R or L Phas
FO_COND | EST I | DUB | 901550055 | DO | 2 | 1 | 1[218-219]Conductor Sampling R or L Phas
FO_COND | EST I | DUB | 901550056 | DO | 2 | 1 | 1[240-241]Conductor Sampling R or L Phas
FO_COND | EST I | DUB | 901550057 | DO | 2 | 1 | 1[241-246]Earth wire Sampling
FO_COND | EST I | DUB | 901561664 | DO | 2 | 1 | 1[185-209]Conductor Sampling R or L Phas
FO_COND | EST I | DUB | 901561665 | DO | 2 | 1 | 1[220-225]Conductor Sampling R or L Phas
FO_COND | EST I | DUB | 901561666 | DO | 2 | 1 | 1[226-229]Conductor Sampling DC Right Si
FO_STDMG | EST I | DUB | 901430052 | DO | 1 | 3 | 2022LP-1[244] Remove Bolt from EW Peak
FO_MISC | EST I | DUB | 901430063 | DO | 1 | 3 | 2022LP-1[218]Insulator Aux Replace
| EST I | DUB | 901643203 | DO | 1 | 4 | 2024HP-1[212]Off_Plumb_Pole_&_Insulators
OS | RNW | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
CA_110 | RNW | - | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
| RNW |  |  | DO | 2 |  | P1 Protection maintenance of 7SA511
110kV FEEDER - ENNIS SLIEVECALLAN [Boolinrudda/Knockalassa WF]
TO-25-ENN-SLC-1-01 Window: Jul Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
AICX4/2F | ENN | - | 901212142 | DO | 2 | 1 | Cable Insp. 110kV XLPE
OPT | ENN | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
OPT | SLC | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
220kV FEEDER - FINGLAS HUNTSTOWN [Huntstown HNC]
TO-25-FIN-HN-1-01 ISO week: 18mo - 19th Date: 26 Apr - 08 May Duration: 13 Days (8 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 8 | N/A | Total Maintenance Outage Duration Requested
AMCAB | CABLE | - | ESBN TO CONFIRM | DO | 3 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
OSSF6220 | FIN | - | 901300960 | DO | 6 | 2 | 220kV SF6 Cubicle Ordinary Service
GENERATOR TRANSFORMER - GALLANSTOWN T133 [Gallanstown SF (IA01)]
TO-25-GLN-T133-02 ISO week: 13mo - 13fr Date: 24 Mar - 28 Mar Duration: 5 Days (5 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
|  |  |  | DO |  |  | Outage to facilitate IPP HV Maintenance and commissioning of the new Rathlockstown feeder from 9am 24th March to 5pm 28th March
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
| GLN | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
COUPLER/SECTIONALISING CB - GARROW 110SA1-2CB [Coomacheo WF (CZ1)]
TO-25-GRO-110SA1-2CB-01 Window: May Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
| GRO | 110SA1-2CB | 901543312 | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
GENERATOR TRANSFORMER - GARROW T122 [Coomacheo WF (CZ1)]
TO-25-GRO-T122-01 Window: May Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
| GRO | 110 | 901543363 | DO | 5 | 1 | O-Ring Replacement to prevent SF6 leaks
| GRO | 110 | 901596169 | DO | 4 | 4 | 2024PM_Repl. BL's (x6)_Water_OD3Days
| GRO | 110 | 901596168 | DO | 1 | 4 | 2024PM_Clean CSE SO Ins_GRW SS_OD 1Day
| GRO | 110 | 901596170 | DO | 1 | 4 | 2024PM_Install phase labelling within link box at T122 end of the cable section
| GRO | 110 | 901596171 | DO | 1 | 4 | 2024PM_Retest following Corr Wrks_OD1Day
GENERATOR TRANSFORMER - GARVAGH T121 [Garvagh 1/2 WFs (GH1/GH2)]
TO-25-GRV-T121-02 Window: Jul Duration: (6 WD) Status: Planned
N/A | - | - | N/A | DO | 6 | N/A | Total Maintenance Outage Duration Requested
| GAR |  |  | DO | 2 |  | P3 Protection maintenance of 7SA611 ,7SJ804
OSSF6110 | GRV | 110 | 901396852 | DO | 5 | 3 | 110kV SF6 Cubicle Ordinary Service
GENERATOR TRANSFORMER - GLANAGOW T2001 [Whitegate (WG1)]
TO-25-GGO-T2001-01 Window: Sep Duration: (4 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
OS | GGO | 220 | ESBN TO CONFIRM | DO | 4 | 4 | 220kV GIS Cubicle Ordinary Service
| GGO | 220 | 901650121 | DO | 3 | 4 | 2024PM_T2001 CSE Pipe Weep@Trafo_OD3Days
110kV FEEDER - GLENLARA KNOCKACUMMER [Knockacummer WF (KC1)]
TO-25-GLE-KCR-1-01 ISO week: 14mo - 15fr Date: 31 Mar - 11 Apr Duration: 12 Days (10 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
| - | - | 901588669 | DO | 5 | 4 | 2024PM_High leakage @JB07-9_S-Ph_OD4Days
| - | - | 901588670 | DO | 5 | 4 | 2024PM_High leakage @JB05-7_S-Ph_OD4Days
| - | - | 901588671 | DO | 5 | 4 | 2024PM_High leakage @JB05-7_R-Ph_OD4Days
| - | - | 901588666 | DO | 4 | 1 | 2024PM_Replace JB01 Link Box_OD 4Days
| - | - | 901588667 | DO | 4 | 1 | 2024PM_Replace JB03 Link Box_OD 4Days
| - | - | 901588668 | DO | 4 | 1 | 2024PM_Replace JB09 Link Box_OD 4Days
| - | - | 901588664 | DO | 3 | 4 | 2024PM_Raise JB03 LB Chamber_OD 2 Days
| - | - | 901588665 | DO | 2 | 1 | 2024PM_Repl BL's in Glenlara Stn_OD2Days
| - | - | 901588662 | DO | 1 | 4 | 2024PM_Clean SO Ins_Glenlara_OD1Day
| - | - | 901588663 | DO | 1 | 4 | 2024PM_Clean SO Ins_Knockacummer_OD1Day
| GLE |  |  | DO | 2 |  | P1 Protection maintenance of 7SA612
OPT | GLE | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
| KCR |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612 ,GRL100
OPT | KCR | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - GOLAGH tee CLOGHER
TO-25-GOL,T-CLO-1-01 Window: May Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
SAG6_HV | - | - | 901347692 | DO | 10 | 3 | 2023 HV Sag Check -[0.206km]TRAN
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
OSGIS110 | CLO | - | 901300587 | DO | 5 | 2 | 110kV GIS Cubicle Ordinary Service
CA_110 | CLO | - | ESBN TO CONFIRM | DO | 3 | 4 | 110KV CUBICLE CONDITION ASSESSMENT
| CLO |  |  | DO | 2 |  | P1 Protection maintenance of 7SA612,GRL100
XLPCI_F | CLO | - | 901535583 | DO | 2 | 3 | Cable Insp. 110kV XLPE
| GOL |  |  | DO | 2 |  | P1 Protection maintenance of 7SA612,GRL100
110kV FEEDER - GOLAGH tee GOLAGH [Golagh WF/Battery (GOL1/GO2)]
TO-25-GOL,T-GOL-1-01 Window: May Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
SAG6_HV | - | - | 901347708 | DO | 10 | 3 | 2023 HV Sag Check -[3.951km]TRAN
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
OS | GOL | - | ESBN TO CONFIRM | DO | 5 | 1 | 110kV SF6 Cubicle Ordinary Service
CA_110 | GOL | - | ESBN TO CONFIRM | DO | 3 | 4 | 110KV CUBICLE CONDITION ASSESSMENT
FO_MISC | NTH | LET | 901502602 | DO | 1 | 4 | 2023HP-1[312]Off Plumb (Pole&Insulators)
FO_MISC | NTH | LET | 901502603 | DO | 1 | 4 | 2023HP-1[316]Off Plumb (Pole&Insulators)
FO_MISC | NTH | LET | 901502604 | DO | 1 | 4 | 2023HP-1[317]Off Plumb (Pole&Insulators)
FO_MISC | NTH | LET | 901502605 | DO | 1 | 4 | 2023HP-1[318]Off Plumb (Pole&Insulators)
FO_MISC | NTH | LET | 901502606 | DO | 1 | 4 | 2023HP-1[319]Off Plumb (Pole&Insulators)
| NTH | LET | 901643501 | DO | 1 | 4 | 2024HP-1[189]Insulator_Plumb
| NTH | LET | 901643502 | DO | 1 | 4 | 2024HP-1[182]Check_Paint_
110kV FEEDER - GOLAGH tee LETTERKENNY
TO-25-GOL,T-LET-1-01 Window: May Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
SAG6_HV | - | - | 901347718 | DO | 10 | 3 | 2023 HV Sag Check -[38.262km]TRAN
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
| GOL |  |  | DO | 2 |  | P1 Protection maintenance of 7SA612,GRL100
OS | LET | - | ESBN TO CONFIRM | DO | 6 | 1 | 110kV MO Cubicle Ordinary Service (excludes busbar disconnects)
| LET |  |  | DO | 2 |  | P1 Protection maintenance of 7SA612,GRL100
FO_MISC | NTH | LET | 901503360 | DO | 3 | 4 | 2023HP-1[209]Earths-Replace S/Arrestor
FOSTRHW | NTH | LET | 901503382 | DO | 3 | 4 | 2023HP-1[175]Replace Pole,Insul&HW T/Rot
FO_MISC | NTH | LET | 901503393 | DO | 3 | 4 | 2023HP-1[217]Stays-Replace Slack & Rusty
FO_STDMG | NTH | LET | 901503356 | DO | 1 | 4 | 2023HP-1[164]Crossarm Slight Rust
FO_STDMG | NTH | LET | 901503357 | DO | 1 | 4 | 2023HP-1[257]Crossarm Slight Rust on Arm
FO_STDMG | NTH | LET | 901503358 | DO | 1 | 4 | 2023HP-1[292]Crossarm Slight Rust
FO_STDMG | NTH | LET | 901503359 | DO | 1 | 4 | 2023HP-1[297]Crossarm Slight Rust
FO_MISC | NTH | LET | 901503376 | DO | 1 | 4 | 2023HP-1[132]Off Plumb Insulator L/side
FO_MISC | NTH | LET | 901503377 | DO | 1 | 4 | 2023HP-1[179]Off Plumb (Pole&Insulators)
FO_MISC | NTH | LET | 901503378 | DO | 1 | 4 | 2023HP-1[187]Off Plumb (Pole&Insulators)
FO_MISC | NTH | LET | 901503379 | DO | 1 | 4 | 2023HP-1[194]Off Plumb (Pole&Insulators)
FO_MISC | NTH | LET | 901503380 | DO | 1 | 4 | 2023HP-1[205]Off Plumb (Pole&Insulators)
FO_MISC | NTH | LET | 901503381 | DO | 1 | 4 | 2023HP-1[212]Off Plumb (Pole&Insulators)
| NTH | LET | 901643434 | DO | 1 | 4 | 2024HP-1[107]Off_Plumb_
| NTH | LET | 901643449 | DO | 1 | 4 | 2024HP-1[80]Earths-Replace_
| NTH | LET | 901643450 | DO | 1 | 4 | 2024HP-1[81]Earths-Replace_
| NTH | LET | 901643452 | DO | 1 | 4 | 2024HP-1[84]Insulator_Plumb
| NTH | LET | 901643453 | DO | 1 | 4 | 2024HP-1[87]Earths-Replace_
GENERATOR TRANSFORMER - GORMAN T122 [Gorman Battery GF1]
TO-25-GOR-T122-01 ISO week: 14we - 14fr Date: 02 Apr - 04 Apr Duration: 3 Days (3 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | GOR | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
OPTSF61 | GOR | 110 | 901432254 | DO | 2 | 3 | 110KV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - HUNTSTOWN T2002 [Huntstown HN2]
TO-25-HN-T2002-01 Status: Unscheduled
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
AICX4/2F | HUN | - | 901299975 | DO | 2 | 2 | Cable Insp. 400 & 220kV Feeder XLPE
OPT | HUN | 220 | ESBN TO CONFIRM | DO | 1 | 4 | 220kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - HUNTSTOWN T2010/11 [Huntstown HNC]
TO-25-HN-T2010/11-01 ISO week: 18mo - 19th Date: 26 Apr - 08 May Duration: 13 Days (8 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
| HUN | 220-DL/DE | 901543798 | DO | 4 | 1 | P1 Hotspot on Hunstown DL/DE R phase required immediately
AMCAB | HUN | 220 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
OPT | HUN | 220 | 901542511 | DO | 1 | 4 | 220kV SF6 Cubicle Operational Test
110kV FEEDER - IKERRIN tee IKERRIN
TO-25-IKE,T-IKE-1-04 Window: Jun Duration: (1 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OPT | IKE | - | 901542247 | DO | 1 | 4 | 110kV MO Cubicle Operational Test
110kV FEEDER - IKERRIN tee SHANNONBRIDGE
TO-25-IKE,T-SH-1-05 Window: Jul - Aug Duration: (20 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 20 | N/A | Total Maintenance Outage Duration Requested
FOSTRHW | - | - | 901311071 | DO | 3 | 2 | Poleset replacement @38
FOSTRHW | - | - | 901324409 | DO | 2 | 2 | 1[219]Replace Pole Rot Confirmed (Drone)
FOSTRHW | - | - | 901324406 | DO | 1 | 2 | 1[137]Replace Pole Rot Confirmed (Drone)
FO_MISC | - | - | 901370781 | DO | 1 | 3 | 2022HP-24[261-285]Danger Notices Replace
FO_MISC | - | - | 901504230 | DO | 1 | 1 | 2023HP-1[236]Bird Nests (Remove)
FOSTRHW | - | - | 901504231 | DO | 1 | 4 | 2023HP-1[126]Check Structure (Top Rot)S2
FOSTRHW | - | - | 901504232 | DO | 1 | 4 | 2023HP-1[137]Check Structure (Top Rot)S2
FOSTRHW | - | - | 901504233 | DO | 1 | 4 | 2023HP-1[199]Check Structure (Top Rot)S2
FOSTRHW | - | - | 901504235 | DO | 1 | 4 | 2023HP-1[241]Check Structure (Top Rot)S2
FOSTRHW | - | - | 901504236 | DO | 1 | 4 | 2023HP-1[253]Check Structure (Top Rot)S2
FOSTRHW | - | - | 901504237 | DO | 1 | 4 | 2023HP-1[27]Check Structure (Top Rot)-S2
FOSTRHW | - | - | 901504238 | DO | 1 | 4 | 2023HP-1[37]Check Structure (Top Rot)-S2
FOSTRHW | - | - | 901504239 | DO | 1 | 4 | 2023HP-1[38]Check Structure (Top Rot)-S2
FOSTRHW | - | - | 901504240 | DO | 1 | 4 | 2023HP-1[57]Check Structure (Top Rot)-S2
FOSTRHW | - | - | 901504241 | DO | 1 | 4 | 2023HP-1[9]Check Structure (Top Rot)-S2
FO_MISC | - | - | 901504242 | DO | 1 | 4 | 2023HP-1[17-18]Conflicts Shed underline
FO_MISC | - | - | 901504246 | DO | 1 | 4 | 2023HP-1[117]Stays-Replace (Bog Stays)
FOSTRHW | - | - | 901504252 | DO | 1 | 4 | 2023HP-1[282]Check Structure (Top Rot)S2
| - | - | 901646220 | DO | 1 | 4 | 2024HP-1[17]Bird_Nests_
CORRECT | SH~ | - | 901365415 | DO | 1 | 3 | Replace bellows on T-phase CTVT
CORRECT | SH~ | - | 901365416 | DO | 1 | 3 | Replace surge counter on R-phase SA
CORRECT | SH~ | - | 901365417 | DO | 1 | 3 | Replace surge counter on T-phase SA
110kV FEEDER - IKERRIN tee THURLES
TO-25-IKE,T-THU-1-05 ISO week: 17th - 18we Date: 24 Apr - 30 Apr Duration: 7 Days (5 WD) Status: Proposed
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
FO_MISC | - | - | 901126159 | DO | 1 | 1 | 2019LP-1[291]Off Plumb - Pole
OPT | THU | - | 901542248 | DO | 1 | 4 | 110kV MO Cubicle Operational Test
GENERATOR TRANSFORMER - INNISCARRA T101 [Lee LE1; Lee LE2]
TO-25-IA-T101-02 Window: Jun Duration: (4 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
OS | IA~ | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| IA~ | 110 | 901547782 | DO | 3 | 4 | O1-Surge counters damaged/unable to read
| IA~ | 110 | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 Leaks, DOF required
CA_110 | IA~ | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
GENERATOR TRANSFORMER - IRISHTOWN T2001 [Dublin Bay DB1]
TO-25-ISH-T2001-01 ISO week: 13tu - 13fr Date: 25 Mar - 28 Mar Duration: 4 Days (4 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | ISH | 220 | ESBN TO CONFIRM | DO | 4 | 4 | 220kV GIS Cubicle Ordinary Service
AIC4/2A | ISH | 220 | 901280821 | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
GENERATOR TRANSFORMER - IRISHTOWN T2002/3 [Irishtown IS2/IS3]
TO-25-ISH-T2002/3-01 Window: May Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
N/A | ISH | 220 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
N/A | ISH | 220 | ESBN TO CONFIRM | DO | 1 | 4 | 220kV GIS Cubicle Operational Test
GENERATOR TRANSFORMER - KILCUMBER T131 [Cloncreen WF/Bat (OE1/OE2)]
TO-25-KIR-T131-04 Window: Jun Duration: (2 WD) Status: Planned
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
| KIR | 110 | ESBN TO CONFIRM | DO | 1 | 3 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - KILL HILL T131 [Kill Hill WF (KH1)]
TO-25-KHL-T131-01 Window: Jun - Jul Duration: (7 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 7 | N/A | Total Maintenance Outage Duration Requested
OS | KHL | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
CA_110 | KHL | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
GENERATOR TRANSFORMER - KILTEEL T131 [Porterstown Battery PN1]
TO-25-KTL-T131-01 ISO week: 14we Date: 02 Apr Duration: 1 Day (1 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
| KTL | 110 | 901397142 | DO | 1 | 3 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - KNOCKALOUGH KNOCKRANNY [Knockalough WF (KU1)]
TO-25-KLH-KNY-1-01 Window: May Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
| KLH |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612 ,GRL100
OPTSF61 | KLH | - | 901396808 | DO | 2 | 3 | 110kV SF6 Cubicle Operational Test
AMCAB | KLH | - | ESBN TO CONFIRM | DO | 2 | 1 | Cable Insp. 110kV XLPE
CORRECT | KLH | - | 901343446 | DO | 1 | 3 | Master Sub Remote Switch
CORRECT | KLH | - | 901343450 | DO | 1 | 3 | Surge Arrestor Counter Covers
CORRECT | KLH | - | 901343451 | DO | 1 | 3 | V.T Secondary fuse holders
| KNY |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612 ,GRL100 702D
OPTSF61 | KNY | - | 901396809 | DO | 2 | 3 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - KNOCKRANNY UGGOOL [Seecon/Uggool WF (SO1/UG1)]
TO-25-KNY-UGL-1-01 Window: May Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
AMCAB | Cable | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
OPT | KNY | - | 901542172 | DO | 2 | 4 | 110kV GIS Cubicle Operational Test
OPT | UGL | - | 901542173 | DO | 2 | 4 | 110kV GIS Cubicle Operational Test
GENERATOR TRANSFORMER - LISDRUM T131 [Lisdrumdoagh Battery LF1]
TO-25-LIS-T131-01 Window: May Duration: (8 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 8 | N/A | Total Maintenance Outage Duration Requested
OS | LIS | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
CA_110 | LIS | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
AMCAB | LIS | 110 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
GENERATOR TRANSFORMER - LISHEEN T131 [Lisheen 3 WF (LS3)]
TO-25-LSN-T131-04 Window: May Duration: (5 WD) Status: Planned
N/A | - | - | N/A | DO | 6 | N/A | Total Maintenance Outage Duration Requested
N/A | LSN | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
110kV FEEDER - LISHEEN THURLES [Lisheen 1/2/3 WF (LS1/LS2/LS3)]
TO-25-LSN-THU-1-03 Window: May Duration: (5 WD) Status: Planned
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OPT | LSN | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - LISLEA T131 [Drumlins WF (LA1)]
TO-25-LSA-T131-01 Window: May Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
OPT | LSA | - | ESBN TO CONFIRM | DO | 2 | 4 | 110kV GIS Cubicle Operational Test
GENERATOR TRANSFORMER - LONG POINT T2002 [Aghada AD2]
TO-25-LPT-T2002-01 Window: Sep Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | LPT | 220 | ESBN TO CONFIRM | DO | 5 | 4 | 220kV SF6 Cubicle Ordinary Service
CA_220 | LPT | 220 | ESBN TO CONFIRM | DO | 3 | 4 | 220KV CUBICLE CONDITION ASSESSMENT
AMCAB | LPT | 220 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
GENERATOR TRANSFORMER - MEENTYCAT T121 [Meentycat WF (MCT)]
TO-25-MEE-T121-01 Window: Jun Duration: (9 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 9 | N/A | Total Maintenance Outage Duration Requested
OS | MEE | 110 | ESBN TO CONFIRM | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service
CA_110 | MEE | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV CUBICLE CONDITION ASSESSMENT
GENERATOR TRANSFORMER - MONEYPOINT GIS T121 [Moneypoint WF (MP9)]
TO-25-MP GIS-T121-02 Window: Jun Duration: (5 WD) Status: Planned
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
OPT | MP~ | 110 | ESBN TO CONFIRM | DO | 2 | 4 | 110KV GIS Cubicle Operational Test
GENERATOR TRANSFORMER - MONEYPOINT GIS T4001 [Moneypoint MP1]
TO-25-MP GIS-T4001-02 Window: May Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
| MP |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612
AMCAB | MP~ | 400 | ESBN TO CONFIRM | DO | 3 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
GENERATOR TRANSFORMER - MONEYPOINT GIS T4002 [Moneypoint MP2]
TO-25-MP GIS-T4002-01 ISO week: 14mo - 14fr Date: 31 Mar - 04 Apr Duration: 5 Days (5 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
| MP |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612
N/A | MP~ | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
AMCAB | MP~ | 400 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
GENERATOR TRANSFORMER - MONEYPOINT GIS T4003 [Moneypoint MP3]
TO-25-MP GIS-T4003-02 Window: Sep - Oct Duration: (8 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 8 | N/A | Total Maintenance Outage Duration Requested
CA_400 | MP~ | 400 | ESBN TO CONFIRM | DO | 4 | 4 | 400KV CUBICLE CONDITION ASSESSMENT
OS | MP~ | 400 | ESBN TO CONFIRM | DO | 3 | 4 | 400kV GIS Cubicle Ordinary Service
AMCAB | MP~ | 400 | 901542928 | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
GENERATOR TRANSFORMER - MOUNTLUCAS T121 [Mountlucas WF (MO1)]
TO-25-MLC-T121-02 Window: May Duration: (2 WD) Status: Planned
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
OPT | MLC | 110 | 901542474 | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - POLLAPHUCA T101 [Liffey LI1/LI2/LI4]
TO-25-PA-T101-02 Window: May Duration: (15 WD) Status: Planned
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
| PA |  |  | DO | 2 |  | P3 Protection maintenance of 7SA511
OPT | POL | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV MO Cubicle Operational Test
GENERATOR TRANSFORMER - POOLBEG T2007/8 [Poolbeg PB7/PB8]
TO-25-PB-T2007/8-01 Window: Aug Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
N/A | PB~ | CABLE | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
N/A | PB~ | - | ESBN TO CONFIRM | DO | 1 | 4 | 220kV GIS Cubicle Operational Test
GENERATOR TRANSFORMER - RATRUSSAN T121 [Bindoo WF (BD1)]
TO-25-RRU-T121-01 Window: Jun Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO |  | N/A | Total Maintenance Outage Duration Requested
| RRU | 110 | 901543364 | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
GENERATOR TRANSFORMER - RATRUSSAN T122 [Mountain Lodge WF (ML1)]
TO-25-RRU-T122-02 ISO week: 16mo - 16fr Date: 14 Apr - 18 Apr Duration: 5 Days (4 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
| RRU | 110 | 901543365 | DO | 3 | 1 | O-Ring Replacement to prevent SF6 leaks
OPT | RRU | 110 | ESBN TO CONFIRM | DO | 2 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - REAMORE TRALEE
TO-25-REM-TRL-1-01 ISO week: 14mo - 14fr Date: 31 Mar - 04 Apr Duration: 5 Days (5 WD) Status: Proposed
N/A | - | - | N/A | DO | 8 | N/A | Total Maintenance Outage Duration Requested
FO_CABLE | - | - | 901452070 | DO | 3 | 3 | 2023PM_Raise JB15 cham lid 100mm OD:3Day
FO_CABLE | - | - | 901452081 | DO | 3 | 1 | 2023PM_Mntr Leak Current JB1-2 OD:3 Day
FO_CABLE | - | - | 901452082 | DO | 3 | 1 | 2023PM_Mntr Leak Current JB2-3 OD:3 Day
FO_CABLE | - | - | 901452087 | DO | 3 | 1 | 2023PM_Mntr Leak Current JB3-6_OD 3 Days
FO_CABLE | - | - | 901452088 | DO | 3 | 1 | 2023PM_Mntr Leak Current JB6-9_OD 3 Days
FO_CABLE | - | - | 901452089 | DO | 3 | 1 | 2023PM_Mntr Leak Current JB9-12_OD 3 Day
FO_CABLE | - | - | 901452090 | DO | 3 | 1 | 2023PM_Mntr Leak Current JB12-15_OD 3Day
FO_CABLE | - | - | 901452091 | DO | 3 | 3 | 2023PM_Repl.JB18 LB-bad connect.-OD3days
FO_CABLE | - | - | 901452076 | DO | 1 | 3 | 2023PM_Replace JB01 LB bolts x6-OD 1 Day
FO_CABLE | - | - | 901452080 | DO | 1 | 3 | 2023PM_Install all LB # labels-OD 1 Day
CORRECT | REM | - | 901445458 | DO | 5 | 3 | CB overhaul required. Pole radial seals.
OPT | REM | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
OPT | TRL | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - ROSSPILE T131 [Rosspile SF (R01)]
TO-25-ROP-T131-02 ISO week: 17we Date: 23 Apr Duration: 1 Day (1 WD) Status: Proposed
N/A | - | - | N/A | DO | 1 | N/A | Total Maintenance Outage Duration Requested
| ROSS | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - SEALROCK T103 [Sealrock SK3]
TO-25-SK-T103-01 Window: Jul - Aug Duration: (15 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
| SK~ | 110 | 901547193 | DO | 3 | 4 | 2024CM_Repl. CSE SO's@SS End_OD 2Days
OPT | SK~ | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110KV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - SEALROCK T104 [Sealrock SK4]
TO-25-SK-T104-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | SK~ | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110KV SF6 Cubicle Ordinary Service
AMCAB | SK~ | 110 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
GENERATOR TRANSFORMER - SHELLYBANKS T2014 [Poolbeg PB14]
TO-25-SHL-T2014-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | SHL | 220-DL | 901542682 | DO | 5 | 4 | 220kV Sect / Dist Ordinary Service
| SHL |  |  | DO | 2 |  | P3 Protection maintenance of 7SA513
AMCAB | SHL | cable | 901542868 | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
GENERATOR TRANSFORMER - SHELLYBANKS T2015 [Poolbeg PB15]
TO-25-SHL-T2015-01 Window: Jun Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OSSEC220 | SHL | 220-DL | 901130137 | DO | 5 | 4 | 220kV Sect / Dist Ordinary Service
| SHL |  |  | DO | 2 |  | P3 Protection maintenance of 7SA513
AIC4/2A | SHL | - | 901281053 | DO | 1 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
GENERATOR TRANSFORMER - SHELLYBANKS T2016 [Poolbeg PB16]
TO-25-SHL-T2016-02 Status: Unscheduled
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | SHL | 220-DL | ESBN TO CONFIRM | DO | 2 | 4 | 220kV Sect / Dist Ordinary Service
AMCAB | SHL | 220 | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 400 & 220kV Feeder XLPE
GENERATOR TRANSFORMER - SLIABH BAWN T132 [Sliabh Bawn WF (SB1)]
TO-25-SLB-T132-02 Window: Jun Duration: (2 WD) Status: Planned
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
OPT | SLB | 110 | ESBN TO CONFIRM | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - SLIEVECALLAN T121 [Knockalassa WF (KD1)]
TO-25-SLC-T121-01 Window: Jul Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO |  | N/A | Total Maintenance Outage Duration Requested
| SLC |  |  | DO | 2 |  | P3 Protection maintenance of 7SA611, 7SJ804
OPT | SLC | 110 | ESBN TO CONFIRM | DO | 2 | 4 | 110kV MO Cubicle Operational Test
GENERATOR TRANSFORMER - SLIEVECALLAN T122 [Boolinrudda WF (RD1)]
TO-25-SLC-T122-01 Window: Jul Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO |  | N/A | Total Maintenance Outage Duration Requested
| SLC |  |  | DO | 2 |  | P3 Protection maintenance of 7SA611, 7SJ804
OPT | SLC | 110 | 901617786 | DO | 1 | 2 | 110kV MO Cubicle Operational Test
SECTIONALISING DISCONNECT - SRAHNAKILLY 110SA1 [Oweninny WF (OY2)]
TO-25-SKY-110SA1-01 Window: May Duration: (11 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
OPT | SKY | 110-SA1 | ESBN TO CONFIRM | DO | 2 | 4 | 110kV Sect / Dist Operational Test
SECTIONALISING DISCONNECT - SRAHNAKILLY 110SA2 [Oweninny WF (OY2)]
TO-25-SKY-110SA2-01 Window: May Duration: (11 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
OPT | SKY | 110-SA2 | ESBN TO CONFIRM | DO | 2 | 4 | 110kV Sect / Dist Operational Test
GENERATOR TRANSFORMER - SRAHNAKILLY T131 [Oweninny WF (OY1)]
TO-25-SKY-T131-02 Window: May Duration: (11 WD) Status: Planned
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
| SKY | 110 | 901576522 | DO | 2 | 4 | FOMO DT NOT MAINTAINED AS IT IS A POINT
OPT | SKY | 110 | ESBN TO CONFIRM | DO | 2 | 4 | 110kV SF6 Cubicle Operational Test
110kV FEEDER - STRATFORD tee CARLOW [Liffey LI1/LI2/LI4]
TO-25-STR,T-CLW-1-02 Window: May Duration: (15 WD) Status: Planned
N/A | - | - | N/A | DO | 15 | N/A | Total Maintenance Outage Duration Requested
OPT | CLW | - | 901542428 | DO | 1 | 4 | 110kV SF6 Cubicle Operational Test
FO_COND | EST II | PLS | 901472696 | DO | 2 | 1 | 1[169-170]Conductor Samp R or L Phase
FO_COND | EST II | PLS | 901472697 | DO | 2 | 1 | 1[90-91]Conductor Sampling R or L Phase
FO_COND | EST II | PLS | 901472699 | DO | 2 | 1 | 1[127-128]Conductor Sampling R or L Phas
FO_COND | EST II | PLS | 901472780 | DO | 2 | 1 | 1[153-154]Conductor Sampling R or L Phas
FO_COND | EST II | PLS | 901472781 | DO | 2 | 1 | 1[71-72]Conductor Sampling R or L Phase
FO_COND | EST II | PLS | 901472782 | DO | 2 | 1 | 1[5-6]Conductor Sampling R or L Phase
FOSTRHW | EST II | PLS | 901500728 | DO | 1 | 4 | 2023HP-1[94]Check Structure (Top Rot)S2
110kV FEEDER - STRATFORD tee POLLAPHUCA [Liffey LI1/LI2/LI4]
TO-25-STR,T-PA-1-02 Window: May Duration: (15 WD) Status: Planned
N/A | - | - | N/A | DO | 15 | N/A | Total Maintenance Outage Duration Requested
FO_MISC | - | - | 901085001 | DO | 2 | 4 | 2019HP-1[13]Off Plumb -plumb poles
FO_STDMG | EST II | PLS | 901454006 | DO | 3 | 3 | 2023LP-1[14]Crossarm Treat/Replace
FO_MISC | EST II | PLS | 901454007 | DO | 1 | 3 | 2023LP-1[11]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454008 | DO | 1 | 3 | 2023LP-1[17]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454009 | DO | 1 | 3 | 2023LP-1[28]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454010 | DO | 1 | 3 | 2023LP-1[34]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454011 | DO | 1 | 3 | 2023LP-1[37]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454012 | DO | 1 | 3 | 2023LP-1[41]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454013 | DO | 1 | 3 | 2023LP-1[43]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454014 | DO | 1 | 3 | 2023LP-1[49]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454015 | DO | 1 | 3 | 2023LP-1[51]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454016 | DO | 1 | 3 | 2023LP-1[57]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454017 | DO | 1 | 3 | 2023LP-1[59]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454018 | DO | 1 | 3 | 2023LP-1[61]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901454019 | DO | 1 | 3 | 2023LP-1[64]Insulator (Re-Plumb)
FO_MISC | EST II | PLS | 901504153 | DO | 1 | 4 | 2023HP-1[49]Repl./Retire pole butts
| PA |  |  | DO | 2 |  | P1 Protection maintenance of 7SA511
OS | POL | - | 901614178 | DO | 6 | 1 | 110kV MO Cubicle Ordinary Service (excludes busbar disconnects)
| STR |  |  | DO | 2 |  | P1 Protection maintenance of 7SA511
GENERATOR TRANSFORMER - TAWNAGHMORE T1/T2 [Tawnaghmore TP1]
TO-25-TAW-T1/T2-01 Window: Jun Duration: (9 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 9 | N/A | Total Maintenance Outage Duration Requested
OS | TAW | 110 | ESBN TO CONFIRM | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| TAW | 110 | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 Leaks, DOF required
CA_110 | TAW | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV SF6 Cubicle Condition Assessment (excludes busbar disconnects)
GENERATOR TRANSFORMER - TAWNAGHMORE T3 [Tawnaghmore TP3]
TO-25-TAW-T3-01 Window: Jun Duration: (9 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 9 | N/A | Total Maintenance Outage Duration Requested
OS | TAW | 110 | ESBN TO CONFIRM | DO | 5 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| TAW | 110 | ESBN TO CONFIRM | DO | 3 | 1 | O-Ring Replacement to prevent SF6 Leaks, DOF required
CA_110 | TAW | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV SF6 Cubicle Condition Assessment (excludes busbar disconnects)
GENERATOR TRANSFORMER - TULLABEG T131 [Tullabeg SF (TL1)]
TO-25-TTU-131-01 Window: Nov Duration: (2 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 2 | N/A | Total Maintenance Outage Duration Requested
| TTU | - | ESBN TO CONFIRM | DO | 2 | 4 | Cable Insp. 110kV XLPE
OPT | TTU | - | ESBN TO CONFIRM | DO | 1 | 4 | 110kV GIS Cubicle Operational Test
110kV FEEDER - TULLABRACK tee BOOLTIAGH
TO-25-TBK,T-BOL-1-01 Window: Jun - Jul Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
OS | BOL | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
CA_110 | BOL | - | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
110kV FEEDER - TULLABRACK tee MONEYPOINT GIS
TO-25-TBK,T-MP GIS-1-01 Window: Jun - Jul Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
| MP |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,GRZ100
AMCAB | MP~ | - | ESBN TO CONFIRM | DO | 2 | 4 | Annual Insp. 110kV Feeder XLPE Cable
| TBK |  |  | DO | 2 |  | P3 Protection maintenance of 7SA612,GRZ100
110kV FEEDER - TULLABRACK tee TULLABRACK
TO-25-TBK,T-TBK-1-01 Window: Jun - Jul Duration: (10 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 10 | N/A | Total Maintenance Outage Duration Requested
FO_CABLE | TBK | - | 901365241 | DO | 8 | 3 | 2022PM_Replace SVL holders in link box a
OS | TBK | - | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service
CA_110 | TBK | - | 901300000 | DO | 3 | 2 | 110KV CUBICLE CONDITION ASSESSMENT
AMCAB | TBK | - | ESBN TO CONFIRM | DO | 2 | 4 | Annual Insp. 110kV Feeder XLPE Cable
FO_CABLE | TBK | - | 901364439 | DO | 1 | 3 | 2022PM_Clean cable sealing end stand-off
GENERATOR TRANSFORMER - TURLOUGH HILL T2001/2 [Turlough Hill TH1/TH2]
TO-25-TH-T2001/2-02 ISO week: 12su - 14tu Date: 23 Mar - 01 Apr Duration: 10 Days (7 WD) Status: Proposed
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | TH~ | 220 | ESBN TO CONFIRM | DO | 5 | 1 | 220kV MO Cubicle Ordinary Service
AMCAB | TH~ | 220 | ESBN TO CONFIRM | DO | 2 | 4 | Annual Insp. 400 & 220 Station OF Cable
GENERATOR TRANSFORMER - TURLOUGH HILL T2003/4 [Turlough Hill TH3/TH4]
TO-25-TH-T2003/4-02 ISO week: 14we - 15fr Date: 02 Apr - 11 Apr Duration: 10 Days (8 WD) Status: Proposed
|  |  |  | DO |  |  | TH 220 kV A2/B2 bars in turn required to facilitate OS on TH 2003/4 bay
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
| TH |  |  | DO | 2 |  | P3 Protection maintenance of S,R1Z23b
OS | TH~ | 220 | ESBN TO CONFIRM | DO | 5 | 1 | 220kV MO Cubicle Ordinary Service
AIFFC_S | TH~ | 220 | 901432318 | DO | 2 | 1 | Annual Insp. 400 & 220 Station OF Cable
GENERATOR TRANSFORMER - TYNAGH T2001/2 [Tynagh TYC]
TO-25-TY-T2001/2-02 Window: Aug Duration: (5 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 5 | N/A | Total Maintenance Outage Duration Requested
OS | TYN | 220 | ESBN TO CONFIRM | DO | 5 | 4 | 220kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
| TYN | 220 | 901544802 | DO | 3 | 1 | P2 Hotspot on T2001/2 220kV VT S-ph. Due 6 months. 04.10.2024
COUPLER/SECTIONALISING CB - UGGOOL 110SA1-2CB [Seecon WF (SO1)]
TO-25-UGL-110SA1-2CB-01 Window: May Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
OPT | UGL | 110-SA1-2 | 901542187 | DO | 2 | 4 | 110kV GIS Cubicle Operational Test
GENERATOR TRANSFORMER - UGGOOL T131 [Uggool WF (UG1)]
TO-25-UGL-T131-01 Window: May Duration: (8 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 8 | N/A | Total Maintenance Outage Duration Requested
AICX110F | UG | 110 | 901212057 | DO | 2 | 3 | Cable Insp. 110kV XLPE
OS | UGL | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
CA_110 | UGL | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)
GENERATOR TRANSFORMER - UGGOOL T132 [Seecon WF (SO1)]
TO-25-UGL-T132-01 Window: May Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
AICX110F | UG | 110 | 901212058 | DO | 2 | 3 | Cable Insp. 110kV XLPE
OPT | UGL | 110 | ESBN TO CONFIRM | DO | 2 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - UGGOOL T134 [Seecon WF (SO1)]
TO-25-UGL-T134-01 Window: May Duration: (3 WD) Status: Planned
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 3 | N/A | Total Maintenance Outage Duration Requested
AICX110F | UG | 110 | 901212059 | DO | 2 | 3 | Cable Insp. 110kV XLPE
OPT | UGL | 110 | ESBN TO CONFIRM | DO | 2 | 4 | 110kV SF6 Cubicle Operational Test
GENERATOR TRANSFORMER - WOODHOUSE T122 [Woodhouse WF (WS1)]
TO-25-WOH-T122-01 ISO week: 14mo - 14we Date: 31 Mar - 02 Apr Duration: 3 Days (3 WD) Status: Proposed
WORK | LOCATION |  | WORK ID | STATUS | DAYS | PRIORITY | DESCRIPTION/COMMENTS
N/A | - | - | N/A | DO | 4 | N/A | Total Maintenance Outage Duration Requested
OS | WOH | 110 | ESBN TO CONFIRM | DO | 4 | 4 | 110kV SF6 Cubicle Ordinary Service (excludes busbar disconnects)
CA_110 | WOH | 110 | ESBN TO CONFIRM | DO | 3 | 4 | 110KV Cubicle Condition Assessment (excludes busbar disconnects)