## Slide 1: EirGrid GCRP Meeting
25 September 2025
25/09/2025
1

## Slide 2: EirGrid GCRP Agenda
25/09/2025
INTRODUCTION: 10 mins
Welcome to Members;
Minutes and Actions from Previous Meeting (04 December 2024).
PROPOSALS: 50 mins
MPID339 – FASS Reserve Products Review;
MPID343 – Clarification of Curve 1 and Curve 2 for PPMs;
MPID341 – Stranded Definitions;
MPID342 – Clarification PPM Section Solar;
UPDATES: 15 mins
Approved Grid Code Modifications since previous meeting;
Grid Code Derogations;
CRU.
AOB 5 mins

## Slide 3: MPID339 FASS Reserve Products Review
25/09/2025
1. Proposed Modification: 10 minutes

## Slide 4: MPID339
This mod proposal was presented and discussed at the JGCRP.
Do members support the submission of MPID339 to the CRU for review and decision?
25/09/2025

## Slide 5: MPID 343 Clarification of Curve 1 and Curve 2 for PPMs
25/09/2025
2. Proposed Modification: 10 minutes

## Slide 6: MPID343
25/09/2025
The Grid Code is constantly evolving to adapt to operational needs and industry best practices. This proposal introduces focused updates to improve clarity and consistency in the application of Power-Frequency Curves.
Sections Impacted:
Definitions
PPM1.5.3.6
PPM1.5.3.7
PPM1.7.1.5
Justification for Modification:
Improved Clarity: Updates aim to clarify the operational differences between Power-Frequency Curve 1 and Curve 2.
Enhanced Definitions: The term Resource Following Mode is being revised to better distinguish the behaviour of Controllable PPMs under each curve.
Reduced Ambiguity: Current wording could lead to misinterpretation of Curve 1 characteristics.
Operational Consistency: Reference tables are being updated to align Grid Code documentation with established operational practices.

## Slide 7: Resource Following Mode definition
x | 
Resource Following Mode | A mode of operation of a Controllable PPM, with the exception of ESPSs, where the system frequency is within FB-FC, according to the active power-frequency response curve in operation (curve 1 or curve 2) and the Controllable PPM is not under Active Power Control by the TSO. allowing the Controllable PPM to produce up to 100% of its Available Active Power, depending on the Power-Frequency Curve in operation. In power-frequency response curve 1 the Controllable PPM adjusts its Active Power output to produce up to 100% of its Available Active Power. In power-frequency response curve 2 When operating on Power-Frequency Curve 2, the Controllable PPM is required to maintain its Active Power output at a fixed percentage of its Available Active Power. when Transmission System Frequency is within the range FB-FC.
Resource Following Mode | A mode of operation of a Controllable PPM, with the exception of ESPSs, where the system frequency is within FB-FC, according to the active power-frequency response curve in operation (curve 1 or curve 2) and the Controllable PPM is not under Active Power Control by the TSO. In power-frequency response curve 1 the Controllable PPM adjusts its Active Power output to produce up to 100% of its Available Active Power. In power-frequency curve 2 the Controllable PPM is required to maintain its Active Power output at a fixed percentage of its Available Active Power.

## Slide 8: PPM1.5.3.2
Figure PPM 1.5.3.1.b–Example of Power-Frequency Response Curve 2 for Resource Following Mode | Figure PPM 1.5.3.1.b–Example of Power-Frequency Response Curve 2 for Resource Following Mode

## Slide 9: PPM1.5.3.6
Table PPM 1.5.3.6: Transmission System Frequency and Controllable PPM Active Power Output % Available Active Power Settings for the Points ‘A’, ‘B’, ‘C’, ‘D’ and ‘E’ illustrated in Figure PPM 1.5.3.1.b. | Table PPM 1.5.3.6: Transmission System Frequency and Controllable PPM Active Power Output Settings for the Points ‘A’, ‘B’, ‘C’, ‘D’ and ‘E’ illustrated in Figure PPM 1.5.3.1.b.
Point | Transmission System Frequency (Hz) | Controllable PPM Active Power Output
A | FA | PA =100% % of Available Active Power
B | FB | Minimum of [fix spacing]: PB or Active Power Control Set-point (converted to a % of Available Active Power)
C | FC | Minimum of: PC or Active Power Control Set-point (converted to a % of Available Active Power)
D | FD | Minimum of: PD or Active Power Control Set-point (converted to a % of Available Active Power)
E | FE | PE = 0 %
Point | Transmission System Frequency (Hz) | Controllable PPM Active Power Output
A | FA | PA =100% % of Available Active Power
B | FB | Minimum of: PB or Active Power Control Set-point
C | FC | Minimum of: PC or Active Power Control Set-point
D | FD | Minimum of: PD or Active Power Control Set-point
E | FE | PE = 0 %

## Slide 10: PPM1.5.3.7
 | Transmission System Frequency (Hz) |  | Percentage of Available Active Power (%)
 |  |  | Registered Capacity ≥ 5 MW
FA | 47.0-49.5 | PA | 50-100
FB | 49.5-50 | PB | 15-100
FC | 50-50.5 | PC | 
FD | 50.5-52.0 | PD | 15-100 but not less than DMOL
FE |  | PE | 0
 | Transmission System Frequency (Hz) |  | Percentage of Available Active Power (%)
 |  |  | Registered Capacity ≥ 5 MW
FA | 47.0-49.5 | PA | 100
FB | 49.5-50 | PB | 15-100
FC | 50-50.5 | PC | 
FD | 50.5-52.0 | PD | DMOL
FE |  | PE | 0

## Slide 11: PPM1.7.11.5 Signals List #5
Signals List #5 The Controllable PPM shall make the following signals available as specified in the relevant specifications and site-specific signal lists: a) Frequency Response Curve (i.e. Power-Frequency Response Curve 1 or Curve 2 or Mode (1 to 5)); | Signals List #5 The Controllable PPM shall make the following signals available as specified in the relevant specifications and site-specific signal lists: a) Frequency Response Curve (i.e. Power-Frequency Response Curve 1 or Curve 2 or Mode (1 to 5));

## Slide 12: MPID341 Removal of Stranded Definitions
25/09/2025
3. Proposed Modification: 10 minutes

## Slide 13: MPID341
Modification Proposal Justification:
The purpose of this modification is to eliminate redundant definitions that are no longer utilised within the Grid Code or any other Market Code.
These definitions were included in previous versions of the Grid Code but have become obsolete as the Grid Code definitions have evolved. Such unused definitions are now considered stranded and are targeted for removal to ensure clarity and relevance.
25/09/2025

## Slide 14: MPID341
Stranded Definitions Proposed for Removal
Demand Side Unit Energy Profile
  Definition: Estimated energy requirement for demand sites, submitted to TSO.
  Reason for Removal: Isolated to glossary, not used in operational or compliance clauses.
Capacity Adequacy Indicator
  Definition: TSO-issued indication of generation capacity vs. demand for weekly peaks.
  Reason for Removal: No cross-references in operational or forecasting sections.
De-maximisation Instruction
  Definition: Instruction to generators to cease maximisation.
  Reason for Removal: Not referenced in dispatch or operational clauses; redundant terminology.
25/09/2025

## Slide 15: MPID341
Red-Line and Green-Line Changes
25/09/2025

## Slide 16: MPID 342 Clarification PPM Section Solar
25/09/2025
4. Proposed Modification: 10 minutes

## Slide 17: MPID342
The Grid Code is constantly evolving to adapt to operational needs and technology-specific requirements. This proposal introduces clarifying updates to improve consistency in the treatment of solar-powered Controllable PPMs.
Sections Impacted:
PPM1.7.1.2 – Signals List #2
PPM1.7.1.3 – Signals List #3
Justification:
Improves Clarity: Consolidates solar-specific provisions that were previously scattered or embedded within broader requirements.
Simplifies Compliance: Makes it easier for Users with solar-powered Controllable PPMs to understand and meet Grid Code obligations.
Enhances Transparency: Clearly distinguishes solar requirements from those for wind, ESPS, and other PPMs.
Editorial in Nature: These changes do not alter technical obligations or intent—only improve structure and readability.
Modification Proposal Justification:

## Slide 18: PPM1.7.1.2 Signals List #2
PPM1.7.1.2 Signals List #2
Wind-powered Controllable PPMs
PPM1.7.1.2.1 Wind-powered Controllable PPMs comprising of Wind Turbine Generators with a MEC in excess of 10 MW shall make the following meteorological data signals available as specified in the relevant specifications and site-specific signal lists:
(a) Wind speed (at hub height or as agreed with the TSO) - measurand signal;
(b) Wind direction (at hub height or as agreed with the TSO) - measurand signal;
(c) Air temperature- measurand signal;
(d) Air pressure- measurand signal.
Solar-powered Controllable PPMs
PPM1.7.1.2.2.1
PPM1.7.1.2.3 Solar-powered Controllable PPMs with a MEC in excess of 10 MW shall make the following meteorological data signals available as specified in the relevant specifications and site-specific signal lists:
Global Horizontal Irradiance (GHI) - measurand signal;
Diffused Horizontal Irradiance (DHI) - measurand signal;
Direct Normal Irradiance (DNI) (required for solar tracking panels only) - measurand signal;
Air temperature - measurand signal;
Back panel temperature - measurand signal;
Wind speed - measurand signal;
Wind direction - measurand signal;
Precipitation – measurand signal;
Air pressure - measurand signal.
Other Controllable PPMs (excluding wind and solar)
PPM1.7.1.2.3
PPM1.7.1.2.5 Controllable PPMs, in excess of 5 MW, with the exception of wind-powered and solar-powered Controllable PPMs, shall make relevant meteorological data signals available, which may include but are not limited to solar irradiance and tidal streams, as agreed with the TSO and specified in the relevant specifications and site-specific signal lists.
The actual signals required shall be specified by the TSO at least 120 Business Days prior to the Controllable PPM’s scheduled Operational Date.

## Slide 19: PPM1.7.1.3 Signals List #3
PPM1.7.1.3 Signals List #3
Wind-powered Controllable PPMs
PPM1.7.1.3.1 Wind-powered Controllable PPMs with a MEC in excess of 10 MW shall make the following signals available as specified in the relevant specifications and site-specific signal lists:
Wind-powered Controllable PPM Availability (0-100 % signal);
Percentage of WTG Shutdown due to high wind-speed conditions (0-100 %);
Percentage of WTG not generating due low wind-speed Shutdown (0-100 %).
Solar-powered Controllable PPMs
PPM1.7.1.3.2.1
PPM1.7.1.3.3 Solar-powered Controllable PPMs with a MEC in excess of 10 MW shall make the following signals available as specified in the relevant specifications and site-specific signal lists:
Solar-powered Controllable PPM Availability (0-100 % signal).
Energy Storage Power Stations (ESPSs)
PPM1.7.1.3.5 The Controllable PPM consisting of ESPSs shall make the following signals available as specified in the relevant specifications and site-specific signal lists:
a). ESPS available export capacity (+MWh)
b). ESPS available import capacity (-MWh)
Other Controllable PPMs (excluding wind, solar, and ESPs)
PPM1.7.1.3.3
PPM1.7.1.3.6 Controllable PPMs, with a MEC in excess of 5 MW, with the exception of wind-powered and solar-powered Controllable PPMs, shall make the following signals available as specified in the relevant specifications and site-specific signal lists:
Controllable PPM Availability (0-100 % signal);
Percentage of Generation Unit shutdown due to high resource conditions (0-100 %);
Percentage of Generation Unit not generating due to low resource conditions (0-100 %).

## Slide 20: MPID340 SCU RoCoF and Protection Requirements
25/09/2025
5. Proposed Modification: 10 minutes

## Slide 21: Purpose
At the June 2025 GCRP meeting, MPID319 SCU Incorporation was recommended for submission to the Regulators for decision.
As part of that modification proposal, a clause relating to Rate of Change of Frequency (RoCoF) requirements for SCUs was mistakenly omitted, and references to Generator-specific protection clauses were mistakenly added to the SCU protection section.
The aim of this modification proposal is to include a clause relating to Rate of Change of Frequency (RoCoF) requirements for SCUs (where a similar requirement applies to both Generators and Interconnectors under the Grid Code) and to correct the protection references so they refer to SCU-specific protection requirements rather than Generator requirements.
The changes proposed are changes to MPID319 SCU Incorporation, where:
  the black text is text already present in the MPID319 modification proposal
  The red text is text to be removed from MPID319, and
  the blue text is new text proposed in addition to MPID319

## Slide 22: Proposed RoCoF text

## Slide 23: Correct references to protection clauses

## Slide 24
Thank you!
Questions?

## Slide 25: 3. Updates: 30 minutes
  Grid Code Derogations;
  CRU;
  Grid Code Modification Stats since previous meeting
25/09/2025

## Slide 26: Update Derogations
25/09/2025

## Slide 27: Current Derogations Stats for GCRP September 2025
Total
Under TSO Assessment 161
Approved by CRU 513
Still Valid 111
With CRU 132
Under TSO Assessment
Type
WFPS 77
Conventional 45
TEG 5
BESS 18
DSU 23
Categories
APC/Frequency 58
Reactive Power 34
FRT 31
RoCoF 4
Since last GCRP 27 March 2024
Submitted to TSO 5
Forwarded to CRU 9
Approved by CRU 3
Withdrawn 1
25/09/2025

## Slide 28: Update CRU
25/09/2025

## Slide 29: JGCRP/ GCRP Meeting 26 June 2025
CRU Update
JGCRP Modifications Update since 26 June 2025
New Modification requests: 1 (MPID 319)
Joint Modification recommendations under review: 3 (MPID 293, MPID 319, MPID 327)
GCRP Modifications Update since 26 June 2025
New Modification requests: 3 (MPID 319, MPID 335, MPID 336)
CRU Modification decisions: 6 (MPID 321, MPID 322, MPID 325, MPID 332, MPID 335, MPID 336)
Modification recommendations under review: 5 (MPID 293, MPID 319, MPID 320, MPID 327, MPID 329)

## Slide 30: Update Grid Code Modification Stats
25/09/2025

## Slide 31: Modification Update
Modification | #
Decisions made by CRU since 26 June 2025 | 6
Recommendation papers with CRU for decision | 5
Housekeeping Modification Batches (since 26 June): Approved With CRU for Decision | All up to date
Modifications proposed at GCRP 25 September (today) | 4
Further information on modifications can be found on the EirGrid website here.
25/09/2025
31
Notes: Approved Modifications:
MPID 321 IOS Reference Correction – effective 04/07/2025
MPID 322 CNC and non-CNC Definitions – effective 07/07/2025
MPID 325 PPM Introduction – effective 08/07/2025
MPID 332 Reactive Energy Definition – effective 8 July 2025
MPID 335 Definition for Current – effective 12 September 2025
MPID 336 Housekeeping Process – effective 15 September 2025
Awaiting Decision:
MPID 329 Demarcation of Requirements
MPID 327 Notice to React
MPID 320 NPDR
MPID 319 Incorporation of SCUs
MPID293 DRAI DSU Maximum Downtime

## Slide 32: AOB
25/09/2025
32

## Slide 33: Thank you
25/09/2025
33
Meeting Minutes will be issued by COB 09 October 2025