## Slide 1: JGCRP Meeting
27 March 2025
1

## Slide 2: Agenda
27/03/2025
Introduction: 10 mins Welcome Members. Minutes and Actions from Previous Meeting. Modifications: 20 mins MPID328 and SPID_XX_2025 – Demand Side Units Notice to Respond. MPID 319 and SPID_07_2024 – Incorporation of the SCU Requirements; Updates: 10 mins CRU; and Utility Regulator. AOB. 5 mins

## Slide 3: 1. Introduction: 10 minutes
  Welcome Members
  Minutes and Actions from Previous Meeting
27/03/2025

## Slide 4: MPID328 and SPID_XX_2025 – Demand Side Units Notice to Respond
27/03/2025
2. Modifications: 10 minutes

## Slide 5: Solving the stated problem
Situations occur where a unit fails to deliver a response when dispatched and the TSO has to source MW elsewhere. The TSO needs to be able to exclude the failed unit.
  This is an important problem to solve
  DRAI would like to see it solved for DSUs
MPID 327 doesn’t solve the problem stated above
  No minimum response level defined
  Site that do not meaningfully respond, but do a small amount (e.g. 10%) will not be excluded
Key issue: MPID 327 copies the rules around synchronisation of generators, but DSUs do not have an equivalent to the synchronisation step
Unintended consequence
  Introduces new requirement for response to be visible within 15 minutes of effective time
  Large consumers who participate as a DSU and respond as per their Grid Code requirements and TOD would routinely, and wrongly, be caught by this
Possible outcomes
  Sites leave DSUs, reducing capacity available on the system
  Sites require retesting to change TOD – much admin, but no actual improvements

## Slide 6: Intent of MPID 328
The intent of this modification is to introduce a mechanism to exclude a DSU from dispatch if it fails to respond, roughly equivalent to the “Failure to Follow Notice to Synchronise” mechanism for generators, but adapted as necessary to accommodate DSUs, which (a) do not have a synchronisation step, and (b) do not follow any particular shape of ramp.
In addition, we are seeking both (a) to avoid imposing new requirements which would prevent useful customers from participating, and (b) to avoid leaving loopholes which would make it easy for a poorly-performing customer to avoid exclusion.

## Slide 7: Explicit new requirement in MPID 328
At least 80% of Demand Side Unit MW Response by the Demand Side Unit MW Response Time

## Slide 8
Proposed Text
SDC2.4.2.11 Action Required from Users | (e) Where the TSO issues a Notice to Respond Instruction via a Dispatch Instruction to a Demand Side Unit Operator and the Demand Side Unit Operator identifies that the Demand Side Unit will not be providing at least 80% of its instructed Demand Side Unit MW Response by the end of its Demand Side Unit MW Response Time, the Demand Side Unit Operator must immediately (at the time the discrepancy is identified) inform the TSO of the situation and estimate the achievable Demand Side Unit MW Response that the Demand Side Unit will be able to deliver by that time. (f) If the Demand Side Unit has not responded by providing at least 80% of its instructed Demand Side Unit MW Response within its Demand Side Unit MW Response Time following a Notice to Respond instruction, the TSO will issue a Failure to Follow Notice to Respond Instruction and the Demand Side Unit Operator shall re-declare, by Electronic Interface or by other form as the TSO may reasonably notify them from time to time, the Availability of the Demand Side Unit to the achievable Demand Side Unit MW response, for the effective time of the original Notice to Respond.
Definitions | 
Notice to Respond | A Dispatch Instruction issued by the TSO to a Demand Side Unit Operator to initiate Demand Side Unit MW Response from a zero MW value at the stated effective time.
Failure to Follow Notice to Respond Instruction | A Dispatch Instruction issued by the TSO to a Demand Side Unit Operator in respect of its Demand Side Unit confirming that it has failed to provide at least 80% of its instructed Demand Side Unit MW Response by the end of its Demand Side Unit MW Response Time.

## Slide 9
Thank you!
Questions?
27/03/2025

## Slide 10: MPID319 and SPID_07_2024 Incorporation of Synchronous Condenser Units
27/03/2025
2. Modification: 10 minutes

## Slide 11: Purpose of Proposed Modification
To incorporate the Grid Code Implementation Note for Synchronous Condensers and Industry feedback received thereon.
  Originally published October 2022
  Requirements would hence be regulated, giving certainty to all parties
Ensure the needs of Low Carbon Sources of Inertia (LCSI) System Services are captured within the Grid Code.
Future proof for Scheduling and Dispatch Tranche 2, where possible.

## Slide 12: New User Type
SONI and EirGrid propose that Synchronous Condenser Units (SCUs) are an entirely new user type within the Grid Codes.
  They are not bound by any existing EU Connection Network Codes (including the RfG).
  They are not a subset of an existing user type, such as Generators or PPMs.
  Existing synchronous generators with a clutch for synchronous compensation should apply existing Generator requirements, not SCU.
SCU requirements are modified versions of Generator requirements.
SCUs have been included explicitly within PC, PC.A, CC, OC, SDC1, SDC2 and Definitions sections.

## Slide 13: Background
SCU Implementation Note
Discussion Item – SCUs Grid Code User Type
TSO Response Document
Issued on 26 July 2024 and requested further feedback by 16 August 2024
Published Oct 2022 to offer guidance to those planning to connect SCUs to provide system services
JGCRP 20 March 2024, red and green lines circulated to members for feedback by 3rd May 2024
Further engagements with Industry
Fed into modification proposal brought to 4th Dec JCGRP
Public Consultation & revised Modification Proposal
Feedback received over this period has fed into revised modification proposal presented at this JGCRP

## Slide 14: Changes to mod proposal since Dec 2024 driven by industry feedback
PC.A10.1: SCUs are required to submit “Maximum continuous operation losses (MW)” as part of their Planning Data, as opposed to “Continuous operation consumption(MW)”;
SCU1.4.3: The requirement for SCUs to provide synchronisation via the Grid Connected Transformer HV circuit breakers has been removed with revised text to be included;
SCU1.7.1.1: For SCUs with a Connection Point on the HV side of the Grid Connected transformer, the requirement to provide signals from the HV side of the Grid Connected Transformer has been removed;
No requirement to submit PNs - aligns with current market mod discussions. No requirement to submit COD in latest circulated version of GC mod, but this requirement will be included, and an updated GC mod document will be circulated post this meeting.
Some typos and auto referencing errors have been corrected

## Slide 15: Addressing remaining feedback
PC.A10.6 § Excitation System:
Provide parameters and supply a Laplace-domain control block diagram (or as otherwise agreed with the TSO) completely specifying all time constants and gains to fully explain the transfer function from the compensator or generator terminal voltage and field current to generator field voltage. These parameters may include but are not limited to:" [Table included in redline and greenline documents]
Question: whether standard model according to IEEE 421.5 are acceptable as Laplace representation of the control block diagram.
Answer: TSOs currently reviewing modelling capabilities and requirements. Users can submit this standard model, and TSO will request further information if required.

## Slide 16: Addressing remaining feedback
PC.A10.7 § Control Devices (including Power System Stabilisers) and Protection Relays
Supply any additional Laplace domain control diagrams and associated parameters for any outstanding control devices including Power System Stabiliser or special protection relays in the Synchronous Condenser Unit, which automatically impinge on its Operating Characteristics within 30 seconds following a System Disturbance and which have a minimum time constant of at least 0.02 seconds.
Question: whether this is mandatory for SCUs as Power System Stabilizer typically not activated.
Answer: SCU1.6.10 TSO may require an SCU to install additional protection and/or control schemes, where the TSO can reasonably show that it is prudent or necessary to do so. These schemes may include but are not limited to the following: (f) Power System stabiliser.
Where the TSO requires an SCU User to have PSS, the User will need to submit relevant models.

## Slide 17: Addressing remaining feedback
AVR and tap changer sequence comment
The correct and optimal sequencing of AVR and tap change voltage regulation (i.e. which comes first) depends on scenario at the time of the need. For example, if it is from an EDIL instruction this should be a slower response and thus the tap change should come first followed by the AVR on the generator terminals. If the adjustment is as a result of a transient (i.e. fast voltage) change in the grid, then the AVR should respond first. Details of operation should be agreed by the synchronous condenser operator and the TSO for each unit separately.
Comment: This sequencing principle should be codified in the Grid Code, and any deviation must be agreed between TSO and user.
Answer: TSOs do not believe a sequencing principle should be codified in the Grid Codes as it could be addressed on a case-by-case basis, where the relevant TSO and the user would come to an agreement on the details of operation.

## Slide 18: Addressing remaining feedback
Availability Definition
At any given time, the measure of Active Power a Synchronous Condenser Unit is capable of importing to the Connection Point and the term “Availabilities” shall be constructed construed accordingly. This can be calculated as a gross figure.
Question: significant reservations regarding the definition of availability with respect to active power (even if it is defined as with respect to "Active Power Demand"). SCUs should have binary availability (1 or 0) or is rated in terms of available Inertia. As various SCUs will have different active power demand levels depending on operation, what should the declared availability level be, and use of this to NCC?
Answer: In terms of Forecast Availability profile for SCUs, this value will just be zero.
In terms of Forecast Minimum Output profile for SCUs, this value will be zero or some negative value (at least -1 MW), indicating consumption of MW, as SCUs will consume MW in order to provide inertia. This is the value the TSO will be referring to.

## Slide 19: Addressing remaining feedback
Reactive Power Capability
Question: the region within the proposed Grid Code rectangular reactive power requirement (i.e. ≤0.8 p.u and ≥-0.4 p.u) should be clipped to address the issue of non-ideal operating conditions and increased costs associated with the TSO proposed requirements
Answer: SCUs are designed to provide reactive power capability and to replace synchronous generators at high levels of SNSP. The TSOs do not believe the requirements are onerous - The proposed SCU minimum leading capability is slightly less than for a synchronous generator, while the proposed lagging capability (0.8p.u.) is above that of a synchronous generator but is still well below the 1.0p.u. rating of the SCU and accounts for transformer losses.
The TSOs want to ensure we get capability on the system which may be used partially or fully as the grid evolves, e.g. production of reactive power at high voltage (i.e. 1.1 pu voltage) may be necessary to support voltage in weak grid areas, maintain voltage stability in high load conditions, prevent voltage collapse in long transmission lines, control power flow and reduce line overloading, support the system during extreme scenarios such as power system restoration. Requiring a rectangular V/Q capability is also in line with what SONI and EirGrid require for synchronous generators, HVDC interconnectors and PPMs.

## Slide 20
Thank you!
Questions?
27/03/2025

## Slide 21: 4. Updates: 10 minutes
  CRU; and
  Utility Regulator.
27/03/2025

## Slide 22: AOB
Meeting Minutes will be issued by COB 10 April 2025
22
27/03/2025