## Changes to GC Text
Location | Description
PC.A2.2.1 | The text " which is assumed to be at the HV bushings of the Grid Connected Transfromer" has been removed.
CC.5.3 | Inclusion of new naming designation for 220 / 66 kV Offshore Connection transformers
CC.7.3.1.1(x) | Inclusion of 66 kV voltage range
CC.8.3.1 | Inclusion of 66 kV voltage range "(d) 66 kV system: 63 kV to 69 kV"
CC.8.3.2 | Inclusion of 66 kV voltage range "(d) 66 kV system: 60 kV to 72 kV"
CC.8.5 | Deletion of "The Transmission System is an effectively earthed neutral system with an earth fault factor of less than 1.4"
CC.8.5.1 | Inclusion of "For 400kV, 220 kV and 110kV, the Transmission System is an effectively earthed neutral system with an earth fault factor of less than 1.4."
CC.8.5.2 | Inclusion of "The 66 kV system is an impedance earthed system, and as a result, the 66 kV insulation systems must be fully rated for the maximum line to line voltage."
CC.8.6 | Inclusion of "(e) 25 kA on the 66 kV system generally"
CC.10.1 | Inclusion of "(a) For the 66 kV system: 1) 400 ms for single-phase faults; 2) 100 ms for two and three phase faults;"
CC.12.2(e) | For signals and indications required to be provided by Users, inclusion of "and Offshore Connection Transformer" in sentence "kV at Generator Transformer and Offshore Connection Transformer LV terminals"
OC.4.4.1.3 | Inclusion of tap-changing on "Offshore Connection Transformer" as voltage control strategy used by TSO
OC.4.4.5.9 | Inclusion of 220 /66 kV Transmission System transformers
OC.11.4.1 | Inclusion of the text "EirGrid Safety Rules, or Users Safety Rules" as appropriate" and ", EirGrid Safety Rules"
OC.11.4.3 | Inclusion of the text "In the event of a conflict between the provisions of this Code and the provisions of the Eirgrid Safety Rules, the provisions of the Eirgrid Safety Rules shall take precedence."
OC.11.4.5 | Inclusion of the text "or EirGrid Safety Rules", "or Eirgrid Safety Rules" and ", as appropriate".
PPM1.3.2 | inclusion of OC.4.4.5.6 in the excluded connection conditions
PPM1.6.1 | Inclusion of the text ", excluding Offshore PPMs," Inclusion of the text "Offshore PPMs shall remain continuously connected to the Transmission System at maximum Available Active Power or Controllable Active Power and operate within the ranges of the Transmission System Voltage at the Connection Point, as specified below: (a) 66 kV system: 63 kV to 69 kV (0.95 p.u. to 1.05 p.u.) for an unlimited time period (b) 66 kV system: 60 kV to 63kV (0.909 p.u to 0.95 p.u.) and 69 kV to 72 kV (1.05 p.u to 1.09 p.u.) for a period of 15 minutes."
PPM1.6.2.1 | Exclusion of Offshore PPMs from Automatic Voltage Regulation
PPM1.6.2.2(a) | Exclusion of Offshore PPMs from Automatic Voltage Regulation
PPM1.6.2.2(b) | Exclusion of Offshore PPMs from Automatic Voltage Regulation
PPM1.6.2.2(c) | Exclusion of Offshore PPMs from Automatic Voltage Regulation
PPM1.6.2.3 | Exclusion of Offshore PPMs from Automatic Voltage Regulation
PPM1.6.2.4 | Exclusion of Offshore PPMs from Automatic Voltage Regulation
PPM1.6.3.1(a) | Previously labelled as PPM1.6.3.1. Offshore PPMs are excluded from this section.
PPM1.6.3.1(b) | A new section which states "b). (b) Offshore PPMs operate at at least unity Power Factor, or as agreed with the TSO, at the Connection Point, as measured over the normal Voltage ranges as defined in CC.8.3.2. During disturbed Voltages as defined in CC.8.3.2, Offshore PPMs may deviate from operating at unity Power Factor."
PPM1.6.3.4 | Exclusion of offshore PPMs
PPM1.6.3.5 | Renumbering of existing text "In the event of power oscillations, Controllable PPMs shall retain steady-state stability when operating at any operating point of the Reactive Power capability."
PPM1.6.3.6 | Formatting correction- 2nd sentence had previously been numbered as a separate clause.
PPM1.6.5.1 | Exclusion of offshore PPMs.
PPM1.7.1.1.1 | Exclusion of offshore PPMs
PPM1.7.1.1.2 | Inclusion of signal requirements for offshore PPMs
PPM1.7.2.2 | Removal of the text "of a single analogue value and a strobe pulse to enable". Inclusion of the text "as specified in the relevant signal list"
PPM1.7.2.4 | Exclusion of Offshore PPMs.

## Changes to GC Defintions
Description | New / Modified existing Defintion | Defintion wording
EirGrid Safety Rules | New | The current version of the document prepared by the TSO and entitled “EirGrid Safety Rules”
Offshore Connection Transformer | New | A transformer located on an offshore platform, forming part of the Plant and Apparatus of the Transmission System, providing the connection between an Offshore PPM and the Network.
Offshore PPM | New | A Controllable PPM that has a single Connection Point on an offshore platform to the Transmission System.
Power Park Module (PPM) | Modified existing definition | A Generation Unit or ensemble of Generation Units generating electricity which; • Is connected to the Network non-synchronously or through power electronics, • Has a single Connection Point onshore to a Transmission System, Distribution System or HVDC System.
Transmission Asset Owner (TAO) | Modified existing definition | The ESB, acting in its capacity as a Transmission System Owner, pursuant to section 14.1(f) of the Act.
Transmission System Operator (TSO) | Modified existing definition | The holder of the licence granted pursuant to Section 14.1(e) of the Act 1999 to operate a Transmission System.
Transmission System Owner | Removed existing definition | The holder of the licence granted pursuant to Section 14 of the Act to own the Transmission System.
Voltage | Modified existing definition | Voltage of relevant section of Transmission System - nominally 400kV, 220kV, 110kV or 66 kV.