## Slide 1: JGCRP Meeting
O4 December 2024
04/12/2024
1

## Slide 2: Agenda
Introduction: Welcome Members. Minutes and Actions from Previous Meeting. Modifications: MPID319 and SPID_07_2024 - Incorporation of Synchronous Condenser Units. Discussion: Large Energy Users Fault-ride-through. Updates: CRU; and Utility Regulator. AOB.
04/12/2024

## Slide 3: 1. Introduction: 10 minutes
  Welcome Members
  Minutes and Actions from Previous Meeting (24 Sept 2024)
04/12/2024

## Slide 4: MPID319 and SPID_07_2024 Incorporation of Synchronous Condenser Units
04/12/2024
2. Modification: 15 minutes

## Slide 5: Purpose of Proposed Modification
To incorporate the Grid Code Implementation Note for Synchronous Condensers and Industry feedback received thereon.
  Originally published October 2022
  Requirements would hence be regulated, giving certainty to all parties
Ensure the needs of Low Carbon Sources of Inertia (LCSI) System Services are captured within the Grid Code.
Future proof for Scheduling and Dispatch Tranche 2, where possible.
04/12/2024

## Slide 6: Background
Implementation Note for SCUs was published by SONI and EirGrid in Oct 2022 to offer guidance to those planning to connect SCUs to provide system services.
This I.N. did not propose any Grid Code modifications at the time but allowed for the submission of stakeholder feedback on its contents with the intention of implementing SCUs into the Grid Codes in the future.
On 20 March 2024, the incorporation of SCUs into the Grid Codes as a new User type was brought as a discussion item to the SONI and EirGrid JGCRP, with draft red- and green-line versions of both Grid Codes circulated to members for feedback by 3rd May 2024.
Upon receiving feedback from industry, the TSO issued a response document on 26 July 2024 and requested further feedback by 16 August 2024.
After TSO review of additional feedback, further engagement was required between the TSO, industry and OEMs to solidify voltage regulation requirements for SCUs, which was indicated to JGCRP members at the JGCRP meeting on 24th September 2024.
A revised modification incorporating feedback from these engagements is presented today.
04/12/2024

## Slide 7: New User Type
SONI and EirGrid propose that Synchronous Condenser Units (SCUs) are an entirely new user type within the Grid Codes.
  They are not bound by any existing EU Connection Network Codes (including the RfG).
  They are not a subset of an existing user type, such as Generators or PPMs.
  Existing synchronous generators with a clutch for synchronous compensation should apply existing Generator requirements, not SCU.
SCU requirements are modified versions of Generator requirements.
SCUs have been included explicitly within PC, PC.A, CC, OC, SDC1, SDC2 and Definitions sections.
04/12/2024

## Slide 8: Key Inclusions
New PC.A section is proposed for Planning Data Requirements
Mvar Set Point Control and Voltage Set Point Control are both be included and will be measured at the Connection Point
New CC Schedule section (SONI only)
A new SCU section has been added (EirGrid Only)
SCU signal list included (EirGrid only)
Modification to PPM Settings Schedule is required (SONI only)
04/12/2024

## Slide 9: Key Changes since discussion item
04/12/2024
Voltage control strategies used by the TSO will include utilisation of SCU Reactive Power capability by means of suitably acting Voltage Regulation System control of SCUs only. SCUs are not required to have the capability to receive and respond to Mvar Dispatch Instructions issued by the TSO.
Regarding Dispatch Instructions, SCUs will only be required to have the capability to receive and respond to Sync and Desync Dispatch Instructions from the TSO.
In SCU1.4.7.2, the word “implemented” has been replaced with the word “initiated” to clarify the requirement that SCUs shall initiate a change to the Reactive Power (Q) control set-point or Voltage Regulation (kV) Set-point within 20 seconds of receipt of the appropriate signal from the TSO. The change is not required to be completed within 20 seconds.
In SCU1.6.10, addition of loss of excitation protection.

## Slide 10: Additional Change since circulation
04/12/2024
Additional text under SCU1.4.7.1
Synchronous Condenser Units shall have a continuously variable and continuously acting Voltage Regulation System with similar response characteristics to a conventional Automatic Voltage Regulator and shall perform generally as described in BS4999 part 140, or equivalent European Standards and the characteristics of which have been accepted by the TSO prior to the Connection Date, such acceptance not to be unreasonably withheld.
Additional text under SCU1.4.7.2
The excitation system of each Synchronous Condenser Unit shall normally be operated under the control of a continuously acting AVR, which shall be set so as to maintain a constant terminal voltage.
The Synchronous Condenser Unit may not disable or restrict the operation of the Voltage Regulation System except in accordance with SCU1.4.7.3, in which event the Synchronous Condenser Unit shall notify the TSO without delay.

## Slide 11: Additional change since circulation
04/12/2024
New text under SCU1.4.7.3
The Synchronous Condenser Unit may only disable or restrict Voltage Regulation System action where:
the action is essential for the safety of personnel and/or Plant; or
in order to (acting in accordance with Good Industry Practice), secure the reliability of the Synchronous Condenser Unit; or
the restriction is agreed between the TSO and the Synchronous Condenser Unit in advance.
New text under SCU1.4.7.4
The Voltage Regulation System slope shall be capable of being set to any value between 1% and 10%. This setting shall be settable online by the TSO.
The parameters and settings of the components of the Voltage Regulation System shall be agreed between the Synchronous Condenser Unit Operator and the TSO.

## Slide 12: Additional Change since circulation
04/12/2024
Removal of SCU1.4.7.5
The speed of response of the Voltage Regulation System shall be such that, following a step change in Voltage at the Connection Point the Synchronous Condenser Unit shall achieve 90 % of its steady-state Reactive Power response within 5 seconds. The response may require a transition from maximum Mvar production to maximum Mvar absorption or vice-versa.
Addition of VRS slope setting to SCU signal list SCU1.7.1.1
Signals and indications required to be provided by Synchronous Condenser Units to the TSO will include but shall not be limited to the following: […]
(e)
  v. Voltage Regulation System slope setting (%);

## Slide 13
Thank you!
Questions?
04/12/2024

## Slide 14: Fault Ride-Through Requirements for Demand Facilities
JGCRP Meeting
04 December 2024
3. Discussion: 15 minutes

## Slide 15: Fault Ride-Through Requirements for Demand Facilities
The TSOs are proposing the inclusion of Demand Facility Fault Ride-Through Requirements in the Grid Codes to address the issue with some Demand Facilities reducing and restoring their demand in response to remote system faults.
A draft modification proposal was originally presented as a discussion item to the JGCRP on 24th September 2024. The TSOs were aiming to submit a draft modification to members at the December 2024 JGCRP/GCRPs.
The TSOs hosted an industry webinar on October 22nd to discuss our draft proposal and seek feedback. Based on the feedback we have received, and requests to provide more time for consideration of the issues, we have decided to delay bringing forward our Grid Code modification proposal to facilitate further engagement with industry.
We will hold a further Industry Webinar on December 10th to provide an update on our proposal and next steps. There will also be an opportunity for any Demand Facility customer to present on work they are undertaking to address this issue.
The TSOs are aiming to complete this engagement and submit a revised draft modification to members at the March 2025 JGCRP/GCRPs.

## Slide 16: Further Consideration for Grid Code Amendments
Frequency and Voltage range standards
These standards are now only applied on DCC units.
Also apply these standards to Non-DCC units.
Rate of Change of Frequency
Include the application of the Rate of Change of Frequency (RoCoF) standard for Ireland and NI power systems ( +/- 1.0 Hz/s)
Active Power Recovery
Add requirements for the recovery of the Demand Facilities’ load following system fault.
Define recovery timeframes
EirGrid Grid Code – ‘DCC Unit’ Standards

## Slide 17: Further Consideration for Grid Code Amendments
Position Paper on Connection Requirements for Power to Gas Demand Facilities
ENTSO-E published a position paper recommending an implementation of connection requirements for Power-to-Gas demand facilities.
“A large number of new power-to-gas units will likely be connected to the system before the new network code provisions are normally nationally implemented. The connection of these units without appropriate and coordinated technical requirements may therefore create an important risk for system robustness”.
The position paper recommends TSOs establish minimum technical requirements for Power to Gas demand facilities to ensure grid resilience, including fault ride through requirements, RoCoF robustness, and post fault active power recovery.

## Slide 18: Next Steps
The TSOs are hosting a second online industry webinar on the Demand Facility Fault Ride Through proposal.
  Date/Time: Tuesday 10 December 2024, 10:00 to 12:00
The TSOs intend to return to the March 2025 JGCRP, and individual EirGrid and SONI GC panels, to seek recommendations for the proposal.

## Slide 19: Open Discussion
19
04/12/2024

## Slide 20: 4. Updates: 10 minutes
  CRU; and
  Utility Regulator.
04/12/2024

## Slide 21: AOB
Meeting Minutes will be issued by COB 18 December 2024
21
04/12/2024