## Cover Sheet
Signal List and Control System Parameter settings for WINDFARM NAME (TLC) Type XX XX MW v1.0
Disclaimer:
This Signal List contains information (and/or attachments) which may be privileged or confidential. All content is intended solely for the use of the individual or entity to whom it is addressed. If you are not the intended recipient please be aware that any disclosure, copying, distribution or use of the contents of this message is prohibited. If you suspect that you have received this Signal List in error please notify EirGrid immediately. Further information can be found at: http://www.eirgridgroup.com/legal/

## Version Control
WINDFARM NAME (TLC)Signal List Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by
0.1 | 2020-02-01 | D Molloy | J McGuckin | D Gillespie | first draft
Note on D3: Administrator: All signal lists circulated to EMS and ESBT for Review before issuance.

## Req, Process & Notes Topology 3
Requirements as per the Distribution Code DCC11.1.4
Topology | 3 | Type C Wind Farm Power Station (WFPS) as per DCC11.1.4: A WFPS connected to the Distribution System via a dedicated feeder into an existing 110kV station.
Existing Type C
Wind Farm Registered Capacity | <5 MW | >= 5 MW | >= 10 MW
EirGrid RTU requirement
| No TSO RTU installed | TSO RTU Installed | TSO RTU Installed
Wind farm controls
|  | Active Power Control system | Active Power Control system
|  | Frequency Response system | Frequency Response system
Wind farm signals
|  | Available Active Power | Available Active Power
|  | Wind Farm Availability | Wind Farm Availability
|  | %WTG not generating due to high wind | %WTG not generating due to high wind
|  | %WTG not generating due to low wind | %WTG not generating due to low wind
Wind Speed
Wind Direction
|  |  | Air Temperature | DCC11.1.4 Figure 6
Air Pressure
Station controls
|  | Remote Control Enable Switch | Remote Control Enable Switch
|  | Dispatch Fail Lamp | Dispatch Fail Lamp
|  | Blue Alert Lamp | Blue Alert Lamp
Station signals
|  | Active Power Measurement | Active Power Measurement
|  | Reactive Power Measurement | Reactive Power Measurement
|  | Voltage Measurement | Voltage Measurement
|  | DSO cable protection signals | DSO cable protection signals
|  | Connection and / or Transformer HV CB | Connection and / or Transformer HV CB
|  | Connection and / or Transformer HV CB | Connection and / or Transformer MV CB
|  | Feeder 20kV CB's | Feeder 20kV CB's
Detailed Process Overview
Additional Notes
General Process Notes: |  |  | Reference Documents:
More information on the testing process for DSO connected wind farms can be found at the following link: |  |  |  | EirGrid Telecoms Interface Cabinet Connection Details (using ETI Ref)
Recommended ESBTS cabling standards advised on signal list
http://www.eirgridgroup.com/site-files/library/EirGrid/DSO-TSO-WFPS-process-Rev.1.0-.pdf |  |  |  | Network Operator Initiated Shutdown Specification
Remote Control Specification
|  |  | Grid Code | http://www.eirgridgroup.com/site-files/library/EirGrid/GridCodeVersion6.pdf
|  |  | Distribution Code: | https://www.esbnetworks.ie/docs/default-source/publications/distribution-code-v5-0.pdf?sfvrsn=6
|  |  | Available Active Power Standard | http://www.eirgridgroup.com/site-files/library/EirGrid/QualityStandardforWindfarmActivePower.pdf
Abbreviations
|  |  |  | TSO | Transmission System Operator - EirGrid
|  |  |  | EMS | Energy Management System - EirGrid
|  |  |  | DSO | Distribution System Operator - ESBN
|  |  |  | ESBN | ESB Networks
|  |  |  | ESBTS | ESB Telecoms Services
|  |  |  | RTU | Remote Terminal Unit
|  |  |  | ETIE | EirGrid Terminal Interface Enclosure
|  |  |  | NOIS | Network Operator Initiated Shutdown
|  |  |  | WTG | Wind Turbine Generator
|  |  |  | CB | Circuit Breaker
|  |  |  | MEC | Maximum Export Capacity (In accordance with the User's Connection Agreement)
|  |  |  | WFPS | Wind Farm Power Station
|  |  |  | GCCT | Grid Code Compliance Testing
|  |  |  | MV | i.e. 20kV
|  |  |  | HV | i.e. 38kV / 110KV
|  |  |  | DCC | Distribution Control Centre
|  |  |  | SDCC | South Distribution Control Centre, ESBN
|  |  |  | NDCC | North Distribution Control Centre, ESBN
|  |  |  | NCC | National Control Centre, EirGrid

## Req, Process & Notes Topology 4
Requirements as per the Distribution Code DCC11.1.4
Topology | 4 | Wind Farm Power Stations are classed as being Connection Type D when connected to the Distribution System via a dedicated 38kV, 20kV or 10kV feeder into an existing 38kV distribution station.
Exisitng Type D
Wind Farm Size | <5 MW | >= 5 MW | >= 10 MW
TSO RTU requirement
| No TSO RTU installed | TSO RTU Installed | TSO RTU Installed
Station controls
|  | EirGrid Remote Control Switch | EirGrid Remote Control Switch
|  | Network Operator Initiated Shutdown | Network Operator Initiated Shutdown
Wind farm signals
|  | Available Active Power | Available Active Power
|  | Wind Farm Availability | Wind Farm Availability
|  | %WTG not generating due to high wind | %WTG not generating due to high wind
|  | %WTG not generating due to low wind | %WTG not generating due to low wind
Wind Speed
|  |  | Wind Direction | DCC11.1.4 Figure 7
Air Temperature
Air Pressure
Station controls
|  | Remote Control Enable Switch | Remote Control Enable Switch
|  | Dispatch Fail Lamp | Dispatch Fail Lamp
|  | Blue Alert Lamp | Blue Alert Lamp
Station signals
|  | Active Power Measurement | Active Power Measurement
|  | Reactive Power Measurement | Reactive Power Measurement
|  | Voltage Measurement | Voltage Measurement
|  | DSO cable protection signals | DSO cable protection signals
|  | Connection and / or Transformer HV CB | Connection and / or Transformer HV CB
|  | Connection and / or Transformer MV CB | Connection and / or Transformer MV CB
|  | Feeder 20kV CB's | Feeder 20kV CB's
Detailed Process Overview
Additional Notes | [5 empty] | Reference Documents:
More information on the testing process for DSO connected wind farms can be found at the following link: | [6 empty] | EirGrid Telecoms Interface Cabinet Connection Details (using ETI Ref)
http://www.eirgridgroup.com/site-files/library/EirGrid/DSO-TSO-WFPS-process-Rev.1.0-.pdf | [6 empty] | Recommended ESBTS cabling standards advised on signal list
Network Operator Initiated Shutdown Specification
Remote Control Specification
[6 empty] | Grid Code | http://www.eirgridgroup.com/site-files/library/EirGrid/GridCodeVersion6.pdf
[6 empty] | Distribution Code: | https://www.esbnetworks.ie/docs/default-source/publications/distribution-code-v5-0.pdf?sfvrsn=6
[6 empty] | Available Active Power Standard | http://www.eirgridgroup.com/site-files/library/EirGrid/QualityStandardforWindfarmActivePower.pdf
Abbreviations
[7 empty] | TSO | Transmission System Operator - EirGrid
[7 empty] | EMS | Energy Management System - EirGrid
[7 empty] | DSO | Distribution System Operator - ESBN
[7 empty] | ESBN | ESB Networks
[7 empty] | ESBTS | ESB Telecoms Services
[7 empty] | RTU | Remote Terminal Unit
[7 empty] | ETIE | EirGrid Terminal Interface Enclosure
[7 empty] | NOIS | Network Operator Initiated Shutdown
[7 empty] | WTG | Wind Turbine Generator
[7 empty] | CB | Circuit Breaker
[7 empty] | MEC | Maximum Export Capacity (In accordance with the User's Connection Agreement)
[7 empty] | WFPS | Wind Farm Power Station
[7 empty] | GCCT | Grid Code Compliance Testing
[7 empty] | MV | i.e. 20kV
[7 empty] | HV | i.e. 38kV / 110KV
[7 empty] | DCC | Distribution Control Centre
[7 empty] | SDCC | South Distribution Control Centre, ESBN
[7 empty] | NDCC | North Distribution Control Centre, ESBN
[7 empty] | NCC | National Control Centre, EirGrid

## Req, Process & Notes Topology 5
Requirements as per the Distribution Code DCC11.1.4
Topology | 5 | Wind Farm Power Stations are classed as being Connection Type E when connected to an existing distribution line with load.
Existing RfG Type E
Wind Farm Size | <5 MW | >= 5 MW | >= 10 MW
TSO RTU requirement
| No TSO RTU installed | TSO RTU Installed | TSO RTU Installed
Station controls
|  | EirGrid Remote Control Switch | EirGrid Remote Control Switch
|  | Network Operator Initiated Shutdown | Network Operator Initiated Shutdown
Wind farm signals
|  | Available Active Power | Available Active Power
|  | Wind Farm Availability | Wind Farm Availability
|  | %WTG not generating due to high wind | %WTG not generating due to high wind
|  | %WTG not generating due to low wind | %WTG not generating due to low wind
|  |  | Wind Speed | DCC11.1.4 Figure 8
Wind Direction
Air Temperature
Air Pressure
Station controls
|  | Remote Control Enable Switch | Remote Control Enable Switch
|  | Dispatch Fail Lamp | Dispatch Fail Lamp
|  | Blue Alert Lamp | Blue Alert Lamp
Station signals
|  | Active Power Measurement | Active Power Measurement
|  | Reactive Power Measurement | Reactive Power Measurement
|  | Voltage Measurement | Voltage Measurement
|  | DSO cable protection signals | DSO cable protection signals
|  | Connection and / or Transformer HV CB | Connection and / or Transformer HV CB
|  | Connection and / or Transformer MV CB | Connection and / or Transformer MV CB
|  | Feeder 20kV CB's | Feeder 20kV CB's
Detailed Process Overview
Additional Notes |  |  |  |  | Reference Documents:
More information on the testing process for DSO connected wind farms can be found at the following link: | [5 empty] | EirGrid Telecoms Interface Cabinet Connection Details (using ETI Ref)
http://www.eirgridgroup.com/site-files/library/EirGrid/DSO-TSO-WFPS-process-Rev.1.0-.pdf | [5 empty] | Recommended ESBTS cabling standards advised on signal list
Network Operator Initiated Shutdown Specification
Remote Control Specification
[5 empty] | Grid Code | http://www.eirgridgroup.com/site-files/library/EirGrid/GridCodeVersion6.pdf
[5 empty] | Distribution Code: | https://www.esbnetworks.ie/docs/default-source/publications/distribution-code-v5-0.pdf?sfvrsn=6
[5 empty] | Available Active Power Standard | http://www.eirgridgroup.com/site-files/library/EirGrid/QualityStandardforWindfarmActivePower.pdf
Abbreviations
[6 empty] | TSO | Transmission System Operator - EirGrid
[6 empty] | EMS | Energy Management System - EirGrid
[6 empty] | DSO | Distribution System Operator - ESBN
[6 empty] | ESBN | ESB Networks
[6 empty] | ESBTS | ESB Telecoms Services
[6 empty] | RTU | Remote Terminal Unit
[6 empty] | ETIE | EirGrid Terminal Interface Enclosure
[6 empty] | NOIS | Network Operator Initiated Shutdown
[6 empty] | WTG | Wind Turbine Generator
[6 empty] | CB | Circuit Breaker
[6 empty] | MEC | Maximum Export Capacity (In accordance with the User's Connection Agreement)
[6 empty] | WFPS | Wind Farm Power Station
[6 empty] | GCCT | Grid Code Compliance Testing
[6 empty] | MV | i.e. 20kV
[6 empty] | HV | i.e. 38kV / 110KV
[6 empty] | DCC | Distribution Control Centre
[6 empty] | SDCC | South Distribution Control Centre, ESBN
[6 empty] | NDCC | North Distribution Control Centre, ESBN
[6 empty] | NCC | National Control Centre, EirGrid

## Signal Specification
TSO Remote Control Enable Switch (RCES)
RCES shall block all commands from the TSO RTU to the WFPS, including set-point enable pulses (except for the Blue Alert Lamp indication in TSO WFs following a Black Start Shutdown Command)
Turning the RCES ON or OFF shall not impact/change the status of any signals, commands, set-points or control modes (other than the position indication of the RCES).
For TSO WFPS
Blackstart Shutdown
See the "Blackstart Shutdown" tab for details on the functionality of Blackstart Shutdown.
Blackstart Shutdown feedback is provided from the associated transmission station, not from the WFPS
For DSO WFPS
Dispatch Fail Lamp
Dispatch Fail Lamp ON command shall turn on indication lamp in WFPS control room unless TSO RCES is OFF
Dispatch Fail Lamp OFF command shall turn off indication lamp in WFPS control room unless TSO RCES is OFF
Blue Alert Lamp
TSO WF: Black Start Shutdown ON command shall turn on Blue Alert indication lamp in WFPS control room
TSO WF: Black Start Shutdown OFF command shall turn off Blue Alert indication lamp in WFPS control room
DSO WF: Blue Alert Lamp ON command shall turn on indication lamp in WFPS control room unless TSO RCES is OFF
DSO WF: Blue Alert Lamp OFF command shall turn off indication lamp in WFPS control room unless TSO RCES is OFF
Set-point Enable Pulse
When a WFPS receives a set-point enable pulse (e.g. Active Power Control Set-point Enable), it shall implement the set-point on the associated analogue input (e.g. implement the Active Power Control set-point being received at that time).
If an analogue set-point signal changes and a corresponding set-point enable pulse is not issued, the WFPS shall ignore the change in the analogue signal.
Feedback for Analogue Signals
Feedback for analogue signals shall reflect the last received valid signal
i.e. feedback signals should not be looped from the analogue input. They should only change value when an Enable Pulse is received, and should not change value when the corresponding mode (e.g. Active Power Control) is turned off or the Remote Control Enable Switch is turned off.
Active Power Control ON/OFF
When Active Power Control is turned off, the set-point feedback shall not change, but wind farm output shall increase to maximum available MW.
Set-points received while Active Power Control is OFF should be ignored.
Active Power Control Set-point (Feedback)
The Active Power Control set-point feedback should not change when APC is switched on or off. It should reflect the last valid set-point that the WFPS received from NCC.
Note. Locally implemented set-points should not be fed back to NCC.
Worked Example:
● NCC turns APC on and issues a set-point of 10 MW (feedback goes to 10 MW, WFPS implements 10 MW set-point)
● NCC issues a set-point of 8 MW (feedback goes to 8 MW, WFPS implements 8 MW set-point)
● NCC turns APC off (feedback remains at 8 MW, WFPS ramps to minimum of AAP and Registered Capacity)
● NCC issues a set-point of 5 MW (feedback remains at 8 MW, WFPS remains at minimum of AAP and Registered Capacity)
● NCC turns APC on (feedback remains at 8 MW, WFPS ramps to 8 MW)
● NCC issues a set-point of Registered Capacity and turns APC off (feedback goes to Registered Capacity, WFPS ramps to minimum of AAP and Registered Capacity)
If the WFPS is reset, the default settings for the various controls should commit current state to memory (if this is not possible, default should be APC off, FQR on, Curve 1 etc.)
Frequency Response ON/OFF
When Frequency Response is Off, the WFPS shall not respond to any changes in Frequency. When Frequency Response is On, the WFPS shall respond to frequency in line with the specified frequency response settings.
When Frequency Response is turned On or Off, the selected Frequency Curve (and feedback) shall not be affected. i.e. Curve signal does not go suspect, and does not reset to a default value.
If Frequency Response is OFF, the Curve should not change.
Frequency Droop
Droop set-points received while Frequency Response is OFF should be ignored.
Frequency Droop must be settable in the range 2% to 10%, per Grid Code V7 clause PPM1.5.3.1
WFPS should treat any set-point <= 2% as 2% (implement 2% and provide 2% feedback)
WFPS should treat any set-point >= 10% as 10% (implement as 10% and provide 10% feedback)
Frequency Droop signal is specified in the range 0% to 12%, to facilitate signals at the upper and lower ends of the scale
In the case of hardware/software update or reset, the existing value shall be maintained. In the case that the existing value is lost, the WFPS shall default to 4%.
This signal shall be implemented in increments of 0.1% i.e. to 1 decimal place.
For TSO WFPS or DSO Type A or B WFPS
Reactive Power Control Modes (kV, Mvar, PF)
One control mode will be ON (in operation) at all time: Voltage Control (kV), Mvar Control (Q), or Power Factor Control (PF).
There are no individual OFF commands. NCC will toggle between control modes by sending an ON command for the required mode.
Position indication for the mode in operation will indicate ON and position indication for the other two modes will indicate OFF.
Response time to a change in set-point: as per Grid Code V7 clause PPM1.6.2.2
Power Factor Set-points:
Power Factor set-points are issued as an angle (±90 degrees), to avoid the signalling difficulties associated with issuing the non-linear Power Factor set-points.
If a positive angle is issued, the Power Factor implemented by the controll will be positive. If a negative angle is issued, the Power Factor implemented by the controller will be negative.
Worked Examples:
1) NCC issues A set-point of +18.19 degrees, WFPS implements a set-point of +cos(18.19) = +0.95 PF
2) NCC issues A set-point of -18.19 degrees, WFPS implements a set-point of -cos(18.19) = -0.95 PF
3) NCC issues A set-point of 0 degrees, WFPS implements a set-point of cos(0) = 1 PF
4) A WFPS exporting 100 MW with a set-point of +18.19 degrees would export +32.85 Mvar. i.e. Tan(+18.19)*100
Changing Control Modes (Bumpless Transfer):
1. WFPS calculates a set-point which will cause no change in Mvar. 2. WFPS continues to regulate to calculated set-point in the new mode.
Worked Example:
A WFPS with a Registered Capacity of 100 MW is exporting 50 MW, operating at a voltage slope setting of 4%. System voltage Is 118 kV and the kV set-point is 115 kV, therefore the WFPS is absorbing its maximum leading capability of 32.9 Mvar.
● NCC issues Mvar (Q) Control ON.
● WFPS calculates and implements a Mvar set-point of 32.9 Mvar, consistent with the current Mvar output. WFPS returns Mvar (Q) Control feedback ON, Voltage (kV) Control feedback OFF and Power Factor (PF) Control feedback OFF. Set-point feedback signals do not change.
● NCC issues a Mvar set-point of 10 Mvar.
● TSO RTU issues a Mvar (Q) Control set-point enable pulse to the WFPS. WFPS returns a set-point feedback of 10 Mvar and implements the set-point of 10 Mvar.
● NCC issues Power Factor (PF) Control ON.
● WFPS calculates and implements a Power Factor set-point of +0.98, consistent with the current MW and Mvar output. WFPS returns Power Factor (PF) Control feebdack ON, Voltage (kV) Control feedback OFF and Mvar (Q) Control feedback OFF. Set-point feedback signals do not change.
● NCC issues a Power Factor set-point of 0 degrees.
● TSO RTU issues a Power Factor (PF) set-point enable pulse to the WFPS. WFPS returns a set-point feedback of 0 degrees and implements the set-point of 0 degrees (1 PF).
● NCC issues Voltage (kV) Control ON.
● WFPS calculates and implements a Voltage set-point of 118 kV, consistent with the current system voltage and Mvar output. WFPS returns Voltage (kV) Control feebdack ON, Power Factor (PF) Control feedback OFF and Mvar (Q) Control feedback OFF. Set-point feedback signals do not change.
● NCC issues a Voltage set-point of 115 kV.
● TSO RTU issues a Voltage (kV) set-point enable pulse to the WFPS. WFPS returns a set-point feedback of 115 kV and implements the set-point of 115 kV.
Available Active Power
AAP must reflect what the WFPS is capable of exporting at that point in time
While a WTG is Shut down for maintenance, fault, high or low wind speed Shut down, flicker or noise, that turbine shall not be included in AAP
While a the output of a WTG is reduced due to Active Power Control Set-Point or frequency response, AAP shall reflect what the WFPS would be exporting if that APC set-point was not in place (accounting for WTGs that are shut down for reasons, above)
AAP shall not be greater than MEC.
% Availability
Specified in Grid Code and signal list as 0-100%
Grid Code definition of Controllable WFPS Availability: The amount of MW the Controllable WFPS can produce given favourable wind conditions
i.e. The combined capacity of all WTGs in service (including WTGs shut down due to APC set-point, or high/low wind speed shutdown) as a percentage of installed capacity.
This signal is independent of wind conditions and high or low wind speed shutdown.
Note. Any WTG which is stopped or shut down (not due to APC set-point, or high/low wind speed shutdown) should reduce the % Availability accordingly.
Worked examples:
1) Wind farm with 10 * 1 MW turbines
● Registered Capacity = 10 MW
● Out Of Service: 2 * 1 MW
2) Wind farm with 5*1 MW turbines and 5*2 MW turbines
● Registered Capacity = 15 MW
● Out of service: 1*1 MW turbine and 2*2 MW turbines
3) Wind farm with 20*1 MW turbines with an MEC of 18 MW
● Registered Capacity = 18 MW
● Out of service: 2 * 1 MW Turbines
% High Wind Speed Shutdown
% of installed MW that is shut down due to high wind speed
Worked example:
● Wind farm with 5*1 MW turbines and 5*2 MW turbines (15 MW total installed capacity) with an MEC of 13 MW
● Registered Capacity = 13 MW
● Out of service: 1*1 MW turbine and 2*2 MW turbines
● Shut down due to high wind speed: 1*1 MW turbine and 1*2 MW turbine
% Low Wind Speed Shutdown
% of installed MW that is shut down due to low wind speed
Worked example:
● Wind farm with 5*1 MW turbines and 5*2 MW turbines (15 MW total installed capacity) with an MEC of 13 MW
● Registered Capacity = 13 MW
● Out of service: 3*2 MW turbines
● Shut down due to low wind speed: 3*1 MW turbines
Emulated Inertia
Emulated Inertia FFR Availability
Defined in the "DS3 System Services New Signals Requirements for the Regulated Arrangements"
Emulated Inertia POR Availability
Defined in the "DS3 System Services New Signals Requirements for the Regulated Arrangements"
Transformer Tap Position
Transformer tap position is indicated via a 0-10 mA analogue signal. The lowest tap will be enumerated as 1 in the EirGrid EMS.
Worked Example:
1) A transformer tap range of -13 to +13 is represented as tap 1 to 27.
2) A transformer tap range of -13 to +7 is represented as tap 1 to 21.
Post Energisation
During Post energisation signals testing there should be NO external influencing factors, e.g. no commissioning works should take place on any turbines on site, as this may influence the outcome of the test.
% 𝐻𝑖𝑔ℎ 𝑊𝑖𝑛𝑑 𝑆𝑝𝑒𝑒𝑑 𝑆ℎ𝑢𝑡𝑑𝑜𝑤𝑛= (1∗1 𝑀𝑊+1∗2 𝑀𝑊)/(15 𝑀𝑊)∗100=20%
% 𝐴𝑣𝑎𝑖𝑙𝑎𝑏𝑖𝑙𝑖𝑡𝑦= (10 𝑀𝑊−(2∗1 𝑀𝑊))/(10 𝑀𝑊)∗100=80%
% 𝐴𝑣𝑎𝑖𝑙𝑎𝑏𝑖𝑙𝑖𝑡𝑦= (15 𝑀𝑊−(1∗1 𝑀𝑊+2∗2 𝑀𝑊))/(15 𝑀𝑊)∗100=66.666%
% 𝐴𝑣𝑎𝑖𝑙𝑎𝑏𝑖𝑙𝑖𝑡𝑦= (20 𝑀𝑊−(2∗1 𝑀𝑊))/(20 𝑀𝑊)∗100=90%
% 𝐴𝑣𝑎𝑖𝑙𝑎𝑏𝑖𝑙𝑖𝑡𝑦= (𝐼𝑛𝑠𝑡𝑎𝑙𝑙𝑒𝑑 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 −𝑐𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝑜𝑓 𝑊𝑇𝐺𝑠 𝑛𝑜𝑡 𝑖𝑛 𝑠𝑒𝑟𝑣𝑖𝑐𝑒 (𝑒.𝑔. 𝑢𝑛𝑑𝑒𝑟 𝑚𝑎𝑖𝑛𝑡𝑒𝑛𝑎𝑛𝑐𝑒 𝑜𝑟 𝑓𝑎𝑢𝑙𝑡))/(𝐼𝑛𝑠𝑡𝑎𝑙𝑙𝑒𝑑 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦)∗100
% 𝐻𝑖𝑔ℎ 𝑊𝑖𝑛𝑑 𝑆𝑝𝑒𝑒𝑑 𝑆ℎ𝑢𝑡𝑑𝑜𝑤𝑛= (𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝑜𝑓 𝑊𝑇𝐺𝑠 𝑖𝑛 𝐻𝑖𝑔ℎ 𝑊𝑖𝑛𝑑 𝑆𝑝𝑒𝑒𝑑 𝑆ℎ𝑢𝑡𝑑𝑜𝑤𝑛)/(𝐼𝑛𝑠𝑡𝑎𝑙𝑙𝑒𝑑 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦)∗100
% 𝐿𝑜𝑤 𝑊𝑖𝑛𝑑 𝑆𝑝𝑒𝑒𝑑 𝑆ℎ𝑢𝑡𝑑𝑜𝑤𝑛= (𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝑜𝑓 𝑊𝑇𝐺𝑠 𝑖𝑛 𝐿𝑜𝑤 𝑊𝑖𝑛𝑑 𝑆𝑝𝑒𝑒𝑑 𝑆ℎ𝑢𝑡𝑑𝑜𝑤𝑛)/(𝐼𝑛𝑠𝑡𝑎𝑙𝑙𝑒𝑑 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦)∗100
% 𝐿𝑜𝑤 𝑊𝑖𝑛𝑑 𝑆𝑝𝑒𝑒𝑑 𝑆ℎ𝑢𝑡𝑑𝑜𝑤𝑛= (3∗1 𝑀𝑊)/(15 𝑀𝑊)∗100=20%
M𝑣𝑎𝑟= 𝑇𝑎𝑛(𝑠𝑒𝑡𝑝𝑜𝑖𝑛𝑡)∗𝑀𝑊 𝑂𝑢𝑡𝑝𝑢𝑡

## DSO Required Inputs
WFPS Inputs for Signal List Development
1 | Wind Farm Power Station (WFPS) Name (including alternative names) | Included in submission 
2 | WFPS Connection Type as per the Distribution Code DCC11.1.4 | Included in submission 
3 | WFPS Maximum Export Capacity | Included in submission 
4 | WFPS Installed Capacity (for Phase developments, i.e. MEC 20MW Phase 1 10MWQ1 2014, Phase 2 additional 10MW Q2 2015 ) | Included in submission 
5 | The number of Market Units at the WFPS (Phase 1 &2 is one market unit or two separate market units, noting that if the WFPS consists of two market units then additional signals will be required). | Included in submission 
6 | Turbine Manufacturer | Included in submission 
7 | Tubrine Procurement Date | Included in submission 
8 | Turbine Design Minimum Operating Level | Included in submission 
9 | Energisation Date | Included in submission 
10 | Single Line Diagram (Note that for changes in SLD's, the Signal list requirements may change) | Included in submission 
| · Revision Number | Included in submission 
| · Ownership boundaries | Included in submission 
| · HV CB positions (WFPS and ESBN as applicable) | Included in submission 
| · MV CB positions | Included in submission 
| · MV Feeders | Included in submission 
11 | Number of and Height of Met Masts on site - (if WFPS ≥10MW) | Included in submission 
12 | Nearest 110kV Station - normal feeding arrangements for WFPS | Included in submission 
13 | Connecting DSO Station - normal feeding arrangements for WFPS | Included in submission 
14 | Confirmation of DSO RTU for the WFPS? | Included in submission 
15 | If there is no DSO RTU submission of DCC signals to be included within the DSO RTU (1-18). | Included in submission 
16 | System Services Provided | Fast Frequency Response:  Primary Operating Reserve:  Secondary Operating Reserve:  Tertiary Operating Reserve: 
Information to be submitted to generator_testing@eirgrid.com via NDCC/SDCC

## 0) Signal List
WINDFARM NAME (TLC) |  | Topology | XX | XX | MW | v1.0 |  | Signals List is based on this Single Line Diagram (SLD) as inserted.
EirGrid Signals, Command & Control Specification (Ref: DCC11.5)
Signals List |  | Registered Capacity: XX MW |  |  |  | Installed Plant: XXX MW |  | MEC: XXX MW
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
| Double Point Status Indications | (each individual input identified separately for clarity) | [5 empty] | Note: Signals treated as 2-bit binary
Digital Input Signals from Sub Station to EirGrid
A1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open |  |  | ESBN | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A2 | ESBN 20 kV interface switch (Nulec Recloser) |  | closed |  |  | ESBN | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A3 | WINDFARM NAME (TLC) T421 WFPS 20 kV CB |  | open |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A4 | WINDFARM NAME (TLC) T421 WFPS 20 kV CB |  | closed |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 | Typical SLD for a wind farm connecting to the system through a 38/20 kV transformer
A5 | WINDFARM NAME (TLC) Feeder 1 20 kV CB |  | open |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A6 | WINDFARM NAME (TLC) Feeder 1 20 kV CB |  | closed |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A7 | WINDFARM NAME (TLC) Feeder 2 20 kV CB |  | open |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A8 | WINDFARM NAME (TLC) Feeder 2 20 kV CB |  | closed |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A9 | WINDFARM NAME (TLC) Feeder 3 20 kV CB |  | open |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A10 | WINDFARM NAME (TLC) Feeder 3 20 kV CB |  | closed |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A11 | WINDFARM NAME (TLC) Feeder 4 20 kV CB |  | open |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A12 | WINDFARM NAME (TLC) Feeder 4 20 kV CB |  | closed |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | WFPS | N/A | Distribution Code Signals List #1 DCC11.5.1.1 (Blocks all commands to WFPS equipment, located on WFPS side)
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | WFPS | N/A | Distribution Code Signals List #1 DCC11.5.1.1 (Blocks all commands to WFPS equipment, located on WFPS side)
A15 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN
A16 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN
A17 | Blue Alert Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN
A18 | Blue Alert Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A23 | Reactive Device >5 Mvar N |  | off |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A24 | Reactive Device >5 Mvar N |  | on |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B7 | Emulated Inertia status (Feedback) |  | off |  |  | WFPS | ESBN | Feedback from IPP to confirm the status of emulated inertia service
B8 | Emulated Inertia status (Feedback) |  | on |  |  | WFPS | ESBN | Feedback from IPP to confirm the status of emulated inertia service
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (125% of Registered Cpapacity)
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (150% of Reactive Power at Registered Capacity)
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (125% of nominal conection voltage)
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (125% of Registered Capacity)
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4 (125% of Registered Capacity)
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | WFPS | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Analogue WTG Availability
D4 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | ESBN | Distribution Code Signals List #3 DCC11.5.1.3
D5 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | ESBN | Distribution Code Signals List #3 DCC11.5.1.3
D6 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A | Distribution Code Signals List #3 DCC11.5.1.3
Analogue Availability
D7 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Provides a reading of the available MW of FFR from Emulated Inertia
D8 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Provides a reading of the available MW of POR from Emulated Inertia
Met 1 (if Registered Capacity >= 10 MW)
D9 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D10 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West), 10mA = 360deg (from the North)).
D11 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D12 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6
Met N (if Registered Capacity >= 10 MW)
D13 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D14 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6 (0mA = 0deg (from the East), 2.5mA = 90deg (from the North), 5mA = 180deg (from the West), 10mA = 360deg (from the East))
D15 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D16 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E7 | Emulated Inertia |  | off | pulse | 0.5 seconds | WFPS | N/A | Control from NCC to enable emulated inertia service
E8 | Emulated Inertia |  | on | pulse | 0.5 seconds | WFPS | N/A | Control from NCC to enable emulated inertia service
Digital Output Signals from EirGrid to Sub Station
F1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open | pulse | 0.5 seconds | ESBN | ESBN
F2 | ESBN 20 kV interface switch (Nulec Recloser) |  | close | pulse | 0.5 seconds | ESBN | ESBN
F3 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off | pulse | 0.5 seconds | WFPS | ESBN
F4 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on | pulse | 0.5 seconds | WFPS | ESBN
F5 | Blue Alert Lamp - WFPS Panel |  | off | pulse | 0.5 seconds | WFPS | ESBN
F6 | Blue Alert Lamp - WFPS Panel |  | on | pulse | 0.5 seconds | WFPS | ESBN
Strobe Enable Pulses
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4
E10 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | WFPS | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | WFPS | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | WFPS | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | WFPS | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | WFPS | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
Recommended cable 15-pair cable, 15 x 2 x 0.6sqmm, TP, stranded, external sheath
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4 (125% of Registered Capacity)
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | WFPS | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
Note on D1: Administrator: Insert the Type of the Wind Farm
Note on E1: Administrator: Insert the Registered Capacity of the WFPS
Note on A5: EirGrid Telecoms Interface Enclosure
Note on H5: No IPP involvement unless otherwise confirmed
Note on B9: Position indications required for all circuit breakers from connection point to wind farm feeders
Note on B13: Turbine Circuit Breakers are not Included. The number of Feeders is checked against the SLD attached above.
Note on B21: Described as TSO remote control enable switch in DSO code.
Note on D29: Typically reactive power device breaker. Open Closed maybe more correct.
Note on E49: +/-125%
Note on E51: 110kV: 0 to 132kV 38kV: 0 to 46.2kV 20kV: 0 to 24 kV
Note on E54: 0-125%
Note on E55: 0-125%
Note on E64: 0-10% Reg.Cap
Note on I113: Administrator: ESBN to provide reference to this document.
Note on E137: 0 to 125%

## 1a) Inst.Info & Contact Details
WINDFARM NAME (TLC) Information and Contact Details to be sent by WFPS via ESB Networks to EirGrid (generator_testing@EirGrid.com)
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
DATE
| HV SUB STATION NAME |  |  |  |  | ESBTS Team |  | Liam Boland
[6 empty] | Nessan Heaslip | Karl O'Keeffe | Noel Cowhey
| EirGrid Contact Person | C&T Team | PHONE: |  | (+353) 1 2370583 | Robert Groarke | Oisín Goulding
| OSP Generic Email: Generator_testing@eirgrid.com |  |  |  |  | Frank Donnelly | Colm MacManus
| EMS Generic Email: ems.services@eirgrid.com |  |  |  |  | Liam Delany | C&T Team
[6 empty] | Niall Molloy | Ciarán Maguire
| ESBTS Project Manager | ESBTS Team | PHONE: |  | (+353) 1 7027835
| ESBTS Commissioner | ESBTS Team | PHONE: |  | (+353) 1 7027835
ESBTS Generic Email: esbts.scada.services@esb.ie
| ESB Networks (SPOC) |  | PHONE:
ESB Networks Build Generic Email: IPPdelivery@esb.ie
| ESB Networks (switchgear) |  | PHONE: |  | (+ )
| ESB Networks (metering) |  | PHONE: |  | (+ )
| WFPS Project Manager |  | PHONE: |  | (+ )
| Electrical Contractor |  | PHONE: |  | (+ )
| Turbine Contractor |  | PHONE: |  | (+ )
| Work Programme / Schedule (.mpp format) |  |  | Insert File
| Single Line Diagram |  |  | Insert file
| Site Layout Drawing on OS Map |  |  | Insert file
| Substation & Control Building Layout Drawing on OS Map |  |  | Insert file
| WFPS Energy Management System %error |  |  | %
| Directions including Map to the Wind Farm Power Station | Insert Map and brief description
| Safety & Site information | WFPS to provide details
ESBTS Standard Requirements from WFPS (may be customised for particular sites):
1) 90sq mm earth for Telecoms earth bar. 2) 35sq mm bonded from external earth grid to GPS clock antenna mounting bracket and if applicable Satellite antenna mounting bracket. 3) 48V DC Power System consisting of Switched Mode Power Supply (SMPS) with sealed cell battery. 4) If applicable - Fibre termination cabinet with fibre termination unit and fibre to distant station. 5) Satellite link consisting of Satellite transceiver and antenna if applicable. Satellite antenna preferably on a south facing wall with a clear view of the horizon. 6) Install and terminate process control and signal cables in ETI (the wiring schedule is available as a worksheet in the signal list excel file).
| ESB Telecom Services - Indicative Timelines for on site works | 1) 3 weeks notice required by ESBTS to schedule resources. 2) ~1 week to install the RTU cabinet with integrated ETI and GPS clock, GPS clock antenna. 3) ~1 week to pre commission the RTU referenced to frozen signal list with WFPS electrical and WTG contractors. 4) ~1 week to install and commission the satellite link including antenna (if applicable). 5) ~2 days to commission the fibre link (if applicable). 6) ~1 week to commission the RTU with WFPS electrical and WTG contractors.

## 1b) WFPS Wiring Completion Cert
WINDFARM NAME (TLC) |  | Topology | XX | XX | MW | v1.0 |  | Signals List is based on this Single Line Diagram (SLD) as inserted. | Wiring Completion Cert
EirGrid Signals, Command & Control Specification (Ref: DCC11.5) | [8 empty] | Continuity Check Complete
WFPS Wiring Completion Certificate (to EirGrid ETIE/RTU) to be sent by WFPS via ESBN to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open |  |  | ESBN | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A2 | ESBN 20 kV interface switch (Nulec Recloser) |  | closed |  |  | ESBN | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A3 | WINDFARM NAME (TLC) T421 WFPS 20 kV CB |  | open |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A4 | WINDFARM NAME (TLC) T421 WFPS 20 kV CB |  | closed |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A5 | WINDFARM NAME (TLC) Feeder 1 20 kV CB |  | open |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A6 | WINDFARM NAME (TLC) Feeder 1 20 kV CB |  | closed |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A7 | WINDFARM NAME (TLC) Feeder 2 20 kV CB |  | open |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A8 | WINDFARM NAME (TLC) Feeder 2 20 kV CB |  | closed |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A9 | WINDFARM NAME (TLC) Feeder 3 20 kV CB |  | open |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A10 | WINDFARM NAME (TLC) Feeder 3 20 kV CB |  | closed |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A11 | WINDFARM NAME (TLC) Feeder 4 20 kV CB |  | open |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A12 | WINDFARM NAME (TLC) Feeder 4 20 kV CB |  | closed |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | WFPS | N/A | Distribution Code Signals List #1 DCC11.5.1.1 (Blocks all commands to WFPS equipment, located on WFPS side)
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | WFPS | N/A | Distribution Code Signals List #1 DCC11.5.1.1 (Blocks all commands to WFPS equipment, located on WFPS side)
A15 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN
A16 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN
A17 | Blue Alert Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN
A18 | Blue Alert Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A23 | Reactive Device >5 Mvar N |  | off |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A24 | Reactive Device >5 Mvar N |  | on |  |  | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B7 | Emulated Inertia status (Feedback) |  | off |  |  | WFPS | ESBN | Feedback from IPP to confirm the status of emulated inertia service
B8 | Emulated Inertia status (Feedback) |  | on |  |  | WFPS | ESBN | Feedback from IPP to confirm the status of emulated inertia service
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (125% of Registered Cpapacity)
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (150% of Reactive Power at Registered Capacity)
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (125% of nominal conection voltage)
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (125% of Registered Capacity)
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4 (125% of Registered Capacity)
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | WFPS | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Analogue WTG Availability
D4 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | ESBN | Distribution Code Signals List #3 DCC11.5.1.3
D5 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | ESBN | Distribution Code Signals List #3 DCC11.5.1.3
D6 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A | Distribution Code Signals List #3 DCC11.5.1.3
Analogue Availability
D7 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Provides a reading of the available MW of FFR from Emulated Inertia
D8 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Provides a reading of the available MW of POR from Emulated Inertia
D9 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D10 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West), 10mA = 360deg (from the North)).
D11 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D12 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6
Met N (if Registered Capacity >= 10 MW)
D13 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D14 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6 (0mA = 0deg (from the East), 2.5mA = 90deg (from the North), 5mA = 180deg (from the West), 10mA = 360deg (from the East))
D15 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D16 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Distribution Code Signals List #6 DCC11.5.1.6
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E7 | Emulated Inertia |  | off | pulse | 0.5 seconds | WFPS | N/A | Control from NCC to enable emulated inertia service
E8 | Emulated Inertia |  | on | pulse | 0.5 seconds | WFPS | N/A | Control from NCC to enable emulated inertia service
Digital Output Signals from EirGrid to Sub Station
F1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open | pulse | 0.5 seconds | ESBN | ESBN
F2 | ESBN 20 kV interface switch (Nulec Recloser) |  | close | pulse | 0.5 seconds | ESBN | ESBN
F3 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off | pulse | 0.5 seconds | WFPS | ESBN
F4 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on | pulse | 0.5 seconds | WFPS | ESBN
F5 | Blue Alert Lamp - WFPS Panel |  | off | pulse | 0.5 seconds | WFPS | ESBN
F6 | Blue Alert Lamp - WFPS Panel |  | on | pulse | 0.5 seconds | WFPS | ESBN
Strobe Enable Pulses
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4
E10 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | WFPS | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | WFPS | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | WFPS | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | WFPS | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | WFPS | ESBN | ESBN to specify Alarm type to WFPS. (not required if DSO RTU is installed)
Recommended cable 15-pair cable, 15 x 2 x 0.6sqmm, TP, stranded, external sheath
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A | Distribution Code Signals List #4 DCC11.5.1.4 (125% of Registered Capacity)
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | WFPS | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet must be clearly marked with labels for identification. |  |  |  | Confirmed  |  |  |  | How are each of the MET signals generated? E.g. From a MET mast or WTGs
All cables for interfacing at station interface cabinet or EirGrid telecoms interface cabinet must be terminated at connection terminals (i.e. stripped, crimped and marked at terminal connections). |  |  |  | Confirmed  |  |  |  | Wind Speed: Wind Direction: Air Temperature: Air Pressure:
All cables for interfacing at station interface cabinet or EirGrid telecoms interface cabinet must use colour coding agreed by all parties i.e. ESBTS & WFPS. |  |  |  | Confirmed 
All analogue and digital interface signals must be tested and simulated for compliance with the frozen signal list agreed by all parties. |  |  |  | Confirmed 
ESBTS Satellite Dish bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed 
ESBTS GPS clock antenna bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed 
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 | [6 empty] | WFPS Name / Position | 0
WFPS Signature
Date
Note on A3: Administrator: To be completed by the IPP and sent to EirGrid to schedule ESBTS site attendance to perform continuity check
Note on A5: EirGrid Telecoms Interface Enclosure

## 2) ESB Telecoms Completion Cert
WINDFARM NAME (TLC) |  | Topology | XX | XX | MW | v1.0 |  | Completion Cert
EirGrid Signals, Command & Control Specification (Ref: DCC11.5) | [7 empty] | Local SCADA Checks/Tests
ESB Telecoms Completion Cert to be sent by ESB Telecoms Services to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open |  |  | ESBN | ESBN
A2 | ESBN 20 kV interface switch (Nulec Recloser) |  | closed |  |  | ESBN | ESBN
A3 | WINDFARM NAME (TLC) T421 WFPS 20 kV CB |  | open |  |  | WFPS | ESBN
A4 | WINDFARM NAME (TLC) T421 WFPS 20 kV CB |  | closed |  |  | WFPS | ESBN
A5 | WINDFARM NAME (TLC) Feeder 1 20 kV CB |  | open |  |  | WFPS | ESBN
A6 | WINDFARM NAME (TLC) Feeder 1 20 kV CB |  | closed |  |  | WFPS | ESBN
A7 | WINDFARM NAME (TLC) Feeder 2 20 kV CB |  | open |  |  | WFPS | ESBN
A8 | WINDFARM NAME (TLC) Feeder 2 20 kV CB |  | closed |  |  | WFPS | ESBN
A9 | WINDFARM NAME (TLC) Feeder 3 20 kV CB |  | open |  |  | WFPS | ESBN
A10 | WINDFARM NAME (TLC) Feeder 3 20 kV CB |  | closed |  |  | WFPS | ESBN
A11 | WINDFARM NAME (TLC) Feeder 4 20 kV CB |  | open |  |  | WFPS | ESBN
A12 | WINDFARM NAME (TLC) Feeder 4 20 kV CB |  | closed |  |  | WFPS | ESBN
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | WFPS | N/A
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | WFPS | N/A
A15 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN
A16 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN
A17 | Blue Alert Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN
A18 | Blue Alert Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | ESBN
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | ESBN
A23 | Reactive Device >5 Mvar N |  | off |  |  | WFPS | ESBN
A24 | Reactive Device >5 Mvar N |  | on |  |  | WFPS | ESBN
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A
B7 | Emulated Inertia status (Feedback) |  | off |  |  | WFPS | ESBN
B8 | Emulated Inertia status (Feedback) |  | on |  |  | WFPS | ESBN
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | ESBN
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | ESBN
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | WFPS | ESBN
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | ESBN
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | WFPS | N/A
Analogue WTG Availability
D4 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | ESBN
D5 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | ESBN
D6 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A
Analogue Availability
D7 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN
D8 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN
D9 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A
D10 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A
D11 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A
D12 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A
Met N (if Registered Capacity >= 10 MW)
D13 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A
D14 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A
D15 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A
D16 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A
E7 | Emulated Inertia |  | off | pulse | 0.5 seconds | WFPS | N/A
E8 | Emulated Inertia |  | on | pulse | 0.5 seconds | WFPS | N/A
Digital Output Signals from EirGrid to Sub Station
F1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open | pulse | 0.5 seconds | ESBN | ESBN
F2 | ESBN 20 kV interface switch (Nulec Recloser) |  | close | pulse | 0.5 seconds | ESBN | ESBN
F3 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off | pulse | 0.5 seconds | WFPS | ESBN
F4 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on | pulse | 0.5 seconds | WFPS | ESBN
F5 | Blue Alert Lamp - WFPS Panel |  | off | pulse | 0.5 seconds | WFPS | ESBN
F6 | Blue Alert Lamp - WFPS Panel |  | on | pulse | 0.5 seconds | WFPS | ESBN
Strobe Enable Pulses
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A
E10 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | TSO Pass-through to
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | WFPS | ESBN
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | WFPS | ESBN
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | WFPS | ESBN
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | WFPS | ESBN
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | WFPS | ESBN
Recommended cable 15-pair cable, 15 x 2 x 0.6sqmm, TP, stranded, external sheath
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | WFPS | N/A
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet are installed and correct. |  |  |  | Confirmed  |  |  | ESBTS Name / Position | ESBTS Team
ESBTS Signature
Date
| NOTE: Non operable WFPS signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  | Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
Note on A5: EirGrid Telecoms Interface Enclosure

## 2 a) EMS Database Setup Cert
WINDFARM NAME (TLC) |  | Topology | XX | XX | MW | v1.0
EirGrid Signals, Command & Control Specification (Ref: DCC11.5)
Energy Management System (EMS) Database setup Certificate
Completion Cert
Continuity Check Complete
Generator Modelled
Lines Modelled
Station Modelled
Calculations Updated
RTU Modelled
Display Work Completed:
WF SLD
Station SLD
Station List
Windfarm List
Embedded Wind
Windfarm Control
Station Wind MW
Wind Overview
Windfarm Availability Data
Blue Alert Page
Windfarm Weather Data
DCC signals provided via ICCP
EMS Name
EMS Signature
Date
EirGrid Internal Document - no IPP requirements. For Information only
Note on A3: Administrator: DCC to be Informed

## 3)Pre Energ. Sign&Con Test Cert
WINDFARM NAME (TLC) |  | Topology | XX | XX | MW | v1.0 |  | Pre Energisation Signals and Controls Test
EirGrid Signals, Command & Control Specification (Ref: DCC11.5) | [7 empty] | Simulated □/Real □ value tested | mA Range | Value Range | Comment
Pre Energisation Signals & Controls Certificate to be sent by ESBT to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open |  |  | ESBN | ESBN | Real □
A2 | ESBN 20 kV interface switch (Nulec Recloser) |  | closed |  |  | ESBN | ESBN | Real □
A3 | WINDFARM NAME (TLC) T421 WFPS 20 kV CB |  | open |  |  | WFPS | ESBN | Real □
A4 | WINDFARM NAME (TLC) T421 WFPS 20 kV CB |  | closed |  |  | WFPS | ESBN | Real □
A5 | WINDFARM NAME (TLC) Feeder 1 20 kV CB |  | open |  |  | WFPS | ESBN | Real □
A6 | WINDFARM NAME (TLC) Feeder 1 20 kV CB |  | closed |  |  | WFPS | ESBN | Real □
A7 | WINDFARM NAME (TLC) Feeder 2 20 kV CB |  | open |  |  | WFPS | ESBN | Real □
A8 | WINDFARM NAME (TLC) Feeder 2 20 kV CB |  | closed |  |  | WFPS | ESBN | Real □
A9 | WINDFARM NAME (TLC) Feeder 3 20 kV CB |  | open |  |  | WFPS | ESBN | Real □
A10 | WINDFARM NAME (TLC) Feeder 3 20 kV CB |  | closed |  |  | WFPS | ESBN | Real □
A11 | WINDFARM NAME (TLC) Feeder 4 20 kV CB |  | open |  |  | WFPS | ESBN | Real □
A12 | WINDFARM NAME (TLC) Feeder 4 20 kV CB |  | closed |  |  | WFPS | ESBN | Real □
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | WFPS | N/A | Real □
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | WFPS | N/A | Real □
A15 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN | Real □
A16 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN | Real □
A17 | Blue Alert Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN | Real □
A18 | Blue Alert Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN | Real □
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN | Real □
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN | Real □
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | ESBN | Real □
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | ESBN | Real □
A23 | Reactive Device >5 Mvar N |  | off |  |  | WFPS | ESBN | Real □
A24 | Reactive Device >5 Mvar N |  | on |  |  | WFPS | ESBN | Real □
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A | Simulated □
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A | Simulated □
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A | Simulated □
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A | Simulated □
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A | Simulated □
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A | Simulated □
B7 | Emulated Inertia status (Feedback) |  | off |  |  | WFPS | ESBN | Simulated □
B8 | Emulated Inertia status (Feedback) |  | on |  |  | WFPS | ESBN | Simulated □
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | ESBN | Real □
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | ESBN | Real □
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | WFPS | ESBN | Real □
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | ESBN | Simulated □
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Simulated □
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | WFPS | N/A | Simulated □
Analogue WTG Availability
D4 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | ESBN | Simulated □
D5 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | ESBN | Simulated □
D6 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A | Simulated □
Analogue Availability
D7 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Simulated □
D8 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Simulated □
D9 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Simulated □
D10 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A | Simulated □
D11 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A | Simulated □
D12 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Simulated □
Met N (if Registered Capacity >= 10 MW)
D13 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Simulated □
D14 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A | Simulated □
D15 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A | Simulated □
D16 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Simulated □
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E7 | Emulated Inertia |  | off | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E8 | Emulated Inertia |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
Digital Output Signals from EirGrid to Sub Station
F1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open | pulse | 0.5 seconds | ESBN | ESBN | Simulated □
F2 | ESBN 20 kV interface switch (Nulec Recloser) |  | close | pulse | 0.5 seconds | ESBN | ESBN | Simulated □
F3 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off | pulse | 0.5 seconds | WFPS | ESBN | Simulated □
F4 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on | pulse | 0.5 seconds | WFPS | ESBN | Simulated □
F5 | Blue Alert Lamp - WFPS Panel |  | off | pulse | 0.5 seconds | WFPS | ESBN | Simulated □
F6 | Blue Alert Lamp - WFPS Panel |  | on | pulse | 0.5 seconds | WFPS | ESBN | Simulated □
Strobe Enable Pulses
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E10 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Simulated □
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | TSO Pass-through to
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN | Simulated □
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN | Simulated □
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN | Simulated □
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN | Simulated □
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN | Simulated □
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN | Simulated □
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN | Simulated □
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN | Simulated □
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN | Simulated □
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN | Simulated □
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN | Simulated □
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN | Simulated □
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN | Simulated □
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | WFPS | ESBN | Simulated □
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | WFPS | ESBN | Simulated □
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | WFPS | ESBN | Simulated □
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | WFPS | ESBN | Simulated □
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | WFPS | ESBN | Simulated □
Recommended cable 15-pair cable, 15 x 2 x 0.6sqmm, TP, stranded, external sheath
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A | Simulated □
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | WFPS | N/A | Simulated □
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
Simulation Point
Simulation Method
[6 empty] | WFPS Name / Position |  | 0
WFPS Signature
EMS Name
EMS Signature
| NOTE: Non operable WFPS signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  |  |  |  | ESB Telecoms Name / Position |  | ESBTS Team
| Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 |  |  |  |  | ESB Telecoms Signature
Date
Note on I1: Administrator: ESBTS Commission from NCC control desk to / via ETI to IPP plant.
Note on I2: Administrator: the electrical characteristics of IPP signals not tested due to plant unavailability must be simulated by IPP.
Note on A5: EirGrid Telecoms Interface Enclosure

## 4) Post Ener Pre Grid Code Cert
WINDFARM NAME (TLC) |  | Topology | XX | XX | MW | v1.0 |  | Post Energisation Signals and Controls Test
EirGrid Signals, Command & Control Specification (Ref: DCC11.5) | [7 empty] | Simulated □/Real □ value tested | mA Range | Value Range | Comment
Post Energisation Pre Grid Code Cert to be provided by ESBT to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open |  |  | ESBN | ESBN | Real □
A2 | ESBN 20 kV interface switch (Nulec Recloser) |  | closed |  |  | ESBN | ESBN | Real □
A3 | WINDFARM NAME (TLC) T421 WFPS 20 kV CB |  | open |  |  | WFPS | ESBN | Real □
A4 | WINDFARM NAME (TLC) T421 WFPS 20 kV CB |  | closed |  |  | WFPS | ESBN | Real □
A5 | WINDFARM NAME (TLC) Feeder 1 20 kV CB |  | open |  |  | WFPS | ESBN | Real □
A6 | WINDFARM NAME (TLC) Feeder 1 20 kV CB |  | closed |  |  | WFPS | ESBN | Real □
A7 | WINDFARM NAME (TLC) Feeder 2 20 kV CB |  | open |  |  | WFPS | ESBN | Real □
A8 | WINDFARM NAME (TLC) Feeder 2 20 kV CB |  | closed |  |  | WFPS | ESBN | Real □
A9 | WINDFARM NAME (TLC) Feeder 3 20 kV CB |  | open |  |  | WFPS | ESBN | Real □
A10 | WINDFARM NAME (TLC) Feeder 3 20 kV CB |  | closed |  |  | WFPS | ESBN | Real □
A11 | WINDFARM NAME (TLC) Feeder 4 20 kV CB |  | open |  |  | WFPS | ESBN | Real □
A12 | WINDFARM NAME (TLC) Feeder 4 20 kV CB |  | closed |  |  | WFPS | ESBN | Real □
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | WFPS | N/A | Real □
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | WFPS | N/A | Real □
A15 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN | Real □
A16 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN | Real □
A17 | Blue Alert Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN | Real □
A18 | Blue Alert Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN | Real □
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN | Real □
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN | Real □
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | ESBN | Real □
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | ESBN | Real □
A23 | Reactive Device >5 Mvar N |  | off |  |  | WFPS | ESBN | Real □
A24 | Reactive Device >5 Mvar N |  | on |  |  | WFPS | ESBN | Real □
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A | Real □
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A | Real □
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A | Real □
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A | Real □
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A | Real □
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A | Real □
B7 | Emulated Inertia status (Feedback) |  | off |  |  | WFPS | ESBN | Real □
B8 | Emulated Inertia status (Feedback) |  | on |  |  | WFPS | ESBN | Real □
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | ESBN | Real □
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | ESBN | Real □
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | WFPS | ESBN | Real □
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | ESBN | Real □
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Real □
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | WFPS | N/A
Analogue WTG Availability
D4 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | ESBN | Real □
D5 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | ESBN | Real □
D6 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A | Real □
Analogue Availability
D7 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Real □
D8 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Real □
D9 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Real □
D10 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A | Real □
D11 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A | Real □
D12 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Real □
Met N (if Registered Capacity >= 10 MW)
D13 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Real □
D14 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A | Real □
D15 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A | Real □
D16 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Real □
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A | Real □
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A | Real □
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A | Real □
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A | Real □
E7 | Emulated Inertia |  | off | pulse | 0.5 seconds | WFPS | N/A | Real □
E8 | Emulated Inertia |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
Digital Output Signals from EirGrid to Sub Station
F1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open | pulse | 0.5 seconds | ESBN | ESBN | Real □
F2 | ESBN 20 kV interface switch (Nulec Recloser) |  | close | pulse | 0.5 seconds | ESBN | ESBN | Real □
F3 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off | pulse | 0.5 seconds | WFPS | ESBN | Real □
F4 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on | pulse | 0.5 seconds | WFPS | ESBN | Real □
F5 | Blue Alert Lamp - WFPS Panel |  | off | pulse | 0.5 seconds | WFPS | ESBN | Real □
F6 | Blue Alert Lamp - WFPS Panel |  | on | pulse | 0.5 seconds | WFPS | ESBN | Real □
Strobe Enable Pulses
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Real □
E10 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Real □
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | TSO Pass-through to
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | WFPS | ESBN | Real / Point Tested □
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | WFPS | ESBN | Real / Point Tested □
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | WFPS | ESBN | Real / Point Tested □
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | WFPS | ESBN | Real / Point Tested □
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | WFPS | ESBN | Real / Point Tested □
Recommended cable 15-pair cable, 15 x 2 x 0.6sqmm, TP, stranded, external sheath
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A | Real □
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | WFPS | N/A | Real □
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
Confirm the source of the MET signals e.g. from MET mast or from WTGs
| Wind Speed source: |  |  |  |  | WFPS Name |  | 0
| Wind Direction source: |  |  |  |  | WFPS Signature
| Air Temperature source: |  |  |  |  | EMS Name
| Air Pressure source: |  |  |  |  | EMS Signature
| NOTE: Non operable WFPS signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  |  |  |  | ESB Telecoms Name / Position |  | ESBTS Team
| Note: That for the duration of the Post Energization Test, there should be NO external influencing factors |  |  |  |  | ESB Telecoms Signature
| Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 |  |  |  |  | Date
Note on A5: EirGrid Telecoms Interface Enclosure

## ETIE ¦ RTU Location
EirGrid Telecoms Interface Enclosure (ETIE)
Typical EirGrid RTU cabinet with integrated ETI and GPS clock 2.0m x 0.8m x 0.6m (rear access not required).
Note: This is for a typical installation and may vary from project to project. Any queries should be directed to generator_testing@eirgrid.com or esbts.scada.services@esb.ie
ETIE General Description
There will be four rows of terminals labelled Row 1, 2, 3, 4 as shown in the Layout drawing and Photograph above
Trunking shall be separated into WFPS and EirGrid Telecoms trunking.
EirGrid Telecoms cabling to be in EirGrid Telecoms designated trunking only
WFPS cabling to be in WFPS designated trunking only
Access to terminals will be as follows:
Upper side to be used for EirGrid Telecoms use only
Lower side to be used for WFPS use only
Isolating link to sever all connection between the WFPS connection and EirGrid Telecoms connection
Command terminals to be covered with a Perspex cover and labelled "DO NOT ENERGISE"
Earthing of cabinet to be completed in accordance with 35 sq mm earth cable to EirGrid Telecoms earth bar
RTU Location:
The TSO RTU will be located in the ESB Networks substation at the WFPS site

## ETIE Layout
Designation: Indications/Signals |  | ETIE Ref | ETIE ROW 1
POSITIVE 24V or 48V DC DOUBLE POINT INDICATION |  |  | +
ESBN 20 kV interface switch (Nulec Recloser) | open | A1 | 1
ESBN 20 kV interface switch (Nulec Recloser) | closed | A2 | 2
WINDFARM NAME (TLC) T421 WFPS 20 kV CB | open | A3 | 3
WINDFARM NAME (TLC) T421 WFPS 20 kV CB | closed | A4 | 4
WINDFARM NAME (TLC) Feeder 1 20 kV CB | open | A5 | 5
WINDFARM NAME (TLC) Feeder 1 20 kV CB | closed | A6 | 6
WINDFARM NAME (TLC) Feeder 2 20 kV CB | open | A7 | 7
WINDFARM NAME (TLC) Feeder 2 20 kV CB | closed | A8 | 8
WINDFARM NAME (TLC) Feeder 3 20 kV CB | open | A9 | 9
WINDFARM NAME (TLC) Feeder 3 20 kV CB | closed | A10 | 10
WINDFARM NAME (TLC) Feeder 4 20 kV CB | open | A11 | 11
WINDFARM NAME (TLC) Feeder 4 20 kV CB | closed | A12 | 12
TSO Dispatch Control Enable Switch | off | A13 | 13
TSO Dispatch Control Enable Switch | on | A14 | 14
Dispatch Fail Market Command Lamp - WFPS Panel | off | A15 | 15
Dispatch Fail Market Command Lamp - WFPS Panel | on | A16 | 16
Blue Alert Lamp - WFPS Panel | off | A17 | 17
Blue Alert Lamp - WFPS Panel | on | A18 | 18
ESB SCADA Remote Control Switch | off | A19 | 19
ESB SCADA Remote Control Switch | on | A20 | 20
Reactive Device >5 Mvar 1 | off | A21 | 21
Reactive Device >5 Mvar 1 | on | A22 | 22
Reactive Device >5 Mvar N | off | A23 | 23
Reactive Device >5 Mvar N | on | A24 | 24
Active Power Control facility status (feedback) | off | B1 | 25
Active Power Control facility status (feedback) | on | B2 | 26
Frequency Response System Mode Status (feedback) | off | B3 | 27
Frequency Response System Mode Status (feedback) | on | B4 | 28
Frequency Response Curve (feedback) | Curve 1 | B5 | 29
Frequency Response Curve (feedback) | Curve 2 | B6 | 30
Emulated Inertia status (Feedback) | off | B7 | 31
Emulated Inertia status (Feedback) | on | B8 | 32
33
34
35
36
37
38
POSITIVE 24V or 48V DC SINGLE POINT INDICATION |  |  | +
ESBN Alarm 1 |  | N1 | 41
ESBN Alarm 2 |  | N2 | 42
ESBN Alarm 3 |  | N3 | 43
ESBN Alarm 4 |  | N4 | 44
ESBN Alarm 5 |  | N5 | 45
ESBN Alarm 6 |  | N6 | 46
ESBN Alarm 7 |  | N7 | 47
ESBN Alarm 8 |  | N8 | 48
ESBN Alarm 9 |  | N9 | 49
ESBN Alarm 10 |  | N10 | 50
ESBN Alarm 11 |  | N11 | 51
ESBN Alarm 12 |  | N12 | 52
ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  | N13 | 53
ESBN Alarm 14 (AC FAIL) |  | N14 | 54
ESBN Alarm 15 (G10 protection trip) |  | N15 | 55
ESBN Alarm 16 (Customer traffo protection trip) |  | N16 | 56
ESBN Alarm 17 (Fire Alarm for ESB Room) |  | N17 | 57
ESBN Alarm 18 (Intruder Alarm for ESB Room) |  | N18 | 58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
Designation: Measurands | Polarity | ETIE Ref | ETIE ROW 2
Active Power Output at Connection Point | + | C1 | 1
Active Power Output at Connection Point | - | C1 | 2
Reactive Power at Connection Point | + | C2 | 3
Reactive Power at Connection Point | - | C2 | 4
Voltage at Connection Point | + | C3 | 5
Voltage at Connection Point | - | C3 | 6
Available Active Power | + | D1 | 7
Available Active Power | - | D1 | 8
Active Power Control Setpoint (feedback) | + | D2 | 9
Active Power Control Setpoint (feedback) | - | D2 | 10
Frequency Droop Setting (feedback) | + | D3 | 11
Frequency Droop Setting (feedback) | - | D3 | 12
%WTG not generating due to high wind | + | D4 | 13
%WTG not generating due to high wind | - | D4 | 14
%WTG not generating due to low wind | + | D5 | 15
%WTG not generating due to low wind | - | D5 | 16
Wind Farm Availability | + | D6 | 17
Wind Farm Availability | - | D6 | 18
Emulated Inertia FFR availability | + | D7 | 19
Emulated Inertia FFR availability | - | D7 | 20
Emulated Inertia POR availability | + | D8 | 21
Emulated Inertia POR availability | - | D8 | 22
Wind Speed 1 | + | D9 | 23
Wind Speed 1 | - | D9 | 24
Wind Direction 1 | + | D10 | 25
Wind Direction 1 | - | D10 | 26
Air Temperature 1 | + | D11 | 27
Air Temperature 1 | - | D11 | 28
Air Pressure 1 | + | D12 | 29
Air Pressure 1 | - | D12 | 30
Wind Speed N | + | D13 | 31
Wind Speed N | - | D13 | 32
Wind Direction N | + | D14 | 33
Wind Direction N | - | D14 | 34
Air Temperature N | + | D15 | 35
Air Temperature N | - | D15 | 36
Air Pressure N | + | D16 | TBC
Air Pressure N | - | D16 | TBC
Analogue Output MW | Polarity | ETIE Ref | +
Analogue Output Active Power Control Setpoint | + | G1 | 33
Analogue Output Active Power Control Setpoint | - | G1 | 34
Frequency Droop Setting | + | G2 | 35
Frequency Droop Setting | - | G2 | 36
Analogue Output kV |  |  | +
37
38
39
40
Designation: Commands |  | ETIE Ref | ETIE ROW 3
Active Power Control facility status | off | E1 | 1
Command Negative |  |  | 2
Active Power Control facility status | on | E2 | 3
Frequency Response System Mode Status | off | E3 | 4
Command Negative |  |  | 5
Frequency Response System Mode Status | on | E4 | 6
Frequency Response Curve Select | Curve 1 | E5 | 7
Command Negative |  |  | 8
Frequency Response Curve Select | Curve 2 | E6 | 9
Emulated Inertia | off | E7 | 10
Command Negative |  |  | 11
Emulated Inertia | on | E8 | 12
ESBN 20 kV interface switch (Nulec Recloser) | open | F1 | 13
Command Negative |  |  | 14
ESBN 20 kV interface switch (Nulec Recloser) | close | F2 | 15
Dispatch Fail Market Command Lamp - WFPS Panel | off | F3 | 16
Command Negative |  |  | 17
Dispatch Fail Market Command Lamp - WFPS Panel | on | F4 | 18
Blue Alert Lamp - WFPS Panel | off | F5 | 19
Command Negative |  |  | 20
Blue Alert Lamp - WFPS Panel | on | F6 | 21
Command Output |  |  | 22
Command Negative |  |  | 23
Command Output |  |  | 24
Command Output |  |  | 25
Command Negative |  |  | 26
Command Output |  |  | 27
Command Output |  |  | 28
Command Negative |  |  | 29
Command Output |  |  | 30
Command Output |  |  | 31
Command Negative |  |  | 32
Command Output |  |  | 33
Command Output |  |  | 34
Command Negative |  |  | 35
Command Output |  |  | 36
Command Output |  |  | 37
Command Negative |  |  | 38
Command Output |  |  | 39
Command Output |  |  | 40
Command Negative |  |  | 41
Command Output |  |  | 42
Command Output |  |  | 43
Command Negative |  |  | 44
Command Output |  |  | 45
Command Output |  |  | 46
Command Negative |  |  | 47
Command Output |  |  | 48
Designation: Controls |  | ETIE Ref | ETIE ROW 4
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
Single Controls |  |  | +
Digital Output Active Power Control Setpoint Enable |  | E9 | 37
|  | E9 | 38
Digital Output Frequency Droop Setting Enable |  | E10 | 39
|  | E10 | 40
41
42
43
44
45
46
47
48
Note on D2: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4
Note on D74: Administrator: Administrator: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4
Note on D123: Administrator: There is a gap between the off / on commands for command negative
Note on D172: Administrator: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4

## Freq,Ramping,Voltage Settings
Frequency, Ramp Rate and Voltage Settings to be implemented in Wind Farm Control System
Definitions:
| AAP | Available Active Power
| DMOL | Designed Minimum Operating Level
| APC | Active Power Control
Frequency Response Mode On | [5 empty] | Frequency Response Diagrams
Curve 1: Wind Following Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 48 |  | 100% of AAP
|  | FA | 48 | PA | 100% of AAP
|  | Under Frequency Response | 48 < f < 49.8 |  | 100% of AAP
|  | FB | f = 49.8 | PB | 100% of AAP
|  | +/-0.2Hz Deadband | 49.8 < f < 50.2 |  | 100% of AAP
|  | FC | f = 50.2 | PC | 100% of AAP
|  | Over Frequency Response | 50.2 < f < 51.9 |  | AAP + ∆MW2
|  | FD | f = 51.9 | PD | Minimum of: AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Curve 1: Active Power Control Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 48 |  | 100% of AAP
|  | FA | f = 48 | PA | 100% of AAP
|  | Under Frequency Response | 48 < f < 49.985 |  | Minimum of: APC Setpoint + ∆MW and AAP
|  | FB | f = 49.985 | PB | Minimum of: APC Setpoint and AAP
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | Minimum of: APC Setpoint and AAP
|  | FC | f = 50.015 | PC | Minimum of: APC Setpoint and AAP
|  | Over Frequency Response | 50.015 < f < 51.9 |  | Minimum of: APC Setpoint + ∆MW and AAP + ∆MW1, 2
|  | FD | f = 51.9 | PD | Minimum of: APC Setpoint and AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Curve 2: Wind Following Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f <49.3 |  | 100% of AAP
|  | FA | f = 49.3 | PA | 100% of AAP
|  | Under Frequency Response | 49.3 < f < 49.985 |  | 95% of Available Active Power + ∆MW
|  | FB | f = 49.985 | PB | 95% of Available Active Power. This is = to 5% Reserve.
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | 95% of Available Active Power. This is = to 5% Reserve.
|  | FC | f = 50.015 | PC | 95% of Available Active Power. This is = to 5% Reserve.
|  | Over Frequency Response | 50.015 < f < 51.9 |  | 95% of AAP + ∆MW2
|  | FD | f = 51.9 | PD | Minimum of: AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Curve 2: Active Power Control Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 49.3 |  | 100% of AAP
|  | FA | f = 49.3 | PA | 100% of AAP
|  | Under Frequency Response | 49.3 < f < 49.985 |  | Minimum of: APC Setpoint + ∆MW and 95% of AAP + ∆MW
|  | FB | f = 49.985 | PB | Minimum of: APC Setpoint and 95% of AAP
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | Minimum of: APC Setpoint and 95% of AAP
|  | FC | f = 50.015 | PC | Minimum of: APC Setpoint and 95% of AAP
|  | Over Frequency Response | 50.015 < f < 51.9 |  | Minimum of: APC Setpoint + ∆MW and 95% of AAP + ∆MW1, 2
|  | FD | f = 51.9 | PD | Minimum of: APC Setpoint and AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Minimum reserve level in Curve 2 is 5% of Available Active Power, not lower than DMOL (settable between DMOL and 100%)
Frequency Response Mode OFF
Curve 1 and Curve 2: Wind Following Mode
|  |  | Transmission System Frequency (Hz) |  | Required Active Power Output
|  |  | 47.5 ≤ f ≥ 52 | No governor action | 100% of AAP
Curve 1 and Curve 2: Active Power Control Mode
|  |  | Transmission System Frequency (Hz) |  | Required Active Power Output
|  |  | 47.5 ≤ f ≥ 52 | No governor action | Minimum of: AAP and APC Setpoint
1 APC Setpoint + ∆MW shall have a lower limit of the minimum of: APC Setpoint and DMOL.
2 (95% of) AAP + ∆MW shall have a lower limit of the minimum of AAP and DMOL
3 Any WTG which has disconnected due to high frequency shall be brought back on load as fast as technically feasible, provided the Frequency has fallen below 50.2Hz.
DMOL shall not be greater than 12% of Registered Capacity
If AAP < DMOL and f < FE, maximise output
Ramp Rates:
|  | Mode | Rate | Priority | Comment
|  | Frequency Response | As fast as technically possible. 60% of its expected Active Power response within 5 seconds 100% of its expected Active Power response within 15 seconds. | 1
|  | Active Power Dispatch | 20% of Registered Capacity per Minute | 2 | Settable between: 1-100% Registered Capacity per Minute
|  | Wind Following | 20% of Registered Capacity per Minute | 3 | Settable between: 1-100% Registered Capacity per Minute
Frequency Droop:
|  | Frequency Droop | Droop Calculation | Comment
|  | 4% |  | Settable between: 2-10%, online
Rate of Change of Frequency:
If possible, ROCOF should be disabled on Transmission System-connected Windfarms. If this is not possible, ROCOF should be set to max that machine is capable of. Under no circumstances should ROCOF be set to less than 0.5 Hz/s
Proposed Modification to Grid Code. (Ref#MPID 229).

## Turbine Protection Settings
Recommended Wind Farm Power Station (WFPS) Turbine Protection Settings to be applied by WFPS
| Underfrequency stage 1 Setpoint | f< | 47.5 Hz | If only two stages available for underfrequency on relay, use stage 2 and stage 3
| Underfrequency stage 1 time delay | t< | 3600 s
| Underfrequency stage 2 Setpoint | f<< | 47.4 Hz
| Underfrequency stage 2 time delay | t<< | 20 s
| Underfrequency stage 3 Setpoint | f<<< | 46.9 Hz
| Underfrequency stage 3 time delay | t<<< | 1 s
| Overfrequency stage 1 Setpoint | f> | 52Hz
| Overfrequency stage 1 time delay | t> | 3600 s
| Overfrequency stage 2 Setpoint | f>> | 52.1 Hz
| Overfrequency stage 2 time delay | t>> | 1 s
| Rate of Change of Frequency setpoint | df/dt | Max | If possible, ROCOF should be disabled on Transmission System-connected Windfarms. If this is not possible, ROCOF should be set to max that machine is capable of. Under no circumstances should ROCOF be set to less than 1 Hz/s over 500 ms
| Rate of Change of Frequency delay | t | Max
| Undervoltage stage 1 Setpoint | U< | 0.89 pu
| Undervoltage stage 1 time delay | t< | 3 s
| Undervoltage stage 2 Setpoint | U<< | 0.14 pu
| Undervoltage stage 2 time delay | t<< | 0.625 s
| Overvoltage stage 1 Setpoint | U> | 1.11 pu
| Overvoltage stage 1 time delay | t> | 60 s | This is the minimum time delay we would recommend. If the plant can operate at this voltage for longer periods, then a longer time delay (at the discretion of the WFPS) should be implemented.
| Overvoltage stage 2 Setpoint | U>> | 1.2 pu
| Overvoltage stage 2 time delay | t>> | 15 s | This is the minimum time delay we would recommend. If the plant can operate at this voltage for longer periods, then a longer time delay (at the discretion of the WFPS) should be implemented.
| Fault Ride Through Events | N | N/A | Trip & Lockout Settings. i.e No. of events within specified time period. Confirm if time period is rolling. NB. Lockout is not recommended by EirGrid.
| Fault Ride Though Time Period (Rolling) | t | N/A

## Test Schedule and Templates
Grid Code Compliance Test Schedule and Test Procedure templates
SCHEDULE OF GRID CODE COMPLIANCE TESTS
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_Schedule_of_GridCodeComplianceTests.xlsx
Test Procedure Templates
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_TestProcedureActivePowerControl.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_TestProcedureBlackStartShutdown.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_TestProcedureFrequencyResponse.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_TestProcedureReactivePowerCapability.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_TestProcedureReactivePowerControl.docx