## Register of Granted Derogations
Register of Granted Grid Code Derogations |  |  |  |  | Version 18 04/05/2016
* Remaining service life of facility or equipment responsible for non-compliance to the Grid Code.
DAID | Submitted by | Plant | Type | Section | Clause | Grid Code Version No | The Period of the Derogation | Extent of Compliance to the Provision | Has derogation expired, been superceded, or plant no longer in operation? | Is derogation still relevant? (May have expired, been superceded, the Grid Code clause may no longer be in force, the plant may now comply or no longer be in operation) | Comment
18 | ESBNG (now EirGrid plc) | Lisheen 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.88pu for Summer 2002. Voltage collapse may occur following contingency during Summer maintenance 2002. Voltages following contingency could be 0.89pu for Summer maintenance 2005 | Yes | No
21 | ESBNG (now EirGrid plc) | Athlone 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 28/02/2006 | Voltages following contingency could be 0.86pu for Summer Maintenance 2002. Voltages following contingency could be 0.84pu for Winter 2002/3 and Winter 2005/6. Voltages following contingency could be 0.89pu for Summer Maintenance 2003, Winter 2003/4, Summer 2005 and Summer Maintenance 2005. Voltages following contingency could be 0.87pu for Winter 2004/5. | Yes | No
36 | ESBNG (now EirGrid plc) | Drybridge 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.86pu for Summer maintenance 2002 and Summer maintenance 2004. Voltages following contingency could be 0.88pu for Summer maintenance 2003. | Yes | No
37 | ESBNG (now EirGrid plc) | Drumline 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.81pu for Summer maintenance 2002. Voltages following contingency could be 0.84pu for Summer maintenance 2003. Voltages following contingency could be 0.82pu for Summer maintenance 2004. Voltages following contingency could be 0.80 for Summer maintenance. | Yes | No
40 | ESBNG (now EirGrid plc) | Ennis 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.84pu for Summer maintenance 2002. Voltages following contingency could be 0.87pu for Summer maintenance 2003. Voltages following contingency could be 0.85pu for Summer maintenance 2004. Voltages following contingency could be 0.83 for Summer maintenance 2005. | Yes | No
53 | ESBNG (now EirGrid plc) | Kiltoy 1&2 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 28/02/2005 | Voltages following contingency could be 0.84pu for Summer maintenance 2002. Voltages following contingency could be 0.89pu for Winter 2004/5. | Yes | No
54 | ESBNG (now EirGrid plc) | Knockumber 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.86pu for Summer maintenance 2002. Voltages following contingency could be 0.87pu for Summer maintenance 2003 and Summer maintenance 2005. Voltages following contingency could be 0.85pu for Summer maintenance 2004 | Yes | No
59 | ESBNG (now EirGrid plc) | Lisdrum 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/12/2008 | During Transmission System disturbances or following transmission faults, the voltage may fall to 94 kV during Summer 2006 and 92 kV during Summer 2007. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
63 | ESBNG (now EirGrid plc) | Moneypoint 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.82pu for Summer maintenance 2002. Voltages following contingency could be 0.85pu for Summer maintenance 2003. Voltages following contingency could be 0.83pu for Summer maintenance 2004. Voltages following contingency could be 0.81pu for Summer maintenance 2005. | Yes | No
64 | ESBNG (now EirGrid plc) | Moy 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2002 | Voltage collapse may occur following contingency during Summer 2002 and Summer maintenance 2002. Voltages following contingency could be 0.86pu for Summer Maintenance 2004. | Yes | No
68 | ESBNG (now EirGrid plc) | Navan 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.86pu for Summer maintenance 2002. Voltages following contingency could be 0.87pu for Summer maintenance 2003 and 2005. Voltages following contingency could be 0.85pu for Summer maintenance 2004. | Yes | No
69 | ESBNG (now EirGrid plc) | Platin 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.86pu for Summer maintenance 2002. Voltages following contingency could be 0.87pu for Summer maintenance 2003. Voltages following contingency could be 0.85pu for Summer maintenance 2004. | Yes | No
73 | ESBNG (now EirGrid plc) | Sligo 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2004 | Voltages following contingency could be 0.80pu for Summer 2002. Voltage collapse may occur following contingency during Summer maintenance 2002. Voltages following contingency could be 0.86pu for Summer 2004 | Yes | No
74 | ESBNG (now EirGrid plc) | Shankill 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/12/2008 | During Transmission System disturbances or following transmission faults, the voltage may fall to 93 kV during Summer 2006 and 88 kV during Summer 2007. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
75 | ESBNG (now EirGrid plc) | Somerset 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2002 | Voltages following contingency could be 0.87pu for Summer maintenance 2002. | Yes | No
77 | ESBNG (now EirGrid plc) | Tawnaghmore 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2004 | Voltage collapse may occur following contingency during Summer 2002 and Summer maintenance 2002. Voltages following contingency could be 0.86pu for Summer maintenance 2004. | Yes | No
78 | ESBNG (now EirGrid plc) | Trillick 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 28/02/2005 | Voltages following contingency could be 0.89pu for Summer 2002. Voltages following contingency could be 0.87pu for Winter 2004/5. | Yes | No
79 | ESBNG (now EirGrid plc) | Tullabrack 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.82pu for Summer maintenance 2002. Voltages following contingency could be 0.85pu for Summer maintenance 2003. Voltages following contingency could be 0.83pu for Summer maintenance 2004. Voltages following contingency could be 0.81pu for Summer maintenance 2005. | Yes | No
81 | ESBNG (now EirGrid plc) | N/A | Market | SDC2A | 3.3 | V1.0 | Indefinite* | Facility not provided by ESBNG (now EirGrid).
84 | ESBNG (now EirGrid plc) | Kiltoy T101, T102 & T014 |  | CC | 7.2.5.4 | V1.0 | Indefinite* | Facility not provided by ESBNG (now EirGrid).
Anner T101 & T103
Castlefarm T101 & T102
Mungret T101 & T102
Brinny T101 & T102
Dunkettle T1
Gilra T121
Haulbowline T101 & T102/T103/T107
Knockumber T101 & T102
Old Court T101 & T102
Shelton Abbey T101a/T101b & T102
85 | ESBNG (now EirGrid plc) | Bellacorick T1 & T2 |  | CC | 10.9.3 | V1.0 | Indefinite or until refurbishment of associated transmission compounds. | Distance Protection not provided, Overcurrent or Directional Overcurrent protection provided.
Ferbane T101, T102, T103 & T104
Lanesboro T102
Rhode T102 & T103
Pollaphuca T101 & T102
Inniscarra T101
Carrigadhroid T103
Cliff T101 & T102
89 | ESBNG (now EirGrid plc) | Kiltoy T101, T102 & T014 |  | CC | 10.11.3 | V1.0 | Indefinite* | Facility not provided by ESBNG (now EirGrid).
Anner T101 & T103
Castlefarm T101 & T102
Mungret T101 & T102
Brinny T101 & T102
Dunkettle T1
Gilra T121
Haulbowline T101 & T102/T103/T107
Knockumber T101 & T102
Old Court T101 & T102
Shelton Abbey T101a/T101b & T102
90 | ESBNG (now EirGrid plc) | N/A | Market | SDC1 | 6.1 | V1.0 | Until 29/03/2006 | The SSA operates on a Business Day basis, while this clause in the Grid Code implies that the timetable for Generator nominations should be on a Calendar Day basis. | Yes | No | This clause is no longer applicable. SDC1 was modified for the SEM on 31 October 2007.
92 | ESBNG (now EirGrid plc) | N/A | Market | OC3 | 4 | V1.0 | Until 29/03/2006 | The SSA operates the TESS (Transitional Electricity Settlement System) on a Business Day basis, while this clause OC3.4 in the Grid Code implies that the timetable for interconnector “Available Transfer Capacity Determination and Posting” should occur on a Calendar Day basis. | Yes | No | This clause is no longer applicable. OC3 was deleted as part of the modifications for SEM on 31 October 2007.
93 | ESBNG (now EirGrid plc) | N/A | Market | OC3 | 5 | V1.0 | Until 29/03/2006 | The SSA operates on a Business Day basis, while this clause OC3.5 in the Grid Code implies that the timetable for interconnector nominations should be on a Calendar Day basis. | Yes | No | This clause is no longer applicable. OC3 was deleted as part of the modifications for SEM on 31 October 2007.
94 | ESBNG (now EirGrid plc) | N/A | Market | OC3 | 6.1 | V1.0 | Until 29/03/2006 | The SSA operates on a Business Day basis, while this clause OC3.6.1 in the Grid Code implies calendar day activities. | Yes | No | This clause is no longer applicable. OC3 was deleted as part of the modifications for SEM on 31 October 2007.
152 | Airtricity | King's Mountain Wind Farm | Wind | CC | 7.3.1.1 (h) | V1.0 | Indefinite* | Wind farm will remain synchronised to the transmission system during voltage dips of up to:
|  |  | Wind |  |  |  |  | - 20% from nominal voltage as seen at the generator terminals during full load operation where the generator is initially operating at 105% of nominal voltage
|  |  | Wind |  |  |  |  | - 20% from nominal voltage and 500 milliseconds seconds duration as seen at the generator terminals during full load operation provided that the voltage drop takes place over a period of at least 50 milliseconds
|  |  | Wind |  |  |  |  | - 30% as seen at the generator terminals during full-load operation provided that this voltage drop does not persist for more than 100 milliseconds
|  |  | Wind |  |  |  |  | - 40% as seen at the generator terminals during 1300 kW operation provided that this voltage drop does not persist for more than 100ms
155 | Airtricity | King's Mountain Wind Farm | Wind | CC | 7.3.1.1 (u) | V1.0 | Indefinite* | WTGs cannot provide guaranteed operating reserve levels
158 | Airtricity | King's Mountain Wind Farm | Wind | CC | 7.3.8 | V1.0 | Indefinite* | NET must provide an "AVR-type" controller as part of the turbine control system of the wind farm and a switched capacitor bank as part of the local substation which fulfil the function of an AVR.
164 | ESBPG | Aghada OCGT 4 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
165 | ESBPG | Ardnacrusha Unit 2 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
166 | ESBPG | Ardnacrusha Unit 3 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
167 | ESBPG | Ardnacrusha Unit 4 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
168 | ESBPG | Aghada Steam Plant 1 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
170 | ESBPG | Aghada OCGT 1 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
171 | ESBPG | Aghada OCGT 2 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
172 | ESBPG | Ardnacrusha Unit 1 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
173 | ESBPG | Poolbeg 4 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
175 | ESBPG | Erne Unit 1 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
176 | ESBPG | Erne Unit 2 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
177 | ESBPG | Erne Unit 3 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
178 | ESBPG | Erne Unit 4 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
179 | ESBPG | Great Island Unit 1 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
180 | ESBPG | Great Island Unit 2 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
181 | ESBPG | Great Island Unit 3 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
184 | ESBPG | Lee Unit 1 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
185 | ESBPG | Lee Unit 2 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
186 | ESBPG | Lee Unit 3 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
187 | ESBPG | Liffey Unit 1 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
188 | ESBPG | Liffey Unit 2 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
191 | ESBPG | Moneypoint Unit 1 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
192 | ESBPG | Moneypoint Unit 2 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
193 | ESBPG | Moneypoint Unit 3 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
194 | ESBPG | Marina OCGT | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
195 | ESBPG | North Wall Unit 4 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
196 | ESBPG | North Wall Unit 5 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
197 | ESBPG | Poolbeg Unit 1 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
198 | ESBPG | Poolbeg Unit 2 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
199 | ESBPG | Poolbeg Unit 3 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
201 | ESBPG | Turlough Hill Unit 4 | Pumped Storage | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
202 | ESBPG | Poolbeg Unit 6 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
203 | ESBPG | Rhode Unit 3 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens | Yes | No | Plant has been decomissioned.
208 | ESBPG | Tarbert Unit 1 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
209 | ESBPG | Tarbert Unit 2 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
210 | ESBPG | Tarbert Unit 3 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
211 | ESBPG | Tarbert Unit 4 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
212 | ESBPG | Turlough Hill Unit 1 | Pumped Storage | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
213 | ESBPG | Turlough Hill Unit 2 | Pumped Storage | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
214 | ESBPG | Turlough Hill Unit 3 | Pumped Storage | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
215 | ESBPG | Poolbeg Unit 5 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
216 | ESBPG | Turlough Hill Unit 4 | Pumped Storage | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
217 | ESBPG | Ardnacrusha Unit 2 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
218 | ESBPG | Ardnacrusha Unit 3 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
219 | ESBPG | Ardnacrusha Unit 4 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
220 | ESBPG | Aghada Steam Plant 1 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
222 | ESBPG | Aghada OCGT 1 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
223 | ESBPG | Aghada OCGT 2 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
224 | ESBPG | Aghada OCGT 4 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
227 | ESBPG | Erne Unit 1 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
228 | ESBPG | Erne Unit 2 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
229 | ESBPG | Erne Unit 3 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
230 | ESBPG | Erne Unit 4 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
231 | ESBPG | Great Island Unit 1 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
232 | ESBPG | Great Island Unit 2 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
233 | ESBPG | Great Island Unit 3 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
236 | ESBPG | Lee Unit 1 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
237 | ESBPG | Lee Unit 2 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
238 | ESBPG | Lee Unit 3 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
239 | ESBPG | Liffey Unit 1 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
240 | ESBPG | Liffey Unit 2 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
243 | ESBPG | Marina OCGT | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
244 | ESBPG | North Wall Unit 4 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
245 | ESBPG | North Wall Unit 5 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
246 | ESBPG | Poolbeg Unit 1 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
247 | ESBPG | Poolbeg Unit 2 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
248 | ESBPG | Poolbeg Unit 3 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
249 | ESBPG | Rhode Unit 3 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers | Yes | No | Plant has been decomissioned.
254 | ESBPG | Tarbert Unit 1 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
255 | ESBPG | Tarbert Unit 2 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
256 | ESBPG | Tarbert Unit 3 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
257 | ESBPG | Tarbert Unit 4 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
258 | ESBPG | Turlough Hill Unit 1 | Pumped Storage | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
259 | ESBPG | Turlough Hill Unit 2 | Pumped Storage | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
260 | ESBPG | Turlough Hill Unit 3 | Pumped Storage | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
261 | ESBPG | Ardnacrusha Unit 1 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
262 | ESBPG | North Wall Unit 5 | Thermal | CC | 7.2.5.2 | V1.0 | Indefinite* | Transformer windings not connected in delta on lower side and star on higher side. Tertiary star winding added to stabilise star point
264 | ESBPG | North Wall Unit 3 | Thermal | CC | 7.2.5.2 | V1.0 | Indefinite* | Transformer windings not connected in delta on lower side and star on higher side. Tertiary star winding added to stabilise star point
592 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | CC | 7.3.1.1 (h) | V1.0 | Until 01/03/2004 | Wind farm will remain synchronised to the transmission system during voltage dips of up to 25% from nominal (75% retained) as seen on the generator side terminals of the step-up transformer connecting the wind farm to the transmission system | Yes | No
594 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | CC | 7.3.6.1 | V1.0 | Subject to periodic review. Were there a greater requirement for reactive power in the region near to Derrybrien to arise then this derogation may be withdrawn. | At maximum continuous rating the power factor range for individual WTGs is 0.95 leading to 0.98 lagging. At 35% maximum continuous rating the power factor range for the generator is 0.51 leading to 0.51 lagging. | Yes | No
595 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | CC | 7.3.6.2 | V1.0 | Subject to periodic review. Were there a greater requirement for reactive power in the region near to Derrybrien to arise then this derogation may be withdrawn. | At maximum continuous rating the power factor range for individual WTGs is 0.95 leading to 0.98 lagging. At 35% maximum continuous rating the power factor range is 0.51 leading to 0.51 lagging. For values of active power output between 100% and 35% maximum continuous rating, an MVAr capability curve was submitted to ESBNG (now EirGrid). | Yes | No
596 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | CC | 7.3.6.3 | V1.0 | Subject to periodic review. Were there a greater requirement for reactive power in the region near to Derrybrien to arise then this derogation may be withdrawn. | At active power outputs between 12% and 35% maximum continuous rating of individual WTGs, MVAr capability is not less than that at 35% maximum continuous rating. For outputs below 12% maximum continuous rating, an MVAr capability curve was submitted to ESBNG (now EirGrid). | Yes | No
597 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | CC | 7.3.6.4 | V1.0 | Subject to periodic review. Were there a greater requirement for reactive power in the region near to Derrybrien to arise then this derogation may be withdrawn. | See extent of compliance for DAID 594, 595 & 596. | Yes | No
598 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | CC | 7.3.8 | V1.0 | Indefinite* | Derrybrien are required to provide an "AVR-type" continuously acting and adjustable controller as part of the turbine control system of the wind farm. Derrybrien are required to provide and agree the proposed control scheme response characteristics with ESBNG (now EirGrid) prior to commissioning of the wind farm.
601 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | OC4 | 4.5.3 | V1.0 | Indefinite* | Derrybrien are required to provide an "AVR-type" continuously acting and adjustable controller as part of the turbine control system of the wind farm. Derrybrien are required to provide and agree the proposed control scheme response characteristics with ESBNG (now EirGrid) prior to commissioning of the wind farm.
602 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | SDC2 | 8 | V1.0 | Indefinite* | 1. Derrybrien provides ESBNG (now EirGrid) with the ability to remotely control the outputs from the Derrybrien wind farm, the method of communications to be agreed with ESBNG (now EirGrid). 2. When required by ESBNG (now EirGrid), Derrybrien will provide an on-site presence at Derrybrien wind farm within one hour the request. 3. Derrybrien is required to declare to ESBNG (now EirGrid) the various characteristics of the wind farm. After the initial declaration, where there is a change to Derrybrien’s declarations, Derrybrien is required to notify ESBNG (now EirGrid) immediately of the revised declaration. However, Derrybrien is not required to submit daily declarations. 4. Derrybrien are required to submit daily nominations of the expected energy output from the wind farm. ESBNG (now EirGrid) and Derrybrien are required to review the usefulness of the nominations after six months of operation. | Yes | No
603 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | CC | 7.3.1.1 (u) | V1.0 | Indefinite* | WTGs cannot provide guaranteed operating reserve levels | Yes | No
604 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | CC | 7.3.1.2 | V1.0 | Indefinite* | WTG are not fitted with unit governor systems | Yes | No
605 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | CC | 7.3.7 | V1.0 | Indefinite* | WTG are not fitted with unit governor systems | Yes | No
606 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | OC4 | 3.4 | V1.0 | Indefinite* | WTG are not fitted with unit governor systems | Yes | No
609 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | CC | 12.2 (d) to (g) | V1.0 | Indefinite* | The equivalent information relevant to CC12.2 (d) to (g) will be provided for the main grid transformer | Yes | No
610 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | OC7 | 2.4.2.2 | V1.0 | Indefinite* | See DAID 602 | Yes | No
611 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | OC7 | 2.4.2.3 | V1.0 | Indefinite* | See DAID 602 | Yes | No
613 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | OC7 | 2.5.5 | V1.0 | Indefinite* | See DAID 602
614 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | SDC1 | 5 | V1.0 | Indefinite* | See DAID 602 | Yes | No
615 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | SDC1 | 7 | V1.0 | Indefinite* | See DAID 602 | Yes | No
616 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | SDC2 | 6 | V1.0 | Indefinite* | See DAID 602 | Yes | No
617 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | SDC2 | 7 | V1.0 | Indefinite* | See DAID 602 | Yes | No
618 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien Wind Farm | Wind | SDC2 | 8 | V1.0 | Indefinite* | See DAID 602 | Yes | No
621 | ESBNG (now EirGrid plc) | Anner 110kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | During Transmission System disturbances or following transmission faults, the voltage may fall to 0.88pu during Summer 2002, 0.85pu during Summer maintenance 2003, 0.89pu during Summer maintenance 2004 and 0.86pu during Summer Maintenance 2005. Voltage collapse may occur during Transmission System disturbances or following transmission faults during Summer maintenance 2002. | Yes | No
622 | ESBNG (now EirGrid plc) | Ardnacrusha 110 kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | During Transmission System disturbances or following transmission faults, the voltage may fall to 0.84pu during Summer maintenance 2003, 0.82pu during Summer maintenance 2004 and 0.79pu during Summer maintenance 2005. | Yes | No
623 | ESBNG (now EirGrid plc) | Ballydine 110kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | During Transmission System disturbances or following transmission faults, the voltage may fall to 0.88pu during Summer 2002, 0.85pu during Summer maintenance 2003, 0.85pu during Summer maintenance 2005 and 0.88pu during Summer maintenance 2004. Voltage collapse may occur during Transmission System disturbances during Summer maintenance 2002. | Yes | No
624 | ESBNG (now EirGrid plc) | Ballylickey 110 kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2003 | Voltages following contingency could be 0.87pu for Winter 2002/3. Voltages following contingency could be 0.89pu for Summer maintenance 2003. | Yes | No
625 | ESBNG (now EirGrid plc) | Bandon 110kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2003 | Voltages following contingency could be 0.84pu for Summer 2002. Voltage collapse may occur following contingency for Summer maintenance 2002. Voltages following contingency could be 0.86pu for Winter 2002/3. Voltages following contingency could be 0.88pu for Summer maintenance 2003. | Yes | No
626 | ESBNG (now EirGrid plc) | Barrymore 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.83pu for Summer maintenance 2002. Voltages following contingency could be 0.88pu for Winter 2002/3. Voltages following contingency could be 0.81pu for Summer maintenance 2003. Voltages following contingency could be 0.85pu for Summer maintenance 2004. Voltages following contingency could be 0.82pu for Summer maintenance 2005. | Yes | No
628 | ESBNG (now EirGrid plc) | Brinny 110kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2003 | Voltages following contingency could be 0.84pu for Summer 2002. Voltage collapse may occur following contingency for Summer maintenance 2002. Voltages following contingency could be 0.86pu for Winter 2002/3. Voltages following contingency could be 0.88pu for Summer maintenance 2003. | Yes | No
629 | ESBNG (now EirGrid plc) | Butlerstown 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 28/02/2003 | Voltages following contingency could be 0.81pu for Summer 2002. Voltage collapse may occur following contingency during Summer maintenance 2002 and Winter 2002/3. | Yes | No
630 | ESBNG (now EirGrid plc) | Cahir 110 kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltage Collapse may occur following contingency for Summer maintenance 2002. Voltages following contingency could be 0.87pu for Summer maintenance 2003. Voltages following contingency could be 0.88pu for Summer maintenance 2005. | Yes | No
634 | ESBNG (now EirGrid plc) | Doon 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.88pu for Summer 2002. Voltage collapse may occur following contingency during Summer maintenance 2002. Voltages following contingency could be 0.86pu for Summer maintenance 2003 and Summer maintenance 2005. Voltages following contingency could be 0.89pu for Summer maintenance 2004. | Yes | No
636 | ESBNG (now EirGrid plc) | Dunmanway 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2003 | Voltages following contingency could be 0.85pu for Summer 2002. Voltage collapse may occur following contingency during Summer maintenance 2002. Voltages following contingency could be 0.88pu for Summer maintenance 2003 and for Winter 2002/3. | Yes | No
639 | ESBNG (now EirGrid plc) | Griffinrath 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.89pu for Winter 2004/5. | Yes | No
642 | ESBNG (now EirGrid plc) | Knockeragh 110kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 31/12/2008 | Voltage collapse may occur during Transmission System disturbances or following transmission faults during Summer 2006, 2007, 2008 and 2009. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
647 | ESBNG (now EirGrid plc) | Newbridge 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 28/02/2006 | During Transmission System disturbances or following transmission faults, the voltage may fall to 94.6 kV during Winter 2004, 96.8 kV during Winter 2005 and 95.7 kV during Winter 2006. | Yes | No
648 | ESBNG (now EirGrid plc) | Oughtragh 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 31/12/2008 | Voltage collapse may occur during Transmission System disturbances or following transmission faults during Summer 2006, 2007, 2008 and 2009. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
649 | ESBNG (now EirGrid plc) | Thurles 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2003 | During Transmission System disturbances or following transmission faults, the voltage may fall to 0.89pu during Summer 2002 and Summer maintenance 2003. Voltage collapse may occur during Transmission System disturbances o r following transmission faults. | Yes | No
650 | ESBNG (now EirGrid plc) | Tralee 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 03/09/2005 | Voltage collapse may occur during Transmission System disturbances or transmission faults during Summer maintenance 2002, 2003, 2004 and 2005. | Yes | No
651 | ESBNG (now EirGrid plc) | Trien 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 31/12/2008 | Voltage collapse may occur during Transmission System disturbances or following transmission faults during Summer 2006, 2007, 2008 and 2009. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
655 | ESBNG (now EirGrid plc) | Monread 110kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/01/2006 | During Transmission System disturbances or following transmission faults, the voltage may fall to 93.5 kV during Winter 2004, 96.8 kV during Winter 2005 and 94.6 kV during Winter 2006. | Yes | No
720 | Airtricity | King's Mountain Wind Farm | Wind | CC | 7.3.1.1 (g) | V1.0 | Indefinite* | Wind farm operates with a reactive power capability of 0.9 lagging (i.e. producing reactive power) to 0.975 leading (i.e. absorbing reactive power) at maximum continuous rating at the transmission connection point over the voltage range as specified in clause CC.8.3.2 of the Grid Code
766 | Hibernian Wind Power | Mountain Lodge Phase 2 Wind Farm | Wind | CC | 7.3.1.1 (c) | V1.1 | Indefinite* | Wind turbine can operate in the range 47.0Hz to 47.5Hz. However, if the turbine rotor is at maximum speed and experiences a gust of wind, while operating in the range 47.0Hz to 47.5Hz, the turbine will be forced to disconnect.
779 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat Wind Farm | Wind | CC | 12.2 | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
780 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat Wind Farm | Wind | CC | 7.2.5.1 | V1.1 | Indefinite* | On-load tap-changing (OLTC) transformer will be provided at the main substation, instead of individual OLTC transformers at each generator. | Yes | No
781 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat Wind Farm | Wind | CC | 7.3.1.1 (g), 7.3.6.1, 7.3.6.2, 7.3.6.3, 7.3.6.4 | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
782 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat Wind Farm | Wind | CC | 7.3.1.1 (h) | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
783 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat Wind Farm | Wind | CC | 7.3.1.1 (l) | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
784 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat Wind Farm | Wind | CC | 7.3.1.1 (u) | V1.1 | Indefinite* | WTGs cannot provide guaranteed operating reserve levels | Yes | No
785 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat Wind Farm | Wind | CC | 7.3.1.2 & 7.3.7 | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
|  | Meentycat Wind Farm | Wind | OC4 | 3.4 & 3.5 | V1.1 | Indefinite*
786 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat Wind Farm | Wind | CC | 7.3.8 | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
787 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat Wind Farm | Wind | OC7 | 2.4.2.2, 2.4.2.3 & 2.5.5 | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code.
788 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat Wind Farm | Wind | SDC1 | All | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
789 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat Wind Farm | Wind | SDC2 | 6, 7, 8 | V1.1 | Indefinite* |  | Yes | No
813 | ESBPG | West Offaly Power | Thermal | CC | 7.3.1.1 (b) & (c ) | V1.1 | Service life of low pressure turbine blades | Generation unit will remain synchronised within the range 47.5 Hz to 51.5 Hz for a duration of 60 minutes. Generation unit will remain synchronised within the range 51.5 Hz to 52 Hz for a duration of 6 minutes (360 seconds), the period of 360 seconds will be reviewed by ESB National Grid following the first transmission system high frequency (>51.5 Hz) event and ESB National Grid reserve the right to alter this period of 360 seconds between the values of 60 seconds and 3600 seconds. Generation unit will remain synchronised within the range 47.0 Hz to 47.5 Hz for a duration of 20 seconds required each time the frequency is below 47.5 Hz.
816 | ESBNG (now EirGrid plc) | Ratrussan 110 kV station | Transmission | CC | 8.3.2 | V1.1 | Until 31/12/2008 | During Transmission System disturbances or following transmission faults, the voltage may fall to 93 kV during Summer 2006 and 88 kV during Summer 2007. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
817 | Booltiagh Wind Ltd. | Booltiagh Wind Farm | Wind | WFPS1 | 5.1 | V1.1 incl. WFPS1 | Until 01/03/2006 | Wind Farm will comply with all requirements in WF1.5.1, with the exception of the requirement for “No additional WTG shall be started while the Transmission System Frequency is above 50.2Hz”. | Yes | No
818 | Booltiagh Wind Ltd. | Booltiagh Wind Farm | Wind | WFPS1 | 5.2 | V1.1 incl. WFPS1 | Until 01/03/2006 | Booltiagh Wind Farm will postpone implementation of Frequency Control and the signals required to control it. | Yes | No
819 | Booltiagh Wind Ltd. | Booltiagh Wind Farm | Wind | WFPS1 | 5.3 | V1.1 incl. WFPS1 | Until 01/03/2006 | Booltiagh Wind Farm will postpone implementation of ramp rate control as required by WF1.5.3, and its associated signals. | Yes | No
820 | Booltiagh Wind Ltd. | Booltiagh Wind Farm | Wind | WFPS1 | 7.1 | V1.1 incl. WFPS1 | Until 01/03/2006 | Booltiagh Wind Farm will comply will supply WFPS1.7.1 Signals list #1 as required, but will postpone implementation of signals list #2, #3, #4 and #5. | Yes | No
821 | Booltiagh Wind Ltd. | Booltiagh Wind Farm | Wind | WFPS1 | 7.2 | V1.1 incl. WFPS1 | Until 01/03/2006 | Booltiagh Wind Farm will comply with WFPS1.7.2.1 & WFPS1.7.2.5, but implementation of WFPS1.7.2.2, WFPS1.7.2.3 and WFPS1.7.2.4 will be postponed. | Yes | No
824 | Hibernian Wind Power | Derrybrien Wind Farm | Wind | WFPS1 | 1.4 | V1.2 | Indefinite* | WFPS1.4.1: The Fault Ride Through (FRT) capability curve for the WTGs with the installed control system is only marginally non-compliant with WFPS1.4.1. At 100% output, the wind farm as a whole is compliant. The FRT capability of the WTGs with the installed control system is essentially compliant with the requirements for conventional plant. WFPS1.4.2 (a): Plant is fully compliant. WFPS1.4.2 (b): If the WTG experiences voltage dips >60% below nominal that last for between 300 and 700 ms, under certain circumstances it could take up to 2 seconds after the voltage recovers before the turbine is back to 90% of available active power.
825 | Hibernian Wind Power | Derrybrien Wind Farm | Wind | WFPS1 | 5.2.2 | V1.2 | Indefinite* | Facility is marginally non-compliant. Derrybrien submitted a Power-Frequency Response Curve to ESBNG (now EirGrid).
826 | Hibernian Wind Power | Derrybrien Wind Farm | Wind | WFPS1 | 5.3 | V1.2 | Indefinite* | Wind farm is capable of adhering to a maximum ramp rate setting for start-up of the wind farm. Each WTG has a maximum ramp rate limit of ± 50kW/s during start-up. Wind farm does not have the capability to impose overall one-minute and ten-minute average ramp rate limitations.
827 | Hibernian Wind Power | Derrybrien Wind Farm | Wind | WFPS1 | 6.2.3 | V1.2 | Indefinite* | The slope of the Voltage Regulation System is capable of being set to any value between 1% and 5% and give full reactive power range for any active power output. The slope can also be set between 5% and 10%, however this will limit the reactive power range (lagging).
|  | Derrybrien Wind Farm | Wind |  | 6.2.4 | V1.2 | Until May 2006 | Wind farm requires 4 seconds to change from unity to a power factor of 0.98.
844 | ESBPG | West Offaly Power | Thermal | CC | 7.3.6.1 | V1.1 | Until end Summer 2006 | The generator can meet the full reactive power range if active power output is reduced to 134MW.
845 | SWS (Kilgarvan Wind Farm Ltd.) | Coomagearlahy Wind Farm | Wind | WFPS1 | 4.2 (b) | V1.1 incl. WFPS1 | Indefinite* | Following a low voltage incident that is longer than 500ms and lower than 50% retained voltage, the wind farm may take up to 4 seconds to return to 90% active power output. This only occurs under certain other conditions, including wind speeds above 8 m/s, turbulence, and tower oscillation position.
846 | SWS (Kilgarvan Wind Farm Ltd.) | Coomagearlahy Wind Farm | Wind | WFPS1 | 6.2.4 | V1.1 incl. WFPS1 | Until 30/04/2007 | Following a step change in voltage at the connection point, the wind farm power station will achieve 90% of its steady-state reactive power response within 5-20 seconds. | Yes | No
849 | ESBNG (now EirGrid plc) | Coomagearlahy 110kVStation | Transmission | CC | 8.3.2 | V1.2 | Until 01/03/2007 | During Transmission System disturbances or following transmission faults, the voltage may fall to 83 kV during Summer 2006. | Yes | No | Derogation no longer required
850 | ESBNG (now EirGrid plc) | Kilkenny 110kV Station | Transmission | CC | 8.3.2 | V1.2 | Until 31/12/2008 | During Transmission System disturbances or following transmission faults, the voltage may fall to 87 kV during Winter 2008. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
851 | ESBNG (now EirGrid plc) | Kilmurry 110kV Station | Transmission | CC | 8.3.2 | V1.2 | Until 30/09/2008 | During Transmission System disturbances or following transmission faults, the voltage may fall to 94 kv during Winter 2008. | Yes | No
852 | ESBNG (now EirGrid plc) | Tralee 110kV Station | Transmission | CC | 8.3.2 | V1.2 | Until 31/12/2008 | During Summer 2006, voltage collapse may occur during Transmission System disturbances or following transmission faults. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
853 | ESBNG (now EirGrid plc) | Clonkeen 110kV Station | Transmission | CC | 8.3.2 | V1.2 | Until 01/03/2007 | During Summer 2006, voltage collapse may occur during Transmission System disturbances or following transmission faults. | Yes | No | Derogation no longer required
854 | Tynagh Energy Ltd. | Tynagh CCGT | Thermal | CC | 7.3.2 | V1.1 | Indefinite* | Tynagh CCGT is capable of tripping to house load while running on natural gas. However, the plant is incapable of tripping to house load and sustain operation while running on liquid fuel (secondary fuel).
855 | Aughinish Alumina Ltd. | Aughinish CHP Plant | CHP | CC | 7.3.1.1 (k) | V1.1 | Time limited until ESBNG modifies the Grid Code for CHP plant | Plant has a minimum load capability of 50% of its registered capacity, not the required 35% of registered capacity as required for generator units other than CCGTs.
856 | Glanlee Windfarm | Glanlee Windfarm | Wind | WFPS1 | 6.3 |  | Until 31 October 2007 | Power Factor is 0.98 exporting to 0.95 importing until end Oct 2007 when wind farm will comply. | Yes | No
857 | Glanlee Windfarm | Glanlee Windfarm | Wind | WFPS1 | 6.2.4 |  | Until 31 October 2007 | The wind farm can only provide 90% in 4-20 seconds until additional Reactive Power Compensation is installed by October 2007 | Yes | No
858 | Glanlee Windfarm | Glanlee Windfarm | Wind | WFPS1 | 1.4.2 (b) |  | Lifetime of the project | For faults longer than 0.5 seconds and deeper than 50% voltage dip, and with wind speeds that are experiend for only 36% of the year, the turbines shall take up to 4 seconds to provide 90 % Active Power repsonse.
859 | Glanlee Windfarm | Glanlee Windfarm | Wind | WFPS1 | 1.4.2 |  | Until 31 October 2007 | The full FRT capability wil not be available until additional Reactive Power Compensation is installed by October 2007 | Yes | No
870 | EirGrid | Newbridge 110kV station | Transmission | CC | 8.3.2 | v1.2 | Until 31/12/2008 | Voltage may drop to 97 kV in Winter 2007 |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
871 | EirGrid | Monread 110kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 31/12/2008 | Voltage may drop to 97 kV in Winter 2007 and 98 kV in Winter 2008. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
872 | EirGrid | Ballywater 110 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 96 kV in Winter 2007 and the voltage may drop to 89 kV or there may be Voltage collapse in Winter 2008. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
873 | EirGrid | Crane 110 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 96 kV in Winter 2007 and the voltage may drop to 89 kV or there may be Voltage collapse in Winter 2008. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
874 | EirGrid | Wexford 110 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 92 kV in Winter 2007 and the voltage may drop to 93 kV or there may be Voltage collapse in Winter 2008. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
875 | EirGrid | Moneypoint 110 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 98 kV in Summer 2009 |  |  | Derogation no longer required
876 | EirGrid | Ardnacrusha 110 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 98 kV in Summer 2009 |  |  | Derogation no longer required
877 | EirGrid | Drumline 110kV station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 98 kV in Summer 2009 |  |  | Derogation no longer required
878 | EirGrid | Kellis 220 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 194 kV in Winter 2008 |  |  | Derogation no longer required
879 | EirGrid | Kilteel 110 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 96 kV in Winter 2009 |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
507 | ESBPG | Great Island Unit 1 | Thermal | CC | 7.3.1.1 (k) | v1.2 | Lifetime of plant | Minimum load is 44% of Registered Capacity
508 | ESBPG GI2 | Great Island Unit 2 | Thermal | CC | 7.3.1.1 (k) | v1.2 | Lifetime of plant | Minimum load is 44% of Registered Capacity
512 | ESBPG MP1 | Moneypoint Unit 1 | Thermal | CC | 7.3.1.1 (k) | v3.0 | Until 31/05/2009 | Minimum load is 41% of Registered Capacity | Yes |  | Originally requested and approved until end of Dec '07 and subsequently reapplied for and approved until completion of MERP.
513 | ESBPG MP2 | Moneypoint Unit 2 | Thermal | CC | 7.3.1.1 (k) | v3.0 | Until 30/04/2009 | Minimum load is 41% of Registered Capacity | Yes |  | Originally requested and approved until end of Dec '07 and subsequently reapplied for and approved until completion of MERP.
514 | ESBPG MP3 | Moneypoint Unit 3 | Thermal | CC | 7.3.1.1 (k) | v3.0 | Until 31/05/2009 | Minimum load is 41% of Registered Capacity | Yes |  | Originally requested and approved until end of Dec '07 and subsequently reapplied for and approved until completion of MERP.
585 | ESBPG MP1 | Moneypoint Unit 1 | Thermal | CC | 7.3.1.1 (t) | v1.2 | Earlier of 31/12/07 or date which testing is complete. | In hot condition time from synch to min load is 50 minutes | Yes | No | Extension until July 2008 has been sought
586 | ESBPG MP2 | Moneypoint Unit 2 | Thermal | CC | 7.3.1.1 (t) | v1.2 | Earlier of 31/12/07 or date which testing is complete. | In hot condition time from synch to min load is 50 minutes | Yes | No | Extension until Dec 2008 has been sought
587 | ESBPG MP3 | Moneypoint Unit 3 | Thermal | CC | 7.3.1.1 (t) | v1.2 | Earlier of 31/12/07 or date which testing is complete. | In hot condition time from synch to min load is 50 minutes | Yes | No | Extension until July 2008 has been sought
716 | ESBPG MRT | Marina | Thermal | CC | 7.3.5 |  | Lifetime of plant | The generating unit GT does not have a unit transformer connected between the generating unit circuit breaker and the Generator Transformer LV terminals, however the current configuration achieves almost the equivalent result.
483 | ESBPG PB3 | Poolbeg Unit 3 | Thermal | CC | 7.3.1.1 (h) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | Will not remain synchronised during all voltage dips specified in CC 7.3.1.1 h
527 | ESBPG PB3 | Poolbeg Unit 3 | Thermal | CC | 7.3.1.1 (l) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | Ramp up capability is < 2% reg capacity per minute from min load to reg capacity. 1.4% from 130MW to 242MW, otherwise less.
542 | ESBPG PB3 | Poolbeg Unit 3 | Thermal | CC | 7.3.1.1 (n) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | Min uptime is 5.5 hours
558 | ESBPG PB3 | Poolbeg Unit 3 | Thermal | CC | 7.3.1.1 (p) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | Has a forbidden zone of 17%
580 | ESBPG PB3 | Poolbeg Unit 3 | Thermal | CC | 7.3.1.1 (s) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | Cold start is 3.5 hours. Hot start is 18 hours.
588 | ESBPG PB3 | Poolbeg Unit 3 | Thermal | CC | 7.3.1.1 (t) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | Time from synch to min load > allowed
698 | ESBPG PB3 | Poolbeg Unit 3 | Thermal | CC | 7.3.4 | V2.0 | Earlier of 27/05/08 or overhaul is approved.
751 | ESBPG PB3 | Poolbeg Unit 3 | Thermal | CC | 7.3.1.1 (u) (iii) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | TOR1 is 7.41% Registered Capacity
760 | ESBPG PB3 | Poolbeg Unit 3 | Thermal | CC | 7.3.1.1 (u) (iv) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | TOR2 is 7.41% of Registered Capacity
912 | EirGrid | Banoge 110 kV Station | Transmission | CC | 8.3.2 |  | Until 30th September 2009 | Voltage may drop to 87 kV or there may be Voltage collapse in Winter 2008. |  |  | Approved 21/02/2008
863 | Viridian Power Ltd | HP2 | CC | CC | 7.3.1.1 (b) | v2.0 | Indefinite | The station is unable to remain in operation, exporting power to the grid, with system frequency aboce 51.5Hz for sixty (60) minutes. Station can stay operated in this frequency range for 45 seconds. | Generator can remain synchronised down to 47.5Hz. Generator breaker will open on rising frequency at 51.5Hz. Generator can operate continuously betweent the range 47.5Hz and 51.5Hz but is limited to 20 secs between 51.5Hz and 52Hz. Once a cumulatinve dura |  | Granted subject to three conditions
864 | Viridian Power Ltd | HP2 | 7.3.1.1 (c ) | CC | 7.3.1.1 (c ) | v2.0 | Indefinite | Station is unable to remain synchronised to the Transmission System at Transmission System Frequencies within the range 47.0Hz to 47.5Hz for a duration of 20 seconds required each time the Frequency is below 47.5Hz. Station can stay operated in this frequency range for 45 seconds. |  |  | Granted subject to three conditions
865 | Viridian Power Ltd | HP2 | 7.3.1.1 (l) | CC | 7.3.1.1 (l) | v2.0 | Indefinite | Ramp up capability is greater than 1.5% of Registered Capacity per minute between 50% to 95% RC when the Unit is in the Normal Dispatch Condition, but 0.5% of Registered Capacity per minute in the upper load range between 95-100% RC to avoid overshoot.
888 | Viridian Power Ltd | HP2 | 7.3.1.1 (l) | CC | 7.3.1.1 (l) | v2.0 | Indefinite | Backup fuel oil firing: Ramp up capability is greater than 1.5% of Registered Capacity per minute between 50% to 95% RC when the unit is in the Normal Dispatch Condition, but 0.5% of RC per minute in the upper load range between 95%-100% RC.
889 | Tynagh Energy Ltd. | Tynagh |  | CC | 7.3.1.1(k) | v2.0 | 2008-08-31 | The minimum load level is currently at 214 MW exported which is 55.7% of registered capacity. |  |  | Time-limited derogation until 31/08/2008
930 | ESB PG MP1 | Moneypoint Unit 1 |  | CC | 7.3.1.1 (t) (i) | v3.1 | Earlier of 31/07/2008 or the test complete date | Cold loading up rates: From Block load of 8.62 to Min Load of 136MW at a rate of 1.04 MW/Min up to 102.08MW and 1.56 MW/Min up to 136 MW takes 111.61 Minutes. Then there are two soak times for cold start up - 90 minutes at 19 MW and 30 minutes at 102.08 MW. This gives a total time of 231.61 Minutes |  |  | Time limited 31/07/2008 or the test complete date
931 | ESB PG MP2 | Moneypoint Unit 2 |  | CC | 7.3.1.1 (t) (i) | v3.2 | Earlier of 31/12/2008 or the test complete date | Cold loading up rates: From Block load of 8.62 to Min Load of 136MW at a rate of 1.04 MW/Min up to 102.08MW and 1.56 MW/Min up to 136 MW takes 111.61 Minutes. Then there are two soak times for cold start up - 90 minutes at 19 MW and 30 minutes at 102.08 MW. This gives a total time of 231.61 Minutes |  |  | Time limited 31/12/2008 or the test complete date
932 | ESB PG MP3 | Moneypoint Unit 3 |  | CC | 7.3.1.1 (t) (i) | v3.3 | Earlier of 31/07/2008 or the test complete date | Cold loading up rates: From Block load of 8.62 to Min Load of 136MW at a rate of 1.04 MW/Min up to 102.08MW and 1.56 MW/Min up to 136 MW takes 111.61 Minutes. Then there are two soak times for cold start up - 90 minutes at 19 MW and 30 minutes at 102.08 MW. This gives a total time of 231.61 Minutes |  |  | Time limited 31/07/2008 or the test complete date
901 | ESB PG | North Wall CC4 |  | CC | 7.3.1.1 (k) | v2.0 | Indefinite | The min load for North Wall CC is 87.32MWe - a % capacity of 54%
956 | Green Energy Company Ltd | Boggeragh Mountain Windfarm |  | WFPS1 | 4.2(b) | v3.1 | 15 Years | For certain combinations of voltage dip/ duration and the shape of voltage recovery to pre-fault level, the turbines cannot return to their Maximum Active Available Power within 1 second after the Transmission voltage is re-established. Dependant on the unique situations (wind load, turbulence and tower position) the some turbines in a windfarm will return to their available power only within 1-4 seconds.
957 | Green Energy Company Ltd | Boggeragh Mountain Windfarm |  | WFPS1 | 6.3 | v3.1 | 1st April 2010 to 1st April 2011 | The WTG’s do not have the full power factor range required in the grid code and cannot meet the grid code requirement without the provision of reactive power compensation equipment.
958 | Green Energy Company Ltd | Boggeragh Mountain Windfarm |  | WFPS1 | 6.2.4 | v3.1 | 1st April 2010 to 1st April 2011 | The V90-3 MW turbines are not capable of providing 90% of it’s steady state reactive power response within 1 second. The turbines are equipped with a Voltage control feature but it requires between 4 to 20 seconds to reach 90% of requested kVAR response.
889 | Tynagh Energy Limited | Tynagh Power Station |  | CC | 7.3.1.1 | v3.0 | 31st January 2009 | Tynagh Energy Limited (TEL) seeks an extension of its expired derogation (dated 18th April 2008) as currently the plant is unable to run at 50% of its registered capacity in normal operating mode. The minimum load level is currently at 205 MW exported which is 53.4% of registered capacity.
955 | SWS (Kilgarvan Wind Farm Ltd.) | Coomagearlahy Wind Farm Phase 3 |  | WFPS1 | 6.2.4 | v3.1 | March 2009 to December 2009 | The grid code requires that the speed of response of the Voltage Regulation System (AVR) shall be such that, following a step change in Voltage at the Connection Point the Controllable WFPS shall achieve 90 % of its steady-state Reactive Power response within 1 second. The response may require a transition from maximum Mvar production to maximum Mvar absorption or viceversa. In fact Nordex N90 2500kW turbines (more specifically their CWE SCADA control system) can only achieve 90% of its steady state reactive power response within a period of around 20s.
964 | Gort Wind Farms Ltd | Derrybrien Wind Farm, Co. Galway |  | WFPS1 | 6.2.2 | v3.2 | Permanent | The required speed of response of the Set-point Voltage Controller within 20 seconds of a change in Set – Point from EirGrid is not achievable in all circumstances. The attached document details the operation of the voltage control system response.
500 | ESB PG | Ardnacrusha |  | CC | 7.3.1.1(k) | v3.4 | The derogation will apply until the end of December 2015 or until the next refurbishment, whichever is earlier. | Minimum Load Capability is 12 MW.
501 | ESB PG | Ardnacrusha |  | CC | 7.3.1.1(k) | v3.4 | The derogation will apply until the end of December 2015 or until the next refurbishment, whichever is earlier. | Minimum Load Capability is 12 MW.
502 | ESB PG | Ardnacrusha |  | CC | 7.3.1.1(k) | v3.4 | The derogation will apply until the end of December 2015 or until the next refurbishment, whichever is earlier. | Minimum Load Capability is 12 MW.
892 | ESB PG | Ardnacrusha |  | CC | 7.3.1.1(k) | v3.4 | The derogation will apply until the end of December 2015 or until the next refurbishment, whichever is earlier. | Minimum Load Capability is 12 MW.
991 | Endesa | Tarbert Unit 3 |  | CC | 7.3.1.1 (u)(ii) | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | The unit is unable to provide SOR at loads in excess of 240MW (generated).
992 | Endesa | Tarbert Unit 3 |  | CC | 7.3.1.1 (u)(iii) | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | The unit is unable to provide TOR1 at loads in excess of 240MW (generated).
993 | Endesa | Tarbert Unit 3 |  | CC | 7.3.1.1 (u)(iv) | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | The unit is unable to provide TOR2 at loads in excess of 240MW (generated).
975 | Endesa | Tarbert Unit 1 |  | CC | 7.3.6.1 | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | These units are unable to meet the reactive power limits that are set out in the Grid Code of operating at 0.93 pf leading to 0.85 pf lagging at Registered Capacity.
976 | Endesa | Tarbert Unit 2 |  | CC | 7.3.6.1 | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | These units are unable to meet the reactive power limits that are set out in the Grid Code of operating at 0.93 pf leading to 0.85 pf lagging at Registered Capacity.
973 | Endesa | Great Island Unit 1 |  | CC | 7.3.6.1 | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | The unit is unable to provide Reactive Power (leading) capability.
974 | Endesa | Great Island Unit 2 |  | CC | 7.3.6.1 | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | The unit is unable to provide Reactive Power (leading) capability.
986 | Endesa | Great Island Unit 1 |  | CC | 7.3.1.1(u)(iii) | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | TOR1 capability is limited to 3 MW.
987 | Endesa | Great Island Unit 1 |  | CC | 7.3.1.1(u)(iv) | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | TOR2 capability is limited to 3 MW.
988 | Endesa | Great Island Unit 2 |  | CC | 7.3.1.1(u)(iii) | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | TOR1 capability is limited to 3 MW.
989 | Endesa | Great Island Unit 2 |  | CC | 7.3.1.1(u)(iv) | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | TOR2 capability is limited to 3 MW.
990 | Endesa | Tarbert Unit 3 |  | CC | 7.3.1.1(u)(i) | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | The unit is unable to provide POR at loads in excess of 240 MW (generated).
975 | Endesa | Tarbert Unit 1 |  | CC | 7.3.6.1 | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | Reactive Power Capability is limited to 10 MVAr leading and 25 MVAr lagging.
976 | Endesa | Tarbert Unit 2 |  | CC | 7.3.6.1 | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | Reactive Power Capability is limited to 10 MVAr leading and 25 MVAr lagging.
977 | Endesa | Tarbert Unit 3 |  | CC | 7.3.6.1 | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | Reactive Power Capability is limited to 45 MVAr leading and 110 MVAr lagging.
978 | Endesa | Tarbert Unit 4 |  | CC | 7.3.6.1 | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | Reactive Power Capability is limited to 45 MVAr leading and 110 MVAr lagging.
973 | Endesa | Great Island 1 |  | CC | 7.3.6.1 | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | No leading reactive power is available on this unit.
974 | Endesa | Great Island Unit 2 |  | CC | 7.3.6.1 | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | No leading reactive power is available on this unit.
511 | ESBPG | Liffey Unit 4 |  | CC | 7.3.1.1(k) | v3.0 | The derogation will apply until Dec 2015 or the next refurbishment or until the unit is retired, whichever is earlier. | Capable of providing Minimum Load of 3.99 MW
895 | ESBPG | Lee Unit 3 |  | CC | 7.3.1.1(k) | v3.0 | The derogation will apply until Dec 2015 or the next refurbishment or until the unit is retired, whichever is earlier. | Capable of providing Minimum Load of 3 MW
985 | ESBPG | North Wall Unit 4 |  | CC | 7.3.1.1(t)(i) | v3.4 | The derogation will apply until the earlier of: a. 10th Feb 2013 or b. the date on which the unit becomes an open cycle gas turbine | NW4 is capable of synchronising to minimum load in a time of 56 minutes when in a hot state
1013-1015 | Endesa | Tarbert Unit Unit 3 |  | CC | 7.3.1.1(u)(ii) 7.3.1.1(u)(iii) 7.3.1.1(u)(iv) | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired or until the implementation of a new AS Agreement, whichever is earlier. | Tarbert Unit 3 is capable of providing 3 MW of SOR, 3 MW of TOR1 and 8 MW of TOR2
1000 | ESBPG | Aghada Unit 2 |  | CC | 7.3.1.1(h) | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | AD2 will remain synchronised during and following Voltage dips at the HV terminals of the Generator Transformer of 95% of nominal Voltage (5% retained) for duration of 0.15s
1001 | ESBPG | Aghada Unit 2 |  | CC | 7.3.1.1(g) | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | AD2 can absorb Reactive Power at Registered Capacity up to a limit of -150MVAR (0.944pf) leading.
1002 | ESBPG | Aghada Unit 2 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | AD2 can absorb Reactive Power at Registered Capacity up to a limit of -150MVAR (0.944pf) leading.
1011 | Cushaling Power Ltd | Edenderry Unit 3 & Edenderry Unit 5 |  | CC | 7.3.1.1(h) | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Cannot meet the min Fault Ride Through durations in certain dispatch scenarios.
1018-1021 | Endesa Ireland Ltd | Rhode Unit 1, Rhode Unit 2, Tawnaghmore Unit 1, Tawnaghmore Unit 3 |  | CC | 7.3.1.1(h) | v3.4 | Granted until the CER make a decision on DAID 1085 | The Units are unable to ride through faults as per CC.7.3.1.1(h) under the full operating capabilities of the Generation Unit at the Connection Point.
969 | SSE Renewables | Kings Mountain Extension |  | WFPS1 | 6.1 | v3.4 | The derogation shall apply until the installation and full compliance of a suitably sized STATCOM with the Grid Code requirements or 11th April 2012, whichever is earlier. | 90% of the steady state reactive power response within 5 secs
970 | SSE Renewables | Kings Mountain Extension |  | WFPS1 | 6.3 | v3.4 | The derogation shall apply until the installation and full compliance of a suitably sized STATCOM with the Grid Code requirements or 11th April 2012, whichever is earlier. | 90% of the steady state reactive power response within 5 secs
971 | SSE Renewables | Kings Mountain Extension |  | WFPS1 | 6.2.4 | v3.4 | The derogation shall apply until the installation and full compliance of a suitably sized STATCOM with the Grid Code requirements or 11th April 2012, whichever is earlier. | 90% of the steady state reactive power response within 5 secs
979 | Endesa | Rhode Unit 1 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Currently providing 7 Mvar Reactive Power Leading.
980 | Endesa | Rhode Unit 2 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Currently providing 7 Mvar Reactive Power Leading.
981 | Endesa | Tawnaghmore Unit 1 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Currently providing 7 Mvar Reactive Power Leading.
982 | Endesa | Tawnaghmore Unit 3 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Currently providing 7 Mvar Reactive Power Leading.
1016 | Bord Gáis Energy | Whitegate |  | CC | 7.3.1.1(h) | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | At certain leading Reactive Power positions the critical clearance time is less than 200ms.
1045 | Cushaling Power Ltd | Edenderry Unit 3 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Currently not providing Reactive Power Leading.
1046 | Cushaling Power Ltd | Edenderry Unit 5 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Currently not providing Reactive Power Leading.
435 | Synergen | Dublin Bay |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Can provide up to 100 Mvar Reactive Power Leading.
512-514 | ESBPG | Monepoint Unit 1, Moneypoint Unit 2, Moneypoint Unit 3 |  | CC | 7.3.1.1(k) | v1.0 | Valid from 01/02/2010 to 31/03/2010 | Min Load is 41%
880-883 | ESBPG | Turlough Hill Unit 1, Turlough Hill Unit 2, Turlough Hill Unit 3, Turlough Hill Unit 4 |  | CC | 7.3.1.1(p) | v1.2 | Derogation applies until the earlier of the lifetime of the unit or the completion of a major refurbishment | Forbidden Zone of 30 MW (from 10 MW to 40 MW) for all four units.
889 | Tynagh | Tynagh |  | CC | 7.3.1.1(k) | v3.2 | Valid from 31/3/2010 to 30/9/2010 | Min Load is 50.5%
435 | Synergen | Dublin Bay |  | CC | 7.3.6.1 | v3.5 | Valid until 17/02/2012 | Leading Reactive Power is 100 Mvar
1045 | Cushaling Power Ltd | Edenderry Unit 3 |  | CC | 7.3.6.1 | v3.5 | Valid until the derogation process is complete (FRT related) | Leading Reactive Power is 0 Mvar
1046 | Cushaling Power Ltd | Edenderry Unit 5 |  | CC | 7.3.6.1 | v3.5 | Valid until the derogation process is complete (FRT related) | Leading Reactive Power is 0 Mvar
979 | Endesa | Rhode Unit 1 |  | CC | 7.3.6.1 | v3.5 | Valid until a decision is reached on DAID 1084 | Currently providing 7 Mvar Reactive Power Leading.
980 | Endesa | Rhode Unit 2 |  | CC | 7.3.6.1 | v3.5 | Valid until a decision is reached on DAID 1084 | Currently providing 7 Mvar Reactive Power Leading.
981 | Endesa | Tawnaghmore Unit 1 |  | CC | 7.3.6.1 | v3.5 | Valid until a decision is reached on DAID 1084 | Currently providing 7 Mvar Reactive Power Leading.
982 | Endesa | Tawnaghmore Unit 3 |  | CC | 7.3.6.1 | v3.5 | Valid until a decision is reached on DAID 1084 | Currently providing 7 Mvar Reactive Power Leading.
1045 | Cushaling Power Ltd | Edenderry Unit 3 |  | CC | 7.3.6.1 | v3.5 | Valid until the derogation 20 August 2012 | Leading Reactive Power is 0 Mvar
1046 | Cushaling Power Ltd | Edenderry Unit 5 |  | CC | 7.3.6.1 | v3.5 | Valid until the derogation 20 August 2012 | Leading Reactive Power is 0 Mvar
1082 & 1083 | Cushaling Power Ltd | Edenderry Unit 3 and Edenderry Unit 5 |  | CC | 7.3.1.1(h) & 7.3.6.1 | v3.5 | Granted until the earlier of a. 1st Jan 2022; b. notification by EirGrid; after 1 Jan 2017, that the agreement in place is no longer appropriate in the content of system security; c. lifetime of the units; d. the completion of a major refurbishment of the units | Leading Reactive Power is 23 Mvar
1049 | Viridian Power Limited | Huntstown Unit 2 |  | CC | 7.3.1.1(w) | v3.5 | Effective from 15 March 2011 until the earlier of: The lifetime of the plant or the completion of a major refurbishment of the unit. | Operate on Secondary Fuel at no less than 70% of Primary Fuel Registered Capacity.
1050 | Tynagh Energy Ltd. | Tynagh |  | CC | 7.3.1.1(w) | v3.5 | Effective from the 15 March 2011 until the earlier of 30 September 2013 or the completion of a major refurbishment of the unit. | 30 MW for the Secondary Fuel Switchover Output
1052 | ESB PG | Aghada Unit 1 |  | PC.A4.3; CC.7.3.1; CC.7.3.1.1(w); CC.7.3.1.1(x);CC.7.3.1.2; OC10.2.2(e); OC10.2.2(f); OC10.5.5(d); OC10.5.5(e); Definitions: Off-Site Storage Location; Secondary Fuel Switchover Output; Primary Fuel Switchover Output |  | v3.5 | Effective from 15 March 2011 until the earlier of: The lifetime of the plant or the completion of a major refurbishment of the unit. | Derogated from all Secondary Fuel requirements in Grid Code.
1055 | Rusal Aughinish Ltd | Sealrock Unit 3 |  | CC | 7.3.1.1(w) | v3.5 | Effective from the 15 March 2011 until the earlier of 30 September 2013 or the completion of a major refurbishment of either unit. | 4 MW for the Secondary Fuel Switchover Output
1056 | Rusal Aughinish Ltd | Sealrock Unit 4 |  | CC | 7.3.1.1(w) | v3.5 | Effective from the 15 March 2011 until the earlier of 30 September 2013 or the completion of a major refurbishment of either unit. | 4 MW for the Secondary Fuel Switchover Output
1060 | Dublin Bay Power | Dublin Bay |  | CC | 7.3.1.1(w) | v3.5 | A derogation is granted effective from 15 March 2011 until the earlier of: 1st Jan 2015 or the completion of a major refurbishment of the unit.Subject to the submission to EirGrid of an interim report by 30/09/2013 and a proposal to achieve compliance before 31st Dec 2014. | 25 MW for the Primary Fuel Switchover Output and 25 MW for the Secondary Fuel Switchover Output
1086 | Bord Gáis Energy | Whitegate |  | CC | 7.3.1.1(w) | v3.5 | Effective from the 15 March 2011 until the earlier of 30 September 2013 or the completion of a major refurbishment of either unit. | 30 MW for the Secondary Fuel Switchover Output.
1044 | Bord Gáis Energy | Whitegate |  | CC | 7.3.1.1(l) | v4.0 | Effective from 20/10/2010 until the earlier of the lifetime of the unit or completion of a major refurbishment of the unit. | Ramp up capability of 0.6% Registered Capacity when the Unit is operating in the load range 96.3 – 100 % and being fired on Fuel Oil
1008 | Lisheen Wind Farm Ltd | Lisheen WFPS 1 |  | WFPS1 | 6.3.1 | v4.0 | Effective from 29/02/2012 until the earlier of 01/10/2013 or the completion of Lisheen WFPS phase two. | A reduction in Leading Reactive Power capability when the WFPS is operating at an Active Power of greater than 31.5 MW.
1096 | ESB PG | Aghada Open Cycle GT |  | CC | 7.3.1.1(w) | v4.0 | Effective from 05/09/2012 until 31/03/2013 | Cannot carry out an online fuel changeover from Primary Fuel to Secondary Fuel at Primary Fuel Switchover Output and cannot carry out an online fuel changeover from Secondary fuel to Primary Fuel at Secondary Fuel Switchover Output.
1070 - 1081 | ESB PG | Moneypoint Unit 1, Moneypoint Unit 2, Moneypoint Unit 3 |  | CC | 7.3.6.1 | v4.0 | Effective from 21/11/2011 until the earlier of 01/01/2023, the replacement of any or all the Generator Transformers, the lifetime of any of the units or the completion of a major refurbishment of the unit. | The Leading Reactive Power capability of each unit is 112 MVAr.
1089 & 1090 | Endesa Ireland | Great Island Unit 1 & Great Island Unit 2 |  | CC | 7.3.1.1(k) | v4.0 | Effective from 01/06/2009 until the earlier of 31/12/2014 or the completion of a major refurbishment of either unit. | The Minimum Load capability of each unit is 23.7 MW.
1051 | ESB PG | Aghada Unit 2 |  | CC | 7.3.1.1(w) | v4.0 | Subject to the submission to EirGrid of an interim report by 31 Aug 2014 and a proposal to achieve compliance before 30 Nov 2015, the CER grants a temporary derogation until the earlier of 1 Dec 2015 or the completion of a major refurbishment of the plant. | The Primary Fuel Switchover Output capability is 25 MW and the Secondary Fuel Switchover Output capability is 25 MW.
1066-1069 | ESB PG | Aghada Unit 2 |  | CC | 7.3.1.1(g), CC.7.3.6.4, CC.7.3.6.1, CC.7.3.6.2 | v4.0 | This derogation will not indemnify AD2 from any GPI that may be applied in respect of the relevant Grid Code clauses. The derogation is effective from 19 Oct 2011 until the earlier of 1 Jan 2017 or the completion of a major refurbishment of the unit. | The maximum Lagging Reactive Power capabilty is 270 MVAr.
2068 | Tynagh Energy Ltd. | Tynagh CCGT |  | CC | 7.3.1.1(w) | v4.0 | Effective from 6/9/2013 until the earlier of 6 months from the date of the CER's decision on Secondary Fuel; 6th Sept 2018; or the completion of a major refurbishment of the unit. | The level at which the secondary to primary transfer can take place is circa 30 MW.
2042 | SSE Renewables | Bindoo WFPS |  | WFPS1 | 1.6.2.2(a); 1.6.2.2(b) | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2043 | SSE Renewables | Bindoo WFPS |  | WFPS1 | 1.6.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2044 | SSE Renewables | Bindoo WFPS |  | WFPS1 | WFPS1.5.3.1; WFPS1.5.3.2; WFPS1.5.3.3; WFPS1.5.3.4; WFPS1.5.3.5; WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5; WFPS1.7.2.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2045 | SSE Renewables | Bindoo WFPS |  | WFPS1 | WFPS1.4.2 ( c) | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2046 | SSE Renewables | Coomacheo |  | WFPS1 | WFPS1.6.2.2(a); WFPS1.6.2.2(b) | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2047 | SSE Renewables | Coomacheo |  | WFPS1 | WFPS1.4.1; WFPS1.4.2 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2048 | SSE Renewables | Coomacheo |  | WFPS1 | WFPS1.6.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2049 | SSE Renewables | Coomacheo |  | WFPS1 | WFPS1.5.3.1; WFPS1.5.3.2; WFPS1.5.3.3; WFPS1.5.3.4; WFPS1.5.3.5;WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5; WFPS1.7.2.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2050 | SSE Renewables | Dromada |  | WFPS1 | WFPS1.6.2.2(a); WFPS1.6.2.2(b) | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2051 | SSE Renewables | Dromada |  | WFPS1 | WFPS1.5.3.1; WFPS1.5.3.2; WFPS1.5.3.3; WFPS1.5.3.4; WFPS1.5.3.5;WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5; WFPS1.7.2.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2052 | SSE Renewables | Dromada |  | WFPS1 | WFPS1.4.2 (c) | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2053 | SSE Renewables | Dromada |  | WFPS1 | WFPS1.6.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2054 | SSE Renewables | Kingsmountain 2 |  | WFPS1 | WFPS1.6.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2055 | SSE Renewables | Kingsmountain 2 |  | WFPS1 | WFPS1.5.2.1; WFPS1.5.3.1; WFPS1.5.3.2; WFPS1.5.3.3; WFPS1.5.3.4; WFPS1.5.3.5; WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2056 | SSE Renewables | Kingsmountain 2 |  | WFPS1 | WFPS1.4.1; WFPS1.4.2 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2057 | SSE Renewables | Meentycat Wind Farm |  | WFPS1 | WFPS1.6.2.2(a); WFPSI1.6.2.2(b) | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2058 | SSE Renewables | Meentycat Wind Farm |  | WFPS1 | WFPS1.5.3.1; WFPS1.5.3.2; WFPS1.5.3.3; WFPS1.5.3.4; WFPS1.5.3.5; WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2059 | SSE Renewables | Meentycat Wind Farm |  | WFPS1 | WFPS1.4.1; WFPS1.4.2 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2060 | SSE Renewables | Meentycat Wind Farm |  | WFPS1 | WFPS1.6.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2065 | Brookfield | Lisheen 1 & 2 |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015. | MPID 212
2066 | Brookfield | Lisheen 1 |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015. | MPID 227
2067 | Brookfield | Lisheen 2 |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015. | MPID 227
2071 | Brookfield | Coomagearlahy 1 |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that tests demonstrate compliance with the FRT Requirements of Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2072 | Brookfield | Coomagearlahy 2 |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that tests demonstrate compliance with the FRT Requirements of Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2073 | Brookfield | Coomagearlahy 1 |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that tests demonstrate compliance with the FRT Requirements of Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2074 | Brookfield | Coomagearlahy 2 |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that tests demonstrate compliance with the FRT Requirements of Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2090 | Brookfield | Coomagearlahy 3 |  | WFPS1 | WFPS1.5.3.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that compliance is achieved, the date that a remedy has been implemented and tested or 31st December 2015. | MPID 227
2091 | Brookfield | Coomagearlahy 3 |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that compliance is achieved, the date that a remedy has been implemented and tested or 31st December 2015. | MPID 212
2092 | Midas Energy Co | Glanlee Windfarm |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 30th September 2013 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2093 | Midas Energy Co | Glanlee Windfarm |  | WFPS1 | WFPS1.5.2.1, WFPS1.5.3, WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 30th September 2013 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2012 | ESB Renewables | Mountain Lodge |  | WFPS1 | WFPS1.5.2.1 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227 (DMOL)
2013 | ESB Renewables | Garvagh 1 |  | WFPS1 | WFPS1.5.2.1 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227 (DMOL)
2014 | ESB Renewables | Garvagh 2 |  | WFPS1 | WFPS1.5.2.1 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227 (DMOL)
2015 | ESB Renewables | Derrybrien |  | WFPS1 | WFPS1.5.2.1 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227 (DMOL)
2061 | ESB Renewables | Garvagh 1 |  | WFPS1 | WFPS1.4.1, WFPS1.4.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2062 | ESB Renewables | Garvagh 1 |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2063 | ESB Renewables | Garvagh 1 |  | WFPS1 | WFPS1.6.3.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2076 | ESB Renewables | Garvagh 1 |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2, WFPS1.5.3.3, WFPS1.5.4.1, WFPS1.5.4.2, WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2077 | ESB Renewables | Derrybrien |  | WFPS1 | WFPS1.4.1, WFPS1.4.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2078 | ESB Renewables | Derrybrien |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2, WFPS1.5.3.3, WFPS1.5.4.1, WFPS1.5.4.2, WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2079 | ESB Renewables | Derrybrien |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2080 | ESB Renewables | Derrybrien |  | WFPS1 | WFPS1.6.3.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2081 | ESB Renewables | Mountain Lodge |  | WFPS1 | WFPS1.4.1, WFPS1.4.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2082 | ESB Renewables | Mountain Lodge |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2, WFPS1.5.3.3, WFPS1.5.4.1, WFPS1.5.4.2, WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2083 | ESB Renewables | Mountain Lodge |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2084 | ESB Renewables | Mountain Lodge |  | WFPS1 | WFPS1.6.3.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2085 | ESB Renewables | Garvagh 2 |  | WFPS1 | WFPS1.4.1, WFPS1.4.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2086 | ESB Renewables | Garvagh 2 |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2, WFPS1.5.3.3, WFPS1.5.4.1, WFPS1.5.4.2, WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2087 | ESB Renewables | Garvagh 2 |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2088 | ESB Renewables | Garvagh 2 |  | WFPS1 | WFPS1.6.3.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2094 | Midas Energy Co | Glanlee Windfarm |  | WFPS1 | WFPS1.6.3 | v5.0 | Effective from 30th September 2013 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2095 | Green Energy Company Ltd | Boggeragh |  | WFPS1 | WFPS1.5.2.1, WFPS1.5.3, WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 30th September 2013 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2096 | Green Energy Company Ltd | Boggeragh |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 30th September 2013 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2112 | Brookfield | Booltiagh 1 |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 24th March 2014 until the earlier of the date that tests demonstrate compliance with the Grid Code, the date that a rememdy has been implemented and tested or 31st December 2015 | MPID 212
2113 | Brookfield | Booltiagh 1 |  | WFPS1 | WFPS1.5.3.2 | v5.0 | Effective from 24th March 2014 until the earlier of the date that tests demonstrate compliance with the Grid Code, the date that a rememdy has been implemented and tested or 31st December 2015 | MPID 227
2114 | Brookfield | Booltiagh 1 |  | WFPS1 | WFPS1.5.4.1 | v5.0 | Effective from 24th March 2014 until the earlier of the date that tests demonstrate compliance with the Grid Code, the date that a rememdy has been implemented and tested or 31st December 2015 | MPID 227
2115 | Brookfield | Booltiagh 1 |  | WFPS1 | WFPS1.5.4.2 | v5.0 | Effective from 24th March 2014 until the earlier of the date that tests demonstrate compliance with the Grid Code, the date that a rememdy has been implemented and tested or 31st December 2015 | MPID 227
2116 | Brookfield | Booltiagh 1 & 2 |  | WFPS1 | WFPS1.6.3.1 | v5.0 | Effective from 24th March 2014 until the earlier of the date that tests demonstrate compliance with the Grid Code, the date that a rememdy has been implemented and tested or 31st December 2015 | MPID 228
2117 | Brookfield | Lisheen 1 |  | WFPS1 | WFPS1.5.3.3, WFPS1.5.4.1 | v5.0 | Effective from 21st March 2014 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015. | MPID 227
2118 | Brookfield | Lisheen 1 |  | WFPS1 | WFPS1.5.2.1, WFPS1.5.3.5, WFPS1.5.3.6, WFPS1.5.3.7 | v5.0 | Effective from 21st March 2014 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015. | MPID 228
2119 | Brookfield | Lisheen 2 |  | WFPS1 | WFPS1.5.2.1, WFPS1.5.3.5, WFPS1.5.3.6, WFPS1.5.3.7 | v5.0 | Effective from 21st March 2014 until the earlier of the date that compliance is achieved, the date that a remedy has been implemented and tested or 31st December 2015. | MPID 227
2120 | Brookfield | Lisheen 1 |  | WFPS1 | WFPS1.4.1, WFPS1.4.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that tests demonstrate compliance with the FRT Requirements of Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2121 | Brookfield | Lisheen 2 |  | WFPS1 | WFPS1.4.1, WFPS1.4.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that tests demonstrate compliance with the FRT Requirements of Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2122 | Brookfield | Coomagearlahy 1 |  | WFPS1 | WFPS1.4.1; WFPS1.4.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that tests demonstrate compliance with the FRT Requirements of Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2123 | Brookfield | Coomagearlahy 2 |  | WFPS1 | WFPS1.4.1, WFPS1.4.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that tests demonstrate compliance with the FRT Requirements of Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2124 | Brookfield | Coomagearlahy 1 |  | WFPS1 | WFPS1.5.2.1, WFPS1.5.3.5, WFPS1.5.3.6, WFPS1.5.3.7 | v5.0 | Effective from 21st March 2014 until the earlier of the date that tests demonstrate compliance with the FRT Requirements of Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2125 | Brookfield | Coomagearlahy 2 |  | WFPS1 | WFPS1.5.2.1, WFPS1.5.3.5, WFPS1.5.3.6, WFPS1.5.3.7 | v5.0 | Effective from 21st March 2014 until the earlier of the date that tests demonstrate compliance with the FRT Requirements of Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2126 | Brookfield | Coomagearlahy 1 |  | WFPS1 | WFPS1.5.3.3, WFPS1.5.4.1 | v5.0 | Effective from 21st March 2014 until the earlier of the date that tests demonstrate compliance with the FRT Requirements of Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2127 | Brookfield | Coomagearlahy 2 |  | WFPS1 | WFPS1.5.33, WFPS1.5.4.1 | v5.0 | Effective from 21st March 2014 until the earlier of the date that tests demonstrate compliance with the FRT Requirements of Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2128 | SSE Generation Ireland | GI1 |  | CC7 | CC.7.3.6.1 | v5.0 | 31st December 2014 | 0 MVAr (leading)
2129 | SSE Generation Ireland | GI2 |  | CC7 | CC.7.3.6.1 | v5.0 | 31st December 2014 | 0 MVAr (leading)
2132 | Rusal Aughinish Ltd | SK3 |  | CC7 | CC.7.3.1.1 (w) | v5.0 | Effective from 18th November 2014 until the earlier of the lifetime of the unit or one year after the date that a rememdy becomes available, but not later than 25th March 2025 | For Secondary Fuel Switchover Output to 2MW
2133 | Rusal Aughinish Ltd | SK4 |  | CC7 | CC.7.3.1.1 (w) | v5.0 | Effective from 18th November 2014 until the earlier of the lifetime of the unit or one year after the date that a rememdy becomes available, but not later than 25th March 2025 | For Secondary Fuel Switchover Output to 2MW
2136 | Brookfield | Knockacummer |  | WFPS1 | WFPS1.7.1.2 | v5.0 | Effective from 13th January 2014 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015 | Signals
2144 | Brookfield | WG2 |  | CC7 | CC.7.3.1.1 (w) | v5.0 | Effective from 14th March 2014 for the lifetime of the unit or a major refurbishment of the unit but not later than 01/01/18 | For Secondary Fuel Switchover Output to 20MW
2145 | Brookfield | Coomagearlahy 3 |  | WFPS1 | WFPS1.5.4.1, WFPS1.5.4.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that compliance is achieved, the date that a remedy has been implemented and tested or 31st December 2015. | Ramp Rates
2146 | Brookfield | Coomagearlahy 3 |  | WFPS1 | WFPS1.7.1.1 (d) | v5.0 | Effective from 21st March 2014 until the earlier of the date that compliance is achieved, the date that a remedy has been implemented and tested or 31st December 2015. | Signals
2147 | Brookfield | Coomagearlahy 3 |  | WFPS1 | WFPS1.4 | v5.0 | Effective from 21st March 2014 until the earlier of the date that compliance is achieved, the date that a remedy has been implemented and tested or 31st December 2015. | MPID 230
2214 | Pallas Wind Farm Ltd | Clahane Phase 1 |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 1st May 2014 until the earlier of the date that tests demonstrate compliance with Voltage Regulation and Frequency Response and Ramp Rates Requirements of Grid Code, the date that a rememdy has been implented and tested or 31st December 2015 | MPID 212
2215 | Pallas Wind Farm Ltd | Clahane Phase 1 |  | WFPS1 | WFPS1.5.2.1 | v5.0 | Effective from 1st May 2014 until the earlier of the date that tests demonstrate compliance with Voltage Regulation and Frequency Response and Ramp Rates Requirements of Grid Code, the date that a rememdy has been implented and tested or 31st December 2015 | MPID 227
2216 | Pallas Wind Farm Ltd | Clahane Phase 1 |  | WFPS1 | WFPS1.5.3 | v5.0 | Effective from 1st May 2014 until the earlier of the date that tests demonstrate compliance with Voltage Regulation and Frequency Response and Ramp Rates Requirements of Grid Code, the date that a rememdy has been implented and tested or 31st December 2015 | MPID 227
2217 | Pallas Wind Farm Ltd | Clahane Phase 1 |  | WFPS1 | WFPS1.5.4.1, WFPS1.5.4.2 | v5.0 | Effective from 1st May 2014 until the earlier of the date that tests demonstrate compliance with Voltage Regulation and Frequency Response and Ramp Rates Requirements of Grid Code, the date that a rememdy has been implented and tested or 31st December 2015 | MPID 227
2218 | Pallas Wind Farm Ltd | Clahane Phase 1 |  | WFPS1 | WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 1st May 2014 until the earlier of the date that tests demonstrate compliance with Voltage Regulation and Frequency Response and Ramp Rates Requirements of Grid Code, the date that a rememdy has been implented and tested or 31st December 2015 | MPID 227
2443 | Gort Wind Farms Ltd | Derrybrien |  | WFPS1 | WFPS1.5.2.1 | v5.0 | Effective from 26th November 2014 until the earlier of the date the remedy is implemented and tested or 31st December 2015 | WFPS shall commence implementation of Active Power Control Set-point within 5 minutes of receipt of the signal from the TSO. The WFPS is derogated to a tolerance of +/-3MW tolerance across all MW Output.
986 | SSE Generation Ireland Ltd | Great Island 1 |  | CC | CC.7.3.1.1(u)(iii) | v3.5 | Effective from 1 January 2014 until 15 April 2015 | The unit can provide 3MW of TOR1
987 | SSE Generation Ireland Ltd | Great Island 1 |  | CC | CC.7.3.1.1(u)(iv) | v3.5 | Effective from 1 January 2014 until 15 April 2015 | The unit can provide 3MW of TOR2
988 | SSE Generation Ireland Ltd | Great Island 2 |  | CC | CC.7.3.1.1(u)(iii) | v3.5 | Effective from 1 January 2014 until 15 April 2015 | The unit can provide 3MW of TOR1
989 | SSE Generation Ireland Ltd | Great Island 2 |  | CC | CC.7.3.1.1(u)(iv) | v3.5 | Effective from 1 January 2014 until 15 April 2015 | The unit can provide 3MW of TOR2
2103 | SSE Generation Ireland Ltd | Great Island 3 |  | CC | CC.7.3.1.1(m) | v5.0 | Effective from 12 November 2013 until 15 April 2015 | Ramp Down Capability is at 1.5 MW/min
2104 | SSE Generation Ireland Ltd | Great Island 3 |  | CC | CC.7.3.1.1(l) | v5.0 | Effective from 12 November 2013 until 15 April 2015 | Ramp Up Capability is at 1.5 MW/min between 30-80 MW and 0.5 MW/min between 80-120 MW.
2065; 2067; 2119; 2121 | Brookfield Renewable Energy Group | Lisheen WFPS Phase 2 |  | WFPS1 | WFPS1.6.2.2; WFPS1.5.3.1; WFPS 1.5.3.2; WFPS1:5.2.1; WFPS1.5.3.5; WFPS1.5.3.6; WFPS1.5.3.7; WFPS1.4.1; WFPS1.4.2 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | MPID 212; MPID 227; MPID 230
2065; 2066; 2117; 2120 | Brookfield Renewable Energy Group | Lisheen WFPS Phase 1 |  | WFPS1 | WFPS1.6.2.2; WFPS1.5.3.1; WFPS 1.5.3.2; WFPS1.5.3.3; WFPS1.5.4.1; WFPS1.4.1; WFPS1.4.2 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | MPID 212; MPID 227; MPID 230
2090; 2091; 2145; 2146; 2147; 2391 | Brookfield Renewable Energy Group | Coomagearlaghy WFPS Phase 3 |  | WFPS1 | WFPS1.5.3.2; WFPS1.6.2.2; WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.1(d); WFPS1.4; WFPS1.7.1.3.1(b); WFPS1.7.1.3.1(c) | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | MPID 227; MPID 212; Ramp Rates; Signals; MPID 230
2064 | Brookfield Renewable Energy Group | Booltiagh WFPS Phase 1 & 2 |  | WFPS1 | WFPS1.7.1.1 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | Signal List #1
2122; 2123 | Brookfield Renewable Energy Group | Coomagearlahy WFPS Phase 1 & 2 |  | WFPS1 | WFPS1.4.1; WFPS1.4.2 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | MPID 230
2043 | SSE Airtricity | Bindoo WFPS |  | WFPS1 | WFPS1.6.3 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | MPID 228
2050; 2051; 2053 | SSE Airtricity | Dromada WFPS |  | WFPS1 | WFPS1.6.2.2(a); WFPS1.6.2.2(b); WFPS1.5.3.1; WFPS1.5.3.2; WFPS1.5.3.3; WFPS1.5.3.4; WFPS1.5.3.5; WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5; WFPS1.7.2.3; WFPS1.6.3; | v6.0 | Effective from 17 December 2015 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2017. | MPID 227; MPID 212; MPID 228
2059 | SSE Airtricity | Meentycat WFPS |  | WFPS1 | WFPS1.4.1; WFPS1.4.2 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | MPID 230
2492; 2493 | Wind Prospect Ireland Ltd | Boggeragh Mountain WFPS |  | WFPS1 | WFPS1.6.2.2; WFPS1.5.3 | v6.0 | Effective from 06 August 2015 until the earlier of: The date that a remedy has been implemeneted and tested or; 31st December 2016. | MPID 212; Frequency Response Control
2214; 2215; 2216; 2217; 2218 | Gael Force Wind Energy Ltd | Clahane WFPS Phase 1 |  | WFPS1 | WFPS1.6.2.2; WFPS1.5.2.1; WFPS1.5.3; WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5; WFPS1.7.2.3 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | MPID 212; MPID 227;
2062; 2063 | ESB Renewables | Garvagh Glebe WFPS Phase 1 |  | WFPS1 | WFPS1.6.2.2; WFPS1.6.3.3 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | MPID 212; MPID 228
2087 | ESB Renewables | Garvagh Glebe WFPS Phase 2 (Tullynahaw) |  | WFPS1 | WFPS1.6.2.2 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | MPID 212
994; 995; 996; 997 | SSE | Tarbert 4 |  | CC | CC.7.3.1.1(u)(i); CC.7.3.1.1(u)(ii); CC.7.3.1.1(u)(iii); CC.7.3.1.1(u)(iv); | v6.0 | Effective from 01 January 2014. Derogation extension approved until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implented and tested: or 31 May 2016. | The unit can provide 0 MW of POR; 0 MW of SOR; 0 MW TOR1 and 7.5 MW of TOR1.
2293; 2341 | SSE | Great Island 4 |  | CC | CC.7.3.1.1(h); CC.7.3.6.1 | v6.0 | Effective from 28/05/2014 to 31/12/2020 | At 95% of nominal voltage dip (5% retained) derogation is sought to a FRT of 85 ms. At 50% of nominal voltage dip (50% retained) derogation is sought to a FRT Time of 215 ms.0 Mvar (leading) at a SCL of 3.3 kA (below 7.4 kA)
2098 | Activation Energy DSU Ltd | AE1 |  | CC | CC.12.6(a) | v6.0 | Effective from 23/09/2015 to 01/06/2016 | A number of individual sites in AE1 do not have fast acting metering. Typcially these individual sites use pulse metering and have a DSU Capacity of less than 1 MW.
1097 | ESBGWM | PBC |  | CC | 7.3.1.1(t)(i) | v6.0 | Effective from 12/09/2012 to 30/06/2016 | Time from Synchronising to Minimum Load from hot: 69 mins; from warm: 146 mins; from cold: 224 mins.
2511 | ESBGWM | DB1 |  | CC | 7.3.1.1(w) | v6.0 | Effective from 01/01/2015 until the earlier of: the date that compliance with the Grid Code is achieved; the date that a remedy has been implemented and tested; the date the CER withdraws the derogation following a breach of the conditions of the derogation; or 31/12/2022. | 25 MW for the Primary Fuel Switchover Output/25 MW for the Secondary Fuel Switchover Output
2618 | ESBGWM | AD2 |  | CC | 7.3.1.1(w) | v6.0 | Effective from 01/12/2015 until the earlier of: the date that compliance with the Grid Code is achieved; the date that a remedy has been implemented and tested; the date the CER withdraws the derogation following a breach of the conditions of the derogation; or 31/12/2022. | 26 MW for the Primary Fuel Switchover Output/25 MW for the Secondary Fuel Switchover Output
2137 | SSE | TB1 |  | CC | 7.3.6.1 | v6.0 | Effective from the 01/01/2014 until the earlier of: Lifetime of the Generation Units; Or 31st Dec 2023. | 10Mvar (leading) 25Mvar (lagging)
2138 | SSE | TB2 |  | CC | 7.3.6.1 | v6.0 | Effective from the 01/01/2014 until the earlier of: Lifetime of the Generation Units; Or 31st Dec 2023. | 10Mvar (leading) 25Mvar (lagging)
2139 | SSE | TB3 |  | CC | 7.3.6.1 | v6.0 | Effective from the 01/01/2014 until the earlier of: Lifetime of the Generation Units; Or 31st Dec 2023. | 45Mvar (leading) and 110Mvar (lagging)
2140 | SSE | TB4 |  | CC | 7.3.6.1 | v6.0 | Effective from the 01/01/2014 until the earlier of: Lifetime of the Generation Units; Or 31st Dec 2023. | 45Mvar (leading) and 110Mvar (lagging)
2616 | Gealelectric | Ballywater Windfarm |  | WFPS | 1.5.2.1 | v6.0 | Effective From 2nd March 2016 until the earlier of:The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested; or 31st March 2017 | Active Power Control