## Register of Granted Derogations
Register of Granted Grid Code Derogations |  |  |  |  | Version 20 13/03/2019
* Remaining service life of facility or equipment responsible for non-compliance to the Grid Code.
DAID | Submitted by | Plant | Type | Section | Clause | Grid Code Version No | The Period of the Derogation | Extent of Compliance to the Provision | Has derogation expired, been superceded, or plant no longer in operation? | Is derogation still relevant? (May have expired, been superceded, the Grid Code clause may no longer be in force, the plant may now comply or no longer be in operation) | Comment
18 | ESBNG (now EirGrid plc) | Lisheen 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.88pu for Summer 2002. Voltage collapse may occur following contingency during Summer maintenance 2002. Voltages following contingency could be 0.89pu for Summer maintenance 2005 | Yes | No
21 | ESBNG (now EirGrid plc) | Athlone 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 28/02/2006 | Voltages following contingency could be 0.86pu for Summer Maintenance 2002. Voltages following contingency could be 0.84pu for Winter 2002/3 and Winter 2005/6. Voltages following contingency could be 0.89pu for Summer Maintenance 2003, Winter 2003/4, Summer 2005 and Summer Maintenance 2005. Voltages following contingency could be 0.87pu for Winter 2004/5. | Yes | No
36 | ESBNG (now EirGrid plc) | Drybridge 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.86pu for Summer maintenance 2002 and Summer maintenance 2004. Voltages following contingency could be 0.88pu for Summer maintenance 2003. | Yes | No
37 | ESBNG (now EirGrid plc) | Drumline 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.81pu for Summer maintenance 2002. Voltages following contingency could be 0.84pu for Summer maintenance 2003. Voltages following contingency could be 0.82pu for Summer maintenance 2004. Voltages following contingency could be 0.80 for Summer maintenance. | Yes | No
40 | ESBNG (now EirGrid plc) | Ennis 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.84pu for Summer maintenance 2002. Voltages following contingency could be 0.87pu for Summer maintenance 2003. Voltages following contingency could be 0.85pu for Summer maintenance 2004. Voltages following contingency could be 0.83 for Summer maintenance 2005. | Yes | No
53 | ESBNG (now EirGrid plc) | Kiltoy 1&2 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 28/02/2005 | Voltages following contingency could be 0.84pu for Summer maintenance 2002. Voltages following contingency could be 0.89pu for Winter 2004/5. | Yes | No
54 | ESBNG (now EirGrid plc) | Knockumber 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.86pu for Summer maintenance 2002. Voltages following contingency could be 0.87pu for Summer maintenance 2003 and Summer maintenance 2005. Voltages following contingency could be 0.85pu for Summer maintenance 2004 | Yes | No
59 | ESBNG (now EirGrid plc) | Lisdrum 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/12/2008 | During Transmission System disturbances or following transmission faults, the voltage may fall to 94 kV during Summer 2006 and 92 kV during Summer 2007. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
63 | ESBNG (now EirGrid plc) | Moneypoint 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.82pu for Summer maintenance 2002. Voltages following contingency could be 0.85pu for Summer maintenance 2003. Voltages following contingency could be 0.83pu for Summer maintenance 2004. Voltages following contingency could be 0.81pu for Summer maintenance 2005. | Yes | No
64 | ESBNG (now EirGrid plc) | Moy 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2002 | Voltage collapse may occur following contingency during Summer 2002 and Summer maintenance 2002. Voltages following contingency could be 0.86pu for Summer Maintenance 2004. | Yes | No
68 | ESBNG (now EirGrid plc) | Navan 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.86pu for Summer maintenance 2002. Voltages following contingency could be 0.87pu for Summer maintenance 2003 and 2005. Voltages following contingency could be 0.85pu for Summer maintenance 2004. | Yes | No
69 | ESBNG (now EirGrid plc) | Platin 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.86pu for Summer maintenance 2002. Voltages following contingency could be 0.87pu for Summer maintenance 2003. Voltages following contingency could be 0.85pu for Summer maintenance 2004. | Yes | No
73 | ESBNG (now EirGrid plc) | Sligo 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2004 | Voltages following contingency could be 0.80pu for Summer 2002. Voltage collapse may occur following contingency during Summer maintenance 2002. Voltages following contingency could be 0.86pu for Summer 2004 | Yes | No
74 | ESBNG (now EirGrid plc) | Shankill 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/12/2008 | During Transmission System disturbances or following transmission faults, the voltage may fall to 93 kV during Summer 2006 and 88 kV during Summer 2007. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
75 | ESBNG (now EirGrid plc) | Somerset 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2002 | Voltages following contingency could be 0.87pu for Summer maintenance 2002. | Yes | No
77 | ESBNG (now EirGrid plc) | Tawnaghmore 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2004 | Voltage collapse may occur following contingency during Summer 2002 and Summer maintenance 2002. Voltages following contingency could be 0.86pu for Summer maintenance 2004. | Yes | No
78 | ESBNG (now EirGrid plc) | Trillick 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 28/02/2005 | Voltages following contingency could be 0.89pu for Summer 2002. Voltages following contingency could be 0.87pu for Winter 2004/5. | Yes | No
79 | ESBNG (now EirGrid plc) | Tullabrack 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.82pu for Summer maintenance 2002. Voltages following contingency could be 0.85pu for Summer maintenance 2003. Voltages following contingency could be 0.83pu for Summer maintenance 2004. Voltages following contingency could be 0.81pu for Summer maintenance 2005. | Yes | No
81 | ESBNG (now EirGrid plc) | N/A | Market | SDC2A | 3.3 | V1.0 | Indefinite* | Facility not provided by ESBNG (now EirGrid).
84 | ESBNG (now EirGrid plc) | Kiltoy T101, T102 & T014 Anner T101 & T103 Castlefarm T101 & T102 Mungret T101 & T102 Brinny T101 & T102 Dunkettle T1 Gilra T121 Haulbowline T101 & T102/T103/T107 Knockumber T101 & T102 Old Court T101 & T102 Shelton Abbey T101a/T101b & T102 |  | CC | 7.2.5.4 | V1.0 | Indefinite* | Facility not provided by ESBNG (now EirGrid).
85 | ESBNG (now EirGrid plc) | Bellacorick T1 & T2 Ferbane T101, T102, T103 & T104 Lanesboro T102 Rhode T102 & T103 Pollaphuca T101 & T102 Inniscarra T101 Carrigadhroid T103 Cliff T101 & T102 |  | CC | 10.9.3 | V1.0 | Indefinite or until refurbishment of associated transmission compounds. | Distance Protection not provided, Overcurrent or Directional Overcurrent protection provided.
89 | ESBNG (now EirGrid plc) | Kiltoy T101, T102 & T014 Anner T101 & T103 Castlefarm T101 & T102 Mungret T101 & T102 Brinny T101 & T102 Dunkettle T1 Gilra T121 Haulbowline T101 & T102/T103/T107 Knockumber T101 & T102 Old Court T101 & T102 Shelton Abbey T101a/T101b & T102 |  | CC | 10.11.3 | V1.0 | Indefinite* | Facility not provided by ESBNG (now EirGrid).
90 | ESBNG (now EirGrid plc) | N/A | Market | SDC1 | 6.1 | V1.0 | Until 29/03/2006 | The SSA operates on a Business Day basis, while this clause in the Grid Code implies that the timetable for Generator nominations should be on a Calendar Day basis. | Yes | No | This clause is no longer applicable. SDC1 was modified for the SEM on 31 October 2007.
92 | ESBNG (now EirGrid plc) | N/A | Market | OC3 | 4 | V1.0 | Until 29/03/2006 | The SSA operates the TESS (Transitional Electricity Settlement System) on a Business Day basis, while this clause OC3.4 in the Grid Code implies that the timetable for interconnector “Available Transfer Capacity Determination and Posting” should occur on a Calendar Day basis. | Yes | No | This clause is no longer applicable. OC3 was deleted as part of the modifications for SEM on 31 October 2007.
93 | ESBNG (now EirGrid plc) | N/A | Market | OC3 | 5 | V1.0 | Until 29/03/2006 | The SSA operates on a Business Day basis, while this clause OC3.5 in the Grid Code implies that the timetable for interconnector nominations should be on a Calendar Day basis. | Yes | No | This clause is no longer applicable. OC3 was deleted as part of the modifications for SEM on 31 October 2007.
94 | ESBNG (now EirGrid plc) | N/A | Market | OC3 | 6.1 | V1.0 | Until 29/03/2006 | The SSA operates on a Business Day basis, while this clause OC3.6.1 in the Grid Code implies calendar day activities. | Yes | No | This clause is no longer applicable. OC3 was deleted as part of the modifications for SEM on 31 October 2007.
152 | Airtricity | King's Mountain 1 | Wind | CC | 7.3.1.1 (h) | V1.0 | Indefinite* | Wind farm will remain synchronised to the transmission system during voltage dips of up to: - 20% from nominal voltage as seen at the generator terminals during full load operation where the generator is initially operating at 105% of nominal voltage - 20% from nominal voltage and 500 milliseconds seconds duration as seen at the generator terminals during full load operation provided that the voltage drop takes place over a period of at least 50 milliseconds - 30% as seen at the generator terminals during full-load operation provided that this voltage drop does not persist for more than 100 milliseconds - 40% as seen at the generator terminals during 1300 kW operation provided that this voltage drop does not persist for more than 100ms
155 | Airtricity | King's Mountain 1 | Wind | CC | 7.3.1.1 (u) | V1.0 | Indefinite* | WTGs cannot provide guaranteed operating reserve levels
158 | Airtricity | King's Mountain 1 | Wind | CC | 7.3.8 | V1.0 | Indefinite* | NET must provide an "AVR-type" controller as part of the turbine control system of the wind farm and a switched capacitor bank as part of the local substation which fulfil the function of an AVR.
164 | ESBPG | Aghada OCGT 4 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
165 | ESBPG | Ardnacrusha 2 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
166 | ESBPG | Ardnacrusha 3 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
167 | ESBPG | Ardnacrusha 4 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
168 | ESBPG | Aghada Steam Plant 1 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
170 | ESBPG | Aghada OCGT 1 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
171 | ESBPG | Aghada OCGT 2 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
172 | ESBPG | Ardnacrusha 1 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
173 | ESBPG | Poolbeg 4 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
175 | ESBPG | Erne 1 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
176 | ESBPG | Erne 2 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
177 | ESBPG | Erne 3 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
178 | ESBPG | Erne 4 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
179 | ESBPG | Great Island 1 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
180 | ESBPG | Great Island 2 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
181 | ESBPG | Great Island 3 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
184 | ESBPG | Lee 1 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
185 | ESBPG | Lee 2 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
186 | ESBPG | Lee 3 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
187 | ESBPG | Liffey 1 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
188 | ESBPG | Liffey 2 | Hydro | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
191 | ESBPG | Moneypoint 1 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
192 | ESBPG | Moneypoint 2 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
193 | ESBPG | Moneypoint 3 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
194 | ESBPG | Marina OCGT | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
195 | ESBPG | North Wall 4 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
196 | ESBPG | North Wall 5 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
197 | ESBPG | Poolbeg 1 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
198 | ESBPG | Poolbeg 2 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
199 | ESBPG | Poolbeg 3 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
201 | ESBPG | Turlough Hill 4 | Pumped Storage | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
202 | ESBPG | Poolbeg 6 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
203 | ESBPG | Rhode 3 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens | Yes | No | Plant has been decomissioned.
208 | ESBPG | Tarbert 1 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
209 | ESBPG | Tarbert 2 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
210 | ESBPG | Tarbert 3 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
211 | ESBPG | Tarbert 4 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
212 | ESBPG | Turlough Hill 1 | Pumped Storage | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
213 | ESBPG | Turlough Hill 2 | Pumped Storage | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
214 | ESBPG | Turlough Hill 3 | Pumped Storage | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
215 | ESBPG | Poolbeg 5 | Thermal | CC | 7.2.3.1 | V1.0 | Indefinite* | LV cables do not have metallic screens
216 | ESBPG | Turlough Hill 4 | Pumped Storage | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
217 | ESBPG | Ardnacrusha 2 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
218 | ESBPG | Ardnacrusha 3 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
219 | ESBPG | Ardnacrusha 4 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
220 | ESBPG | Aghada Steam Plant 1 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
222 | ESBPG | Aghada OCGT 1 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
223 | ESBPG | Aghada OCGT 2 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
224 | ESBPG | Aghada OCGT 4 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
227 | ESBPG | Erne 1 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
228 | ESBPG | Erne 2 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
229 | ESBPG | Erne 3 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
230 | ESBPG | Erne 4 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
231 | ESBPG | Great Island 1 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
232 | ESBPG | Great Island 2 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
233 | ESBPG | Great Island 3 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
236 | ESBPG | Lee 1 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
237 | ESBPG | Lee 2 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
238 | ESBPG | Lee 3 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
239 | ESBPG | Liffey 1 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
240 | ESBPG | Liffey 2 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
243 | ESBPG | Marina OCGT | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
244 | ESBPG | North Wall 4 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
245 | ESBPG | North Wall 5 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
246 | ESBPG | Poolbeg 1 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
247 | ESBPG | Poolbeg 2 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
248 | ESBPG | Poolbeg 3 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
249 | ESBPG | Rhode 3 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers | Yes | No | Plant has been decomissioned.
254 | ESBPG | Tarbert 1 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
255 | ESBPG | Tarbert 2 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
256 | ESBPG | Tarbert 3 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
257 | ESBPG | Tarbert 4 | Thermal | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
258 | ESBPG | Turlough Hill 1 | Pumped Storage | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
259 | ESBPG | Turlough Hill 2 | Pumped Storage | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
260 | ESBPG | Turlough Hill 3 | Pumped Storage | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
261 | ESBPG | Ardnacrusha 1 | Hydro | CC | 7.2.3.2 | V1.0 | Indefinite* | LV cables are not in concrete troughs with concrete covers
262 | ESBPG | North Wall 5 | Thermal | CC | 7.2.5.2 | V1.0 | Indefinite* | Transformer windings not connected in delta on lower side and star on higher side. Tertiary star winding added to stabilise star point
264 | ESBPG | North Wall 3 | Thermal | CC | 7.2.5.2 | V1.0 | Indefinite* | Transformer windings not connected in delta on lower side and star on higher side. Tertiary star winding added to stabilise star point
592 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | CC | 7.3.1.1 (h) | V1.0 | Until 01/03/2004 | Wind farm will remain synchronised to the transmission system during voltage dips of up to 25% from nominal (75% retained) as seen on the generator side terminals of the step-up transformer connecting the wind farm to the transmission system | Yes | No
594 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | CC | 7.3.6.1 | V1.0 | Subject to periodic review. Were there a greater requirement for reactive power in the region near to Derrybrien to arise then this derogation may be withdrawn. | At maximum continuous rating the power factor range for individual WTGs is 0.95 leading to 0.98 lagging. At 35% maximum continuous rating the power factor range for the generator is 0.51 leading to 0.51 lagging. | Yes | No
595 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | CC | 7.3.6.2 | V1.0 | Subject to periodic review. Were there a greater requirement for reactive power in the region near to Derrybrien to arise then this derogation may be withdrawn. | At maximum continuous rating the power factor range for individual WTGs is 0.95 leading to 0.98 lagging. At 35% maximum continuous rating the power factor range is 0.51 leading to 0.51 lagging. For values of active power output between 100% and 35% maximum continuous rating, an MVAr capability curve was submitted to ESBNG (now EirGrid). | Yes | No
596 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | CC | 7.3.6.3 | V1.0 | Subject to periodic review. Were there a greater requirement for reactive power in the region near to Derrybrien to arise then this derogation may be withdrawn. | At active power outputs between 12% and 35% maximum continuous rating of individual WTGs, MVAr capability is not less than that at 35% maximum continuous rating. For outputs below 12% maximum continuous rating, an MVAr capability curve was submitted to ESBNG (now EirGrid). | Yes | No
597 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | CC | 7.3.6.4 | V1.0 | Subject to periodic review. Were there a greater requirement for reactive power in the region near to Derrybrien to arise then this derogation may be withdrawn. | See extent of compliance for DAID 594, 595 & 596. | Yes | No
598 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | CC | 7.3.8 | V1.0 | Indefinite* | Derrybrien are required to provide an "AVR-type" continuously acting and adjustable controller as part of the turbine control system of the wind farm. Derrybrien are required to provide and agree the proposed control scheme response characteristics with ESBNG (now EirGrid) prior to commissioning of the wind farm.
601 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | OC4 | 4.5.3 | V1.0 | Indefinite* | Derrybrien are required to provide an "AVR-type" continuously acting and adjustable controller as part of the turbine control system of the wind farm. Derrybrien are required to provide and agree the proposed control scheme response characteristics with ESBNG (now EirGrid) prior to commissioning of the wind farm.
602 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | SDC2 | 8 | V1.0 | Indefinite* | 1. Derrybrien provides ESBNG (now EirGrid) with the ability to remotely control the outputs from the Derrybrien wind farm, the method of communications to be agreed with ESBNG (now EirGrid). 2. When required by ESBNG (now EirGrid), Derrybrien will provide an on-site presence at Derrybrien wind farm within one hour the request. 3. Derrybrien is required to declare to ESBNG (now EirGrid) the various characteristics of the wind farm. After the initial declaration, where there is a change to Derrybrien’s declarations, Derrybrien is required to notify ESBNG (now EirGrid) immediately of the revised declaration. However, Derrybrien is not required to submit daily declarations. 4. Derrybrien are required to submit daily nominations of the expected energy output from the wind farm. ESBNG (now EirGrid) and Derrybrien are required to review the usefulness of the nominations after six months of operation. | Yes | No
603 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | CC | 7.3.1.1 (u) | V1.0 | Indefinite* | WTGs cannot provide guaranteed operating reserve levels | Yes | No
604 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | CC | 7.3.1.2 | V1.0 | Indefinite* | WTG are not fitted with unit governor systems | Yes | No
605 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | CC | 7.3.7 | V1.0 | Indefinite* | WTG are not fitted with unit governor systems | Yes | No
606 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | OC4 | 3.4 | V1.0 | Indefinite* | WTG are not fitted with unit governor systems | Yes | No
609 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | CC | 12.2 (d) to (g) | V1.0 | Indefinite* | The equivalent information relevant to CC12.2 (d) to (g) will be provided for the main grid transformer | Yes | No
610 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | OC7 | 2.4.2.2 | V1.0 | Indefinite* | See DAID 602 | Yes | No
611 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | OC7 | 2.4.2.3 | V1.0 | Indefinite* | See DAID 602 | Yes | No
613 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | OC7 | 2.5.5 | V1.0 | Indefinite* | See DAID 602
614 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | SDC1 | 5 | V1.0 | Indefinite* | See DAID 602 | Yes | No
615 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | SDC1 | 7 | V1.0 | Indefinite* | See DAID 602 | Yes | No
616 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | SDC2 | 6 | V1.0 | Indefinite* | See DAID 602 | Yes | No
617 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | SDC2 | 7 | V1.0 | Indefinite* | See DAID 602 | Yes | No
618 | Powergen Renewables Ireland Limited (now owned by Hibernian Wind Power) | Derrybrien | Wind | SDC2 | 8 | V1.0 | Indefinite* | See DAID 602 | Yes | No
621 | ESBNG (now EirGrid plc) | Anner 110kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | During Transmission System disturbances or following transmission faults, the voltage may fall to 0.88pu during Summer 2002, 0.85pu during Summer maintenance 2003, 0.89pu during Summer maintenance 2004 and 0.86pu during Summer Maintenance 2005. Voltage collapse may occur during Transmission System disturbances or following transmission faults during Summer maintenance 2002. | Yes | No
622 | ESBNG (now EirGrid plc) | Ardnacrusha 110 kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | During Transmission System disturbances or following transmission faults, the voltage may fall to 0.84pu during Summer maintenance 2003, 0.82pu during Summer maintenance 2004 and 0.79pu during Summer maintenance 2005. | Yes | No
623 | ESBNG (now EirGrid plc) | Ballydine 110kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | During Transmission System disturbances or following transmission faults, the voltage may fall to 0.88pu during Summer 2002, 0.85pu during Summer maintenance 2003, 0.85pu during Summer maintenance 2005 and 0.88pu during Summer maintenance 2004. Voltage collapse may occur during Transmission System disturbances during Summer maintenance 2002. | Yes | No
624 | ESBNG (now EirGrid plc) | Ballylickey 110 kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2003 | Voltages following contingency could be 0.87pu for Winter 2002/3. Voltages following contingency could be 0.89pu for Summer maintenance 2003. | Yes | No
625 | ESBNG (now EirGrid plc) | Bandon 110kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2003 | Voltages following contingency could be 0.84pu for Summer 2002. Voltage collapse may occur following contingency for Summer maintenance 2002. Voltages following contingency could be 0.86pu for Winter 2002/3. Voltages following contingency could be 0.88pu for Summer maintenance 2003. | Yes | No
626 | ESBNG (now EirGrid plc) | Barrymore 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.83pu for Summer maintenance 2002. Voltages following contingency could be 0.88pu for Winter 2002/3. Voltages following contingency could be 0.81pu for Summer maintenance 2003. Voltages following contingency could be 0.85pu for Summer maintenance 2004. Voltages following contingency could be 0.82pu for Summer maintenance 2005. | Yes | No
628 | ESBNG (now EirGrid plc) | Brinny 110kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2003 | Voltages following contingency could be 0.84pu for Summer 2002. Voltage collapse may occur following contingency for Summer maintenance 2002. Voltages following contingency could be 0.86pu for Winter 2002/3. Voltages following contingency could be 0.88pu for Summer maintenance 2003. | Yes | No
629 | ESBNG (now EirGrid plc) | Butlerstown 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 28/02/2003 | Voltages following contingency could be 0.81pu for Summer 2002. Voltage collapse may occur following contingency during Summer maintenance 2002 and Winter 2002/3. | Yes | No
630 | ESBNG (now EirGrid plc) | Cahir 110 kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltage Collapse may occur following contingency for Summer maintenance 2002. Voltages following contingency could be 0.87pu for Summer maintenance 2003. Voltages following contingency could be 0.88pu for Summer maintenance 2005. | Yes | No
634 | ESBNG (now EirGrid plc) | Doon 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.88pu for Summer 2002. Voltage collapse may occur following contingency during Summer maintenance 2002. Voltages following contingency could be 0.86pu for Summer maintenance 2003 and Summer maintenance 2005. Voltages following contingency could be 0.89pu for Summer maintenance 2004. | Yes | No
636 | ESBNG (now EirGrid plc) | Dunmanway 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2003 | Voltages following contingency could be 0.85pu for Summer 2002. Voltage collapse may occur following contingency during Summer maintenance 2002. Voltages following contingency could be 0.88pu for Summer maintenance 2003 and for Winter 2002/3. | Yes | No
639 | ESBNG (now EirGrid plc) | Griffinrath 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2005 | Voltages following contingency could be 0.89pu for Winter 2004/5. | Yes | No
642 | ESBNG (now EirGrid plc) | Knockeragh 110kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 31/12/2008 | Voltage collapse may occur during Transmission System disturbances or following transmission faults during Summer 2006, 2007, 2008 and 2009. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
647 | ESBNG (now EirGrid plc) | Newbridge 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 28/02/2006 | During Transmission System disturbances or following transmission faults, the voltage may fall to 94.6 kV during Winter 2004, 96.8 kV during Winter 2005 and 95.7 kV during Winter 2006. | Yes | No
648 | ESBNG (now EirGrid plc) | Oughtragh 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 31/12/2008 | Voltage collapse may occur during Transmission System disturbances or following transmission faults during Summer 2006, 2007, 2008 and 2009. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
649 | ESBNG (now EirGrid plc) | Thurles 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 30/09/2003 | During Transmission System disturbances or following transmission faults, the voltage may fall to 0.89pu during Summer 2002 and Summer maintenance 2003. Voltage collapse may occur during Transmission System disturbances o r following transmission faults. | Yes | No
650 | ESBNG (now EirGrid plc) | Tralee 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 03/09/2005 | Voltage collapse may occur during Transmission System disturbances or transmission faults during Summer maintenance 2002, 2003, 2004 and 2005. | Yes | No
651 | ESBNG (now EirGrid plc) | Trien 110kV station | Transmission | CC | 8.3.2 | V1.0 | Until 31/12/2008 | Voltage collapse may occur during Transmission System disturbances or following transmission faults during Summer 2006, 2007, 2008 and 2009. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
655 | ESBNG (now EirGrid plc) | Monread 110kV Station | Transmission | CC | 8.3.2 | V1.0 | Until 30/01/2006 | During Transmission System disturbances or following transmission faults, the voltage may fall to 93.5 kV during Winter 2004, 96.8 kV during Winter 2005 and 94.6 kV during Winter 2006. | Yes | No
720 | Airtricity | King's Mountain 1 | Wind | CC | 7.3.1.1 (g) | V1.0 | Indefinite* | Wind farm operates with a reactive power capability of 0.9 lagging (i.e. producing reactive power) to 0.975 leading (i.e. absorbing reactive power) at maximum continuous rating at the transmission connection point over the voltage range as specified in clause CC.8.3.2 of the Grid Code
766 | Hibernian Wind Power | Mountain Lodge 2 | Wind | CC | 7.3.1.1 (c) | V1.1 | Indefinite* | Wind turbine can operate in the range 47.0Hz to 47.5Hz. However, if the turbine rotor is at maximum speed and experiences a gust of wind, while operating in the range 47.0Hz to 47.5Hz, the turbine will be forced to disconnect.
779 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat | Wind | CC | 12.2 | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
780 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat | Wind | CC | 7.2.5.1 | V1.1 | Indefinite* | On-load tap-changing (OLTC) transformer will be provided at the main substation, instead of individual OLTC transformers at each generator. | Yes | No
781 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat | Wind | CC | 7.3.1.1 (g), 7.3.6.1, 7.3.6.2, 7.3.6.3, 7.3.6.4 | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
782 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat | Wind | CC | 7.3.1.1 (h) | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
783 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat | Wind | CC | 7.3.1.1 (l) | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
784 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat | Wind | CC | 7.3.1.1 (u) | V1.1 | Indefinite* | WTGs cannot provide guaranteed operating reserve levels | Yes | No
785 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat | Wind | CC OC4 | CC7.3.1.2 & 7.3.7 OC4 - 3.4 & 3.5 | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
786 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat | Wind | CC | 7.3.8 | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
787 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat | Wind | OC7 | 2.4.2.2, 2.4.2.3 & 2.5.5 | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code.
788 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat | Wind | SDC1 | All | V1.1 | Indefinite* | Facility can comply with all requirements as outlined in the proposed version of the Wind Grid Code as of the 25/03/2004. Meentycat Wind Farm will endeavour to comply with the final CER approved version of the Wind Grid Code. | Yes | No
789 | Meentycat Wind farm ROI Ltd. (Airtricity) | Meentycat | Wind | SDC2 | 6, 7, 8 | V1.1 | Indefinite* |  | Yes | No
813 | ESBPG | West Offaly Power | Thermal | CC | 7.3.1.1 (b) & (c ) | V1.1 | Service life of low pressure turbine blades | Generation unit will remain synchronised within the range 47.5 Hz to 51.5 Hz for a duration of 60 minutes. Generation unit will remain synchronised within the range 51.5 Hz to 52 Hz for a duration of 6 minutes (360 seconds), the period of 360 seconds will be reviewed by ESB National Grid following the first transmission system high frequency (>51.5 Hz) event and ESB National Grid reserve the right to alter this period of 360 seconds between the values of 60 seconds and 3600 seconds. Generation unit will remain synchronised within the range 47.0 Hz to 47.5 Hz for a duration of 20 seconds required each time the frequency is below 47.5 Hz.
816 | ESBNG (now EirGrid plc) | Ratrussan 110 kV station | Transmission | CC | 8.3.2 | V1.1 | Until 31/12/2008 | During Transmission System disturbances or following transmission faults, the voltage may fall to 93 kV during Summer 2006 and 88 kV during Summer 2007. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
817 | Booltiagh Wind Ltd. | Booltiagh 1 | Wind | WFPS1 | 5.1 | V1.1 incl. WFPS1 | Until 01/03/2006 | Wind Farm will comply with all requirements in WF1.5.1, with the exception of the requirement for “No additional WTG shall be started while the Transmission System Frequency is above 50.2Hz”. | Yes | No
818 | Booltiagh Wind Ltd. | Booltiagh 1 | Wind | WFPS1 | 5.2 | V1.1 incl. WFPS1 | Until 01/03/2006 | Booltiagh Wind Farm will postpone implementation of Frequency Control and the signals required to control it. | Yes | No
819 | Booltiagh Wind Ltd. | Booltiagh 1 | Wind | WFPS1 | 5.3 | V1.1 incl. WFPS1 | Until 01/03/2006 | Booltiagh Wind Farm will postpone implementation of ramp rate control as required by WF1.5.3, and its associated signals. | Yes | No
820 | Booltiagh Wind Ltd. | Booltiagh 1 | Wind | WFPS1 | 7.1 | V1.1 incl. WFPS1 | Until 01/03/2006 | Booltiagh Wind Farm will comply will supply WFPS1.7.1 Signals list #1 as required, but will postpone implementation of signals list #2, #3, #4 and #5. | Yes | No
821 | Booltiagh Wind Ltd. | Booltiagh 1 | Wind | WFPS1 | 7.2 | V1.1 incl. WFPS1 | Until 01/03/2006 | Booltiagh Wind Farm will comply with WFPS1.7.2.1 & WFPS1.7.2.5, but implementation of WFPS1.7.2.2, WFPS1.7.2.3 and WFPS1.7.2.4 will be postponed. | Yes | No
824 | Hibernian Wind Power | Derrybrien | Wind | WFPS1 | 1.4 | V1.2 | Indefinite* | WFPS1.4.1: The Fault Ride Through (FRT) capability curve for the WTGs with the installed control system is only marginally non-compliant with WFPS1.4.1. At 100% output, the wind farm as a whole is compliant. The FRT capability of the WTGs with the installed control system is essentially compliant with the requirements for conventional plant. WFPS1.4.2 (a): Plant is fully compliant. WFPS1.4.2 (b): If the WTG experiences voltage dips >60% below nominal that last for between 300 and 700 ms, under certain circumstances it could take up to 2 seconds after the voltage recovers before the turbine is back to 90% of available active power.
825 | Hibernian Wind Power | Derrybrien | Wind | WFPS1 | 5.2.2 | V1.2 | Indefinite* | Facility is marginally non-compliant. Derrybrien submitted a Power-Frequency Response Curve to ESBNG (now EirGrid).
826 | Hibernian Wind Power | Derrybrien | Wind | WFPS1 | 5.3 | V1.2 | Indefinite* | Wind farm is capable of adhering to a maximum ramp rate setting for start-up of the wind farm. Each WTG has a maximum ramp rate limit of ± 50kW/s during start-up. Wind farm does not have the capability to impose overall one-minute and ten-minute average ramp rate limitations.
827 | Hibernian Wind Power | Derrybrien | Wind | WFPS1 | 6.2.3 | V1.2 | Indefinite* | The slope of the Voltage Regulation System is capable of being set to any value between 1% and 5% and give full reactive power range for any active power output. The slope can also be set between 5% and 10%, however this will limit the reactive power range (lagging).
827 | Hibernian Wind Power | Derrybrien | Wind | WFPS1 | 6.2.4 | V1.2 | Until May 2006 | Wind farm requires 4 seconds to change from unity to a power factor of 0.98.
844 | ESBPG | West Offaly Power | Thermal | CC | 7.3.6.1 | V1.1 | Until end Summer 2006 | The generator can meet the full reactive power range if active power output is reduced to 134MW.
845 | SWS (Kilgarvan Wind Farm Ltd.) | Coomagearlahy 1 | Wind | WFPS1 | 4.2 (b) | V1.1 incl. WFPS1 | Indefinite* | Following a low voltage incident that is longer than 500ms and lower than 50% retained voltage, the wind farm may take up to 4 seconds to return to 90% active power output. This only occurs under certain other conditions, including wind speeds above 8 m/s, turbulence, and tower oscillation position.
846 | SWS (Kilgarvan Wind Farm Ltd.) | Coomagearlahy 1 | Wind | WFPS1 | 6.2.4 | V1.1 incl. WFPS1 | Until 30/04/2007 | Following a step change in voltage at the connection point, the wind farm power station will achieve 90% of its steady-state reactive power response within 5-20 seconds. | Yes | No
849 | ESBNG (now EirGrid plc) | Coomagearlahy 110kV Station | Transmission | CC | 8.3.2 | V1.2 | Until 01/03/2007 | During Transmission System disturbances or following transmission faults, the voltage may fall to 83 kV during Summer 2006. | Yes | No | Derogation no longer required
850 | ESBNG (now EirGrid plc) | Kilkenny 110kV Station | Transmission | CC | 8.3.2 | V1.2 | Until 31/12/2008 | During Transmission System disturbances or following transmission faults, the voltage may fall to 87 kV during Winter 2008. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
851 | ESBNG (now EirGrid plc) | Kilmurry 110kV Station | Transmission | CC | 8.3.2 | V1.2 | Until 30/09/2008 | During Transmission System disturbances or following transmission faults, the voltage may fall to 94 kv during Winter 2008. | Yes | No
852 | ESBNG (now EirGrid plc) | Tralee 110kV Station | Transmission | CC | 8.3.2 | V1.2 | Until 31/12/2008 | During Summer 2006, voltage collapse may occur during Transmission System disturbances or following transmission faults. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
853 | ESBNG (now EirGrid plc) | Clonkeen 110kV Station | Transmission | CC | 8.3.2 | V1.2 | Until 01/03/2007 | During Summer 2006, voltage collapse may occur during Transmission System disturbances or following transmission faults. | Yes | No | Derogation no longer required
854 | Tynagh Energy Ltd. | Tynagh CCGT | Thermal | CC | 7.3.2 | V1.1 | Indefinite* | Tynagh CCGT is capable of tripping to house load while running on natural gas. However, the plant is incapable of tripping to house load and sustain operation while running on liquid fuel (secondary fuel).
855 | Aughinish Alumina Ltd. | Aughinish CHP Plant | CHP | CC | 7.3.1.1 (k) | V1.1 | Time limited until ESBNG modifies the Grid Code for CHP plant | Plant has a minimum load capability of 50% of its registered capacity, not the required 35% of registered capacity as required for generator units other than CCGTs.
856 | Glanlee Windfarm | Glanlee Windfarm | Wind | WFPS1 | 6.3 |  | Until 31 October 2007 | Power Factor is 0.98 exporting to 0.95 importing until end Oct 2007 when wind farm will comply. | Yes | No
857 | Glanlee Windfarm | Glanlee Windfarm | Wind | WFPS1 | 6.2.4 |  | Until 31 October 2007 | The wind farm can only provide 90% in 4-20 seconds until additional Reactive Power Compensation is installed by October 2007 | Yes | No
858 | Glanlee Windfarm | Glanlee Windfarm | Wind | WFPS1 | 1.4.2 (b) |  | Lifetime of the project | For faults longer than 0.5 seconds and deeper than 50% voltage dip, and with wind speeds that are experiend for only 36% of the year, the turbines shall take up to 4 seconds to provide 90 % Active Power repsonse.
859 | Glanlee Windfarm | Glanlee Windfarm | Wind | WFPS1 | 1.4.2 |  | Until 31 October 2007 | The full FRT capability wil not be available until additional Reactive Power Compensation is installed by October 2007 | Yes | No
870 | EirGrid | Newbridge 110kV station | Transmission | CC | 8.3.2 | v1.2 | Until 31/12/2008 | Voltage may drop to 97 kV in Winter 2007 |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
871 | EirGrid | Monread 110kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 31/12/2008 | Voltage may drop to 97 kV in Winter 2007 and 98 kV in Winter 2008. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
872 | EirGrid | Ballywater 110 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 96 kV in Winter 2007 and the voltage may drop to 89 kV or there may be Voltage collapse in Winter 2008. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
873 | EirGrid | Crane 110 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 96 kV in Winter 2007 and the voltage may drop to 89 kV or there may be Voltage collapse in Winter 2008. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
874 | EirGrid | Wexford 110 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 92 kV in Winter 2007 and the voltage may drop to 93 kV or there may be Voltage collapse in Winter 2008. |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
875 | EirGrid | Moneypoint 110 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 98 kV in Summer 2009 |  |  | Derogation no longer required
876 | EirGrid | Ardnacrusha 110 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 98 kV in Summer 2009 |  |  | Derogation no longer required
877 | EirGrid | Drumline 110kV station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 98 kV in Summer 2009 |  |  | Derogation no longer required
878 | EirGrid | Kellis 220 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 194 kV in Winter 2008 |  |  | Derogation no longer required
879 | EirGrid | Kilteel 110 kV Station | Transmission | CC | 8.3.2 | v1.2 | Until 30th September 2009 | Voltage may drop to 96 kV in Winter 2009 |  |  | Update sent to CER 01/10/2007. Approved 21/02/2008.
507 | ESBPG | Great Island 1 | Thermal | CC | 7.3.1.1 (k) | v1.2 | Lifetime of plant | Minimum load is 44% of Registered Capacity
508 | ESBPG GI2 | Great Island 2 | Thermal | CC | 7.3.1.1 (k) | v1.2 | Lifetime of plant | Minimum load is 44% of Registered Capacity
512 | ESBPG MP1 | Moneypoint 1 | Thermal | CC | 7.3.1.1 (k) | v3.0 | Until 31/05/2009 | Minimum load is 41% of Registered Capacity | Yes |  | Originally requested and approved until end of Dec '07 and subsequently reapplied for and approved until completion of MERP.
513 | ESBPG MP2 | Moneypoint 2 | Thermal | CC | 7.3.1.1 (k) | v3.0 | Until 30/04/2009 | Minimum load is 41% of Registered Capacity | Yes |  | Originally requested and approved until end of Dec '07 and subsequently reapplied for and approved until completion of MERP.
514 | ESBPG MP3 | Moneypoint 3 | Thermal | CC | 7.3.1.1 (k) | v3.0 | Until 31/05/2009 | Minimum load is 41% of Registered Capacity | Yes |  | Originally requested and approved until end of Dec '07 and subsequently reapplied for and approved until completion of MERP.
585 | ESBPG MP1 | Moneypoint 1 | Thermal | CC | 7.3.1.1 (t) | v1.2 | Earlier of 31/12/07 or date which testing is complete. | In hot condition time from synch to min load is 50 minutes | Yes | No | Extension until July 2008 has been sought
586 | ESBPG MP2 | Moneypoint 2 | Thermal | CC | 7.3.1.1 (t) | v1.2 | Earlier of 31/12/07 or date which testing is complete. | In hot condition time from synch to min load is 50 minutes | Yes | No | Extension until Dec 2008 has been sought
587 | ESBPG MP3 | Moneypoint 3 | Thermal | CC | 7.3.1.1 (t) | v1.2 | Earlier of 31/12/07 or date which testing is complete. | In hot condition time from synch to min load is 50 minutes | Yes | No | Extension until July 2008 has been sought
716 | ESBPG MRT | Marina | Thermal | CC | 7.3.5 |  | Lifetime of plant | The generating unit GT does not have a unit transformer connected between the generating unit circuit breaker and the Generator Transformer LV terminals, however the current configuration achieves almost the equivalent result.
483 | ESBPG PB3 | Poolbeg 3 | Thermal | CC | 7.3.1.1 (h) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | Will not remain synchronised during all voltage dips specified in CC 7.3.1.1 h
527 | ESBPG PB3 | Poolbeg 3 | Thermal | CC | 7.3.1.1 (l) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | Ramp up capability is < 2% reg capacity per minute from min load to reg capacity. 1.4% from 130MW to 242MW, otherwise less.
542 | ESBPG PB3 | Poolbeg 3 | Thermal | CC | 7.3.1.1 (n) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | Min uptime is 5.5 hours
558 | ESBPG PB3 | Poolbeg 3 | Thermal | CC | 7.3.1.1 (p) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | Has a forbidden zone of 17%
580 | ESBPG PB3 | Poolbeg 3 | Thermal | CC | 7.3.1.1 (s) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | Cold start is 3.5 hours. Hot start is 18 hours.
588 | ESBPG PB3 | Poolbeg 3 | Thermal | CC | 7.3.1.1 (t) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | Time from synch to min load > allowed
698 | ESBPG PB3 | Poolbeg 3 | Thermal | CC | 7.3.4 | V2.0 | Earlier of 27/05/08 or overhaul is approved.
751 | ESBPG PB3 | Poolbeg 3 | Thermal | CC | 7.3.1.1 (u) (iii) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | TOR1 is 7.41% Registered Capacity
760 | ESBPG PB3 | Poolbeg 3 | Thermal | CC | 7.3.1.1 (u) (iv) | V2.0 | Earlier of 27/05/08 or overhaul is approved. | TOR2 is 7.41% of Registered Capacity
912 | EirGrid | Banoge 110 kV Station | Transmission | CC | 8.3.2 |  | Until 30th September 2009 | Voltage may drop to 87 kV or there may be Voltage collapse in Winter 2008. |  |  | Approved 21/02/2008
863 | Viridian Power Ltd | HP2 | CC | CC | 7.3.1.1 (b) | v2.0 | Indefinite | The station is unable to remain in operation, exporting power to the grid, with system frequency aboce 51.5Hz for sixty (60) minutes. Station can stay operated in this frequency range for 45 seconds. | Generator can remain synchronised down to 47.5Hz. Generator breaker will open on rising frequency at 51.5Hz. Generator can operate continuously betweent the range 47.5Hz and 51.5Hz but is limited to 20 secs between 51.5Hz and 52Hz. Once a cumulatinve dura |  | Granted subject to three conditions
864 | Viridian Power Ltd | HP2 | 7.3.1.1 (c ) | CC | 7.3.1.1 (c ) | v2.0 | Indefinite | Station is unable to remain synchronised to the Transmission System at Transmission System Frequencies within the range 47.0Hz to 47.5Hz for a duration of 20 seconds required each time the Frequency is below 47.5Hz. Station can stay operated in this frequency range for 45 seconds. |  |  | Granted subject to three conditions
865 | Viridian Power Ltd | HP2 | 7.3.1.1 (l) | CC | 7.3.1.1 (l) | v2.0 | Indefinite | Ramp up capability is greater than 1.5% of Registered Capacity per minute between 50% to 95% RC when the Unit is in the Normal Dispatch Condition, but 0.5% of Registered Capacity per minute in the upper load range between 95-100% RC to avoid overshoot.
888 | Viridian Power Ltd | HP2 | 7.3.1.1 (l) | CC | 7.3.1.1 (l) | v2.0 | Indefinite | Backup fuel oil firing: Ramp up capability is greater than 1.5% of Registered Capacity per minute between 50% to 95% RC when the unit is in the Normal Dispatch Condition, but 0.5% of RC per minute in the upper load range between 95%-100% RC.
889 | Tynagh Energy Ltd. | Tynagh |  | CC | 7.3.1.1(k) | v2.0 | 2008-08-31 | The minimum load level is currently at 214 MW exported which is 55.7% of registered capacity. |  |  | Time-limited derogation until 31/08/2008
930 | ESB PG MP1 | Moneypoint 1 |  | CC | 7.3.1.1 (t) (i) | v3.1 | Earlier of 31/07/2008 or the test complete date | Cold loading up rates: From Block load of 8.62 to Min Load of 136MW at a rate of 1.04 MW/Min up to 102.08MW and 1.56 MW/Min up to 136 MW takes 111.61 Minutes. Then there are two soak times for cold start up - 90 minutes at 19 MW and 30 minutes at 102.08 MW. This gives a total time of 231.61 Minutes |  |  | Time limited 31/07/2008 or the test complete date
931 | ESB PG MP2 | Moneypoint 2 |  | CC | 7.3.1.1 (t) (i) | v3.2 | Earlier of 31/12/2008 or the test complete date | Cold loading up rates: From Block load of 8.62 to Min Load of 136MW at a rate of 1.04 MW/Min up to 102.08MW and 1.56 MW/Min up to 136 MW takes 111.61 Minutes. Then there are two soak times for cold start up - 90 minutes at 19 MW and 30 minutes at 102.08 MW. This gives a total time of 231.61 Minutes |  |  | Time limited 31/12/2008 or the test complete date
932 | ESB PG MP3 | Moneypoint Unit 3 |  | CC | 7.3.1.1 (t) (i) | v3.3 | Earlier of 31/07/2008 or the test complete date | Cold loading up rates: From Block load of 8.62 to Min Load of 136MW at a rate of 1.04 MW/Min up to 102.08MW and 1.56 MW/Min up to 136 MW takes 111.61 Minutes. Then there are two soak times for cold start up - 90 minutes at 19 MW and 30 minutes at 102.08 MW. This gives a total time of 231.61 Minutes |  |  | Time limited 31/07/2008 or the test complete date
901 | ESB PG | North Wall CC4 |  | CC | 7.3.1.1 (k) | v2.0 | Indefinite | The min load for North Wall CC is 87.32MWe - a % capacity of 54%
956 | Green Energy Company Ltd | Boggeragh 1 |  | WFPS1 | 4.2(b) | v3.1 | 15 Years | For certain combinations of voltage dip/ duration and the shape of voltage recovery to pre-fault level, the turbines cannot return to their Maximum Active Available Power within 1 second after the Transmission voltage is re-established. Dependant on the unique situations (wind load, turbulence and tower position) the some turbines in a windfarm will return to their available power only within 1-4 seconds.
957 | Green Energy Company Ltd | Boggeragh 1 |  | WFPS1 | 6.3 | v3.1 | 1st April 2010 to 1st April 2011 | The WTG’s do not have the full power factor range required in the grid code and cannot meet the grid code requirement without the provision of reactive power compensation equipment.
958 | Green Energy Company Ltd | Boggeragh 1 |  | WFPS1 | 6.2.4 | v3.1 | 1st April 2010 to 1st April 2011 | The V90-3 MW turbines are not capable of providing 90% of it’s steady state reactive power response within 1 second. The turbines are equipped with a Voltage control feature but it requires between 4 to 20 seconds to reach 90% of requested kVAR response.
889 | Tynagh Energy Limited | Tynagh |  | CC | 7.3.1.1 | v3.0 | 31st January 2009 | Tynagh Energy Limited (TEL) seeks an extension of its expired derogation (dated 18th April 2008) as currently the plant is unable to run at 50% of its registered capacity in normal operating mode. The minimum load level is currently at 205 MW exported which is 53.4% of registered capacity.
955 | SWS (Kilgarvan Wind Farm Ltd.) | Coomagearlahy 3 |  | WFPS1 | 6.2.4 | v3.1 | March 2009 to December 2009 | The grid code requires that the speed of response of the Voltage Regulation System (AVR) shall be such that, following a step change in Voltage at the Connection Point the Controllable WFPS shall achieve 90 % of its steady-state Reactive Power response within 1 second. The response may require a transition from maximum Mvar production to maximum Mvar absorption or viceversa. In fact Nordex N90 2500kW turbines (more specifically their CWE SCADA control system) can only achieve 90% of its steady state reactive power response within a period of around 20s.
964 | Gort Wind Farms Ltd | Derrybrien |  | WFPS1 | 6.2.2 | v3.2 | Permanent | The required speed of response of the Set-point Voltage Controller within 20 seconds of a change in Set – Point from EirGrid is not achievable in all circumstances. The attached document details the operation of the voltage control system response.
500 | ESB PG | Ardnacrusha |  | CC | 7.3.1.1(k) | v3.4 | The derogation will apply until the end of December 2015 or until the next refurbishment, whichever is earlier. | Minimum Load Capability is 12 MW.
501 | ESB PG | Ardnacrusha |  | CC | 7.3.1.1(k) | v3.4 | The derogation will apply until the end of December 2015 or until the next refurbishment, whichever is earlier. | Minimum Load Capability is 12 MW.
502 | ESB PG | Ardnacrusha |  | CC | 7.3.1.1(k) | v3.4 | The derogation will apply until the end of December 2015 or until the next refurbishment, whichever is earlier. | Minimum Load Capability is 12 MW.
892 | ESB PG | Ardnacrusha |  | CC | 7.3.1.1(k) | v3.4 | The derogation will apply until the end of December 2015 or until the next refurbishment, whichever is earlier. | Minimum Load Capability is 12 MW.
991 | Endesa | Tarbert 3 |  | CC | 7.3.1.1 (u)(ii) | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | The unit is unable to provide SOR at loads in excess of 240MW (generated).
992 | Endesa | Tarbert 3 |  | CC | 7.3.1.1 (u)(iii) | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | The unit is unable to provide TOR1 at loads in excess of 240MW (generated).
993 | Endesa | Tarbert 3 |  | CC | 7.3.1.1 (u)(iv) | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | The unit is unable to provide TOR2 at loads in excess of 240MW (generated).
975 | Endesa | Tarbert 1 |  | CC | 7.3.6.1 | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | These units are unable to meet the reactive power limits that are set out in the Grid Code of operating at 0.93 pf leading to 0.85 pf lagging at Registered Capacity.
976 | Endesa | Tarbert 2 |  | CC | 7.3.6.1 | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | These units are unable to meet the reactive power limits that are set out in the Grid Code of operating at 0.93 pf leading to 0.85 pf lagging at Registered Capacity.
973 | Endesa | Great Island 1 |  | CC | 7.3.6.1 | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | The unit is unable to provide Reactive Power (leading) capability.
974 | Endesa | Great Island 2 |  | CC | 7.3.6.1 | v3.4 | Shall apply until the end of Dec 2013 or until the next refurbishment or until the units are retired, whichever is earlier. | The unit is unable to provide Reactive Power (leading) capability.
986 | Endesa | Great Island 1 |  | CC | 7.3.1.1(u)(iii) | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | TOR1 capability is limited to 3 MW.
987 | Endesa | Great Island 1 |  | CC | 7.3.1.1(u)(iv) | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | TOR2 capability is limited to 3 MW.
988 | Endesa | Great Island 2 |  | CC | 7.3.1.1(u)(iii) | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | TOR1 capability is limited to 3 MW.
989 | Endesa | Great Island 2 |  | CC | 7.3.1.1(u)(iv) | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | TOR2 capability is limited to 3 MW.
990 | Endesa | Tarbert 3 |  | CC | 7.3.1.1(u)(i) | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | The unit is unable to provide POR at loads in excess of 240 MW (generated).
975 | Endesa | Tarbert 1 |  | CC | 7.3.6.1 | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | Reactive Power Capability is limited to 10 MVAr leading and 25 MVAr lagging.
976 | Endesa | Tarbert 2 |  | CC | 7.3.6.1 | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | Reactive Power Capability is limited to 10 MVAr leading and 25 MVAr lagging.
977 | Endesa | Tarbert 3 |  | CC | 7.3.6.1 | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | Reactive Power Capability is limited to 45 MVAr leading and 110 MVAr lagging.
978 | Endesa | Tarbert 4 |  | CC | 7.3.6.1 | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | Reactive Power Capability is limited to 45 MVAr leading and 110 MVAr lagging.
973 | Endesa | Great Island 1 |  | CC | 7.3.6.1 | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | No leading reactive power is available on this unit.
974 | Endesa | Great Island 2 |  | CC | 7.3.6.1 | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired, whichever is earlier. | No leading reactive power is available on this unit.
511 | ESBPG | Liffey 4 |  | CC | 7.3.1.1(k) | v3.0 | The derogation will apply until Dec 2015 or the next refurbishment or until the unit is retired, whichever is earlier. | Capable of providing Minimum Load of 3.99 MW
895 | ESBPG | Lee 3 |  | CC | 7.3.1.1(k) | v3.0 | The derogation will apply until Dec 2015 or the next refurbishment or until the unit is retired, whichever is earlier. | Capable of providing Minimum Load of 3 MW
985 | ESBPG | North Wall 4 |  | CC | 7.3.1.1(t)(i) | v3.4 | The derogation will apply until the earlier of: a. 10th Feb 2013 or b. the date on which the unit becomes an open cycle gas turbine | NW4 is capable of synchronising to minimum load in a time of 56 minutes when in a hot state
1013-1015 | Endesa | Tarbert 3 |  | CC | 7.3.1.1(u)(ii) 7.3.1.1(u)(iii) 7.3.1.1(u)(iv) | v3.4 | The derogation will apply until the end of Dec 2013 or until the next refurbishment or until the unit is retired or until the implementation of a new AS Agreement, whichever is earlier. | Tarbert Unit 3 is capable of providing 3 MW of SOR, 3 MW of TOR1 and 8 MW of TOR2
1000 | ESBPG | Aghada 2 |  | CC | 7.3.1.1(h) | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | AD2 will remain synchronised during and following Voltage dips at the HV terminals of the Generator Transformer of 95% of nominal Voltage (5% retained) for duration of 0.15s
1001 | ESBPG | Aghada 2 |  | CC | 7.3.1.1(g) | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | AD2 can absorb Reactive Power at Registered Capacity up to a limit of -150MVAR (0.944pf) leading.
1002 | ESBPG | Aghada 2 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | AD2 can absorb Reactive Power at Registered Capacity up to a limit of -150MVAR (0.944pf) leading.
1011 | Cushaling Power Ltd | Edenderry 3 & 5 |  | CC | 7.3.1.1(h) | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Cannot meet the min Fault Ride Through durations in certain dispatch scenarios.
1018-1021 | Endesa Ireland Ltd | Rhode 1, Rhode 2, Tawnaghmore 1, Tawnaghmore 3 |  | CC | 7.3.1.1(h) | v3.4 | Granted until the CER make a decision on DAID 1085 | The Units are unable to ride through faults as per CC.7.3.1.1(h) under the full operating capabilities of the Generation Unit at the Connection Point.
969 | SSE Renewables | Kings Mountain Extension |  | WFPS1 | 6.1 | v3.4 | The derogation shall apply until the installation and full compliance of a suitably sized STATCOM with the Grid Code requirements or 11th April 2012, whichever is earlier. | 90% of the steady state reactive power response within 5 secs
970 | SSE Renewables | Kings Mountain Extension |  | WFPS1 | 6.3 | v3.4 | The derogation shall apply until the installation and full compliance of a suitably sized STATCOM with the Grid Code requirements or 11th April 2012, whichever is earlier. | 90% of the steady state reactive power response within 5 secs
971 | SSE Renewables | Kings Mountain Extension |  | WFPS1 | 6.2.4 | v3.4 | The derogation shall apply until the installation and full compliance of a suitably sized STATCOM with the Grid Code requirements or 11th April 2012, whichever is earlier. | 90% of the steady state reactive power response within 5 secs
979 | Endesa | Rhode 1 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Currently providing 7 Mvar Reactive Power Leading.
980 | Endesa | Rhode 2 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Currently providing 7 Mvar Reactive Power Leading.
981 | Endesa | Tawnaghmore 1 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Currently providing 7 Mvar Reactive Power Leading.
982 | Endesa | Tawnaghmore 3 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Currently providing 7 Mvar Reactive Power Leading.
1016 | Bord Gáis Energy | Whitegate |  | CC | 7.3.1.1(h) | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | At certain leading Reactive Power positions the critical clearance time is less than 200ms.
1045 | Cushaling Power Ltd | Edenderry 3 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Currently not providing Reactive Power Leading.
1046 | Cushaling Power Ltd | Edenderry Unit 5 |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Currently not providing Reactive Power Leading.
435 | Synergen | Dublin Bay |  | CC | 7.3.6.1 | v3.4 | Valid for 60 working days following the CER's approval of any Grid Code Modifications resulting from the outcome of the review of the FRT Working Group. | Can provide up to 100 Mvar Reactive Power Leading.
512-514 | ESBPG | Monepoint 1, Moneypoint 2, Moneypoint 3 |  | CC | 7.3.1.1(k) | v1.0 | Valid from 01/02/2010 to 31/03/2010 | Min Load is 41%
880-883 | ESBPG | Turlough Hill 1, Turlough Hill 2, Turlough Hill 3, Turlough Hill 4 |  | CC | 7.3.1.1(p) | v1.2 | Derogation applies until the earlier of the lifetime of the unit or the completion of a major refurbishment | Forbidden Zone of 30 MW (from 10 MW to 40 MW) for all four units.
889 | Tynagh | Tynagh |  | CC | 7.3.1.1(k) | v3.2 | Valid from 31/3/2010 to 30/9/2010 | Min Load is 50.5%
435 | Synergen | Dublin Bay |  | CC | 7.3.6.1 | v3.5 | Valid until 17/02/2012 | Leading Reactive Power is 100 Mvar
1045 | Cushaling Power Ltd | Edenderry 3 |  | CC | 7.3.6.1 | v3.5 | Valid until the derogation process is complete (FRT related) | Leading Reactive Power is 0 Mvar
1046 | Cushaling Power Ltd | Edenderry 5 |  | CC | 7.3.6.1 | v3.5 | Valid until the derogation process is complete (FRT related) | Leading Reactive Power is 0 Mvar
979 | Endesa | Rhode 1 |  | CC | 7.3.6.1 | v3.5 | Valid until a decision is reached on DAID 1084 | Currently providing 7 Mvar Reactive Power Leading.
980 | Endesa | Rhode 2 |  | CC | 7.3.6.1 | v3.5 | Valid until a decision is reached on DAID 1084 | Currently providing 7 Mvar Reactive Power Leading.
981 | Endesa | Tawnaghmore 1 |  | CC | 7.3.6.1 | v3.5 | Valid until a decision is reached on DAID 1084 | Currently providing 7 Mvar Reactive Power Leading.
982 | Endesa | Tawnaghmore 3 |  | CC | 7.3.6.1 | v3.5 | Valid until a decision is reached on DAID 1084 | Currently providing 7 Mvar Reactive Power Leading.
1045 | Cushaling Power Ltd | Edenderry 3 |  | CC | 7.3.6.1 | v3.5 | Valid until the derogation 20 August 2012 | Leading Reactive Power is 0 Mvar
1046 | Cushaling Power Ltd | Edenderry 5 |  | CC | 7.3.6.1 | v3.5 | Valid until the derogation 20 August 2012 | Leading Reactive Power is 0 Mvar
1082 & 1083 | Cushaling Power Ltd | Edenderry 3 & 5 |  | CC | 7.3.1.1(h) & 7.3.6.1 | v3.5 | Granted until the earlier of a. 1st Jan 2022; b. notification by EirGrid; after 1 Jan 2017, that the agreement in place is no longer appropriate in the content of system security; c. lifetime of the units; d. the completion of a major refurbishment of the units | Leading Reactive Power is 23 Mvar
1049 | Viridian Power Limited | Huntstown 2 |  | CC | 7.3.1.1(w) | v3.5 | Effective from 15 March 2011 until the earlier of: The lifetime of the plant or the completion of a major refurbishment of the unit. | Operate on Secondary Fuel at no less than 70% of Primary Fuel Registered Capacity.
1050 | Tynagh Energy Ltd. | Tynagh |  | CC | 7.3.1.1(w) | v3.5 | Effective from the 15 March 2011 until the earlier of 30 September 2013 or the completion of a major refurbishment of the unit. | 30 MW for the Secondary Fuel Switchover Output
1052 | ESB PG | Aghada 1 |  | PC.A4.3; CC.7.3.1; CC.7.3.1.1(w); CC.7.3.1.1(x);CC.7.3.1.2; OC10.2.2(e); OC10.2.2(f); OC10.5.5(d); OC10.5.5(e); Definitions: Off-Site Storage Location; Secondary Fuel Switchover Output; Primary Fuel Switchover Output |  | v3.5 | Effective from 15 March 2011 until the earlier of: The lifetime of the plant or the completion of a major refurbishment of the unit. | Derogated from all Secondary Fuel requirements in Grid Code.
1055 | Rusal Aughinish Ltd | Sealrock 3 |  | CC | 7.3.1.1(w) | v3.5 | Effective from the 15 March 2011 until the earlier of 30 September 2013 or the completion of a major refurbishment of either unit. | 4 MW for the Secondary Fuel Switchover Output
1056 | Rusal Aughinish Ltd | Sealrock 4 |  | CC | 7.3.1.1(w) | v3.5 | Effective from the 15 March 2011 until the earlier of 30 September 2013 or the completion of a major refurbishment of either unit. | 4 MW for the Secondary Fuel Switchover Output
1060 | Dublin Bay Power | Dublin Bay |  | CC | 7.3.1.1(w) | v3.5 | A derogation is granted effective from 15 March 2011 until the earlier of: 1st Jan 2015 or the completion of a major refurbishment of the unit.Subject to the submission to EirGrid of an interim report by 30/09/2013 and a proposal to achieve compliance before 31st Dec 2014. | 25 MW for the Primary Fuel Switchover Output and 25 MW for the Secondary Fuel Switchover Output
1086 | Bord Gáis Energy | Whitegate |  | CC | 7.3.1.1(w) | v3.5 | Effective from the 15 March 2011 until the earlier of 30 September 2013 or the completion of a major refurbishment of either unit. | 30 MW for the Secondary Fuel Switchover Output.
1044 | Bord Gáis Energy | Whitegate |  | CC | 7.3.1.1(l) | v4.0 | Effective from 20/10/2010 until the earlier of the lifetime of the unit or completion of a major refurbishment of the unit. | Ramp up capability of 0.6% Registered Capacity when the Unit is operating in the load range 96.3 – 100 % and being fired on Fuel Oil
1096 | ESB PG | Aghada Open Cycle GT |  | CC | 7.3.1.1(w) | v4.0 | Effective from 05/09/2012 until 31/03/2013 | Cannot carry out an online fuel changeover from Primary Fuel to Secondary Fuel at Primary Fuel Switchover Output and cannot carry out an online fuel changeover from Secondary fuel to Primary Fuel at Secondary Fuel Switchover Output.
1070 - 1081 | ESB PG | Moneypoint 1, 2 & 3 |  | CC | 7.3.6.1 | v4.0 | Effective from 21/11/2011 until the earlier of 01/01/2023, the replacement of any or all the Generator Transformers, the lifetime of any of the units or the completion of a major refurbishment of the unit. | The Leading Reactive Power capability of each unit is 112 MVAr.
1089 & 1090 | Endesa Ireland | Great Island 1 & 2 |  | CC | 7.3.1.1(k) | v4.0 | Effective from 01/06/2009 until the earlier of 31/12/2014 or the completion of a major refurbishment of either unit. | The Minimum Load capability of each unit is 23.7 MW.
1051 | ESB PG | Aghada 2 |  | CC | 7.3.1.1(w) | v4.0 | Subject to the submission to EirGrid of an interim report by 31 Aug 2014 and a proposal to achieve compliance before 30 Nov 2015, the CER grants a temporary derogation until the earlier of 1 Dec 2015 or the completion of a major refurbishment of the plant. | The Primary Fuel Switchover Output capability is 25 MW and the Secondary Fuel Switchover Output capability is 25 MW.
1066-1069 | ESB PG | Aghada 2 |  | CC | 7.3.1.1(g), CC.7.3.6.4, CC.7.3.6.1, CC.7.3.6.2 | v4.0 | This derogation will not indemnify AD2 from any GPI that may be applied in respect of the relevant Grid Code clauses. The derogation is effective from 19 Oct 2011 until the earlier of 1 Jan 2017 or the completion of a major refurbishment of the unit. | The maximum Lagging Reactive Power capabilty is 270 MVAr.
2068 | Tynagh Energy Ltd. | Tynagh CCGT |  | CC | 7.3.1.1(w) | v4.0 | Effective from 6/9/2013 until the earlier of 6 months from the date of the CER's decision on Secondary Fuel; 6th Sept 2018; or the completion of a major refurbishment of the unit. | The level at which the secondary to primary transfer can take place is circa 30 MW.
2042 | SSE Renewables | Bindoo |  | WFPS1 | 1.6.2.2(a); 1.6.2.2(b) | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2043 | SSE Renewables | Bindoo |  | WFPS1 | 1.6.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2044 | SSE Renewables | Bindoo |  | WFPS1 | WFPS1.5.3.1; WFPS1.5.3.2; WFPS1.5.3.3; WFPS1.5.3.4; WFPS1.5.3.5; WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5; WFPS1.7.2.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2045 | SSE Renewables | Bindoo |  | WFPS1 | WFPS1.4.2 ( c) | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2046 | SSE Renewables | Coomacheo |  | WFPS1 | WFPS1.6.2.2(a); WFPS1.6.2.2(b) | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2047 | SSE Renewables | Coomacheo |  | WFPS1 | WFPS1.4.1; WFPS1.4.2 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2048 | SSE Renewables | Coomacheo |  | WFPS1 | WFPS1.6.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2049 | SSE Renewables | Coomacheo |  | WFPS1 | WFPS1.5.3.1; WFPS1.5.3.2; WFPS1.5.3.3; WFPS1.5.3.4; WFPS1.5.3.5;WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5; WFPS1.7.2.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2050 | SSE Renewables | Dromada |  | WFPS1 | WFPS1.6.2.2(a); WFPS1.6.2.2(b) | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2051 | SSE Renewables | Dromada |  | WFPS1 | WFPS1.5.3.1; WFPS1.5.3.2; WFPS1.5.3.3; WFPS1.5.3.4; WFPS1.5.3.5;WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5; WFPS1.7.2.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2052 | SSE Renewables | Dromada |  | WFPS1 | WFPS1.4.2 (c) | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2053 | SSE Renewables | Dromada |  | WFPS1 | WFPS1.6.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2054 | SSE Renewables | Kingsmountain 2 |  | WFPS1 | WFPS1.6.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2055 | SSE Renewables | Kingsmountain 2 |  | WFPS1 | WFPS1.5.2.1; WFPS1.5.3.1; WFPS1.5.3.2; WFPS1.5.3.3; WFPS1.5.3.4; WFPS1.5.3.5; WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2056 | SSE Renewables | Kingsmountain 2 |  | WFPS1 | WFPS1.4.1; WFPS1.4.2 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2057 | SSE Renewables | Meentycat |  | WFPS1 | WFPS1.6.2.2(a); WFPSI1.6.2.2(b) | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2058 | SSE Renewables | Meentycat |  | WFPS1 | WFPS1.5.3.1; WFPS1.5.3.2; WFPS1.5.3.3; WFPS1.5.3.4; WFPS1.5.3.5; WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2059 | SSE Renewables | Meentycat |  | WFPS1 | WFPS1.4.1; WFPS1.4.2 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2060 | SSE Renewables | Meentycat |  | WFPS1 | WFPS1.6.3 | v5.0 | Effective from 15th August 2013 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2065 | Brookfield | Lisheen 1 & 2 |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that a remedy has been implemented and tested or 31st December 2018. Withdrawn 05/02/2019 | MPID 212
2066 | Brookfield | Lisheen 1 |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that a remedy has been implemented and tested or 31st December 2018. Withdrawn 05/02/2019 | MPID 227
2067 | Brookfield | Lisheen 2 |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2 | v5.0 | Effective from 21st March 2014 until the earlier of the date that a remedy has been implemented and tested or 31st December 2018. | MPID 227
2092 | Midas Energy Co | Glanlee Windfarm |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 30th September 2013 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2093 | Midas Energy Co | Glanlee Windfarm |  | WFPS1 | WFPS1.5.2.1, WFPS1.5.3, WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 30th September 2013 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2012 | ESB Renewables | Mountain Lodge |  | WFPS1 | WFPS1.5.2.1 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227 (DMOL)
2013 | ESB Renewables | Garvagh 1 |  | WFPS1 | WFPS1.5.2.1 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227 (DMOL)
2014 | ESB Renewables | Garvagh 2 |  | WFPS1 | WFPS1.5.2.1 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227 (DMOL)
2015 | ESB Renewables | Derrybrien |  | WFPS1 | WFPS1.5.2.1 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227 (DMOL)
2061 | ESB Renewables | Garvagh 1 |  | WFPS1 | WFPS1.4.1, WFPS1.4.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2062 | ESB Renewables | Garvagh 1 |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2063 | ESB Renewables | Garvagh 1 |  | WFPS1 | WFPS1.6.3.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2076 | ESB Renewables | Garvagh 1 |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2, WFPS1.5.3.3, WFPS1.5.4.1, WFPS1.5.4.2, WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2077 | ESB Renewables | Derrybrien |  | WFPS1 | WFPS1.4.1, WFPS1.4.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2078 | ESB Renewables | Derrybrien |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2, WFPS1.5.3.3, WFPS1.5.4.1, WFPS1.5.4.2, WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2079 | ESB Renewables | Derrybrien |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2080 | ESB Renewables | Derrybrien |  | WFPS1 | WFPS1.6.3.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2081 | ESB Renewables | Mountain Lodge |  | WFPS1 | WFPS1.4.1, WFPS1.4.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2082 | ESB Renewables | Mountain Lodge |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2, WFPS1.5.3.3, WFPS1.5.4.1, WFPS1.5.4.2, WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2083 | ESB Renewables | Mountain Lodge |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2084 | ESB Renewables | Mountain Lodge |  | WFPS1 | WFPS1.6.3.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2085 | ESB Renewables | Garvagh 2 |  | WFPS1 | WFPS1.4.1, WFPS1.4.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 230
2086 | ESB Renewables | Garvagh 2 |  | WFPS1 | WFPS1.5.3.1, WFPS1.5.3.2, WFPS1.5.3.3, WFPS1.5.4.1, WFPS1.5.4.2, WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2087 | ESB Renewables | Garvagh 2 |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2088 | ESB Renewables | Garvagh 2 |  | WFPS1 | WFPS1.6.3.3 | v5.0 | Effective from 4th April 2014 until the earlier of the date that studies demonstrate compliance with the specific requirements of the Grid Code, the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2094 | Midas Energy Co | Glanlee |  | WFPS1 | WFPS1.6.3 | v5.0 | Effective from 30th September 2013 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015 | MPID 228
2095 | Green Energy Company Ltd | Boggeragh |  | WFPS1 | WFPS1.5.2.1, WFPS1.5.3, WFPS1.7.1.5, WFPS1.7.2.3 | v5.0 | Effective from 30th September 2013 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015 | MPID 227
2096 | Green Energy Company Ltd | Boggeragh |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 30th September 2013 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015 | MPID 212
2112 | Brookfield | Booltiagh 1 |  | WFPS1 | WFPS1.6.2.2 | v5.0 | Effective from 24th March 2014 until the earlier of the date that tests demonstrate compliance with the Grid Code, the date that a rememdy has been implemented and tested or 31st December 2015 | MPID 212
2113 | Brookfield | Booltiagh 1 |  | WFPS1 | WFPS1.5.3.2 | v5.0 | Effective from 24th March 2014 until the earlier of the date that tests demonstrate compliance with the Grid Code, the date that a rememdy has been implemented and tested or 31st December 2015 | MPID 227
2114 | Brookfield | Booltiagh 1 |  | WFPS1 | WFPS1.5.4.1 | v5.0 | Effective from 24th March 2014 until the earlier of the date that tests demonstrate compliance with the Grid Code, the date that a rememdy has been implemented and tested or 31st December 2015 | MPID 227
2115 | Brookfield | Booltiagh 1 |  | WFPS1 | WFPS1.5.4.2 | v5.0 | Effective from 24th March 2014 until the earlier of the date that tests demonstrate compliance with the Grid Code, the date that a rememdy has been implemented and tested or 31st December 2015 | MPID 227
2116 | Brookfield | Booltiagh 1 & 2 |  | WFPS1 | WFPS1.6.3.1 | v5.0 | Effective from 24th March 2014 until the earlier of the date that tests demonstrate compliance with the Grid Code, the date that a rememdy has been implemented and tested or 31st December 2015 | MPID 228
2118 | Brookfield | Lisheen 1 |  | WFPS1 | WFPS1.5.2.1, WFPS1.5.3.5, WFPS1.5.3.6, WFPS1.5.3.7 | v5.0 | Effective from 21st March 2014. Permanent | MPID 228
2128 | SSE Generation Ireland | Great Island 1 |  | CC7 | CC.7.3.6.1 | v5.0 | 31st December 2014 | 0 MVAr (leading)
2129 | SSE Generation Ireland | Great Island 2 |  | CC7 | CC.7.3.6.1 | v5.0 | 31st December 2014 | 0 MVAr (leading)
2132 | Rusal Aughinish Ltd | Seal Rock 3 |  | CC7 | CC.7.3.1.1 (w) | v5.0 | Effective from 18th November 2014 until the earlier of the lifetime of the unit or one year after the date that a rememdy becomes available, but not later than 25th March 2025 | For Secondary Fuel Switchover Output to 2MW
2133 | Rusal Aughinish Ltd | Seal Rock 4 |  | CC7 | CC.7.3.1.1 (w) | v5.0 | Effective from 18th November 2014 until the earlier of the lifetime of the unit or one year after the date that a rememdy becomes available, but not later than 25th March 2025 | For Secondary Fuel Switchover Output to 2MW
2136 | Brookfield | Knockacummer |  | WFPS1 | WFPS1.7.1.2 | v5.0 | Effective from 13th January 2014 until the earlier of the date that a remedy has been implemented and tested or 31st December 2015 | Signals
2144 | Brookfield | Whitegate |  | CC7 | CC.7.3.1.1 (w) | v5.0 | Effective from 14th March 2014 for the lifetime of the unit or a major refurbishment of the unit but not later than 01/01/18 | For Secondary Fuel Switchover Output to 20MW
2443 | Gort Wind Farms Ltd | Derrybrien |  | WFPS1 | WFPS1.5.2.1 | v5.0 | Effective from 26th November 2014 until the earlier of the date the remedy is implemented and tested or 31st December 2015 | WFPS shall commence implementation of Active Power Control Set-point within 5 minutes of receipt of the signal from the TSO. The WFPS is derogated to a tolerance of +/-3MW tolerance across all MW Output.
986 | SSE Generation Ireland Ltd | Great Island 1 |  | CC | CC.7.3.1.1(u)(iii) | v3.5 | Effective from 1 January 2014 until 15 April 2015 | The unit can provide 3MW of TOR1
987 | SSE Generation Ireland Ltd | Great Island 1 |  | CC | CC.7.3.1.1(u)(iv) | v3.5 | Effective from 1 January 2014 until 15 April 2015 | The unit can provide 3MW of TOR2
988 | SSE Generation Ireland Ltd | Great Island 2 |  | CC | CC.7.3.1.1(u)(iii) | v3.5 | Effective from 1 January 2014 until 15 April 2015 | The unit can provide 3MW of TOR1
989 | SSE Generation Ireland Ltd | Great Island 2 |  | CC | CC.7.3.1.1(u)(iv) | v3.5 | Effective from 1 January 2014 until 15 April 2015 | The unit can provide 3MW of TOR2
2103 | SSE Generation Ireland Ltd | Great Island 3 |  | CC | CC.7.3.1.1(m) | v5.0 | Effective from 12 November 2013 until 15 April 2015 | Ramp Down Capability is at 1.5 MW/min
2104 | SSE Generation Ireland Ltd | Great Island 3 |  | CC | CC.7.3.1.1(l) | v5.0 | Effective from 12 November 2013 until 15 April 2015 | Ramp Up Capability is at 1.5 MW/min between 30-80 MW and 0.5 MW/min between 80-120 MW.
2065; 2067; 2121 | Brookfield Renewable Energy Group | Lisheen 2 |  | WFPS1 | WFPS1.6.2.2; WFPS1.5.3.1; WFPS 1.5.3.2; WFPS1.4.1; WFPS1.4.2 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or 31st December 2018. | MPID 212; MPID 227; MPID 230
2065; 2066; 2120 | Brookfield Renewable Energy Group | Lisheen 1 |  | WFPS1 | WFPS1.6.2.2; WFPS1.5.3.1; WFPS 1.5.3.2; WFPS1.5.3.3; WFPS1.5.4.1; WFPS1.4.1; WFPS1.4.2 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or 31st December 2018. | MPID 212; MPID 227; MPID 230
2146; 2147; 2391 | Brookfield | Coomagearlahy 3 |  | WFPS1 | WFPS1.7.1.1(d); WFPS1.4; WFPS1.7.1.3.1(b); WFPS1.7.1.3.1(c) | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2018. | MPID 227; MPID 212; Ramp Rates; Signals; MPID 230
2064 | Brookfield Renewable Energy Group | Booltiagh 1 & 2 |  | WFPS1 | WFPS1.7.1.1 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | Signal List #1
2122; 2123 | Brookfield | Coomagearlahy 1 & 2 |  | WFPS1 | WFPS1.4.1; | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2018. | MPID 230
2043 | SSE Airtricity | Bindoo |  | WFPS1 | WFPS1.6.3 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | MPID 228
2050; 2051; 2053 | SSE Airtricity | Dromada |  | WFPS1 | WFPS1.6.2.2(a); WFPS1.6.2.2(b); WFPS1.5.3.1; WFPS1.5.3.2; WFPS1.5.3.3; WFPS1.5.3.4; WFPS1.5.3.5; WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5; WFPS1.7.2.3; WFPS1.6.3; | v6.0 | Effective from 17 December 2015 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2017. | MPID 227; MPID 212; MPID 228
2059 | SSE Airtricity | Meentycat |  | WFPS1 | WFPS1.4.1; WFPS1.4.2 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | MPID 230
2492; 2493 | Wind Prospect Ireland Ltd | Boggeragh 1 |  | WFPS1 | WFPS1.6.2.2; WFPS1.5.3 | v6.0 | Effective from 06 August 2015 until the earlier of: The date that a remedy has been implemeneted and tested or; 31st December 2016. | MPID 212; Frequency Response Control
2214; 2215; 2216; 2217; 2218 | Gael Force Wind Energy Ltd | Clahane 1 |  | WFPS1 | WFPS1.6.2.2; WFPS1.5.2.1; WFPS1.5.3; WFPS1.5.4.1; WFPS1.5.4.2; WFPS1.7.1.5; WFPS1.7.2.3 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31 December 2018 | MPID 212; MPID 227;
2062; 2063 | ESB Renewables | Garvagh Glebe |  | WFPS1 | WFPS1.6.2.2; WFPS1.6.3.3 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | MPID 212; MPID 228
2087 | ESB Renewables | Garvagh Tullynahaw |  | WFPS1 | WFPS1.6.2.2 | v6.0 | Effective from 01 January 2016 until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested or; 31st December 2016. | MPID 212
994; 995; 996; 997 | SSE | Tarbert 4 |  | CC | CC.7.3.1.1(u)(i); CC.7.3.1.1(u)(ii); CC.7.3.1.1(u)(iii); CC.7.3.1.1(u)(iv); | v6.0 | Effective from 01 January 2014. Derogation extension approved until the earlier of: The date that compliance with Grid Code is achieved; The date that a remedy has been implented and tested: or 31 May 2016. | The unit can provide 0 MW of POR; 0 MW of SOR; 0 MW TOR1 and 7.5 MW of TOR1.
2293; 2341 | SSE | Great Island 4 |  | CC | CC.7.3.1.1(h); CC.7.3.6.1 | v6.0 | Effective from 28/05/2014 to 31/12/2020 | At 95% of nominal voltage dip (5% retained) derogation is sought to a FRT of 85 ms. At 50% of nominal voltage dip (50% retained) derogation is sought to a FRT Time of 215 ms.0 Mvar (leading) at a SCL of 3.3 kA (below 7.4 kA)
2098 | Activation Energy DSU Ltd | AE1 |  | CC | CC.12.6(a) | v6.0 | Effective from 23/09/2015 to 01/06/2016 | A number of individual sites in AE1 do not have fast acting metering. Typcially these individual sites use pulse metering and have a DSU Capacity of less than 1 MW.
1097 | ESBGWM | Poolbeg |  | CC | 7.3.1.1(t)(i) | v6.0 | Effective from 12/09/2012 to 30/06/2016 | Time from Synchronising to Minimum Load from hot: 69 mins; from warm: 146 mins; from cold: 224 mins.
2511 | ESBGWM | Dublin Bay |  | CC | 7.3.1.1(w) | v6.0 | Effective from 01/01/2015 until the earlier of: the date that compliance with the Grid Code is achieved; the date that a remedy has been implemented and tested; the date the CER withdraws the derogation following a breach of the conditions of the derogation; or 31/12/2022. | 25 MW for the Primary Fuel Switchover Output/25 MW for the Secondary Fuel Switchover Output
2618 | ESBGWM | Aghada 2 |  | CC | 7.3.1.1(w) | v6.0 | Effective from 01/12/2015 until the earlier of: the date that compliance with the Grid Code is achieved; the date that a remedy has been implemented and tested; the date the CER withdraws the derogation following a breach of the conditions of the derogation; or 31/12/2022. | 26 MW for the Primary Fuel Switchover Output/25 MW for the Secondary Fuel Switchover Output
2137 | SSE | Tarbert 1 |  | CC | 7.3.6.1 | v6.0 | Effective from the 01/01/2014 until the earlier of: Lifetime of the Generation Units; Or 31st Dec 2023. | 10Mvar (leading) 25Mvar (lagging)
2138 | SSE | Tarbert 2 |  | CC | 7.3.6.1 | v6.0 | Effective from the 01/01/2014 until the earlier of: Lifetime of the Generation Units; Or 31st Dec 2023. | 10Mvar (leading) 25Mvar (lagging)
2139 | SSE | Tarbert 3 |  | CC | 7.3.6.1 | v6.0 | Effective from the 01/01/2014 until the earlier of: Lifetime of the Generation Units; Or 31st Dec 2023. | 45Mvar (leading) and 110Mvar (lagging)
2140 | SSE | Tarbert 4 |  | CC | 7.3.6.1 | v6.0 | Effective from the 01/01/2014 until the earlier of: Lifetime of the Generation Units; Or 31st Dec 2023. | 45Mvar (leading) and 110Mvar (lagging)
2616 | Gaelectric | Ballywater |  | WFPS | 1.5.2.1 | v6.0 | Effective From 2nd March 2016 until the earlier of:The date that compliance with Grid Code is achieved; The date that a remedy has been implemented and tested; or 31st March 2017 | Active Power Control
2564 | Brookfield | Coomagearlahy 1 & 2 |  | WFPS1 | WFPS1.6.2.2 | v6.0 | Permanent | MPID 212 Reactive Power Control Modes The WFPS does not provide 3 switchable control modes.
2565 | Brookfield | Coomagearlahy 1 & 2 |  | WFPS1 | WFPS1.5.3.1 WFPS1.5.3.2 | v6.0 | Permanent | MPID 227 - Replaces 2073 Current Control System is not capable of delivering performance required by this modificaction
2566 | Brookfield | Coomagearlahy 1 & 2 |  | WFPS1 | WFPS1.5.2.1 WFPS1.5.3.5 WFPS1.5.3.6 WFPS1.5.3.7 | v6.0 | Permanent | Replaces 2124 & 2125 Frequency Response The V90-3MW VCS can handle a DMOL between 25% and 40%.
2567 | Brookfield | Coomagearlahy 1 & 2 |  | WFPS1 | WFPS1.5.3.3 WFPS1.5.4.1 | v6.0 | Permanent | Replaces 2126 & 2127 MPID 227 Ramp Rates All ramp rates per GC v4.0 can be achieved. Control system is not capable of delivering performance required by this modification.
2634 | Brookfield | Coomagearlahy 1 & 2 |  | WFPS1 | WFPS1.4.2 | v6.0 | Permanent | Partially replaces 2122 & 2123. WFPS1.4.2 only. Fault Ride Through WFPS is not able to provide active power in proportion to retained voltage during fault as required in the Grid Code. Commissioned under earlier version of GC.
2635 | Brookfield | Coomagearlahy 1 |  | WFPS1 | WFPS1.6.2.2 | v6.0 | Permanent | MPID 212 Reactive Power Control Modes The WFPS does not provide 3 switchable control modes.
2636 | Brookfield | Coomagearlahy 2 |  | WFPS1 | WFPS1.6.2.2 | v6.0 | Permanent | Replaces 2072 MPID 212 Reactive Power Control Modes The WFPS does not provide 3 switchable control modes.
2665 | Brookfield | Coomagearlahy 3 |  | WFPS1 | WFPS1.5.3.2 | v6.0 | Permanent | MPID 227, 245, 262 Frequency Response No wiring for frequency droop setting signals from TSO In APC Mode, FR On command must be issued for WFPS to respond to frequency variations w.r.t Curve 1/2 Settings
2666 | Brookfield | Coomagearlahy 3 |  | WFPS1 | WFPS1.6.2.2 | v6.0 | Permanent | Voltage Regulation Delivered at LV side of Grid Transformer NCC cannot issue remote PF & Reactive Power instructions.
2667 | Brookfield | Coomagearlahy 3 |  | WFPS1 | WFPS1.5.4.1 WFPS1.5.4.2 | v6.0 | Permanent | Ramp Rates Ramp Rates do not meet requirements of WFPS 1.5.4.1 and priority between functions is not implemented. 1 minute/10 minute ramp rate range is currently operating as per GC v3
2447 | Sonneborn Wind | Castledockrell |  | WFPS1 | WFPS1.6.2.2 | v5.0 | 31st December 2018 | MPID 212 Reactive Power Control Modes The WFPS does not provide 3 switchable control modes. The WFPS has demonstrated compliance with GC v3.4
2448 | Sonneborn Wind | Castledockrell |  | WFPS2 | WFPS1.5.2.1 WFPS1.5.3 WFPS1.5.4.1 WFPS1.5.4.2 WFPS1.7.1.5 WFPS1.7.2.3 | v5.0 | 31st December 2018 | MPID 227 APC, Frequency Response, Ramp Rates, Signals The WFPS does not provide all the functionality as required by GC v5.0. The WFPS can receive APC Setpoints, implements a power frequency response and responds with 1 & 10 minute ramp rates.The WFPS has demonstrated compliance with GC v3.4
2648 | ESB Renewables | Mountain Lodge |  | WFPS1 | WFPS1.5.3.8 | v6.0 | 31st December 2018 | Frequency Response Additional time required to investigate the loss of one WGT during frequency testing.
2649 | ESB Renewables | Mountain Lodge |  | WFPS1 | WFPS1.6.2.3 | v6.0 | 31st December 2018 | Automatic Voltage Regulation Voltage Regulation System Slope Setting cannot be changed from 4%.
2600 | Brookfield | Lisheen 1 & 2 |  | WFPS1 | WFPS1.5.2.1 | v6.0 | 31st December 2018 Withdrawn 05/02/2019 | Start Up Turbines failed to start up within 3 minutes, due to flushing of hydraulic system when turbine is paused.
2601 | Brookfield | Lisheen 1 & 2 |  | WFPS1 | WFPS1.5.3.10 | v6.0 | 31st December 2018 Withdrawn 05/02/2019 | Frequency Response Frequency Response not as expected. WTGs ramped up at Frequency = 50.2 Hz after disconnecting at 50.8 Hz.
2602 | Brookfield | Lisheen 1 & 2 |  | WFPS1 | WFPS1.5.3 | v6.0 | 31st December 2018 Withdrawn 05/02/2019 | Frequency Response When Frequency Control is in Off Mode,it is not possible to simulate an increase in frequency to demonstrate that the windform does not respond (as expected)
2616 | Ballywater Windfarm | Ballywater |  | WFPS1 | WFPS1.5.2.2 | v6.0 | 31st March 2017 | Active Power Control MW Setpoint Tolerance of ± 2.5 MW (GC Requirement ±1 MW)
2668 | SSE | Uggool |  | WFPS1 | WFPS1.4.2(d) | v6.0 | 30th June 2018 | Fault Ride Through Spike in reactive current when control is transferred from turbine control during FRT to SCADA control post FRT.
2669 | SSE | Seecon |  | WFPS1 | WFPS1.4.2(d) | v6.0 | 30th June 2018 | Fault Ride Through Spike in reactive current when control is transferred from turbine control during FRT to SCADA control post FRT.
2675 | ESB Wind | Derrybrien |  | WFPS1 | WFPS1.5.2.1 WFPS1.5.4.1 | v6.0 | 31st December 2018 | Active Power Responds to Setpoint within 2 minutes & acheves within 3.5 minutes.(GC Requirement 10s/2 3 min) Ramp Rates Deviation +90 MW/minute (GC Requirement ±11.9 MW/min)
2694 | Gaelectric | Ballywater |  | WFPS1 | WFPS1.6.3 WFPS1.6.2.2 WFPS1.5.2.1 WFPS1.5.3 WFPS1.5.4.1 WFPS1.5.4.2 WFPS1.7.1.5 WFPS1.7.2.3 | v6.0 | 31st December 2018 | MW Curtailment The WFPS currently does not respond with sufficient accuracy to Active Power Control Setpoints issued by the TSO.
2721 | ESB GWM | Marina (MRC) |  | PCA | PC4.5 | v6.0 | Permanent | Derogated Closure Date - 10/09/2018
2722 | ESB GWM | Aghada (AD1) |  | PCA | PC4.5 | v6.0 | Permanent | Derogated Closure Date - 01/10/2019
2739 | ESB GWM | Liffey (LI4) |  | CC7 | CC7.3.1.1(k) | v6.0 | 31st December 2023 | Min Load = 3.99 MW
2746 | ESB GWM | West Offaly Power (WO4) |  | CC7 | CC7.3.1.1(t)(i) | v6.0 | 31st December 2025 | Time Sync to Min Load Hot = 73 min Time Sync to Min Load Warm = 100 min
2747 | ESB GWM | West Offaly Power (WO4) |  | CC7 | CC7.3.1.1(t)(ii) | v6.0 | 31st December 2025 | Deload = 49 minutes
2748 | ESB GWM | West Offaly Power (WO4) |  | CC7 | CC7.3.1.1(s) | v6.0 | 31st December 2025 | Time to Sync Warm = 12 hours
2765 | ESB GWM | Aghada AT1, AT2 & AT4 |  | OC4 | OC4.3.6 | v6.0 | 31st December 2025 | No AGC
2381 | ESB GWM | Erne 2 (ER2) |  | CC7 | CC7.3.1.1(k) | v7.0 | Until Next Major Refurbishment | Minimum Load = 4MW
2432 | ESB GWM | Erne 2 (ER2) |  | CC7 | CC7.3.1.1(q) | v7.0 | Until Next Major Refurbishment | Block Load = 4 MW
2454 | ESB GWM | Erne 2 (ER2) | Erne 2 (ER2) | CC7 | CC7.3.1.1(u) | v7.0 | Until Next Major Refurbishment | Minimum POR = 0.25 MW
2630 | ESB GWM | Erne 1 (ER1) |  | CC7 | CC7.3.1.1(u) | v7.0 | Until Next Major Refurbishment | Minimum POR = 0.25 MW
2631 | ESB GWM | Erne 1 (ER1) |  | CC7 | CC7.3.1.1(q) | v7.0 | Until Next Major Refurbishment | Block Load = 4 MW
2632 | ESB GWM | Erne 1 (ER1) |  | CC7 | CC7.3.1.1(k) | v7.0 | Until Next Major Refurbishment | Minimum Load = 4MW
2742 | ESB GWM | Moneypoint |  | OC4 | OC4.3.6 | v7.0 | 31st December 2025 | No AGC