## Cover Sheet
TSO Schedule of Tests for AAAAA WPFS XXX MW RfG PPM Type XX
Disclaimer:
This Progress summary contains information (and/or attachments) which may be privileged or confidential. All content is intended solely for the use of the individual or entity to whom it is addressed. If you are not the intended recipient please be aware that any disclosure, copying, distribution or use of the contents of this message is prohibited. If you suspect that you have received this Progress Summary in error please notify EirGrid immediately. Further information can be found at: http://www.eirgrid.com/aboutus/legal/

## Issues Log
No. | Issue Description | Owner | Action | Decision | Status
1 | An issue related to the commissioning of the Unit | EirGrid | Action to mitigate/resolve issue |  | Open
2
3
4
5
6
The Issues Log shall be populated with any items that are identified outside of the prescribed tests, identified following the closure of a prescribed test, or during performance monitoring of the unit, prior to issuance of an Operational Certificate. All items in the Issues Log shall be closed prior to the issuance of an Operational Certificate.

## Summary
| Energisation Date | dd/mm/yyyy
| Operational Readiness Confirmation Deadline | dd/mm/yyyy
| Operational Certificate Deadline | dd/mm/yyyy
EON | Description | Status | Deadline
1 | PPM Commissioning schedule | Open | 12 months before energisation
2 | Study Requirements | Open | 18 months before energisation
3 | Power Quality Report | Open | 12 months before energisation
4 | Voltage Fault Ride Through | Open | 12 months before energisation
5 | Dynamic Model | Open | 12 months before energisation
6 | Reactive Power Capability and Transmission System Voltage Range | Open | 12 months before energisation
7 | Notification Of Study Status | N/A | 4 weeks before energisation
8 | Signal List | Open | 9 months before energisation
9 | ROCOF Capability | Open | 12 months before energisation
10 | Transmission System Frequency Ranges | Open | 4 weeks before energisation
11 | Data Sheets | Open | 4 weeks before energisation
12 | Grid Connected Transformer | Open | 4 weeks before energisation
13 | Agree Protection Settings | Open | 4 months before energisation
14 | Implemented Protection Settings | Open | 4 weeks before energisation
15 | Controller settings (Frequency Response, Voltage Droop etc.) | Open | 1 week before energisation
16 | Metering Equipment | Open | N/A
17 | Authorisation to Construct | Open
18 | Connection Agreement Pre-requisites to Energisation | Open
19 | Market Registration | Open | Submission 60 working days before energisation
20 | Operational Information | Open | 4 weeks before energisation
21 | Inspection of PPM Procedures | Open | 4 weeks before energisation
22 | Operation Instruction | Open | 1 week before energisation
23 | Energisation Instruction | Open | 1 week before energisation
24 | Wiring Certificate | Open | 1 week before energisation
25 | Pre-energisation signals and controls check | Open | 1 week before energisation
ION | Description | Status | Deadline
26 | Harmonics Baseline | Open | Immediately following energisation
27 | Post-energisation signals and controls check | Open | 1 week after first export
28 | Dispatch Testing Program | Open | 6 weeks after last WTG installed
29 | Reactive Power Dispatch Test Program | Open | 6 weeks after last WTG installed
30 | WTG Transformer Tap | Open | 6 weeks after last WTG installed
31 | Implemented Protection Settings | Open | 6 weeks after last WTG installed
32 | Installed Plant Survey | Open | 6 weeks after last WTG installed
33 | Harmonics Assessment | Open | 6 weeks after last WTG installed
FON | Description | Status | Deadline
34 | Active Power Control | Open | 12 months after energisation
35 | Frequency Response | Open | 12 months after energisation
36 | Reactive Power Control | Open | 12 months after energisation
37 | Reactive Power Capability | Open | 12 months after energisation
38 | Black Start Shutdown | Open | 12 months after energisation
39 | Test Report | Open | 12 months after energisation
40 | Capacity Test | Open | 12 months after energisation
41 | Generator Data | Open | 12 months after energisation
42 | Model Validation | Open | 12 months after energisation
43 | Harmonics Assessment | Open | 12 months after energisation
System Services | Description | Status | Deadline
44 | Reserve Services | Open | 12 months after energisation
45 | Fast Post Fault Active Power Recovery & Dynamic Reactive Response | Open | 12 months after energisation
46 | Steady State Reactive Power | Open | 12 months after energisation

## EON
Test # | Grid Code Compliance Test Name | Grid Code Reference | Witnessed Test | Details | Comment | Timeline | Status
1 | PPM Commissioning schedule |  | No | Schedule to be provided and updated as required - energisation - turbine commissioning - testing |  | 12 months before energisation | Open
2 | Study Requirements | PPM1.4 PPM1.6.4 | No | EirGrid to issue the following based on the PPM shallow connection method: - Power Quality Limits Report - Minimum System Strength Report |  | 18 months before energisation | Open
3 | Power Quality Report | PPM1.6.4 | No | PPM to report on Harmonics and Voltage Fluctuations in line with template report (http://www.eirgridgroup.com/site-files/library/EirGrid/Note-on-Harmonics-Power-Quality-Requirements-for-Connection-to-Transmission-System.pdf). This is based on Harmonics Limits that are issued to PPM via Power Quality Limits Report |  | 12 months before energisation | Open
4 | Voltage Fault Ride Through | PPM1.4 | No | Provision of studies for the PPM with site specific settings, using Short Circuit Level provided by EirGrid via Minimum System Strength Report |  | 12 months before energisation | Open
5 | Dynamic Model | PC.A5, PC.A8 per MPID239 | No | PPM shall provide both of the following models: 1. User Defined Model for the PPM site in the software format specified in the Minimum System Strength Report. If this model was not used in the Fault Ride Through study it shall be validated against the model used in the study. 2. PSSe V34 2nd generation WECC model for the PPM site. If a WECC model is not available, a Laplace diagram shall be provided for the PPM site, including associated parameters. The models shall be in compliance with PC.A5 and PC.A8 Models should be provided with (i) clear model documentation, and (ii) site specific model parameters. Note these models are to be validated against testing and a model validation report to be submitted in Phase C A document register is required to accompany submissions and be maintained |  | 12 months before energisation | Open
6 | Reactive Power Capability and Transmission System Voltage Range | PPM1.6.1 PPM1.6.2.1 | No | 1. Provide Steady State Reactive Power Capability chart showing the capability of the PPM at different Voltage levels: - nominal connection point Voltage - minimum connection point Voltage per PPM1.6.1 - maximum connection point Voltage per PPM1.6.1 Reactive power capability below 12% of Registered Capacity shall be based on resource. PPM must remain connected to the system and deliver the reactive performance that the Grid Code requires across the full range of system voltages. 2. Provide Steady State Reactive Power Capability of the PPM at the LV terminals of the Grid Connected Transformer, at nominal connection point voltage. (for each unit if there are mulitple units) 3. Provide tap changer relay settings for Grid Connected Transformer (e.g. 20.7 kV +/- 0.5 kV) |  | 12 months before energisation | Open
7 | Notification Of Study Status |  | No | EirGrid to issue Notification Of Study Status (confirming that studies do/don't present issues which prevent energisation) (based on models provided under test 4) | Covered by tests 2-6 | 4 weeks before energisation | N/A
8 | Signal List | PPM1.7 | No | PPM must provide all data required for development of a signal list. Refer to signal list template for data required: http://www.eirgrid.com/operations/gridcode/compliancetesting/ |  | 9 months before energisation | Open
9 | ROCOF Capability | PPM1.5.1 | No | Demonstrate RoCoF capability of PPM via Provision of Studies and/or type test |  | 12 months before energisation | Open
10 | Transmission System Frequency Ranges | PPM1.5.1 | No | Data sheet for WTGs and/or type test with details as per PPM1.5.1 |  | 4 weeks before energisation | Open
11 | Data Sheets | PC.A4.11 PPM1.5.3.12 | No | PPM must provide data sheets for: - WTGs (generator and convertor) - WTG Turbine Transformers (including tap ratios) - any SVCs, STATCOMs, Filters, Cap Banks, Reactors In compliance with RfG please confrim that the PPM will also be capable of operating as per PPM1.5.3.12 (LFSM-U) ie. have th eability to ammend settings to operate to 49.5 Hz |  | 4 weeks before energisation | Open
12 | Grid Connected Transformer | PC.A4.11 | No | PPM must provide: - As built data sheet for Grid Connected Transformer (including all data per PC.A4.11) - Legible photograph of Grid Connected Transformer Name Plate Rating - FAT results of Grid Connected Transformer |  | 4 weeks before energisation | Open
13 | Agree Protection Settings |  | No | Overcurrent protection settings for - Grid Connected Transformer - MV Feeder CBs Voltage, Frequency and RoCoF protection settings for - WTGs - SVCs, STATCOMs, Cap Banks, Filters, Reactors, etc. - Lockout functions PPM to agree protection settings to be applied via e-mail to generator_testing@eirgrid.com and gridprotection@eirgrid.com |  | 4 months before energisation | Open
14 | Implemented Protection Settings |  | No | Signed commisioning documentation to be provided for: (i.e. verification that agreed settings have been implemented and tested by primary injection and CB tripping for transformer protection devices) - Grid Connected Transformer (including Buchholz & Differential) - Turbines - SVCs, STATCOMs, Filters, Cap Banks, Reactors |  | 4 weeks before energisation | Open
15 | Controller settings (Frequency Response, Voltage Droop etc.) | PPM1.5.3.6, PPM1.5.3.15, PPM1.5.4.3, PPM1.6.2.3 | No | Confirm that power output control mechanism in accordance with PPM1.5.2.1 is in place prior to energisation, using settings specified in PPM signal list |  | 1 week before energisation | Open
16 | Metering Equipment |  | No | Check, calibration and sealing of Transmission Station metering including signals to Power Station. ESB Networks (Metering Services) to provide DoF for revenue metering as part of Energisation Instruction. (No action on PPM) |  | N/A | Open
17 | Authorisation to Construct |  |  | PPM shall provide confirmation from Commission for Regulation of Utilities (licensing@cru.ie) of consented MW capacity. PPM to request confirmation of valid authorisation to construct from the CRU via email |  | 4 weeks before energisation | Open
18 | Connection Agreement Pre-requisites to Energisation |  |  | PPM shall provide confirmation that they have met all pre-requisites to Energisation under the Connection Agreement |  | 4 weeks before energisation | Open
19 | Market Registration |  | No | PPM must be registered in the market before energistaion. PPM must submit a fully completed party accession pack and fully complete a particpant notification pack |  | Submission 60 working days before energisation | Open
20 | Operational Information | OC7.2.4.5 | No | Provide the following to EirGrid Customer Relations via e-mail to info@eirgrid.com - 24 hour contacts - Authorised Operators - Authorised DOF givers Note. Authorised Operators must be agreed with ESBN for switching to take place. |  | 4 weeks before energisation | Open
21 | Inspection of PPM Procedures |  | No | Check that Power Station has drawn up operating procedures and that suitable operating personnel are available with call-out procedure and that these are in line with EirGrid operating procedures. Procedures shall cover: following tripping of generator transformer, failure of protection, failure of power supplies etc. |  | 4 weeks before energisation | Open
22 | Operation Instruction |  | No | Operation Instruction written by EirGrid, agreed with ESBN and PPM Must cover all plant and including a check to see that the procedures can be safely followed. Operational Diagram/Safety Rule Boundaries to be clarified. Specify Naming of plant, equipment etc. |  | 1 week before energisation | Open
23 | Energisation Instruction |  | No | Energisation Instruction for 1st energisation of Grid Connected Transformer written by EirGrid, agreed with ESBN and PPM. PPM must issue the following as part of the Energisation Instruction: - DOF for protection - DOF for trip commands between Tx and Power Stations |  | 1 week before energisation | Open
24 | Wiring Certificate | PPM1.7 | No | Submit a completed and signed Wiring Cert, per latest version of the PPM signal list |  | 1 week before energisation | Open
25 | Pre-energisation signals and controls check | PPM1.7 | Yes | Carried out with ESB Telecoms and EirGrid PPM to request EirGrid Project Manager to schedule this test, giving 15 business days notice for the requested test date |  | 1 week before energisation | Open
All EON tests to be completed to achieve Energisation Operational Notification.
It is the responsibility of the PPM to demonstrate compliance with the Grid Code in all tests, above.

## ION
Test # | Grid Code Compliance Test Name | Grid Code Reference | Witnessed Test | Details | Comment | Deadline | Status
26 | Harmonics Baseline | CC.10.13 |  | 1 week assessment to establish harmonics baseline, prior to first export (Grid Connected Transformer de-energised) |  | Immediately following energisation | Open
| Harmonics baseline must be established to achieve Interim Operational Notification |  |  | Interim Operational Notification is required for first export. 5 MW Export Limit is applied |  | Prior to first export | Open
27 | Post-energisation signals and controls check | PPM1.7 | Yes | Carried out with ESB Telecoms and EirGrid PPM to request EirGrid Project Manager to schedule this test, giving 15 business days notice for the requested test date |  | 1 week after first export | Open
28 | Dispatch Testing Program | Controllability Categorisation Policy | Yes | Dispatch Tests carried out by EirGrid, in accordance with the Controllability Categorisation Policy http://www.eirgridgroup.com/site-files/library/EirGrid/Wind%20Farm%20Controllability%20Categorisation%20Policy.pdf PPM to request tests via generator_testing@eirgrid.com, in line with commissioning programme, following post-energisation signals and controls check |  | 6 weeks after last WTG installed | Open
29 | Reactive Power Dispatch Test Program |  | Yes | Reactive Power Dispatch Tests carried out by EirGrid in coordination with the PPM. PPM shall participate in the tests in order to mitigate any performance issues which may impact the transmission system |  | 6 weeks after last WTG installed | Open
30 | WTG Transformer Tap | PC.A4 | No | Confirm the transformer tap position as commissioned for each generation unit |  | 6 weeks after last WTG installed | Open
31 | Implemented Protection Settings |  | No | Signed commisioning documentation to be provided (i.e. verification that agreed settings have been implemented and tested) for any plant not in place before energisation: - Turbines - SVCs, STATCOMs, Filters, Cap Banks, Reactors |  | 6 weeks after last WTG installed | Open
32 | Installed Plant Survey | Connection Agreement PPM 1.5.1 PPM 1.6.1 | Yes | Site survey is scheduled with EirGrid via generator_testing@eirgrid.com, for the purpose of verifying: - installed plant - protection settings (under/over frequency) (under/over voltage) (RoCoF) - transformer tap of WTGs |  | 6 weeks after last WTG installed | Open
33 | Harmonics Assessment | CC.10.13 | No | EirGrid verify that power quality at the PPM connection point has remained within the limits set in the Power Quality Limits Report |  | 6 weeks after last WTG installed | Open
| All EON and ION tests must be completed to achieve Operational Readiness Confirmation |  |  | Deadline for Operational Readiness Confirmation: 6 weeks after installation of final turbine (as agreed with TSO) |  |  | Open
| All Phase EON and ION tests must be completed to achieve Interm Operational Notification |  |  | Deadline for Operational Readiness Confirmation: 6 weeks after installation of final turbine (as agreed with TSO) |  |  | Open
It is the responsibility of the PPM to demonstrate compliance with the Grid Code in all tests, above.

## FON
Test # | Grid Code Compliance Test Name | Grid Code Reference | Test Procedure Reference | Witnessed Test | Details | Comment | Status
34 | Active Power Control | PPM1.5.2 PPM1.5.4 | Draft | Yes | PPM to demonstrate active power control, functioning of available active power and mechanical availablility, when operated from NCC See test procedure for % resource requirement |  | Open
35 | Frequency Response | PPM1.5.1 PPM1.5.2 PPM1.5.3 PPM1.5.4 | Draft | Yes | PPM to demonstrate correct response to changes in grid frequency, in line with settings provided in signal list. This also inlcudes new RfG Frequency modes - FSM, LFSM-U & LFSM-O See test procedure for % resource requirement |  | Open
36 | Reactive Power Control | SDC2.B.1 PPM1.6.2 PPM1.6.3 | Draft | Yes | PPM to demonstrate all 3 methods of voltage control function correctly when operated from NCC See test procedure for % resource requirement |  | Open
37 | Reactive Power Capability | PPM1.6.3 | Draft | Yes | PPM to demonstrate full reactive power capability See test procedure for % resource requirement |  | Open
38 | Black Start Shutdown | OC8, PPM1.7.2.5 | Draft | Yes | PPM to demonstrate that Black Start Shutdown scheme operates per functional specification |  | Open
39 | Test Report |  | Draft | No | PPM to submit a report demonstrating compliance with Grid Code requirements, as tested in tests 30 to 34. deadline: 20 Business Days following completion of testing |  | Open
40 | Capacity Test | Connection Agreement | Per Connection Agreement | No | Verify Exported MW Capacity Test A: 75% of MEC for > 30 minutes Capacity Test B: 95% of MEC for > 30 minutes |  | Open
41 | Generator Data | PC.A5 per MPID239 |  | No | PPM must submit data per PC.A5 following completion of commissioning |  | Open
42 | Model Validation | PC.A8 per MPID239 |  | No | PPM to validate model submitted in test 4 1. Confirm that the model reflects final control parameters for FRT, AVR, F.Response, WTG trafo tap position, etc. 2. Confirm simulated curves for AVR response and F.Response match those measured through testing |  | Open
43 | Harmonics Assessment | CC.10.13 |  | No | EirGrid verify that power quality at the PPM connection point has remained within the limits set in the Power Quality Limits Report |  | Open
| All EON, ION and FON tests must be completed and there must be no open performance monitoring issues in order to achieve Final Operational Certificate |  |  |  | Deadline for achieving Operational Certificate is 1 year from the energisation of the point of connection (as agreed with TSO) |  | Open
It is the responsibility of the PPM to demonstrate compliance with the Grid Code in all tests, above.

## FON (System Services)
Test # | Test | Grid Code Reference | Comment | Test procedure Agreed | Test Status | Link to template procedure on website
44 | Reserve Services |  | FFR, POR, SOR, TOR1 Tested during Operating Reserve Tests Requires data recording at 20 ms resolution for FFR | Open | Open | http://www.eirgridgroup.com/site-files/library/EirGrid/WPFS-OR-test-procedure-template.docx
45 | Fast Post Fault Active Power Recovery & Dynamic Reactive Response |  | Tested through FRT studies | Open | Open
46 | Steady State Reactive Power |  | Demonstrated during Reactive Power Capability test | Open | Open | http://www.eirgridgroup.com/site-files/library/EirGrid/WPFS-SSRP-test-procedure-template.docx