## Cover Sheet
Signal List and Control System Parameter settings for SolarFarmName (TLC) SFPS Topology XX XX MW v0.1
Disclaimer:
This Signal List contains information (and/or attachments) which may be privileged or confidential. All content is intended solely for the use of the individual or entity to whom it is addressed. If you are not the intended recipient please be aware that any disclosure, copying, distribution or use of the contents of this message is prohibited. If you suspect that you have received this Signal List in error please notify EirGrid immediately. Further information can be found at: http://www.eirgridgroup.com/legal/

## Version Control
SolarFarmName (TLC)Signal List Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by
0.1 | 2024-05-01 | Beenish Javaid |  | Colm MacManus
Note on D3: Administrator: All signal lists circulated to EMS and ESBT for Review before issuance.

## Req, Process & Notes Topology 3
Requirements as per the Distribution Code DCC11.1.3
Topology | 3 | Topology 3 Solar Farm Power Station (SFPS) as per DCC11.1.3: A SFPS connected to the Distribution System via a dedicated feeder into an existing 110kV station.
DCC11.1.4 Figure 6
Solar Farm Registered Capacity | 1-5 MW | >= 5 MW | >= 10 MW
EirGrid RTU requirement
| Shared TSO-DSO RTU installed | TSO RTU Installed | TSO RTU Installed
Solar Farm controls
| Active Power Control system | Active Power Control system | Active Power Control system
| Frequency Response system | Frequency Response system | Frequency Response system
Solar Farm signals
| Available Active Power | Available Active Power | Available Active Power
Solar Farm Availability
Global Horizontal Irradiance
Diffused Horizontal Irradiance
Back Panel Temperature
Precipitation
Wind Speed
Wind Direction
Air Temperature
Air Pressure
Station controls
| Remote Control Enable Switch | Remote Control Enable Switch | Remote Control Enable Switch
| Dispatch Fail Lamp | Dispatch Fail Lamp | Dispatch Fail Lamp
| Blue Alert Lamp | Blue Alert Lamp | Blue Alert Lamp
Station signals
| Active Power Measurement | Active Power Measurement | Active Power Measurement
| Reactive Power Measurement | Reactive Power Measurement | Reactive Power Measurement
| Voltage Measurement | Voltage Measurement | Voltage Measurement
| DSO cable protection signals | DSO cable protection signals | DSO cable protection signals
| Connection and / or Transformer HV CB | Connection and / or Transformer HV CB | Connection and / or Transformer HV CB
| Connection and / or Transformer HV CB | Connection and / or Transformer HV CB | Connection and / or Transformer MV CB
| Feeder 20kV CB's | Feeder 20kV CB's | Feeder 20kV CB's
Detailed Process Overview
Additional Notes
General Process Notes: |  |  | Reference Documents:
More information on the testing process for DSO connected Solar Farms can be found at the following link: |  |  |  | EirGrid Telecoms Interface Cabinet Connection Details (using ETI Ref)
Recommended ESBTS cabling standards advised on signal list
http://www.eirgridgroup.com/site-files/library/EirGrid/DSO-TSO-SFPS-process-Rev.1.0-.pdf |  |  |  | Network Operator Initiated Shutdown Specification
Remote Control Specification
|  |  | Grid Code | V8
|  |  | Distribution Code: | V6
|  |  | Available Active Power Standard | http://www.eirgridgroup.com/site-files/library/EirGrid/QualityStandardforSolarfarmActivePower.pdf
Abbreviations
|  |  |  | TSO | Transmission System Operator - EirGrid
|  |  |  | EMS | Energy Management System - EirGrid
|  |  |  | DSO | Distribution System Operator - ESBN
|  |  |  | ESBN | ESB Networks
|  |  |  | ESBTS | ESB Telecoms Services
|  |  |  | RTU | Remote Terminal Unit
|  |  |  | ETIE | EirGrid Terminal Interface Enclosure
|  |  |  | NOIS | Network Operator Initiated Shutdown
|  |  |  | SG | Solar Generator
|  |  |  | CB | Circuit Breaker
|  |  |  | MEC | Maximum Export Capacity (In accordance with the User's Connection Agreement)
|  |  |  | SFPS | Solar Farm Power Station
|  |  |  | GCCT | Grid Code Compliance Testing
|  |  |  | MV | i.e. 20kV
|  |  |  | HV | i.e. 38kV / 110KV
|  |  |  | DCC | Distribution Control Centre
|  |  |  | SDCC | South Distribution Control Centre, ESBN
|  |  |  | NDCC | North Distribution Control Centre, ESBN
|  |  |  | NCC | National Control Centre, EirGrid

## Req, Process & Notes Topology 4
Requirements as per the Distribution Code DCC11.1.3
Topology | 4 | Solar Farm Power Stations are classed as being Connection Topology 4 when connected to the Distribution System via a dedicated 38kV, 20kV or 10kV feeder into an existing 38kV distribution station.
DCC11.1.4 Figure 7
Solar Farm Size | 1-5 MW | >= 5 MW | >= 10 MW
TSO RTU requirement
| Shared TSO-DSO RTU installed | TSO RTU Installed | TSO RTU Installed
Solar Farm controls
| Active Power Control system | Active Power Control system | Active Power Control system
| Frequency Response system | Frequency Response system | Frequency Response system
Solar Farm signals
| Available Active Power | Available Active Power | Available Active Power
Solar Farm Availability
Global Horizontal Irradiance
Diffused Horizontal Irradiance
Back Panel Temperature
Precipitation
Wind Speed
Wind Direction
Air Temperature
Air Pressure
Station controls
|  | TSO Remote Control Enable Switch | TSO Remote Control Enable Switch
| Dispatch Fail Lamp | Dispatch Fail Lamp | Dispatch Fail Lamp
| Blue Alert Lamp | Blue Alert Lamp | Blue Alert Lamp
Station signals
| Active Power Measurement | Active Power Measurement | Active Power Measurement
| Reactive Power Measurement | Reactive Power Measurement | Reactive Power Measurement
| Voltage Measurement | Voltage Measurement | Voltage Measurement
| DSO cable protection signals | DSO cable protection signals | DSO cable protection signals
| Connection and / or Transformer HV CB | Connection and / or Transformer HV CB | Connection and / or Transformer HV CB
| Connection and / or Transformer MV CB | Connection and / or Transformer MV CB | Connection and / or Transformer MV CB
| Feeder 20kV CB's | Feeder 20kV CB's | Feeder 20kV CB's
Detailed Process Overview
Additional Notes |  |  |  |  | Reference Documents:
More information on the testing process for DSO connected Solar Farms can be found at the following link: | [5 empty] | EirGrid Telecoms Interface Cabinet Connection Details (using ETI Ref)
http://www.eirgridgroup.com/site-files/library/EirGrid/DSO-TSO-SFPS-process-Rev.1.0-.pdf | [5 empty] | Recommended ESBTS cabling standards advised on signal list
Network Operator Initiated Shutdown Specification
Remote Control Specification
[5 empty] | Grid Code | V8
[5 empty] | Distribution Code: | V6
[5 empty] | Available Active Power Standard | http://www.eirgridgroup.com/site-files/library/EirGrid/QualityStandardforSolarfarmActivePower.pdf
Abbreviations
[6 empty] | TSO | Transmission System Operator - EirGrid
[6 empty] | EMS | Energy Management System - EirGrid
[6 empty] | DSO | Distribution System Operator - ESBN
[6 empty] | ESBN | ESB Networks
[6 empty] | ESBTS | ESB Telecoms Services
[6 empty] | RTU | Remote Terminal Unit
[6 empty] | ETIE | EirGrid Terminal Interface Enclosure
[6 empty] | NOIS | Network Operator Initiated Shutdown
[6 empty] | SG | Solar Generator
[6 empty] | CB | Circuit Breaker
[6 empty] | MEC | Maximum Export Capacity (In accordance with the User's Connection Agreement)
[6 empty] | SFPS | Solar Farm Power Station
[6 empty] | GCCT | Grid Code Compliance Testing
[6 empty] | MV | i.e. 20kV
[6 empty] | HV | i.e. 38kV / 110KV
[6 empty] | DCC | Distribution Control Centre
[6 empty] | SDCC | South Distribution Control Centre, ESBN
[6 empty] | NDCC | North Distribution Control Centre, ESBN
[6 empty] | NCC | National Control Centre, EirGrid

## Req, Process & Notes Topology 5
Requirements as per the Distribution Code DCC11.1.3
Topology | 5 | Solar Farm Power Stations are classed as being Connection Topology 5 when connected to an existing distribution line with load.
DCC11.1.4 Figure 8
Solar Farm Size | 1-5 MW | >= 5 MW | >= 10 MW
TSO RTU requirement
| Shared TSO-DSO RTU installed | TSO RTU Installed | TSO RTU Installed
Solar Farm controls
| Active Power Control system | Active Power Control system | Active Power Control system
| Frequency Response system | Frequency Response system | Frequency Response system
Solar Farm signals
| Available Active Power | Available Active Power | Available Active Power
Solar Farm Availability
Global Horizontal Irradiance
Diffused Horizontal Irradiance
Back Panel Temperature
Precipitation
Wind Speed
Wind Direction
Air Temperature
Air Pressure
Station controls
|  | Remote Control Enable Switch | Remote Control Enable Switch
| Dispatch Fail Lamp | Dispatch Fail Lamp | Dispatch Fail Lamp
| Blue Alert Lamp | Blue Alert Lamp | Blue Alert Lamp
Station signals
| Active Power Measurement | Active Power Measurement | Active Power Measurement
| Reactive Power Measurement | Reactive Power Measurement | Reactive Power Measurement
| Voltage Measurement | Voltage Measurement | Voltage Measurement
| DSO cable protection signals | DSO cable protection signals | DSO cable protection signals
| Connection and / or Transformer HV CB | Connection and / or Transformer HV CB | Connection and / or Transformer HV CB
| Connection and / or Transformer MV CB | Connection and / or Transformer MV CB | Connection and / or Transformer MV CB
| Feeder 20kV CB's | Feeder 20kV CB's | Feeder 20kV CB's
Detailed Process Overview
Additional Notes |  |  |  |  | Reference Documents:
More information on the testing process for DSO connected Solar Farms can be found at the following link: | [5 empty] | EirGrid Telecoms Interface Cabinet Connection Details (using ETI Ref)
http://www.eirgridgroup.com/site-files/library/EirGrid/DSO-TSO-SFPS-process-Rev.1.0-.pdf | [5 empty] | Recommended ESBTS cabling standards advised on signal list
Network Operator Initiated Shutdown Specification
Remote Control Specification
[5 empty] | Grid Code | V8
[5 empty] | Distribution Code: | V6
[5 empty] | Available Active Power Standard | http://www.eirgridgroup.com/site-files/library/EirGrid/QualityStandardforSolarfarmActivePower.pdf
Abbreviations
[6 empty] | TSO | Transmission System Operator - EirGrid
[6 empty] | EMS | Energy Management System - EirGrid
[6 empty] | DSO | Distribution System Operator - ESBN
[6 empty] | ESBN | ESB Networks
[6 empty] | ESBTS | ESB Telecoms Services
[6 empty] | RTU | Remote Terminal Unit
[6 empty] | ETIE | EirGrid Terminal Interface Enclosure
[6 empty] | NOIS | Network Operator Initiated Shutdown
[6 empty] | SG | Solar Generator
[6 empty] | CB | Circuit Breaker
[6 empty] | MEC | Maximum Export Capacity (In accordance with the User's Connection Agreement)
[6 empty] | SFPS | Solar Farm Power Station
[6 empty] | GCCT | Grid Code Compliance Testing
[6 empty] | MV | i.e. 20kV
[6 empty] | HV | i.e. 38kV / 110KV
[6 empty] | DCC | Distribution Control Centre
[6 empty] | SDCC | South Distribution Control Centre, ESBN
[6 empty] | NDCC | North Distribution Control Centre, ESBN
[6 empty] | NCC | National Control Centre, EirGrid

## DSO Required Inputs
SFPS Inputs for Signal List Development
1 | Solar Farm Power Station (SFPS) Name (including alternative names) | Customer to specify
2 | Company Name | Customer to specify
3 | Point of contact for PPM (state company in bracket) | Customer to specify
4 | SFPS Topology as per the Distribution Code DCC11.1.3.1 | Customer to specify
5 | Confirm connection point voltage | Customer to specify
6 | SFPS Maximum Export Capacity | Customer to specify
7 | SFPS Installed Capacity (for Phase developments, i.e. MEC 20MW Phase 1 10MWQ1 2014, Phase 2 additional 10MW Q2 2015 ) | Customer to specify
8 | The number of Market Units at the SFPS (Phase 1&2 is one market unit or two separate market units, noting that if the SFPS consists of two market units then additional signals will be required). | Customer to specify
9 | Generator Manufacturer | Customer to specify
10 | SFPS Design Minimum Operating Level | Customer to specify
11 | Energisation Date | Customer to specify
12 | Final Single Line Diagram (not draft for approval) including the following: (Note that for changes in SLD's, the Signal list requirements may change) | Included in submission 
| · Document Identifier and Revision Number | Included in submission 
| · Ownership boundaries (including ESBN substation name) | Included in submission 
| · Voltage levels for all switchgear | Included in submission 
| · HV CB positions at 38 kV (ESBN and SFPS as applicable) | Included in submission 
| · MV CB positions (including ESBN as applicable and all 10/20 kV circuits on SFPS side) | Included in submission 
| · MV Feeders and associated transformers | Included in submission 
13 | Number of and Height of Met Stations on site - (if PPM ≥10MW) | Customer to specify
ESBN Inputs can be obtained by ESBN Renewables Project Manager:
14 | Nearest 110kV Station - normal feeding arrangements for SFPS | Customer to specify
15 | Remote DSO Station - normal feeding arrangements for SFPS | Customer to specify
16 | For PPMs >5 MW: Is there a DSO RTU for the SFPS? | Customer to specify
Signal list inputs information to be submitted to both dsogentesting@esb.ie and generator_testing@eirgrid.com via the ESBN Customer Project Manager.

## Dual Wiring Specification
There is a requirement for the customer to wire certain signals to both the TSO and DSO RTUs.
This tab provides technical detail and diagrams regarding the wiring of such signals.
4 | Design considerations
1. Duplication of Circuit Breaker indications:
The indications shall come from a spare set of contacts on the Circuit Breakers.
Multiplier relays are not permitted
2. Duplication of TSO Remote Control Enable Switch
There shall be an extra set of contacts added to the panel switch (1x Normally Open and 1x Normally Closed)
Multiplier relays or Soft Indication of the TSO Remote Control Enable Switch from the DCS are not permitted.
3. Duplication of Blue Alert Lamp and Dispatch Fail Lamp (DFL) Schemes:
For each scheme there shall be a set of interposing relays for each leg of each command
OFF Command From NCC
ON Command From NCC
OFF Command From NDCC
ON Command From NDCC
The supply on the contact side of the interposing relays shall be broken through the TSO Remote Control Enable Switch to prevent Latching Relay toggling while the switch is in the “Off” Position
The Contacts of the interposing relays shall provide a Latch/Unlatch command to a suitable latching relay with the following contacts:
Normally Closed & Normally Open for NCC Indication
Normally Closed & Normally Open for NDCC Indication
Further Contacts for PPM/IPP controller and Panel Lamp as required by the customer. Lamp will only require 1 Normally Open indication
The Blue Alert and Dispatch Fail Lamp schemes should follow the same fundamental design, with the only differences being the lamp colour and signal names.
4. Duplication of Measurements (Analogs)
For each Analog they shall be provided with a dedicated analog output from the customer DCS
Series wiring or sharing of mA circuits is not permitted.
mA ranges and Engineering ranges are to be identical for NCC and NDCC
5 | Additional Information
See attached below for assistance:
Duplication of Circuit Breaker Indications
Duplication of TSO Dispatch Control Switch (RCES) Indication & Dispatch Fail Lamp Control & Indication
Duplication of measurement circuits

## 0) Signal List
SolarFarmName (TLC) |  | Topology | XX | XX | MW | v0.1 |  | Signals List is based on this Single Line Diagram (SLD) as inserted.
|  | RfG Type | XX
EirGrid Signals, Command & Control Specification (Ref: DCC11.6)
Signals List |  | Registered Capacity: XX MW |  |  |  | Installed Plant: XXX MW |  | MEC: XXX MW
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN | Distribution Code reference
For SFPS < 5 MW: Refer to 'Dual Wiring Specification' tab & ESB Wiring Table for instruction on Dual Wiring
| Double Point Status Indications | (each individual input identified separately for clarity) | [5 empty] | Note: Signals treated as 2-bit binary
Digital Input Signals from Sub Station to EirGrid
A1 | RemoteStationName/SolarFarmName 20 kV CB |  | open |  |  | ESBN | N/A | To be hardwired to TSO RTU
A2 | RemoteStationName/SolarFarmName 20 kV CB |  | closed |  |  | ESBN | N/A | To be hardwired to TSO RTU
A3 | SolarFarmName (TLC) T421 SFPS 20 kV CB |  | open |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A4 | SolarFarmName (TLC) T421 SFPS 20 kV CB |  | closed |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1 | Typical SLD for a Solar Farm connecting to the system through a 38/20 kV transformer
A5 | SolarFarmName (TLC) Feeder 1 20 kV CB |  | open |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A6 | SolarFarmName (TLC) Feeder 1 20 kV CB |  | closed |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A7 | SPARE SolarFarmName (TLC) Feeder 2 20 kV CB |  | open |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A8 | SPARE SolarFarmName (TLC) Feeder 2 20 kV CB |  | closed |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A9 | SPARE SolarFarmName (TLC) Feeder 3 20 kV CB |  | open |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A10 | SPARE SolarFarmName (TLC) Feeder 3 20 kV CB |  | closed |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A11 | SPARE SolarFarmName (TLC) Feeder 4 20 kV CB |  | open |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A12 | SPARE SolarFarmName (TLC) Feeder 4 20 kV CB |  | closed |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A13 | TSO Remote Control Enable Switch |  | off |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1 (Blocks all commands to SFPS equipment, located on SFPS side)
A14 | TSO Remote Control Enable Switch |  | on |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1 (Blocks all commands to SFPS equipment, located on SFPS side)
A15 | Dispatch Fail Market Command Lamp - SFPS Panel |  | off |  |  | SFPS | ESBN
A16 | Dispatch Fail Market Command Lamp - SFPS Panel |  | on |  |  | SFPS | ESBN
A17 | Blue Alert Lamp - SFPS Panel |  | off |  |  | SFPS | ESBN
A18 | Blue Alert Lamp - SFPS Panel |  | on |  |  | SFPS | ESBN
A19 | Reactive Device >5 Mvar 1 |  | off |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A20 | Reactive Device >5 Mvar 1 |  | on |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A21 | Reactive Device >5 Mvar N |  | off |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A22 | Reactive Device >5 Mvar N |  | on |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
B1 | Active Power Control facility status (feedback) |  | off |  |  | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4
B2 | Active Power Control facility status (feedback) |  | on |  |  | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
B7 | SPARE |  | off
B8 | SPARE |  | on
B9 | SPARE |  | off
B10 | SPARE |  | on
B11 | SPARE |  | off
B12 | SPARE |  | on
B13 | SPARE |  | off
B14 | SPARE |  | on
B15 | SPARE |  | off
B16 | SPARE |  | on
B17 | SPARE |  | off
B18 | SPARE |  | on
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN | Distribution Code reference
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1 (125% of Registered Cpapacity)
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1 (150% of Reactive Power at Registered Capacity)
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1 (125% of nominal conection voltage)
Analogue Input Signals from SG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1 (125% of Registered Capacity)
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4 (125% of Registered Capacity)
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-14 | % | SFPS | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Analogue SG Availability (PPMs ≥ 10 MW)
D4 | Solar Farm Availability | 0-10 | mA | 0-110 | % | SFPS | N/A | Distribution Code Signals List #3 DCC11.6.1.3
Met 1 (if Registered Capacity ≥ 10 MW)
D5 | Global Horizontal Irradiance 1 | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D6 | Diffused Horizontal Irradiance 1 | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D7 | Back Panel Temperature 1 | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D8 | Precipitation 1 | 0-10 | mA | 0-11 | mm/min | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D9 | Wind Speed 1 | 0-10 | mA | 0 to 50 | m/s | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D10 | Wind Direction 1 | 0-10 | mA | 0 to 360 | deg | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West)
D11 | Air Temperature 1 | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D12 | Air Pressure 1 | 0-10 | mA | 800-1100 | mBar | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
Met N (if Registered Capacity >= 10 MW)
D13 | Global Horizontal Irradiance N | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D14 | Diffused Horizontal Irradiance N | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D15 | Back Panel Temperature N | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D16 | Precipitation N | 0-10 | mA | 0-11 | mm/min | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D17 | Wind Speed N | 0-10 | mA | 0 to 50 | m/s | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D18 | Wind Direction N | 0-10 | mA | 0 to 360 | deg | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West)
D19 | Air Temperature N | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D20 | Air Pressure N | 0-10 | mA | 800-1100 | mBar | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D21 | SPARE
D22 | SPARE
D23 | SPARE
D24 | SPARE
D25 | SPARE
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN | Distribution Code reference
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to SG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
Digital Output Signals from EirGrid to Sub Station
F1 | Dispatch Fail Market Command Lamp - SFPS Panel |  | off | pulse | 0.5 seconds | SFPS | ESBN
F2 | Dispatch Fail Market Command Lamp - SFPS Panel |  | on | pulse | 0.5 seconds | SFPS | ESBN
F3 | Blue Alert Lamp - SFPS Panel |  | off | pulse | 0.5 seconds | SFPS | ESBN
F4 | Blue Alert Lamp - SFPS Panel |  | on | pulse | 0.5 seconds | SFPS | ESBN
F5 | SPARE |  | off
F6 | SPARE |  | on
F7 | SPARE |  | off
F8 | SPARE |  | on
Strobe Enable Pulses
Digital Output Signals from EirGrid to SG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4
E8 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
E9 | SPARE
E10 | SPARE
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | Duplicate to ESBN | Distribution Code reference
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N19 | SPARE |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N20 | SPARE |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N21 | SPARE |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N22 | SPARE |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N23 | SPARE |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N24 | SPARE |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | Duplicate to ESBN | Distribution Code reference
Analogue Output Signals from EirGrid to SG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4 (125% of Registered Capacity)
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-14 | % | SFPS | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
G3 | SPARE
G4 | SPARE
Note on D1: Administrator: Insert the Topology of the PPM
Note on E1: Administrator: Insert the Registered Capacity of the PPM
Note on A6: EirGrid Telecoms Interface Enclosure
Note on B10: Position indications required for all circuit breakers from connection point to PPM feeders
Note on B14: LV Circuit Breakers are not included. The number of feeders is checked against the SLD attached above.
Note on B22: Described as TSO remote control enable switch in DSO code.
Note on D28: Typically reactive power device breaker. Open Closed maybe more correct.
Note on E55: +/-125%
Note on E57: 110kV: 0 to 132kV 38kV: 0 to 46.2kV 33kV: 0 to 40kV 20kV: 0 to 24 kV 10kV: 0 to 12kV
Note on E60: 0-125%
Note on E61: 0-125%
Note on I70: MacManus, Colm: Distribution code modification being proposed.
Note on I126: Administrator: ESBN to provide reference to this document.
Note on E155: 0 to 125%
Registered Capacity is rounded to one decimal place, e.g 4.58 MW to 4.6 MW as per definition in Distribution Code.
MEC betwen 4.95-4.999 MW is rounded down to 4.9 MW, as per ESBN decision.

## 1a) Inst.Info & Contact Details
SolarFarmName (TLC) Information and Contact Details to be sent by SFPS via ESB Networks to EirGrid (generator_testing@EirGrid.com)
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
DATE
| HV SUB STATION NAME |  |  |  |  | ESBTS Team |  | Liam Boland
[6 empty] | Nessan Heaslip | Karl O'Keeffe | Noel Cowhey
| EirGrid Contact Person | C&T Team | PHONE: |  | (+353) 1 2370583 | Robert Groarke | Oisín Goulding
| OSP Generic Email: Generator_testing@eirgrid.com |  |  |  |  | Frank Donnelly | Colm MacManus
| EMS Generic Email: ems.services@eirgrid.com |  |  |  |  | Liam Delany | C&T Team
[6 empty] | Niall Molloy | Ciarán Maguire
| ESBTS Project Manager | ESBTS Team | PHONE: |  | (+353) 1 7027835
| ESBTS Commissioner | ESBTS Team | PHONE: |  | (+353) 1 7027835
ESBTS Generic Email: esbts.scada.services@esb.ie
| ESB Networks (SPOC) |  | PHONE:
ESB Networks Build Generic Email: IPPdelivery@esb.ie
| ESB Networks (switchgear) |  | PHONE: |  | (+ )
| ESB Networks (metering) |  | PHONE: |  | (+ )
| SFPS Project Manager |  | PHONE: |  | (+ )
| Electrical Contractor |  | PHONE: |  | (+ )
| Generator Contractor |  | PHONE: |  | (+ )
| Work Programme / Schedule (.mpp format) |  |  | Insert File
| Single Line Diagram |  |  | Insert file
| Site Layout Drawing on OS Map |  |  | Insert file
| Substation & Control Building Layout Drawing on OS Map |  |  | Insert file
| SFPS Energy Management System %error |  |  | %
| Directions including Map to the Solar Farm Power Station | Insert Map and brief description
| Safety & Site information | SFPS to provide details
ESBTS Standard Requirements from SFPS (may be customised for particular sites):
1) 90sq mm earth for Telecoms earth bar. 2) 35sq mm bonded from external earth grid to GPS clock antenna mounting bracket and if applicable Satellite antenna mounting bracket. 3) 48V DC Power System consisting of Switched Mode Power Supply (SMPS) with sealed cell battery. 4) If applicable - Fibre termination cabinet with fibre termination unit and fibre to distant station. 5) Satellite link consisting of Satellite transceiver and antenna if applicable. Satellite antenna preferably on a south facing wall with a clear view of the horizon. 6) Install and terminate process control and signal cables in ETI (the wiring schedule is available as a worksheet in the signal list excel file).
| ESB Telecom Services - Indicative Timelines for on site works | 1) 3 weeks notice required by ESBTS to schedule resources. 2) ~1 week to install the RTU cabinet with integrated ETI and GPS clock, GPS clock antenna. 3) ~1 week to pre commission the RTU referenced to frozen signal list with SFPS electrical and SG contractors. 4) ~1 week to install and commission the satellite link including antenna (if applicable). 5) ~2 days to commission the fibre link (if applicable). 6) ~1 week to commission the RTU with SFPS electrical and SG contractors.

## 1b) SFPS Wiring Completion Cert
SolarFarmName (TLC) |  | Topology | XX | XX | MW | v0.1 |  | Signals List is based on this Single Line Diagram (SLD) as inserted. | Wiring Completion Cert
|  | RfG Type | XX
EirGrid Signals, Command & Control Specification (Ref: DCC11.6) | [8 empty] | Continuity Check Complete
SFPS Wiring Completion Certificate (to EirGrid ETIE/RTU) to be sent by SFPS via ESBN to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN | Distribution Code reference
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | RemoteStationName/SolarFarmName 20 kV CB |  | open |  |  | ESBN | N/A | To be hardwired to TSO RTU
A2 | RemoteStationName/SolarFarmName 20 kV CB |  | closed |  |  | ESBN | N/A | To be hardwired to TSO RTU
A3 | SolarFarmName (TLC) T421 SFPS 20 kV CB |  | open |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A4 | SolarFarmName (TLC) T421 SFPS 20 kV CB |  | closed |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A5 | SolarFarmName (TLC) Feeder 1 20 kV CB |  | open |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A6 | SolarFarmName (TLC) Feeder 1 20 kV CB |  | closed |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A7 | SPARE SolarFarmName (TLC) Feeder 2 20 kV CB |  | open |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A8 | SPARE SolarFarmName (TLC) Feeder 2 20 kV CB |  | closed |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A9 | SPARE SolarFarmName (TLC) Feeder 3 20 kV CB |  | open |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A10 | SPARE SolarFarmName (TLC) Feeder 3 20 kV CB |  | closed |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A11 | SPARE SolarFarmName (TLC) Feeder 4 20 kV CB |  | open |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A12 | SPARE SolarFarmName (TLC) Feeder 4 20 kV CB |  | closed |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A13 | TSO Remote Control Enable Switch |  | off |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1 (Blocks all commands to SFPS equipment, located on SFPS side)
A14 | TSO Remote Control Enable Switch |  | on |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1 (Blocks all commands to SFPS equipment, located on SFPS side)
A15 | Dispatch Fail Market Command Lamp - SFPS Panel |  | off |  |  | SFPS | ESBN
A16 | Dispatch Fail Market Command Lamp - SFPS Panel |  | on |  |  | SFPS | ESBN
A17 | Blue Alert Lamp - SFPS Panel |  | off |  |  | SFPS | ESBN
A18 | Blue Alert Lamp - SFPS Panel |  | on |  |  | SFPS | ESBN
A19 | Reactive Device >5 Mvar 1 |  | off |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A20 | Reactive Device >5 Mvar 1 |  | on |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A21 | Reactive Device >5 Mvar N |  | off |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
A22 | Reactive Device >5 Mvar N |  | on |  |  | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1
B1 | Active Power Control facility status (feedback) |  | off |  |  | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4
B2 | Active Power Control facility status (feedback) |  | on |  |  | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
B9 | SPARE |  | off
B10 | SPARE |  | on
B11 | SPARE |  | off
B12 | SPARE |  | on
B13 | SPARE |  | off
B14 | SPARE |  | on
B15 | SPARE |  | off
B16 | SPARE |  | on
B17 | SPARE |  | off
B18 | SPARE |  | on
| SPARE |  | off
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN | Distribution Code reference
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1 (125% of Registered Cpapacity)
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1 (150% of Reactive Power at Registered Capacity)
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1 (125% of nominal conection voltage)
Analogue Input Signals from SG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | SFPS | ESBN | Distribution Code Signals List #1 DCC11.6.1.1 (125% of Registered Capacity)
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4 (125% of Registered Capacity)
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-14 | % | SFPS | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Analogue SG Availability (PPMs ≥ 10 MW)
D4 | Solar Farm Availability | 0-10 | mA | 0-110 | % | SFPS | N/A | Distribution Code Signals List #3 DCC11.6.1.3
D5 | Global Horizontal Irradiance 1 | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D6 | Diffused Horizontal Irradiance 1 | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D7 | Back Panel Temperature 1 | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D8 | Precipitation 1 | 0-10 | mA | 0-11 | mm/min | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D9 | Wind Speed 1 | 0-10 | mA | 0 to 50 | m/s | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D10 | Wind Direction 1 | 0-10 | mA | 0 to 360 | deg | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West)
D11 | Air Temperature 1 | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D12 | Air Pressure 1 | 0-10 | mA | 800-1100 | mBar | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
Met N (if Registered Capacity >= 10 MW)
| Global Horizontal Irradiance N | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D13 | Global Horizontal Irradiance N | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D14 | Diffused Horizontal Irradiance N | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D15 | Back Panel Temperature N | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D16 | Precipitation N | 0-10 | mA | 0-11 | mm/min | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D17 | Wind Speed N | 0-10 | mA | 0 to 50 | m/s | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D18 | Wind Direction N | 0-10 | mA | 0 to 360 | deg | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West)
D19 | Air Temperature N | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D20 | Air Pressure N | 0-10 | mA | 800-1100 | mBar | SFPS | N/A | Distribution Code Signals List #6 DCC11.6.1.6
D21 | SPARE
D25 | SPARE
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN | Distribution Code reference
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to SG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #5 DCC11.6.1.5
Digital Output Signals from EirGrid to Sub Station
F1 | Dispatch Fail Market Command Lamp - SFPS Panel |  | off | pulse | 0.5 seconds | SFPS | ESBN
F2 | Dispatch Fail Market Command Lamp - SFPS Panel |  | on | pulse | 0.5 seconds | SFPS | ESBN
F3 | Blue Alert Lamp - SFPS Panel |  | off | pulse | 0.5 seconds | SFPS | ESBN
F4 | Blue Alert Lamp - SFPS Panel |  | on | pulse | 0.5 seconds | SFPS | ESBN
F8 | SPARE |  | on
Strobe Enable Pulses
Digital Output Signals from EirGrid to SG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4
E8 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | SFPS | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | Duplicate to ESBN | Distribution Code reference
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
N24 | SPARE |  |  |  |  | SFPS | ESBN | ESBN to specify Alarm type to SFPS. (not required if DSO RTU is installed)
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | Duplicate to ESBN | Distribution Code reference
Analogue Output Signals from EirGrid to SG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | SFPS | N/A | Distribution Code Signals List #4 DCC11.6.1.4 (125% of Registered Capacity)
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-14 | % | SFPS | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
G3 | SPARE
G4 | SPARE
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet must be clearly marked with labels for identification. |  |  |  | Confirmed  |  |  |  | How are each of the MET signals generated? E.g. From a MET mast or SGs
All analogue and digital interface signals must be tested and simulated for compliance with the frozen signal list agreed by all parties. |  |  |  | Confirmed  |  |  |  | Global Horizontal Irradiance
Diffused Horizontal Irradiance
Back Panel Temperature
Precipitation
Wind Speed
Wind Direction
ESBTS Satellite Dish bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed  |  |  |  | Air Temperature
Air Pressure
ESBTS GPS clock antenna bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed 
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 | [6 empty] | SFPS Name / Position | 0
SFPS Signature
Date
Note on A4: Administrator: To be completed by the IPP and sent to EirGrid to schedule ESBTS site attendance to perform continuity check
Note on A6: EirGrid Telecoms Interface Enclosure

## 2) ESB Telecoms Completion Cert
SolarFarmName (TLC) |  | Topology | XX | XX | MW | v0.1 |  | Completion Cert
|  | RfG Type | XX
EirGrid Signals, Command & Control Specification (Ref: DCC11.6) | [7 empty] | Local SCADA Checks/Tests
ESB Telecoms Completion Cert to be sent by ESB Telecoms Services to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | RemoteStationName/SolarFarmName 20 kV CB |  | open |  |  | ESBN | N/A
A2 | RemoteStationName/SolarFarmName 20 kV CB |  | closed |  |  | ESBN | N/A
A3 | SolarFarmName (TLC) T421 SFPS 20 kV CB |  | open |  |  | SFPS | ESBN
A4 | SolarFarmName (TLC) T421 SFPS 20 kV CB |  | closed |  |  | SFPS | ESBN
A5 | SolarFarmName (TLC) Feeder 1 20 kV CB |  | open |  |  | SFPS | ESBN
A6 | SolarFarmName (TLC) Feeder 1 20 kV CB |  | closed |  |  | SFPS | ESBN
A7 | SPARE SolarFarmName (TLC) Feeder 2 20 kV CB |  | open |  |  | SFPS | ESBN
A8 | SPARE SolarFarmName (TLC) Feeder 2 20 kV CB |  | closed |  |  | SFPS | ESBN
A9 | SPARE SolarFarmName (TLC) Feeder 3 20 kV CB |  | open |  |  | SFPS | ESBN
A10 | SPARE SolarFarmName (TLC) Feeder 3 20 kV CB |  | closed |  |  | SFPS | ESBN
A11 | SPARE SolarFarmName (TLC) Feeder 4 20 kV CB |  | open |  |  | SFPS | ESBN
A12 | SPARE SolarFarmName (TLC) Feeder 4 20 kV CB |  | closed |  |  | SFPS | ESBN
A13 | TSO Remote Control Enable Switch |  | off |  |  | SFPS | ESBN
A14 | TSO Remote Control Enable Switch |  | on |  |  | SFPS | ESBN
A15 | Dispatch Fail Market Command Lamp - SFPS Panel |  | off |  |  | SFPS | ESBN
A16 | Dispatch Fail Market Command Lamp - SFPS Panel |  | on |  |  | SFPS | ESBN
A17 | Blue Alert Lamp - SFPS Panel |  | off |  |  | SFPS | ESBN
A18 | Blue Alert Lamp - SFPS Panel |  | on |  |  | SFPS | ESBN
A19 | Reactive Device >5 Mvar 1 |  | off |  |  | SFPS | ESBN
A20 | Reactive Device >5 Mvar 1 |  | on |  |  | SFPS | ESBN
A21 | Reactive Device >5 Mvar N |  | off |  |  | SFPS | ESBN
A22 | Reactive Device >5 Mvar N |  | on |  |  | SFPS | ESBN
B1 | Active Power Control facility status (feedback) |  | off |  |  | SFPS | N/A
B2 | Active Power Control facility status (feedback) |  | on |  |  | SFPS | N/A
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | SFPS | N/A
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | SFPS | N/A
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | SFPS | N/A
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | SFPS | N/A
B7 | SPARE |  | off
B8 | SPARE |  | on
B9 | SPARE |  | off
B10 | SPARE |  | on
B11 | SPARE |  | off
B12 | SPARE |  | on
B13 | SPARE |  | off
B14 | SPARE |  | on
B15 | SPARE |  | off
B16 | SPARE |  | on
B17 | SPARE |  | off
B18 | SPARE |  | on
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | SFPS | ESBN
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | SFPS | ESBN
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | SFPS | ESBN
Analogue Input Signals from SG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | SFPS | ESBN
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | SFPS | N/A
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-14 | % | SFPS | N/A
Analogue SG Availability (PPMs ≥ 10 MW)
D4 | Solar Farm Availability | 0-10 | mA | 0-110 | % | SFPS | N/A
D5 | Global Horizontal Irradiance 1 | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A
D6 | Diffused Horizontal Irradiance 1 | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A
D7 | Back Panel Temperature 1 | 0-10 | mA | -30 to +50 | C | SFPS | N/A
D8 | Precipitation 1 | 0-10 | mA | 0-11 | mm/min | SFPS | N/A
D9 | Wind Speed 1 | 0-10 | mA | 0 to 50 | m/s | SFPS | N/A
D10 | Wind Direction 1 | 0-10 | mA | 0 to 360 | deg | SFPS | N/A
D11 | Air Temperature 1 | 0-10 | mA | -30 to +50 | C | SFPS | N/A
D12 | Air Pressure 1 | 0-10 | mA | 800-1100 | mBar | SFPS | N/A
Met N (if Registered Capacity >= 10 MW)
D13 | Global Horizontal Irradiance N | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A
D14 | Diffused Horizontal Irradiance N | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A
D15 | Back Panel Temperature N | 0-10 | mA | -30 to +50 | C | SFPS | N/A
D16 | Precipitation N | 0-10 | mA | 0-11 | mm/min | SFPS | N/A
D17 | Wind Speed N | 0-10 | mA | 0 to 50 | m/s | SFPS | N/A
D18 | Wind Direction N | 0-10 | mA | 0 to 360 | deg | SFPS | N/A
D19 | Air Temperature N | 0-10 | mA | -30 to +50 | C | SFPS | N/A
D20 | Air Pressure N | 0-10 | mA | 800-1100 | mBar | SFPS | N/A
D21 | SPARE
D25 | SPARE
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to SG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | SFPS | N/A
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | SFPS | N/A
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | SFPS | N/A
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | SFPS | N/A
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | SFPS | N/A
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | SFPS | N/A
Digital Output Signals from EirGrid to Sub Station
F1 | Dispatch Fail Market Command Lamp - SFPS Panel |  | off | pulse | 0.5 seconds | SFPS | ESBN
F2 | Dispatch Fail Market Command Lamp - SFPS Panel |  | on | pulse | 0.5 seconds | SFPS | ESBN
F3 | Blue Alert Lamp - SFPS Panel |  | off | pulse | 0.5 seconds | SFPS | ESBN
F4 | Blue Alert Lamp - SFPS Panel |  | on | pulse | 0.5 seconds | SFPS | ESBN
F8 | SPARE |  | on
Strobe Enable Pulses
Digital Output Signals from EirGrid to SG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | SFPS | N/A
E8 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | SFPS | N/A
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | Duplicate to ESBN
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | SFPS | ESBN
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | SFPS | ESBN
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | SFPS | ESBN
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | SFPS | ESBN
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | SFPS | ESBN
N24 | SPARE |  |  |  |  | SFPS | ESBN
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | Duplicate to ESBN
Analogue Output Signals from EirGrid to SG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | SFPS | N/A
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-14 | % | SFPS | N/A
G3 | SPARE
G4 | SPARE
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet are installed and correct. |  |  |  | Confirmed  |  |  | ESBTS Name / Position | ESBTS Team
ESBTS Signature
Date
| NOTE: Non operable SFPS signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  | Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
Note on A6: EirGrid Telecoms Interface Enclosure

## 2 a) EMS Database Setup Cert
SolarFarmName (TLC) |  | Topology | XX | XX | MW | v0.1
|  | RfG Type | XX
EirGrid Signals, Command & Control Specification (Ref: DCC11.6)
Energy Management System (EMS) Database setup Certificate
Completion Cert
Continuity Check Complete
Generator Modelled
Lines Modelled
Station Modelled
Calculations Updated
RTU Modelled
Display Work Completed:
SF SLD
Station SLD
Station List
Solarfarm List
Embedded Solar
Solarfarm Control
Station Solar MW
Solar Overview
Solarfarm Availability Data
Blue Alert Page
Solarfarm Weather Data
DCC signals provided via ICCP
EMS Name
EMS Signature
Date
EirGrid Internal Document - no IPP requirements. For Information only
Note on A4: Administrator: DCC to be Informed

## 3)Pre Energ. Sign&Con Test Cert
SolarFarmName (TLC) |  | Topology | XX | XX | MW | v0.1 |  | Pre Energisation Signals and Controls Test
|  | RfG Type | XX
EirGrid Signals, Command & Control Specification (Ref: DCC11.6) | [7 empty] | Simulated □/Real □ value tested | mA Range | Value Range | Comment
Pre Energisation Signals & Controls Certificate to be sent by ESBT to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | RemoteStationName/SolarFarmName 20 kV CB |  | open |  |  | ESBN | N/A | Real □
A2 | RemoteStationName/SolarFarmName 20 kV CB |  | closed |  |  | ESBN | N/A | Real □
A3 | SolarFarmName (TLC) T421 SFPS 20 kV CB |  | open |  |  | SFPS | ESBN | Real □
A4 | SolarFarmName (TLC) T421 SFPS 20 kV CB |  | closed |  |  | SFPS | ESBN | Real □
A5 | SolarFarmName (TLC) Feeder 1 20 kV CB |  | open |  |  | SFPS | ESBN | Real □
A6 | SolarFarmName (TLC) Feeder 1 20 kV CB |  | closed |  |  | SFPS | ESBN | Real □
A7 | SPARE SolarFarmName (TLC) Feeder 2 20 kV CB |  | open |  |  | SFPS | ESBN | Real □
A8 | SPARE SolarFarmName (TLC) Feeder 2 20 kV CB |  | closed |  |  | SFPS | ESBN | Real □
A9 | SPARE SolarFarmName (TLC) Feeder 3 20 kV CB |  | open |  |  | SFPS | ESBN | Real □
A10 | SPARE SolarFarmName (TLC) Feeder 3 20 kV CB |  | closed |  |  | SFPS | ESBN | Real □
A11 | SPARE SolarFarmName (TLC) Feeder 4 20 kV CB |  | open |  |  | SFPS | ESBN | Real □
A12 | SPARE SolarFarmName (TLC) Feeder 4 20 kV CB |  | closed |  |  | SFPS | ESBN | Real □
A13 | TSO Remote Control Enable Switch |  | off |  |  | SFPS | ESBN | Real □
A14 | TSO Remote Control Enable Switch |  | on |  |  | SFPS | ESBN | Real □
A15 | Dispatch Fail Market Command Lamp - SFPS Panel |  | off |  |  | SFPS | ESBN | Real □
A16 | Dispatch Fail Market Command Lamp - SFPS Panel |  | on |  |  | SFPS | ESBN | Real □
A17 | Blue Alert Lamp - SFPS Panel |  | off |  |  | SFPS | ESBN | Real □
A18 | Blue Alert Lamp - SFPS Panel |  | on |  |  | SFPS | ESBN | Real □
A19 | Reactive Device >5 Mvar 1 |  | off |  |  | SFPS | ESBN | Real □
A20 | Reactive Device >5 Mvar 1 |  | on |  |  | SFPS | ESBN | Real □
A21 | Reactive Device >5 Mvar N |  | off |  |  | SFPS | ESBN | Real □
A22 | Reactive Device >5 Mvar N |  | on |  |  | SFPS | ESBN | Real □
B1 | Active Power Control facility status (feedback) |  | off |  |  | SFPS | N/A | Simulated □
B2 | Active Power Control facility status (feedback) |  | on |  |  | SFPS | N/A | Simulated □
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | SFPS | N/A | Simulated □
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | SFPS | N/A | Simulated □
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | SFPS | N/A | Simulated □
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | SFPS | N/A | Simulated □
B7 | SPARE |  | off |  |  |  |  | Simulated □
B8 | SPARE |  | on |  |  |  |  | Simulated □
B9 | SPARE |  | off |  |  |  |  | Simulated □
B10 | SPARE |  | on |  |  |  |  | Simulated □
B11 | SPARE |  | off |  |  |  |  | Simulated □
B12 | SPARE |  | on |  |  |  |  | Simulated □
B13 | SPARE |  | off |  |  |  |  | Simulated □
B14 | SPARE |  | on |  |  |  |  | Simulated □
B15 | SPARE |  | off |  |  |  |  | Simulated □
B16 | SPARE |  | on |  |  |  |  | Simulated □
B17 | SPARE |  | off |  |  |  |  | Simulated □
B18 | SPARE |  | on |  |  |  |  | Simulated □
Simulated □
Simulated □
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | SFPS | ESBN | Real □
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | SFPS | ESBN | Real □
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | SFPS | ESBN | Real □
Analogue Input Signals from SG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | SFPS | ESBN | Simulated □
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | SFPS | N/A | Simulated □
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-14 | % | SFPS | N/A | Simulated □
Analogue SG Availability (PPMs ≥ 10 MW)
D4 | Solar Farm Availability | 0-10 | mA | 0-110 | % | SFPS | N/A | Simulated □
D5 | Global Horizontal Irradiance 1 | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Simulated □
D6 | Diffused Horizontal Irradiance 1 | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Simulated □
D7 | Back Panel Temperature 1 | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Simulated □
D8 | Precipitation 1 | 0-10 | mA | 0-11 | mm/min | SFPS | N/A | Simulated □
D9 | Wind Speed 1 | 0-10 | mA | 0 to 50 | m/s | SFPS | N/A | Simulated □
D10 | Wind Direction 1 | 0-10 | mA | 0 to 360 | deg | SFPS | N/A | Simulated □
D11 | Air Temperature 1 | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Simulated □
D12 | Air Pressure 1 | 0-10 | mA | 800-1100 | mBar | SFPS | N/A | Simulated □
Simulated □
Met N (if Registered Capacity >= 10 MW)
D13 | Global Horizontal Irradiance N | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A
D14 | Diffused Horizontal Irradiance N | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Simulated □
D15 | Back Panel Temperature N | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Simulated □
D16 | Precipitation N | 0-10 | mA | 0-11 | mm/min | SFPS | N/A | Simulated □
D17 | Wind Speed N | 0-10 | mA | 0 to 50 | m/s | SFPS | N/A | Simulated □
D18 | Wind Direction N | 0-10 | mA | 0 to 360 | deg | SFPS | N/A | Simulated □
D19 | Air Temperature N | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Simulated □
D20 | Air Pressure N | 0-10 | mA | 800-1100 | mBar | SFPS | N/A | Simulated □
D21 | SPARE | [6 empty] | Simulated □
D25 | SPARE | [6 empty] | Simulated □
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to SG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | SFPS | N/A | Simulated □
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | SFPS | N/A | Simulated □
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | SFPS | N/A | Simulated □
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | SFPS | N/A | Simulated □
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | SFPS | N/A | Simulated □
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | SFPS | N/A | Simulated □
Digital Output Signals from EirGrid to Sub Station
F1 | Dispatch Fail Market Command Lamp - SFPS Panel |  | off | pulse | 0.5 seconds | SFPS | ESBN | Simulated □
F2 | Dispatch Fail Market Command Lamp - SFPS Panel |  | on | pulse | 0.5 seconds | SFPS | ESBN | Simulated □
F3 | Blue Alert Lamp - SFPS Panel |  | off | pulse | 0.5 seconds | SFPS | ESBN | Simulated □
F4 | Blue Alert Lamp - SFPS Panel |  | on | pulse | 0.5 seconds | SFPS | ESBN | Simulated □
F8 | SPARE |  | on
Strobe Enable Pulses
Digital Output Signals from EirGrid to SG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | SFPS | N/A | Simulated □
E8 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | SFPS | N/A | Simulated □
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | Duplicate to ESBN
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN | Simulated □
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN | Simulated □
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN | Simulated □
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN | Simulated □
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN | Simulated □
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN | Simulated □
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN | Simulated □
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN | Simulated □
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN | Simulated □
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN | Simulated □
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN | Simulated □
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN | Simulated □
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN | Simulated □
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | SFPS | ESBN | Simulated □
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | SFPS | ESBN | Simulated □
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | SFPS | ESBN | Simulated □
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | SFPS | ESBN | Simulated □
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | SFPS | ESBN | Simulated □
N24 | SPARE |  |  |  |  | SFPS | ESBN
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | Duplicate to ESBN
Analogue Output Signals from EirGrid to SG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | SFPS | N/A | Simulated □
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-14 | % | SFPS | N/A | Simulated □
G3 | SPARE
G4 | SPARE
Simulation Point
Simulation Method
[6 empty] | SFPS Name / Position |  | 0
SFPS Signature
EMS Name
EMS Signature
| NOTE: Non operable SFPS signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  |  |  |  | ESB Telecoms Name / Position |  | ESBTS Team
| Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 |  |  |  |  | ESB Telecoms Signature
Date
Note on I1: Administrator: ESBTS Commission from NCC control desk to / via ETI to IPP plant.
Note on I3: Administrator: the electrical characteristics of IPP signals not tested due to plant unavailability must be simulated by IPP.
Note on A6: EirGrid Telecoms Interface Enclosure

## 4) Post Ener Pre Grid Code Cert
SolarFarmName (TLC) |  | Topology | XX | XX | MW | v0.1 |  | Post Energisation Signals and Controls Test
|  | RfG Type | XX
EirGrid Signals, Command & Control Specification (Ref: DCC11.6) | [7 empty] | Simulated □/Real □ value tested | mA Range | Value Range | Comment
Post Energisation Pre Grid Code Cert to be provided by ESBT to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | RemoteStationName/SolarFarmName 20 kV CB |  | open |  |  | ESBN | N/A | Real □
A2 | RemoteStationName/SolarFarmName 20 kV CB |  | closed |  |  | ESBN | N/A | Real □
A3 | SolarFarmName (TLC) T421 SFPS 20 kV CB |  | open |  |  | SFPS | ESBN | Real □
A4 | SolarFarmName (TLC) T421 SFPS 20 kV CB |  | closed |  |  | SFPS | ESBN | Real □
A5 | SolarFarmName (TLC) Feeder 1 20 kV CB |  | open |  |  | SFPS | ESBN | Real □
A6 | SolarFarmName (TLC) Feeder 1 20 kV CB |  | closed |  |  | SFPS | ESBN | Real □
A7 | SPARE SolarFarmName (TLC) Feeder 2 20 kV CB |  | open |  |  | SFPS | ESBN | Real □
A8 | SPARE SolarFarmName (TLC) Feeder 2 20 kV CB |  | closed |  |  | SFPS | ESBN | Real □
A9 | SPARE SolarFarmName (TLC) Feeder 3 20 kV CB |  | open |  |  | SFPS | ESBN | Real □
A10 | SPARE SolarFarmName (TLC) Feeder 3 20 kV CB |  | closed |  |  | SFPS | ESBN | Real □
A11 | SPARE SolarFarmName (TLC) Feeder 4 20 kV CB |  | open |  |  | SFPS | ESBN | Real □
A12 | SPARE SolarFarmName (TLC) Feeder 4 20 kV CB |  | closed |  |  | SFPS | ESBN | Real □
A13 | TSO Remote Control Enable Switch |  | off |  |  | SFPS | ESBN | Real □
A14 | TSO Remote Control Enable Switch |  | on |  |  | SFPS | ESBN | Real □
A15 | Dispatch Fail Market Command Lamp - SFPS Panel |  | off |  |  | SFPS | ESBN | Real □
A16 | Dispatch Fail Market Command Lamp - SFPS Panel |  | on |  |  | SFPS | ESBN | Real □
A17 | Blue Alert Lamp - SFPS Panel |  | off |  |  | SFPS | ESBN | Real □
A18 | Blue Alert Lamp - SFPS Panel |  | on |  |  | SFPS | ESBN | Real □
A19 | Reactive Device >5 Mvar 1 |  | off |  |  | SFPS | ESBN | Real □
A20 | Reactive Device >5 Mvar 1 |  | on |  |  | SFPS | ESBN | Real □
A21 | Reactive Device >5 Mvar N |  | off |  |  | SFPS | ESBN | Real □
A22 | Reactive Device >5 Mvar N |  | on |  |  | SFPS | ESBN | Real □
B1 | Active Power Control facility status (feedback) |  | off |  |  | SFPS | N/A | Real □
B2 | Active Power Control facility status (feedback) |  | on |  |  | SFPS | N/A | Real □
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | SFPS | N/A | Real □
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | SFPS | N/A | Real □
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | SFPS | N/A | Real □
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | SFPS | N/A | Real □
B7 | SPARE |  | off |  |  |  |  | Real □
B8 | SPARE |  | on |  |  |  |  | Real □
B9 | SPARE |  | off |  |  |  |  | Real □
B10 | SPARE |  | on |  |  |  |  | Real □
B11 | SPARE |  | off |  |  |  |  | Real □
B12 | SPARE |  | on |  |  |  |  | Real □
B13 | SPARE |  | off |  |  |  |  | Real □
B14 | SPARE |  | on |  |  |  |  | Real □
B15 | SPARE |  | off |  |  |  |  | Real □
B16 | SPARE |  | on |  |  |  |  | Real □
B17 | SPARE |  | off |  |  |  |  | Real □
B18 | SPARE |  | on |  |  |  |  | Real □
Real □
Real □
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | SFPS | ESBN | Real □
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | SFPS | ESBN | Real □
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | SFPS | ESBN | Real □
Analogue Input Signals from SG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | SFPS | ESBN | Real □
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | SFPS | N/A | Real □
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-14 | % | SFPS | N/A
Analogue SG Availability (PPMs ≥ 10 MW)
D4 | Solar Farm Availability | 0-10 | mA | 0-110 | % | SFPS | N/A | Real □
D5 | Global Horizontal Irradiance 1 | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Real □
D6 | Diffused Horizontal Irradiance 1 | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Real □
D7 | Back Panel Temperature 1 | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Real □
D8 | Precipitation 1 | 0-10 | mA | 0-11 | mm/min | SFPS | N/A | Real □
D9 | Wind Speed 1 | 0-10 | mA | 0 to 50 | m/s | SFPS | N/A | Real □
D10 | Wind Direction 1 | 0-10 | mA | 0 to 360 | deg | SFPS | N/A | Real □
D11 | Air Temperature 1 | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Real □
D12 | Air Pressure 1 | 0-10 | mA | 800-1100 | mBar | SFPS | N/A | Real □
Real □
Met N (if Registered Capacity >= 10 MW)
D13 | Global Horizontal Irradiance N | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A
D14 | Diffused Horizontal Irradiance N | 0-10 | mA | 0-4000 | W/m2 | SFPS | N/A | Real □
D15 | Back Panel Temperature N | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Real □
D16 | Precipitation N | 0-10 | mA | 0-11 | mm/min | SFPS | N/A | Real □
D17 | Wind Speed N | 0-10 | mA | 0 to 50 | m/s | SFPS | N/A | Real □
D18 | Wind Direction N | 0-10 | mA | 0 to 360 | deg | SFPS | N/A | Real □
D19 | Air Temperature N | 0-10 | mA | -30 to +50 | C | SFPS | N/A | Real □
D20 | Air Pressure N | 0-10 | mA | 800-1100 | mBar | SFPS | N/A | Real □
D21 | SPARE | [6 empty] | Real □
D25 | SPARE | [6 empty] | Real □
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | Duplicate to ESBN
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to SG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | SFPS | N/A | Real □
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | SFPS | N/A | Real □
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | SFPS | N/A | Real □
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | SFPS | N/A | Real □
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | SFPS | N/A | Real □
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | SFPS | N/A | Real □
Digital Output Signals from EirGrid to Sub Station
F1 | Dispatch Fail Market Command Lamp - SFPS Panel |  | off | pulse | 0.5 seconds | SFPS | ESBN | Real □
F2 | Dispatch Fail Market Command Lamp - SFPS Panel |  | on | pulse | 0.5 seconds | SFPS | ESBN | Real □
F3 | Blue Alert Lamp - SFPS Panel |  | off | pulse | 0.5 seconds | SFPS | ESBN | Real □
F4 | Blue Alert Lamp - SFPS Panel |  | on | pulse | 0.5 seconds | SFPS | ESBN | Real □
F8 | SPARE |  | on
Strobe Enable Pulses
Digital Output Signals from EirGrid to SG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | SFPS | N/A | Real □
E8 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | SFPS | N/A | Real □
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | Duplicate to ESBN
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | SFPS | ESBN | Real / Point Tested □
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | SFPS | ESBN | Real / Point Tested □
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | SFPS | ESBN | Real / Point Tested □
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | SFPS | ESBN | Real / Point Tested □
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | SFPS | ESBN | Real / Point Tested □
N24 | SPARE |  |  |  |  | SFPS | ESBN
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | Duplicate to ESBN
Analogue Output Signals from EirGrid to SG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | SFPS | N/A | Real □
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-14 | % | SFPS | N/A | Real □
G3 | SPARE | [6 empty] | Real □
G4 | SPARE | [6 empty] | Real □
Confirm the source of the MET signals e.g. from MET mast or from SGs
| Global Horizontal Irradiance |  |  |  |  | SFPS Name |  | 0
Diffused Horizontal Irradiance
Back Panel Temperature
Precipitation
Wind Speed
| Wind Direction |  |  |  |  | SFPS Signature
| Air Temperature |  |  |  |  | EMS Name
| Air Pressure |  |  |  |  | EMS Signature
| NOTE: Non operable SFPS signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  |  |  |  | ESB Telecoms Name / Position |  | ESBTS Team
| Note: That for the duration of the Post Energization Test, there should be NO external influencing factors |  |  |  |  | ESB Telecoms Signature
| Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 |  |  |  |  | Date
Note on A6: EirGrid Telecoms Interface Enclosure

## RTU ETI Layout
Terminal Designations | Description
X0: | Indication and Alarm Positive
X1: | Double Digital Inputs (Indications)
X2: | Single Digital Inputs
X3: | Analogue Inputs
X4: | Analogue Outputs
X5: | Double Digital Outputs (ON/OFF Commands)
X6: | Single Digital Outputs (ON Commands)
X7: | Strobe Pulses (Setpoint Enable Pulses)
ETI Reference | Description |  | Reference
N/A | Indication and Alarm Positives |  | X0:1
N/A | Indication and Alarm Positives |  | X0:2
N/A | Indication and Alarm Positives |  | X0:3
N/A | Indication and Alarm Positives |  | X0:4
Note: Indications Descriptions shaded in Blue are reserved for these locations
Double Digital Inputs (Indications)
ETI Reference | Description | Status | Reference
A1 | RemoteStationName/SolarFarmName 20 kV CB | open | X1:1
A2 | RemoteStationName/SolarFarmName 20 kV CB | closed | X1:2
A3 | SolarFarmName (TLC) T421 SFPS 20 kV CB | open | X1:3
A4 | SolarFarmName (TLC) T421 SFPS 20 kV CB | closed | X1:4
A5 | SolarFarmName (TLC) Feeder 1 20 kV CB | open | X1:5
A6 | SolarFarmName (TLC) Feeder 1 20 kV CB | closed | X1:6
A7 | SPARE SolarFarmName (TLC) Feeder 2 20 kV CB | open | X1:7
A8 | SPARE SolarFarmName (TLC) Feeder 2 20 kV CB | closed | X1:8
A9 | SPARE SolarFarmName (TLC) Feeder 3 20 kV CB | open | X1:9
A10 | SPARE SolarFarmName (TLC) Feeder 3 20 kV CB | closed | X1:10
A11 | SPARE SolarFarmName (TLC) Feeder 4 20 kV CB | open | X1:11
A12 | SPARE SolarFarmName (TLC) Feeder 4 20 kV CB | closed | X1:12
A13 | TSO Remote Control Enable Switch | off | X1:13
A14 | TSO Remote Control Enable Switch | on | X1:14
A15 | Dispatch Fail Market Command Lamp - SFPS Panel | off | X1:15
A16 | Dispatch Fail Market Command Lamp - SFPS Panel | on | X1:16
A17 | Blue Alert Lamp - SFPS Panel | off | X1:17
A18 | Blue Alert Lamp - SFPS Panel | on | X1:18
A19 | Reactive Device >5 Mvar 1 | off | X1:19
A20 | Reactive Device >5 Mvar 1 | on | X1:20
A21 | Reactive Device >5 Mvar N | off | X1:21
A22 | Reactive Device >5 Mvar N | on | X1:22
B1 | Active Power Control facility status (feedback) | off | X1:23
B2 | Active Power Control facility status (feedback) | on | X1:24
B3 | Frequency Response System Mode Status (feedback) | off | X1:25
B4 | Frequency Response System Mode Status (feedback) | on | X1:26
B5 | Frequency Response Curve (feedback) | Curve 1 | X1:27
B6 | Frequency Response Curve (feedback) | Curve 2 | X1:28
B7 | SPARE | off | X1:29
B8 | SPARE | on | X1:30
B9 | SPARE | off | X1:31
B10 | SPARE | on | X1:32
B11 | SPARE | off | X1:33
B12 | SPARE | on | X1:34
B13 | SPARE | off | X1:35
B14 | SPARE | on | X1:36
B15 | SPARE | off | X1:37
B16 | SPARE | on | X1:38
B17 | SPARE | off | X1:39
B18 | SPARE | on | X1:40
Single Digital Inputs (Alarms)
ETI Reference | Description |  | Reference
N1 | ESBN Alarm 1 |  | X2:1
N2 | ESBN Alarm 2 |  | X2:2
N3 | ESBN Alarm 3 |  | X2:3
N4 | ESBN Alarm 4 |  | X2:4
N5 | ESBN Alarm 5 |  | X2:5
N6 | ESBN Alarm 6 |  | X2:6
N7 | ESBN Alarm 7 |  | X2:7
N8 | ESBN Alarm 8 |  | X2:8
N9 | ESBN Alarm 9 |  | X2:9
N10 | ESBN Alarm 10 |  | X2:10
N11 | ESBN Alarm 11 |  | X2:11
N12 | ESBN Alarm 12 |  | X2:12
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  | X2:13
N14 | ESBN Alarm 14 (AC FAIL) |  | X2:14
N15 | ESBN Alarm 15 (G10 protection trip) |  | X2:15
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  | X2:16
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  | X2:17
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  | X2:18
N19 | SPARE |  | X2:19
N20 | SPARE |  | X2:20
N21 | SPARE |  | X2:21
N22 | SPARE |  | X2:22
N23 | SPARE |  | X2:23
N24 | SPARE |  | X2:24
Analogue Inputs
ETI Reference | Description |  | Reference
C1 | Active Power Output at Connection Point | + | X3:1
C1 | Active Power Output at Connection Point | - | X3:2
C2 | Reactive Power at Connection Point | + | X3:3
C2 | Reactive Power at Connection Point | - | X3:4
C3 | Voltage at Connection Point | + | X3:5
C3 | Voltage at Connection Point | - | X3:6
D1 | Available Active Power | + | X3:7
D1 | Available Active Power | - | X3:8
D2 | Active Power Control Setpoint (feedback) | + | X3:9
D2 | Active Power Control Setpoint (feedback) | - | X3:10
D3 | Frequency Droop Setting (feedback) | + | X3:11
D3 | Frequency Droop Setting (feedback) | - | X3:12
D5 | Global Horizontal Irradiance 1 | + | X3:13
D5 | Global Horizontal Irradiance 1 | - | X3:14
D6 | Diffused Horizontal Irradiance 1 | + | X3:15
D6 | Diffused Horizontal Irradiance 1 | - | X3:16
D7 | Back Panel Temperature 1 | + | X3:17
D7 | Back Panel Temperature 1 | - | X3:18
D8 | Precipitation 1 | + | X3:19
D8 | Precipitation 1 | - | X3:20
D9 | Wind Speed 1 | + | X3:21
D9 | Wind Speed 1 | - | X3:22
D10 | Wind Direction 1 | + | X3:23
D10 | Wind Direction 1 | - | X3:24
D11 | Air Temperature 1 | + | X3:25
D11 | Air Temperature 1 | - | X3:26
D12 | Air Pressure 1 | + | X3:27
D12 | Air Pressure 1 | - | X3:28
D13 | Global Horizontal Irradiance N | + | X3:29
D13 | Global Horizontal Irradiance N | - | X3:30
D14 | Diffused Horizontal Irradiance N | + | X3:31
D14 | Diffused Horizontal Irradiance N | - | X3:32
Analogue Inputs
ETI Reference | Description |  | Reference
D15 | Back Panel Temperature N | + | X3:33
D15 | Back Panel Temperature N | - | X3:34
D16 | Precipitation N | + | X3:35
D16 | Precipitation N | - | X3:36
D17 | Wind Speed N | + | X3:37
D17 | Wind Speed N | + | X3:38
D18 | Wind Direction N | - | X3:39
D18 | Wind Direction N | + | X3:40
D19 | Air Temperature N | - | X3:41
D19 | Air Temperature N | + | X3:42
D20 | Air Pressure N | + | X3:43
D20 | Air Pressure N | - | X3:44
D21 | SPARE | + | X3:45
D21 | SPARE | - | X3:46
D22 | SPARE | + | X3:47
D22 | SPARE | + | X3:48
D23 | SPARE | - | X3:49
D23 | SPARE | + | X3:50
D24 | SPARE | - | X3:51
D24 | SPARE | + | X3:52
D25 | SPARE | + | X3:53
D25 | SPARE | - | X3:54
X3:55
X3:56
X3:57
X3:58
X3:59
X3:60
X3:61
X3:62
X3:63
X3:64
Analogue Outputs
ETI Reference | Description |  | Reference
G1 | Analogue Output Active Power Control Setpoint | + | X4:1
G1 | Analogue Output Active Power Control Setpoint | - | X4:2
G2 | Frequency Droop Setting | + | X4:3
G2 | Frequency Droop Setting | - | X4:4
G3 | SPARE | + | X4:5
G3 | SPARE | - | X4:6
G4 | SPARE | + | X4:7
G4 | SPARE | - | X4:8
Double Digital Outputs (ON/OFF Commands)
ETI Reference | Description |  | Reference
E1 | Active Power Control facility status | off | X5:1
| Command Negative |  | X5:2
E2 | Active Power Control facility status | on | X5:3
E3 | Frequency Response System Mode Status | off | X5:4
| Command Negative |  | X5:5
E4 | Frequency Response System Mode Status | on | X5:6
E5 | Frequency Response Curve Select | Curve 1 | X5:7
| Command Negative |  | X5:8
E6 | Frequency Response Curve Select | Curve 2 | X5:9
F1 | Dispatch Fail Market Command Lamp - SFPS Panel | off | X5:10
| Command Negative |  | X5:11
F2 | Dispatch Fail Market Command Lamp - SFPS Panel | on | X5:12
F3 | Blue Alert Lamp - SFPS Panel | off | X5:13
| Command Negative |  | X5:14
F4 | Blue Alert Lamp - SFPS Panel | on | X5:15
F5 | SPARE | off | X5:16
| Command Negative |  | X5:17
F6 | SPARE | on | X5:18
F7 | SPARE | off | X5:19
| Command Negative |  | X5:20
F8 | SPARE | on | X5:21
X5:22
| Command Negative |  | X5:23
X5:24
X5:25
| Command Negative |  | X5:26
X5:27
X5:28
| Command Negative |  | X5:29
X5:30
X5:31
| Command Negative |  | X5:32
X5:33
X5:34
| Command Negative |  | X5:35
X5:36
X5:37
| Command Negative |  | X5:38
X5:39
X5:40
| Command Negative |  | X5:41
X5:42
X5:43
| Command Negative |  | X5:44
X5:45
X5:46
| Command Negative |  | X5:47
X5:48
Single Digital Outputs (ON Commands)
ETI Reference | Description |  | Reference
| SPARE 1 |  | X6:1
| Command Negative |  | X6:2
| SPARE 2 |  | X6:3
| Command Negative |  | X6:4
| SPARE 3 |  | X6:5
| Command Negative |  | X6:6
| SPARE 4 |  | X6:7
| Command Negative |  | X6:8
| SPARE 5 |  | X6:9
| Command Negative |  | X6:10
| SPARE 6 |  | X6:11
| Command Negative |  | X6:12
| SPARE 7 |  | X6:13
| Command Negative |  | X6:14
| SPARE 8 |  | X6:15
| Command Negative |  | X6:16
| SPARE 9 |  | X6:17
| Command Negative |  | X6:18
| SPARE 10 |  | X6:19
| Command Negative |  | X6:20
X6:21
| Command Negative |  | X6:22
X6:23
| Command Negative |  | X6:24
Strobe Pulses (Setpoint Enable Pulses)
ETI Reference | Description |  | Reference
E7 | Digital Output Active Power Control Setpoint Enable |  | X7:1
| Command Negative |  | X7:2
E8 | Digital Output Frequency Droop Setting Enable |  | X7:3
| Command Negative |  | X7:4
E9 | SPARE |  | X7:5
| Command Negative |  | X7:6
E10 | SPARE |  | X7:7
| Command Negative |  | X7:8
Distribution Connected Controllable PPMs with MEC <5 MW use a single RTU for communications with both TSO and DSO.
Instead of using this ETIE Layout, the customer shall wire all signals in line with the Wiring Table, as provided by ESBN.

## Signal Specification
Signal Specification
TSO Remote Control Enable Switch (RCES)
RCES shall block all commands from the TSO RTU to the SFPS, including set-point enable pulses (except for the Blue Alert Lamp indication in TSO SFs following a Black Start Shutdown Command)
Turning the RCES ON or OFF shall not impact/change the status of any signals, commands, set-points or control modes (other than the position indication of the RCES).
For TSO SFPS
Blackstart Shutdown
See the "Blackstart Shutdown" tab for details on the functionality of Blackstart Shutdown.
Blackstart Shutdown feedback is provided from the associated transmission station, not from the SFPS
For DSO SFPS
Dispatch Fail Lamp
Dispatch Fail Lamp ON command shall turn on indication lamp in SFPS control room unless TSO RCES is OFF
Dispatch Fail Lamp OFF command shall turn off indication lamp in SFPS control room unless TSO RCES is OFF
Blue Alert Lamp
TSO SF: Black Start Shutdown ON command shall turn on Blue Alert indication lamp in SFPS control room
TSO SF: Black Start Shutdown OFF command shall turn off Blue Alert indication lamp in SFPS control room
DSO SF: Blue Alert Lamp ON command shall turn on indication lamp in SFPS control room unless TSO RCES is OFF
DSO SF: Blue Alert Lamp OFF command shall turn off indication lamp in SFPS control room unless TSO RCES is OFF
Set-point Enable Pulse
When a SFPS receives a set-point enable pulse (e.g. Active Power Control Set-point Enable), it shall implement the set-point on the associated analogue input (e.g. implement the Active Power Control set-point being received at that time).
If an analogue set-point signal changes and a corresponding set-point enable pulse is not issued, the SFPS shall ignore the change in the analogue signal.
Feedback for Analogue Signals
Feedback for analogue signals shall reflect the last received valid signal
i.e. feedback signals should not be looped from the analogue input. They should only change value when an Enable Pulse is received, and should not change value when the corresponding mode (e.g. Active Power Control) is turned off or the Remote Control Enable Switch is turned off.
Active Power Control ON/OFF
When Active Power Control is turned off, the set-point feedback shall not change, but Solar Farm output shall increase to maximum available MW.
Set-points received while Active Power Control is OFF should be ignored.
Active Power Control Set-point (Feedback)
The Active Power Control set-point feedback should not change when APC is switched on or off. It should reflect the last valid set-point that the SFPS received from NCC.
Note. Locally implemented set-points should not be fed back to NCC.
Worked Example:
● NCC turns APC on and issues a set-point of 10 MW (feedback goes to 10 MW, SFPS implements 10 MW set-point)
● NCC issues a set-point of 8 MW (feedback goes to 8 MW, SFPS implements 8 MW set-point)
● NCC turns APC off (feedback remains at 8 MW, SFPS ramps to minimum of AAP and Registered Capacity)
● NCC issues a set-point of 5 MW (feedback remains at 8 MW, SFPS remains at minimum of AAP and Registered Capacity)
● NCC turns APC on (feedback remains at 8 MW, SFPS ramps to 8 MW)
● NCC issues a set-point of Registered Capacity and turns APC off (feedback goes to Registered Capacity, SFPS ramps to minimum of AAP and Registered Capacity)
If the SFPS is reset, the default settings for the various controls should commit current state to memory (if this is not possible, default should be APC off, FQR on, Curve 1 etc.)
Frequency Response ON/OFF
When Frequency Response is Off, the SFPS shall not respond to any changes in Frequency. When Frequency Response is On, the SFPS shall respond to frequency in line with the specified frequency response settings.
When Frequency Response is turned On or Off, the selected Frequency Curve (and feedback) shall not be affected. i.e. Curve signal does not go suspect, and does not reset to a default value.
If Frequency Response is OFF, the Curve should not change.
Frequency Droop
Droop set-points received while Frequency Response is OFF should be ignored.
Frequency Droop must be settable in the range 2% to 12%, per Grid Code V8 clause PPM1.5.3.1
SFPS should treat any set-point <= 2% as 2% (implement 2% and provide 2% feedback)
SFPS should treat any set-point >= 12% as 12% (implement as 12% and provide 12% feedback)
Frequency Droop signal is specified in the range 0% to 14%, to facilitate signals at the upper and lower ends of the scale
In the case of hardware/software update or reset, the existing value shall be maintained. In the case that the existing value is lost, the SFPS shall default to 4%.
This signal shall be implemented in increments of 0.1% i.e. to 1 decimal place.
For TSO SFPS or DSO Topology 1 or 2 SFPS
Reactive Power Control Modes (kV, Mvar, PF)
One control mode will be ON (in operation) at all time: Voltage Control (kV), Mvar Control (Q), or Power Factor Control (PF).
There are no individual OFF commands. NCC will toggle between control modes by sending an ON command for the required mode.
Position indication for the mode in operation will indicate ON and position indication for the other two modes will indicate OFF.
Response time to a change in set-point: as per Grid Code V8 clause PPM1.6.2.2
Power Factor Set-points:
Power Factor set-points are issued as an angle (±90 degrees), to avoid the signalling difficulties associated with issuing the non-linear Power Factor set-points.
If a positive angle is issued, the Power Factor implemented by the controll will be positive. If a negative angle is issued, the Power Factor implemented by the controller will be negative.
Worked Examples:
1) NCC issues A set-point of +18.19 degrees, SFPS implements a set-point of +cos(18.19) = +0.95 PF
2) NCC issues A set-point of -18.19 degrees, SFPS implements a set-point of -cos(18.19) = -0.95 PF
3) NCC issues A set-point of 0 degrees, SFPS implements a set-point of cos(0) = 1 PF
4) A SFPS exporting 100 MW with a set-point of +18.19 degrees would export +32.85 Mvar. i.e. Tan(+18.19)*100
Changing Control Modes (Bumpless Transfer):
1. SFPS calculates a set-point which will cause no change in Mvar. 2. SFPS continues to regulate to calculated set-point in the new mode.
Worked Example:
A SFPS with a Registered Capacity of 100 MW is exporting 50 MW, operating at a voltage slope setting of 4%. System voltage Is 118 kV and the kV set-point is 115 kV, therefore the SFPS is absorbing its maximum leading capability of 32.9 Mvar.
● NCC issues Mvar (Q) Control ON.
● SFPS calculates and implements a Mvar set-point of 32.9 Mvar, consistent with the current Mvar output. SFPS returns Mvar (Q) Control feedback ON, Voltage (kV) Control feedback OFF and Power Factor (PF) Control feedback OFF. Set-point feedback signals do not change.
● NCC issues a Mvar set-point of 10 Mvar.
● TSO RTU issues a Mvar (Q) Control set-point enable pulse to the SFPS. SFPS returns a set-point feedback of 10 Mvar and implements the set-point of 10 Mvar.
● NCC issues Power Factor (PF) Control ON.
● SFPS calculates and implements a Power Factor set-point of +0.98, consistent with the current MW and Mvar output. SFPS returns Power Factor (PF) Control feebdack ON, Voltage (kV) Control feedback OFF and Mvar (Q) Control feedback OFF. Set-point feedback signals do not change.
● NCC issues a Power Factor set-point of 0 degrees.
● TSO RTU issues a Power Factor (PF) set-point enable pulse to the SFPS. SFPS returns a set-point feedback of 0 degrees and implements the set-point of 0 degrees (1 PF).
● NCC issues Voltage (kV) Control ON.
● SFPS calculates and implements a Voltage set-point of 118 kV, consistent with the current system voltage and Mvar output. SFPS returns Voltage (kV) Control feebdack ON, Power Factor (PF) Control feedback OFF and Mvar (Q) Control feedback OFF. Set-point feedback signals do not change.
● NCC issues a Voltage set-point of 115 kV.
● TSO RTU issues a Voltage (kV) set-point enable pulse to the SFPS. SFPS returns a set-point feedback of 115 kV and implements the set-point of 115 kV.
Available Active Power
AAP must reflect what the SFPS is capable of exporting at that point in time
While a Generating Unit is Shut down for maintenance, fault, or noise, that Generating Unit shall not be included in AAP
While a the output of a Generating Unit is reduced due to Active Power Control Set-Point or frequency response, AAP shall reflect what the SFPS would be exporting if that APC set-point was not in place (accounting for Generating Units that are shut down for reasons, above)
AAP shall not be greater than MEC.
% Availability
Specified in Grid Code and signal list as 0-100%
Grid Code definition of Controllable SFPS Availability: The amount of MW the Controllable SFPS can produce given favourable resource conditions
i.e. The combined capacity of all Generating Units in service (including Generating Units shut down due to APC set-point) as a percentage of installed capacity.
This signal is independent of resource conditions.
Note. Any generation unit which is shut down (not due to APC set-point) should reduce the % Availability accordingly.
Worked examples:
1) Solar Farm with 10 * 1 MW Generating Units
● Registered Capacity = 10 MW
● Out Of Service: 2 * 1 MW
2) Solar Farm with 5*1 MW Generating Units and 5*2 MW Generating Units
● Registered Capacity = 15 MW
● Out of service: 1*1 MW Generating Unit and 2*2 MW Generating Units
3) Solar Farm with 20*1 MW Generating Units with an MEC of 18 MW
● Registered Capacity = 18 MW
● Out of service: 2 * 1 MW Generating Units
Transformer Tap Position
Transformer tap position is indicated via a 0-10 mA analogue signal. The lowest tap will be enumerated as 1 in the EirGrid EMS.
Worked Example:
1) A transformer tap range of -13 to +13 is represented as tap 1 to 27.
2) A transformer tap range of -13 to +7 is represented as tap 1 to 21.
Post Energisation
During Post energisation signals testing there should be NO external influencing factors, e.g. no commissioning works should take place on any Generating Units on site, as this may influence the outcome of the test.
% 𝐴𝑣𝑎𝑖𝑙𝑎𝑏𝑖𝑙𝑖𝑡𝑦= (10 𝑀𝑊−(2∗1 𝑀𝑊))/(10 𝑀𝑊)∗100=80%
% 𝐴𝑣𝑎𝑖𝑙𝑎𝑏𝑖𝑙𝑖𝑡𝑦= (15 𝑀𝑊−(1∗1 𝑀𝑊+2∗2 𝑀𝑊))/(15 𝑀𝑊)∗100=66.666%
% 𝐴𝑣𝑎𝑖𝑙𝑎𝑏𝑖𝑙𝑖𝑡𝑦= (20 𝑀𝑊−(2∗1 𝑀𝑊))/(20 𝑀𝑊)∗100=90%
% 𝐴𝑣𝑎𝑖𝑙𝑎𝑏𝑖𝑙𝑖𝑡𝑦= (𝐼𝑛𝑠𝑡𝑎𝑙𝑙𝑒𝑑 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 −𝑐𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝑜𝑓 𝐺𝑒𝑛𝑒𝑟𝑎𝑡𝑖𝑜𝑛 𝑈𝑛𝑖𝑡𝑠 𝑛𝑜𝑡 𝑖𝑛 𝑠𝑒𝑟𝑣𝑖𝑐𝑒 (𝑒.𝑔. 𝑢𝑛𝑑𝑒𝑟 𝑚𝑎𝑖𝑛𝑡𝑒𝑛𝑎𝑛𝑐𝑒 𝑜𝑟 𝑓𝑎𝑢𝑙𝑡))/(𝐼𝑛𝑠𝑡𝑎𝑙𝑙𝑒𝑑 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦)∗100
M𝑣𝑎𝑟= 𝑇𝑎𝑛(𝑠𝑒𝑡𝑝𝑜𝑖𝑛𝑡)∗𝑀𝑊 𝑂𝑢𝑡𝑝𝑢𝑡

## Freq,Ramping,Voltage Settings
Frequency, Ramp Rate and Voltage Settings to be implemented in Solar Farm Control System
Definitions:
| AAP | Available Active Power
| DMOL | Designed Minimum Operating Level
| APC | Active Power Control
Frequency Response Mode On | [5 empty] | Frequency Response Diagrams
Curve 1: Resource Following Mode (RfG Limited Frequency Sensitive Mode)
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 48 |  | 100% of AAP
|  | FA | 48 | PA | 100% of AAP
|  | Under Frequency Response | 48 < f < 49.8 |  | 100% of AAP
|  | FB | f = 49.8 | PB | 100% of AAP
|  | +/-0.2Hz Deadband | 49.8 < f < 50.2 |  | 100% of AAP
|  | FC | f = 50.2 | PC | 100% of AAP
|  | Over Frequency Response | 50.2 < f < 51.9 |  | AAP + ∆MW2
|  | FD | f = 51.9 | PD | Minimum of: AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Curve 1: Active Power Control Mode (RfG Frequency Sensitive Mode)
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 48 |  | 100% of AAP
|  | FA | f = 48 | PA | 100% of AAP
|  | Under Frequency Response | 48 < f < 49.985 |  | Minimum of: APC Setpoint + ∆MW and AAP
|  | FB | f = 49.985 | PB | Minimum of: APC Setpoint and AAP
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | Minimum of: APC Setpoint and AAP
|  | FC | f = 50.015 | PC | Minimum of: APC Setpoint and AAP
|  | Over Frequency Response | 50.015 < f < 51.9 |  | Minimum of: APC Setpoint + ∆MW and AAP + ∆MW1, 2
|  | FD | f = 51.9 | PD | Minimum of: APC Setpoint and AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Curve 2: Resource Following Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f <49.3 |  | 100% of AAP
|  | FA | f = 49.3 | PA | 100% of AAP
|  | Under Frequency Response | 49.3 < f < 49.985 |  | 95% of Available Active Power + ∆MW
|  | FB | f = 49.985 | PB | 95% of Available Active Power. This is = to 5% Reserve.
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | 95% of Available Active Power. This is = to 5% Reserve.
|  | FC | f = 50.015 | PC | 95% of Available Active Power. This is = to 5% Reserve.
|  | Over Frequency Response | 50.015 < f < 51.9 |  | 95% of AAP + ∆MW2
|  | FD | f = 51.9 | PD | Minimum of: AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Curve 2: Active Power Control Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 49.3 |  | 100% of AAP
|  | FA | f = 49.3 | PA | 100% of AAP
|  | Under Frequency Response | 49.3 < f < 49.985 |  | Minimum of: APC Setpoint + ∆MW and 95% of AAP + ∆MW
|  | FB | f = 49.985 | PB | Minimum of: APC Setpoint and 95% of AAP
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | Minimum of: APC Setpoint and 95% of AAP
|  | FC | f = 50.015 | PC | Minimum of: APC Setpoint and 95% of AAP
|  | Over Frequency Response | 50.015 < f < 51.9 |  | Minimum of: APC Setpoint + ∆MW and 95% of AAP + ∆MW1, 2
|  | FD | f = 51.9 | PD | Minimum of: APC Setpoint and AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Minimum reserve level in Curve 2 is 5% of Available Active Power, not lower than DMOL (settable between DMOL and 100%)
Frequency Response Mode OFF
Curve 1 and Curve 2: Resource Following Mode
|  |  | Transmission System Frequency (Hz) |  | Required Active Power Output
|  |  | 47.5 ≤ f ≤ 52 | No governor action | 100% of AAP
Curve 1 and Curve 2: Active Power Control Mode
|  |  | Transmission System Frequency (Hz) |  | Required Active Power Output
|  |  | 47.5 ≤ f ≤ 52 | No governor action | Minimum of: AAP and APC Setpoint
1 APC Setpoint + ∆MW shall have a lower limit of the minimum of: APC Setpoint and DMOL.
2 (95% of) AAP + ∆MW shall have a lower limit of the minimum of AAP and DMOL
3 Any SG which has disconnected due to high frequency shall be brought back on load as fast as technically feasible, provided the Frequency has fallen below 50.2Hz.
DMOL shall not be greater than 12% of Registered Capacity
If AAP < DMOL and f < FE, maximise output
Ramp Rates:
|  | Mode | Rate | Priority | Comment
|  | Frequency Response | As fast as technically possible. 60% of its expected Active Power response within 5 seconds 100% of its expected Active Power response within 15 seconds. | 1
|  | Active Power Dispatch | 20% of Registered Capacity per Minute | 2 | Settable between: 1-100% Registered Capacity per Minute
|  | Resource Following | 20% of Registered Capacity per Minute | 3 | Settable between: 1-100% Registered Capacity per Minute
Frequency Droop:
|  | Frequency Droop | Droop Calculation | Comment
|  | 4% |  | Settable between: 2-12%, online
Rate of Change of Frequency:
If possible, ROCOF should be disabled on Transmission System-connected Solarfarms. If this is not possible, ROCOF should be set to max that machine is capable of. Under no circumstances should ROCOF be set to less than 0.5 Hz/s
Proposed Modification to Grid Code. (Ref#MPID 229).

## Generator Protection Settings
Recommended Solar Farm Power Station (SFPS) Generator Protection Settings to be applied by SFPS
| Underfrequency stage 1 Setpoint | f< | 47.5 Hz | If only two stages available for underfrequency on relay, use stage 2 and stage 3
| Underfrequency stage 1 time delay | t< | 3600 s
| Underfrequency stage 2 Setpoint | f<< | 47.4 Hz
| Underfrequency stage 2 time delay | t<< | 20 s
| Underfrequency stage 3 Setpoint | f<<< | 46.9 Hz
| Underfrequency stage 3 time delay | t<<< | 1 s
| Overfrequency stage 1 Setpoint | f> | 52Hz
| Overfrequency stage 1 time delay | t> | 3600 s
| Overfrequency stage 2 Setpoint | f>> | 52.1 Hz
| Overfrequency stage 2 time delay | t>> | 1 s
| Rate of Change of Frequency setpoint | df/dt | Max | If possible, ROCOF should be disabled on Transmission System-connected Solarfarms. If this is not possible, ROCOF should be set to max that machine is capable of. Under no circumstances should ROCOF be set to less than 1 Hz/s over 500 ms
| Rate of Change of Frequency delay | t | Max
| Undervoltage stage 1 Setpoint | U< | 0.89 pu
| Undervoltage stage 1 time delay | t< | 3 s
| Undervoltage stage 2 Setpoint | U<< | 0.14 pu
| Undervoltage stage 2 time delay | t<< | 0.625 s
| Overvoltage stage 1 Setpoint | U> | 1.11 pu
| Overvoltage stage 1 time delay | t> | 60 s | This is the minimum time delay we would recommend. If the plant can operate at this voltage for longer periods, then a longer time delay (at the discretion of the SFPS) should be implemented.
| Overvoltage stage 2 Setpoint | U>> | 1.2 pu
| Overvoltage stage 2 time delay | t>> | 15 s | This is the minimum time delay we would recommend. If the plant can operate at this voltage for longer periods, then a longer time delay (at the discretion of the SFPS) should be implemented.
| Fault Ride Through Events | N | N/A | Trip & Lockout Settings. i.e No. of events within specified time period. Confirm if time period is rolling. NB. Lockout is not recommended by EirGrid.
| Fault Ride Though Time Period (Rolling) | t | N/A

## Test Schedule and Templates
Grid Code Compliance Test Schedule and Test Procedure templates
PPM Webpage
http://www.eirgridgroup.com/customer-and-industry/general-customer-information/grid-code-compliance-test/compliance-testing/power-park-modules/
Test Procedure Templates
http://www.eirgridgroup.com/site-files/library/EirGrid/RfG_PPM_Test-Procedure-Active-Power-Control.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/RfG_PPM_Test-Procedure-Frequency-Response.docx