## Version Control
Generator Signal List Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by
1 | 2021-08-19 |  |  |  | first draft
Note on D3: Administrator: All signal lists circulated to EMS and ESBT for Review before issuance.

## OSP
AAAAA |  | Signal List |  | v0.2 | dd-mmm-yy
Based on: |  |  | 1 Market Unit
|  |  | Unit Number | x
| INSERT SLD HERE |  | Registered Capacity | x MW
ETIE Ref | Digital Input Signals (to EirGrid) | [5 empty] | To Be Provided By: | Comment | Gride Code Reference
| Double Point Status Indications |  | (each individual input identified separately for clarity)
| MVDTE AAAAA 21kV DE |  |  | open |  |  |  |  | CC12.2 (a)
| MVDTE AAAAA 21kV DE |  |  | closed |  |  |  |  | CC12.2 (a)
| MVCBG AAAAA 21kV CB |  |  | open |  |  |  |  | CC12.2 (a)
| MVCBG AAAAA 21kV CB |  |  | closed |  |  |  |  | CC12.2 (a)
| MVDTG AAAAA 21kV DT |  |  | open |  |  |  |  | CC12.2 (a)
| MVDTG AAAAA 21kV DT |  |  | closed |  |  |  |  | CC12.2 (a)
| MVCBB 6.6kV CB |  |  | open |  |  |  |  | CC12.2 (a)
| MVCBB 6.6kV CB |  |  | closed |  |  |  |  | CC12.2 (a)
| MVCBB 6.6kV DT |  |  | open |  |  |  | i.e. MVCBB 6.6 kV CB in test / withdrawn position | CC12.2 (a)
| MVCBB 6.6kV DT |  |  | closed |  |  |  | i.e. MVCBB 6.6 kV CB in service position | CC12.2 (a)
| MVCBU 6.6kV CB |  |  | open |  |  |  |  | CC12.2 (a)
| MVCBU 6.6kV CB |  |  | closed |  |  |  |  | CC12.2 (a)
| MVCBU 6.6kV DT |  |  | open |  |  |  | i.e. MVCBU 6.6 kV CB in test / withdrawn position | CC12.2 (a)
| MVCBU 6.6kV DT |  |  | closed |  |  |  | i.e. MVCBU 6.6 kV CB in service position | CC12.2 (a)
| MVCBF 6.6kV CB |  |  | open |  |  |  |  | CC12.2 (a)
| MVCBF 6.6kV CB |  |  | closed |  |  |  |  | CC12.2 (a)
| MVCBF 6.6kV DT |  |  | open |  |  |  | i.e. MVCBF 6.6 kV CB in test / withdrawn position | CC12.2 (a)
| MVCBF 6.6kV DT |  |  | closed |  |  |  | i.e. MVCBF 6.6 kV CB in service position | CC12.2 (a)
| MVDTE2 6.6kV DE |  |  | open |  |  |  |  | CC12.2 (a)
| MVDTE2 6.6kV DE |  |  | closed |  |  |  |  | CC12.2 (a)
| MVDTE3 6.6kV DE |  |  | open |  |  |  |  | CC12.2 (a)
| MVDTE3 6.6kV DE |  |  | closed |  |  |  |  | CC12.2 (a)
| MVCBEX 0.69kV CB |  |  | open |  |  |  |  | CC12.2 (a)
| MVCBEX 0.69kV CB |  |  | closed |  |  |  |  | CC12.2 (a)
| Frequency Response |  |  | Off |  |  | IPP | Generating Station Equipment | OC4.3.4
| Frequency Response |  |  | On |  |  | IPP | Generating Station Equipment | OC4.3.4
Single Point Status Indications
| Fuel Type Indication |  |  | Gas / Distillate |  |  | IPP | Single bit indication is sufficient | CC12.1
| CCGT Mode |  |  | Open / Combined |  |  | IPP |  | CC12.1
| AAAAA Amber Alert |  |  | off |  |  | IPP | Generating Station Equipment | OC9.4
| AAAAA Amber Alert |  |  | on |  |  | IPP | Generating Station Equipment | OC9.4
| AAAAA Amber Alert Acknowledge |  |  | off |  |  | IPP | Generating Station Equipment | OC9.4
| AAAAA Amber Alert Acknowledge |  |  | on |  |  | IPP | Generating Station Equipment | OC9.4
| AAAAA Red Alert |  |  | off |  |  | IPP | Generating Station Equipment | OC9.4
| AAAAA Red Alert |  |  | on |  |  | IPP | Generating Station Equipment | OC9.4
| AAAAA Red Alert Acknowledge |  |  | off |  |  | IPP | Generating Station Equipment | OC9.4
| AAAAA Red Alert Acknowledge |  |  | on |  |  | IPP | Generating Station Equipment | OC9.4
| AAAAA Blue Alert |  |  | off |  |  | IPP | Generating Station Equipment | OC9.4
| AAAAA Blue Alert |  |  | on |  |  | IPP | Generating Station Equipment | OC9.4
| AAAAA Blue Alert Acknowledge |  |  | off |  |  | IPP | Generating Station Equipment | OC9.4
| AAAAA Blue Alert Acknowledge |  |  | on |  |  | IPP | Generating Station Equipment | OC9.4
| AGC Control |  |  | off |  |  | IPP | Generating Station Equipment | CC7.3.1.1 (v) & OC4.3.6
| AGC Control |  |  | on |  |  | IPP | Generating Station Equipment | CC7.3.1.1 (v) & OC4.3.6
| SPS Run-back Stages Enabled (by GEN) |  |  | off |  |  | IPP | To indicate to NCC that the GEN has enabled/disabled the Run-Back stages of the SPS. | CC10.9.2
| SPS Run-back Stages Enabled (by GEN) |  |  | on |  |  | IPP | To indicate to NCC that the GEN has enabled/disabled the Run-Back stages of the SPS. | CC10.9.2
| SPS Runback Stage 1 In Progress |  |  | off/on (single bit) |  |  | IPP | Indication from GEN to NCC that GEN is reducing output to Setpoint 1 | CC10.9.2
| SPS Runback Stage 2 In Progress |  |  | off/on (single bit) |  |  | IPP | Indication from GEN to NCC that GEN is reducing output to Setpoint 2 | CC10.9.2
| SPS Runback Stage 1 Operated |  |  | off/on (single bit) |  |  | ESB Networks | Indication from SPS to NCC that Stage 1 of SPS has operated | CC10.9.2
| SPS Runback Stage 2 Operated |  |  | off/on (single bit) |  |  | ESB Networks | Indication from SPS to NCC that Stage 2 of SPS has operated | CC10.9.2
| SPS Runback Stage 3 Operated |  |  | off/on (single bit) |  |  | ESB Networks | Indication from SPS to NCC that Stage 3 of SPS has operated | CC10.9.2
| SPS Tebit Interface fail/comms alarm |  |  | off/on (single bit) |  |  | ESB Networks | Indication from SPS to NCC of TEBIT failure and/or comms alarm | CC10.9.2
| Generator Wind Down Alarm |  |  | off |  |  | IPP | Signal from GEN to NCC that a generator wind down is not in progress | CC12.1
| Generator Wind Down Alarm |  |  | on |  |  | IPP | Signal from GEN to NCC that a generator wind down is in progress | CC12.1
| T200X 220kV CB Close Command from IPP |  |  | off/on (single bit) |  |  | IPP | provides indication that a CB close command has come from IPP. | CC7.3.3
A29 | T107 110kV CB Close Command from IPP |  |  | off/on(single bit) |  |  | IPP | Proves indication that a CB Close command has come from IPP. | CC7.3.3
| Analogue Input Signals (to EirGrid) | [5 empty] | To be provided by:
In TXXXX Cubicle:
In Generator Cubicle:
| AAAAA MW at Generator |  | -10->0->10 | mA | -500 -> 0 -> 500 | MW | IPP | Generating Station Equipment Please Ensure the SCS has a deadband of 0.5/100 | CC12.2 (d)
| AAAAA Mvar at Generator |  | -10->0->10 | mA | -450 -> 0 -> +450 | Mvar | IPP | Generating Station Equipment Please Ensure the SCS has a deadband of 0.5/100 | CC12.2 (d)
| AAAAA kV at Generator |  | 0 -> 10 | mA | 0-21 | kV | IPP | Generating Station Equipment Please Ensure the SCS has a deadband of 1/100 | CC12.2 (e)
| Tap Position TXXXX |  | 0 -> 10 | mA | 1 - 25 | Taps | IPP | Tap range to be confirmed by customer | CC12.2 (f)
| Unit Transformer UT1 MW |  | -10->0->10 | mA | -30 -> 0 -> 30 | MW | IPP | Generating Station Equipment
| AGC Indication - Upper Limit |  | 0 -> 10 | mA | 0 - 500 | MW | IPP |  | CC7.3.1.1 (v) & OC4.3.6
| AGC Indication - Lower Limit |  | 0 -> 10 | mA | 0 - 500 | MW | IPP |  | CC7.3.1.1 (v) & OC4.3.6
| AGC Setpoint Feedback |  | 0 -> 10 | mA | 0 - 500 | MW | IPP |  | CC7.3.1.1 (v) & OC4.3.6
| Run-back Setpoint 1 Feedback |  | 0 -> 10 | mA | 0 - 500 | MW | IPP | Provide feedback of setpoint 1 from GEN to NCC | CC10.9.2
| Run-back Setpoint 2 Feedback |  | 0 -> 10 | mA | 0 - 500 | MW | IPP | Provide feedback of setpoint 1 from GEN to NCC | CC10.9.2
| Total Fuel Stock Level |  | 0 -> 10 | mA | 0 - 12000 | MWh | IPP | Indicates total level of distillate fuel stock in storage. Maximum volume to be confirmed by GEN. | CC12.2 (i)
| Location A Water Level |  | 0 -> 10 | mA | 0 - 12000 | MWh | IPP |  | CC12.1
| Location B Water Level |  | 0 -> 10 | mA | 0 - 12000 | MWh | IPP |  | CC12.1
| Location C Water Level |  | 0 -> 10 | mA | 0 - 12000 | MWh | IPP |  | CC12.1
| Location D Water Level |  | 0 -> 10 | mA | 0 - 12000 | MWh | IPP |  | CC12.1
| Digital Output Signals (from EirGrid) | [5 empty] | To be provided to:
| Double Command Outputs |  | (each individual relay output identified separately)
In Generator Cubicle:
| AAAAA Amber Alert |  |  | off | pulse | 0.5 second | IPP |  | OC9.4.3
| AAAAA Amber Alert |  |  | on | pulse | 0.5 second | IPP |  | OC9.4.3
| AAAAA Red Alert |  |  | off | pulse | 0.5 second | IPP |  | OC9.4.4
| AAAAA Red Alert |  |  | on | pulse | 0.5 second | IPP |  | OC9.4.4
| AAAAA Blue Alert |  |  | off | pulse | 0.5 second | IPP |  | OC9.4.5
| AAAAA Blue Alert |  |  | on | pulse | 0.5 second | IPP |  | OC9.4.5
| AGC Strobe/Enable Pulse |  |  |  | pulse | 0.5 second | IPP |  | CC7.3.1.1 (v) & OC4.3.6
| SPS Run-back Stages Enabled (by NCC) |  |  | off |  |  | ESB Networks/IPP | Allows NCC to enable/disable the SPS Run-Back stages and provide indication of same to the GEN. | CC10.9.2
| SPS Run-back Stages Enabled (by NCC) |  |  | on |  |  | ESB Networks/IPP | Allows NCC to enable/disable the SPS Run-Back stages and provide indication of same to the GEN. | CC10.9.2
| SPS Trip Stage Enabled (by NCC) |  |  | off |  |  | ESB Networks | Allows NCC to enable/disable the Trip stage of the SPS. | CC10.9.2
| SPS Trip Stage Enabled (by NCC) |  |  | on |  |  | ESB Networks | Allows NCC to enable/disable the Trip stage of the SPS. | CC10.9.2
| SPS Runback Stage 1 Operated |  |  | voltage free contact from SPS |  |  | IPP | Command from SPS to GEN to implement Stage 1 of SPS | CC10.9.2
| SPS Runback Stage 2 Operated |  |  | voltage free contact from SPS |  |  | IPP | Command from SPS to GEN to implement Stage 2 of SPS | CC10.9.2
| SPS Runback Stage 3 (Trip) Operated |  |  | voltage free contact (x2) from SPS |  |  | IPP | Command from SPS to GEN to shut down. | CC10.9.2
| SPS Run-back Setpoint 1 Strobe/Enable Pulse |  |  |  | pulse | 0.5 second | IPP | To enable SPS Setpoint 1 | CC10.9.2
| SPS Run-back Setpoint 2 Strobe/Enable Pulse |  |  |  | pulse | 0.5 second | IPP | To enable SPS Setpoint 2 | CC10.9.2
Analogue Output Signals (from EirGrid)
| AGC Analogue Setpoint Output |  | 4 -> 20 | mA | 0 - 500 | MW | IPP |  | CC7.3.1.1 (v) & OC4.3.6
| Run-back Setpoint 1 |  | 4 -> 20 | mA | 0 - 500 | MW | IPP | Provide Setpoint 1 to GEN from NCC
| Run-back Setpoint 2 |  | 4 -> 20 | mA | 0 - 500 | MW | IPP | Provide Setpoint 2 to GEN from NCC
| Protection Signals To EirGrid |  | NCC Text / Ganged Signal Name
All single bit signals
IPP Protection Interface (signals duplicated from Protection Signals List)
P1 | IPP EMERGENCY TRIP |  | EMER TRIP FROM IPP | off/on |  |  | IPP | See also protection signal list | CC10.9.1
P2 | IPP PROTECTION TRIP COIL 1 |  | PROT TRIP FROM IPP | off/on |  |  | IPP | See also protection signal list | CC10.9.1
P3 | IPP PROTECTION TRIP COIL 2 |  | PROT TRIP FROM IPP | off/on |  |  | IPP | See also protection signal list | CC10.9.1
P4 | IPP CBF START (CURRENT BASED) |  | CBF I> START FROM IPP | off/on |  |  | IPP | See also protection signal list | CC10.8
P5 | IPP CBF START (NON CURRENT BASED) |  | CBF NON I> START FROM IPP | off/on |  |  | IPP | See also protection signal list | CC10.8
Optel Requirements
| Optel phone is required in Generator Control Room | [5 empty] | ESBTS
Note on F93: +/- 120 % of Registered Capacity (round up)
Note on F94: +/- 100 % of Registered Capacity (round up)
Note on F95: 0 V to 120% of generator voltage
Note on E133: The signals are sourced off contacts of interposing relays (relays connected to TEBIT channels 1 & 2). Telecoms can apply whatever voltage they wish across these contacts – presumably 48 V DC.
Note on E134: The signals are sourced off contacts of interposing relays (relays connected to TEBIT channels 1 & 2). Telecoms can apply whatever voltage they wish across these contacts – presumably 48 V DC.
Note on E135: The signals are sourced off contacts of interposing relays (relays connected to TEBIT channels 1 & 2). Telecoms can apply whatever voltage they wish across these contacts – presumably 48 V DC.
Note on F142: macmanus_c: 0 to 120% Reg Cap
Note on I151: Protection signal list may not exist for refurbs
Note on I152: Protection signal list may not exist for refurbs
Note on I153: Protection signal list may not exist for refurbs
Note on I154: Protection signal list may not exist for refurbs
Note on I155: Protection signal list may not exist for refurbs

## Wiring Certificate
AAAAA Wiring Certificate |  |  | v0.2 | dd-mmm-yy
ETIE Ref | Digital Input Signals (to EirGrid) |  |  |  |  | Signal Wired to RTU | Analogue Range Confirmed | On/Off Functionality Confirmed
| Double Point Status Indications | (each individual input identified separately for clarity)
| MVDTE AAAAA 21kV DE |  | open
| MVDTE AAAAA 21kV DE |  | closed
| MVCBG AAAAA 21kV CB |  | open
| MVCBG AAAAA 21kV CB |  | closed
| MVDTG AAAAA 21kV DT |  | open
| MVDTG AAAAA 21kV DT |  | closed
| MVCBB 6.6kV CB |  | open
| MVCBB 6.6kV CB |  | closed
| MVCBB 6.6kV DT |  | open
| MVCBB 6.6kV DT |  | closed
| MVCBU 6.6kV CB |  | open
| MVCBU 6.6kV CB |  | closed
| MVCBU 6.6kV DT |  | open
| MVCBU 6.6kV DT |  | closed
| MVCBF 6.6kV CB |  | open
| MVCBF 6.6kV CB |  | closed
| MVCBF 6.6kV DT |  | open
| MVCBF 6.6kV DT |  | closed
| MVDTE2 6.6kV DE |  | open
| MVDTE2 6.6kV DE |  | closed
| MVDTE3 6.6kV DE |  | open
| MVDTE3 6.6kV DE |  | closed
| MVCBEX 0.69kV CB |  | open
| MVCBEX 0.69kV CB |  | closed
Single Point Status Indications
| Fuel Type Indication |  | Gas / Distillate
| Frequency Response |  | On
| CCGT Mode |  | Open / Combined
| AAAAA Amber Alert |  | off
| AAAAA Amber Alert |  | on
| AAAAA Amber Alert Acknowledge |  | off
| AAAAA Amber Alert Acknowledge |  | on
| AAAAA Red Alert |  | off
| AAAAA Red Alert |  | on
| AAAAA Red Alert Acknowledge |  | off
| AAAAA Red Alert Acknowledge |  | on
| AAAAA Blue Alert |  | off
| AAAAA Blue Alert |  | on
| AAAAA Blue Alert Acknowledge |  | off
| AAAAA Blue Alert Acknowledge |  | on
| AGC Control |  | off
| AGC Control |  | on
| SPS Run-back Stages Enabled (by GEN) |  | off
| SPS Run-back Stages Enabled (by GEN) |  | on
| SPS Runback Stage 1 In Progress |  | off/on (single bit)
| SPS Runback Stage 2 In Progress |  | off/on (single bit)
| SPS Runback Stage 1 Operated |  | off/on (single bit)
| SPS Runback Stage 2 Operated |  | off/on (single bit)
| SPS Runback Stage 3 Operated |  | off/on (single bit)
| SPS Tebit Interface fail/comms alarm |  | off/on (single bit)
| Generator Wind Down Alarm |  | off
| Generator Wind Down Alarm |  | on
| T200X 220kV CB Close Command from IPP |  | off/on (single bit)
| T107 110kV CB Close Command from IPP |  | off/on(single bit)
Analogue Input Signals (to EirGrid)
In TXXXX Cubicle:
In Generator Cubicle:
| AAAAA MW at Generator | -10->0->10 | mA | -500 -> 0 -> 500 | MW
| AAAAA Mvar at Generator | -10->0->10 | mA | -450 -> 0 -> +450 | Mvar
| AAAAA kV at Generator | 0 -> 10 | mA | 0-21 | kV
| Tap Position TXXXX | 0 -> 10 | mA | 1 - 25 | Taps
| Unit Transformer UT1 MW | -10->0->10 | mA | -30 -> 0 -> 30 | MW
| AGC Indication - Upper Limit | 0 -> 10 | mA | 0 - 500 | MW
| AGC Indication - Lower Limit | 0 -> 10 | mA | 0 - 500 | MW
| AGC Setpoint Feedback | 0 -> 10 | mA | 0 - 500 | MW
| Run-back Setpoint 1 Feedback | 0 -> 10 | mA | 0 - 500 | MW
| Run-back Setpoint 2 Feedback | 0 -> 10 | mA | 0 - 500 | MW
| Total Fuel Stock Level | 0 -> 10 | mA | 0 - 12000 | MWh
| Location A Water Level | 0 -> 10 | mA | 0 - 12000 | MWh
| Location B Water Level | 0 -> 10 | mA | 0 - 12000 | MWh
| Location C Water Level | 0 -> 10 | mA | 0 - 12000 | MWh
| Location D Water Level | 0 -> 10 | mA | 0 - 12000 | MWh
Digital Output Signals (from EirGrid)
| Double Command Outputs | (each individual relay output identified separately)
In Generator Cubicle:
| AAAAA Amber Alert |  | off | pulse | 0.5 second
| AAAAA Amber Alert |  | on | pulse | 0.5 second
| AAAAA Red Alert |  | off | pulse | 0.5 second
| AAAAA Red Alert |  | on | pulse | 0.5 second
| AAAAA Blue Alert |  | off | pulse | 0.5 second
| AAAAA Blue Alert |  | on | pulse | 0.5 second
| AGC Strobe/Enable Pulse |  |  | pulse | 0.5 second
| SPS Run-back Stages Enabled (by NCC) |  | off
| SPS Run-back Stages Enabled (by NCC) |  | on
| SPS Trip Stage Enabled (by NCC) |  | off
| SPS Trip Stage Enabled (by NCC) |  | on
| SPS Runback Stage 1 Operated |  | voltage free contact from SPS
| SPS Runback Stage 2 Operated |  | voltage free contact from SPS
| SPS Runback Stage 3 (Trip) Operated |  | voltage free contact (x2) from SPS
| SPS Run-back Setpoint 1 Strobe/Enable Pulse |  |  | pulse | 0.5 second
| SPS Run-back Setpoint 2 Strobe/Enable Pulse |  |  | pulse | 0.5 second
Analogue Output Signals (from EirGrid)
| AGC Analogue Setpoint Output | 4 -> 20 | mA | 0 - 500 | MW
| Run-back Setpoint 1 | 4 -> 20 | mA | 0 - 500 | MW
| Run-back Setpoint 2 | 4 -> 20 | mA | 0 - 500 | MW
| Protection Signals To EirGrid | NCC Text / Ganged Signal Name
All single bit signals
IPP Protection Interface (signals duplicated from Protection Signals List)
| IPP EMERGENCY TRIP | EMER TRIP FROM IPP | off/on
| IPP PROTECTION TRIP COIL 1 | PROT TRIP FROM IPP | off/on
| IPP PROTECTION TRIP COIL 2 | PROT TRIP FROM IPP | off/on
| IPP CBF START (CURRENT BASED) | CBF I> START FROM IPP | off/on
| IPP CBF START (NON CURRENT BASED) | CBF NON I> START FROM IPP | off/on
| Confirmation provided by: |  | Date: