## Cover Sheet
Signal List WINDFARM NAME Type A XX MW v0.2 and Control System Parameter Settings
Disclaimer:
This Signal List contains information (and/or attachments) which may be privileged or confidential. All content is intended solely for the use of the individual or entity to whom it is addressed. If you are not the intended recipient please be aware that any disclosure, copying, distribution or use of the contents of this message is prohibited. If you suspect that you have received this Signal List in error please notify EirGrid immediately. Further information can be found at: http://www.eirgrid.com/aboutus/legal/

## Version Control
WINDFARM NAME Signal List Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by
0.1 |  |  |  |  | first draft
0.2 | 2015-03-23 |  |  |  | Frequency Response updated to clarify performance below DMOL per feedback from industry
Note on D3: Administrator: All signal lists circulated to EMS and ESBT for Review before issuance.

## DSO Required Inputs
IPP Inputs for Signal List Development
1 | Wind Farm Power Station (WFPS) Name (including alternative names) | Included in submission 
2 | WFPS Connection Type as per the Distribution Code DCC11.1.4 | Included in submission 
3 | WFPS Maximum Export Capacity | Included in submission 
4 | WFPS Installed Capacity (for Phase developments, i.e. MEC 20MW Phase 1 10MWQ1 2014, Phase 2 additional 10MW Q2 2015 ) | Included in submission 
5 | The number of Market Units at the WFPS (Phase 1 &2 is one market unit or two separate market units, noting that if the WFPS consists of two market units then additional signals will be required). | Included in submission 
6 | Energisation Date | Included in submission 
7 | Single Line Diagram (Note that for changes in SLD's, the Signal list requirements may change) | Included in submission 
| · Revision Number | Included in submission 
| · Ownership boundaries | Included in submission 
| · HV CB positions (IPP and ESBN as applicable) | Included in submission 
| · MV CB positions | Included in submission 
| · MV Feeders | Included in submission 
8 | Grid Connected Transformer tap range | Included in submission 
9 | Number of Met Masts on site - (if WFPS ≥10MW) | Included in submission 
10 | Nearest 110kV Station - normal feeding arrangements for WFPS | Included in submission 
11 | Confirmation of DSO RTU for the WFPS? | Included in submission 
12 | If there is no DSO RTU submission of DCC signals to be included within the DSO RTU (1-18). | Included in submission 
Information to be submitted to generator_testing@eirgrid.com via NDCC/SDCC

## 0) Signal List
WINDFARM NAME |  | Type | A | XX | MW | v0.2 |  | Signals List is based on this Single Line Diagram (SLD) as inserted.
EirGrid Signals, Command & Control Specification
Signals List |  | Registered Capacity: XX MW |  |  | Installed Plant: XXX MW
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Grid Code reference
| Double Point Status Indications | (each individual input identified separately for clarity) | [5 empty] | Note: Signals treated as 2-bit binary
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 IPP 20 kV CB |  | open |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A2 | WINDFARM T121 IPP 20 kV CB |  | closed |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1 | Typical SLD for a wind farm connecting to the system through a 38/20 kV transformer
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A13 | EirGrid Sub-Remote Control |  | off |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A14 | EirGrid Sub-Remote Control |  | on |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A15 | Blackstart Shutdown |  | off |  |  | IPP | N/A | Connection CB Trip/ Inhibit function
A16 | Blackstart Shutdown |  | on |  |  | IPP | N/A | Connection CB Trip/ Inhibit function
A17 | Reactive Device >5 Mvar 1 |  | off |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A18 | Reactive Device >5 Mvar 1 |  | on |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B2 | Active Power Control facility status (feedback) |  | on |  |  | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Grid Code reference
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1 (125% of Registered Capacity)
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1 (150% of Reactive Power at Registered Capacity)
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1 (125% of nominal connection voltage)
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1 (125% of Registered Capacity)
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4 (125% of Registered Capacity)
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | IPP | N/A | Grid Code Signals List #5 DCC11.5.2.3
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012. Phase angle will be sent by NCC to WFPS Controller.
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | IPP | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
D7 | Transformer Tap Position | 0-10 | mA | 0-21 | Tap | IPP | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | IPP | N/A | Grid Code Signals List #3 WFPS 1.7.1.3
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | IPP | N/A | Grid Code Signals List #3 WFPS 1.7.1.3
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | IPP | N/A | Grid Code Signals List #3 WFPS 1.7.1.3
Met 1 (if Registered Capacity >= 10 MW)
D11 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D12 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West), 10mA = 360deg (from the North)).
D13 | Air Temperature 1 | 0-10 | mA | -40-70 | C | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D14 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
Met N (if Registered Capacity >= 10 MW)
D15 | Wind Speed N | 0-10 | mA | 0-70 | m/s | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D16 | Wind Direction N | 0-10 | mA | 0-360 | deg | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D17 | Air Temperature N | 0-10 | mA | -40-70 | C | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D18 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | IPP | N/A | Connection CB Trip/ Inhibit function
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | IPP | N/A | Connection CB Trip/ Inhibit function
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
E8 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E9 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E10 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E11 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
Single Command Outputs
E12 | Voltage Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #5 DCC11.5.2.3
E13 | Mvar (Q) Control Facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E14 | Power Factor (PF) Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4 (125% of Registered Capacity)
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | IPP | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
Note on D1: Administrator: Insert the Type of the Wind Farm
Note on E1: Administrator: Insert the Registered Capacity of the WFPS
Note on A5: EirGrid Telecoms Interface Enclosure
Note on H5: No IPP involvement unless otherwise confirmed
Note on E47: +/-125%
Note on E49: 110kV: 0 to 132 kV 38kV: 0 to 45.6 kV 20kV: 0 to 24 kV
Note on E52: 0-120%
Note on E53: 0-120%
Note on E54: 110kV: 99 to 132 kV 38kV: 34.2 to 45.6 kV 20kV: 18 to 24 kV
Note on E110: 0 to 125%

## 1a) Inst.Info & Contact Details
WINDFARM NAME Information and Contact Details to be sent by IPP via ESB Networks to EirGrid (generator_testing@EirGrid.com)
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
DATE
| HV SUB STATION NAME |  |  |  |  | ESBTS Team |  | Liam Boland
[6 empty] | Nessan Heaslip | Karl O'Keeffe | Noel Cowhey
| EirGrid Contact Person | Colm MacManus | PHONE: |  | (+353) 1 23 70168 | Robert Groarke | Oisín Goulding
| OSP Generic Email: Generator_testing@eirgrid.com |  |  |  |  | Frank Donnelly | Colm MacManus
| EMS Generic Email: ems.services@eirgrid.com |  |  |  |  | Liam Delany | C&T Team
[6 empty] | Niall Molloy | Ciarán Maguire
| ESBTS Project Manager | ESBTS Team | PHONE: |  | (+353) 1 7027835
| ESBTS Commissioner | ESBTS Team | PHONE: |  | (+353) 1 7027835
ESBTS Generic Email: esbts.scada.services@esb.ie
| ESB Networks (SPOC) |  | PHONE:
ESB Networks Build Generic Email: IPPdelivery@esb.ie
| ESB Networks (switchgear) |  | PHONE: |  | (+ )
| ESB Networks (metering) |  | PHONE: |  | (+ )
| IPP Project Manager |  | PHONE: |  | (+ )
| Electrical Contractor |  | PHONE: |  | (+ )
| Turbine Contractor |  | PHONE: |  | (+ )
| Work Programme / Schedule (.mpp format) |  |  | Insert File
| Single Line Diagram |  |  | Insert file
| Site Layout Drawing on OS Map |  |  | Insert file
| Substation & Control Building Layout Drawing on OS Map |  |  | Insert file
| IPP Energy Management System %error |  |  | %
| Directions including Map to the Wind Farm Power Station | Insert Map and brief description
| Safety & Site information | IPP to provide details
ESBTS Standard Requirements from IPP (may be customised for particular sites):
1) 90sq mm earth for Telecoms earth bar. 2) 35sq mm bonded from external earth grid to GPS clock antenna mounting bracket and if applicable Satellite antenna mounting bracket. 3) 48V DC Power System consisting of Switched Mode Power Supply (SMPS) with sealed cell battery. 4) If applicable - Fibre termination cabinet with fibre termination unit and fibre to distant station. 5) Satellite link consisting of Satellite transceiver and antenna if applicable. Satellite antenna preferably on a south facing wall with a clear view of the horizon. 6) Install and terminate process control and signal cables in ETI (the wiring schedule is available as a worksheet in the signal list excel file).
| ESB Telecom Services - Indicative Timelines for on site works | 1) 3 weeks notice required by ESBTS to schedule resources. 2) ~1 week to install the RTU cabinet with integrated ETI and GPS clock, GPS clock antenna. 3) ~1 week to pre commission the RTU referenced to frozen signal list with IPP electrical and WTG contractors. 4) ~1 week to install and commission the satellite link including antenna (if applicable). 5) ~2 days to commission the fibre link (if applicable). 6) ~1 week to commission the RTU with IPP electrical and WTG contractors.

## 1b) IPP Wiring Completion Cert
WINDFARM NAME |  | Type | A | XX | MW | v0.2 |  | Signals List is based on this Single Line Diagram (SLD) as inserted. | Wiring Completion Cert
EirGrid Signals, Command & Control Specification | [8 empty] | Continuity Check Complete
IPP Wiring Completion Certificate (to EirGrid ETIE/RTU) to be sent by IPP to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Grid Code reference
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 IPP 20 kV CB |  | open |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A2 | WINDFARM T121 IPP 20 kV CB |  | closed |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A13 | EirGrid Sub-Remote Control |  | off |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A14 | EirGrid Sub-Remote Control |  | on |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A15 | Blackstart Shutdown |  | off |  |  | IPP | N/A | Connection CB Trip/ Inhibit function
A16 | Blackstart Shutdown |  | on |  |  | IPP | N/A | Connection CB Trip/ Inhibit function
A17 | Reactive Device >5 Mvar 1 |  | off |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
A18 | Reactive Device >5 Mvar 1 |  | on |  |  | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B2 | Active Power Control facility status (feedback) |  | on |  |  | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Grid Code reference
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1 (125% of Registered Capacity)
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1 (150% of Reactive Power at Registered Capacity)
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1 (125% of nominal connection voltage)
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | IPP | N/A | Grid Code Signals List #1 WFPS 1.7.1 (125% of Registered Capacity)
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4 (125% of Registered Capacity)
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | IPP | N/A | Grid Code Signals List #5 DCC11.5.2.3
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012. Phase angle will be sent by NCC to WFPS Controller.
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | IPP | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
D7 | Transformer Tap Position | 0-10 | mA | 0-21 | Tap | IPP | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | IPP | N/A | Grid Code Signals List #3 WFPS 1.7.1.3
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | IPP | N/A | Grid Code Signals List #3 WFPS 1.7.1.3
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | IPP | N/A | Grid Code Signals List #3 WFPS 1.7.1.3
Met 1 (if Registered Capacity >= 10 MW)
D11 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D12 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West), 10mA = 360deg (from the North)).
D13 | Air Temperature 1 | 0-10 | mA | -40-70 | C | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D14 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
Met N (if Registered Capacity >= 10 MW)
D15 | Wind Speed N | 0-10 | mA | 0-70 | m/s | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D16 | Wind Direction N | 0-10 | mA | 0-360 | deg | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D17 | Air Temperature N | 0-10 | mA | -40-70 | C | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D18 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | IPP | N/A | Connection CB Trip/ Inhibit function
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | IPP | N/A | Connection CB Trip/ Inhibit function
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
E8 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E9 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E10 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E11 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
Single Command Outputs
E12 | Voltage Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Grid Code Signals List #5 DCC11.5.2.3
E13 | Mvar (Q) Control Facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E14 | Power Factor (PF) Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | IPP | N/A | Grid Code Signals List #4 WFPS 1.7.1.4 (125% of Registered Capacity)
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | IPP | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | IPP | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet must be clearly marked with labels for identification. |  |  |  | Confirmed  |  |  |  | How is Black Start Shutdown implemented?
All cables for interfacing at station interface cabinet or EirGrid telecoms interface cabinet must be terminated at connection terminals (i.e. stripped, crimped and marked at terminal connections). |  |  |  | Confirmed 
All cables for interfacing at station interface cabinet or EirGrid telecoms interface cabinet must use colour coding agreed by all parties i.e. ESBTS & IPP. |  |  |  | Confirmed 
All analogue and digital interface signals must be tested and simulated for compliance with the frozen signal list agreed by all parties. |  |  |  | Confirmed 
ESBTS Satellite Dish bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed 
ESBTS GPS clock antenna bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed 
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 | [6 empty] | IPP Name / Position | 0
IPP Signature
Date
Note on A3: Administrator: To be completed by the IPP and sent to EirGrid to schedule ESBTS site attendance to perform continuity check
Note on A5: EirGrid Telecoms Interface Enclosure

## 2) ESB Telecoms Completion Cert
WINDFARM NAME |  | Type | A | XX | MW | v0.2 |  | Completion Cert
EirGrid Signals, Command & Control Specification | [7 empty] | Local SCADA Checks/Tests
Pre Energisation Signals Testing Certificate to be sent by ESB Telecoms Services to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 IPP 20 kV CB |  | open |  |  | IPP | N/A
A2 | WINDFARM T121 IPP 20 kV CB |  | closed |  |  | IPP | N/A
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | IPP | N/A
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | IPP | N/A
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | IPP | N/A
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | IPP | N/A
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | IPP | N/A
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | IPP | N/A
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | IPP | N/A
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | IPP | N/A
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | IPP | N/A
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | IPP | N/A
A13 | EirGrid Sub-Remote Control |  | off |  |  | IPP | N/A
A14 | EirGrid Sub-Remote Control |  | on |  |  | IPP | N/A
A15 | Blackstart Shutdown |  | off |  |  | IPP | N/A
A16 | Blackstart Shutdown |  | on |  |  | IPP | N/A
A17 | Reactive Device >5 Mvar 1 |  | off |  |  | IPP | N/A
A18 | Reactive Device >5 Mvar 1 |  | on |  |  | IPP | N/A
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | IPP | N/A
B2 | Active Power Control facility status (feedback) |  | on |  |  | IPP | N/A
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | IPP | N/A
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | IPP | N/A
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | IPP | N/A
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | IPP | N/A
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | IPP | N/A
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | IPP | N/A
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | IPP | N/A
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | IPP | N/A
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | IPP | N/A
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | IPP | N/A
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | IPP | N/A
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | N/A
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | IPP | N/A
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | IPP | N/A
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | IPP | N/A
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | IPP | N/A
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | N/A
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | IPP | N/A
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | IPP | N/A
D7 | Transformer Tap Position | 0-10 | mA | 0-21 | Tap | IPP | N/A
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | IPP | N/A
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | IPP | N/A
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | IPP | N/A
Met 1 (if Registered Capacity >= 10 MW)
D11 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | IPP | N/A
D12 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | IPP | N/A
D13 | Air Temperature 1 | 0-10 | mA | -40-70 | C | IPP | N/A
D14 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | IPP | N/A
Met N (if Registered Capacity >= 10 MW)
D15 | Wind Speed N | 0-10 | mA | 0-70 | m/s | IPP | N/A
D16 | Wind Direction N | 0-10 | mA | 0-360 | deg | IPP | N/A
D17 | Air Temperature N | 0-10 | mA | -40-70 | C | IPP | N/A
D18 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | IPP | N/A
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | IPP | N/A
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | IPP | N/A
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | IPP | N/A
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | IPP | N/A
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | IPP | N/A
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | IPP | N/A
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | IPP | N/A
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A
E8 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A
E9 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A
E10 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A
E11 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | IPP | N/A
Single Command Outputs
E12 | Voltage Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A
E13 | Mvar (Q) Control Facility status |  | on | pulse | 0.5 seconds | IPP | N/A
E14 | Power Factor (PF) Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | IPP | N/A
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | IPP | N/A
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | IPP | N/A
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | IPP | N/A
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | IPP | N/A
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
How is NOIS implemented?
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet are installed and correct. |  |  |  | Confirmed  |  |  | ESBTS Name / Position | ESBTS Team
ESBTS Signature
Date
| NOTE: Non operable IPP signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  | Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
Note on A5: EirGrid Telecoms Interface Enclosure

## 2 a) EMS Database Setup Cert
WINDFARM NAME |  | Type | A | XX | MW | v0.2
EirGrid Signals, Command & Control Specification
Energy Management System (EMS) Database setup Certificate
Completion Cert
Continuity Check Complete
Generator Modelled
Lines Modelled
Station Modelled
Calculations Updated
RTU Modelled
Display Work Completed:
WF SLD
Station SLD
Station List
Windfarm List
Embedded Wind
Windfarm Control
Station Wind MW
Wind Overview
Windfarm Availability Data
Blue Alert Page
Windfarm Weather Data
DCC signals provided via ICCP
EMS Name
EMS Signature
Date
EirGrid Internal Document - no IPP requirements. For Information only
Note on A3: Administrator: DCC to be Informed

## 3)Pre Energ. Sign&Con Test Cert
WINDFARM NAME |  | Type | A | XX | MW | v0.2 |  | Pre Energisation Signals and Controls Test
EirGrid Signals, Command & Control Specification | [7 empty] | Simulated □/Real □ value tested | mA Range | Value Range | Comment
Pre Energisation Signals & Controls Certificate to be sent by ESBT to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 IPP 20 kV CB |  | open |  |  | IPP | N/A | Real □
A2 | WINDFARM T121 IPP 20 kV CB |  | closed |  |  | IPP | N/A | Real □
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | IPP | N/A | Real □
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | IPP | N/A | Real □
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | IPP | N/A | Real □
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | IPP | N/A | Real □
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | IPP | N/A | Real □
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | IPP | N/A | Real □
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | IPP | N/A | Real □
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | IPP | N/A | Real □
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | IPP | N/A | Real □
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | IPP | N/A | Real □
A13 | EirGrid Sub-Remote Control |  | off |  |  | IPP | N/A | Real □
A14 | EirGrid Sub-Remote Control |  | on |  |  | IPP | N/A | Real □
A15 | Blackstart Shutdown |  | off |  |  | IPP | N/A | Real □
A16 | Blackstart Shutdown |  | on |  |  | IPP | N/A | Real □
A17 | Reactive Device >5 Mvar 1 |  | off |  |  | IPP | N/A | Real □
A18 | Reactive Device >5 Mvar 1 |  | on |  |  | IPP | N/A | Real □
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | IPP | N/A | Simulated □
B2 | Active Power Control facility status (feedback) |  | on |  |  | IPP | N/A | Simulated □
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | IPP | N/A | Simulated □
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | IPP | N/A | Simulated □
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | IPP | N/A | Simulated □
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | IPP | N/A | Simulated □
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | IPP | N/A | Simulated □
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | IPP | N/A | Simulated □
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | IPP | N/A | Simulated □
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | IPP | N/A | Simulated □
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | IPP | N/A | Simulated □
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | IPP | N/A | Simulated □
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | IPP | N/A | Real □
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | N/A | Real □
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | IPP | N/A | Real □
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | IPP | N/A | Simulated □
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | IPP | N/A | Simulated □
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | IPP | N/A | Simulated □
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | N/A | Simulated □
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | IPP | N/A | Simulated □
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | IPP | N/A | Simulated □
D7 | Transformer Tap Position | 0-10 | mA | 0-21 | Tap | IPP | N/A | Simulated □
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | IPP | N/A | Simulated □
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | IPP | N/A | Simulated □
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | IPP | N/A | Simulated □
Met 1 (if Registered Capacity >= 10 MW)
D11 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | IPP | N/A | Simulated □
D12 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | IPP | N/A | Simulated □
D13 | Air Temperature 1 | 0-10 | mA | -40-70 | C | IPP | N/A | Simulated □
D14 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Simulated □
Met N (if Registered Capacity >= 10 MW)
D15 | Wind Speed N | 0-10 | mA | 0-70 | m/s | IPP | N/A | Simulated □
D16 | Wind Direction N | 0-10 | mA | 0-360 | deg | IPP | N/A | Simulated □
D17 | Air Temperature N | 0-10 | mA | -40-70 | C | IPP | N/A | Simulated □
D18 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Simulated □
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | IPP | N/A | Simulated □
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Simulated □
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | IPP | N/A | Simulated □
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | IPP | N/A | Simulated □
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | IPP | N/A | Simulated □
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | IPP | N/A | Simulated □
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | IPP | N/A | Simulated □
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | IPP | N/A | Simulated □
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Simulated □
E8 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Simulated □
E9 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Simulated □
E10 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Simulated □
E11 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Simulated □
Single Command Outputs
E12 | Voltage Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Simulated □
E13 | Mvar (Q) Control Facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Simulated □
E14 | Power Factor (PF) Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Simulated □
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | IPP | N/A | Simulated □
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | IPP | N/A | Simulated □
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | IPP | N/A | Simulated □
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | IPP | N/A | Simulated □
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | IPP | N/A | Simulated □
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
Simulation Point
| How is NOIS implemented? |  |  |  |  | Simulation Method
[6 empty] | IPP Name / Position |  | 0
IPP Signature
EMS Name
EMS Signature
| NOTE: Non operable IPP signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  |  |  |  | ESB Telecoms Name / Position |  | ESBTS Team
| Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 |  |  |  |  | ESB Telecoms Signature
Date
Note on I1: Administrator: ESBTS Commission from NCC control desk to / via ETI to IPP plant.
Note on I2: Administrator: the electrical characteristics of IPP signals not tested due to plant unavailability must be simulated by IPP.
Note on A5: EirGrid Telecoms Interface Enclosure

## 4) Post Ener Pre Grid Code Cert
WINDFARM NAME |  | Type | A | XX | MW | v0.2 |  | Post Energisation Signals and Controls Test
EirGrid Signals, Command & Control Specification | [7 empty] | Simulated □/Real □ value tested | mA Range | Value Range | Comment
Post Energisation Signals and Controls (Pre Grid Code Check) Cert to be sent by ESBT to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 IPP 20 kV CB |  | open |  |  | IPP | N/A | Real □
A2 | WINDFARM T121 IPP 20 kV CB |  | closed |  |  | IPP | N/A | Real □
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | IPP | N/A | Real □
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | IPP | N/A | Real □
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | IPP | N/A | Real □
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | IPP | N/A | Real □
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | IPP | N/A | Real □
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | IPP | N/A | Real □
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | IPP | N/A | Real □
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | IPP | N/A | Real □
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | IPP | N/A | Real □
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | IPP | N/A | Real □
A13 | EirGrid Sub-Remote Control |  | off |  |  | IPP | N/A | Real □
A14 | EirGrid Sub-Remote Control |  | on |  |  | IPP | N/A | Real □
A15 | Blackstart Shutdown |  | off |  |  | IPP | N/A | Real □
A16 | Blackstart Shutdown |  | on |  |  | IPP | N/A | Real □
A17 | Reactive Device >5 Mvar 1 |  | off |  |  | IPP | N/A | Real □
A18 | Reactive Device >5 Mvar 1 |  | on |  |  | IPP | N/A | Real □
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | IPP | N/A | Real □
B2 | Active Power Control facility status (feedback) |  | on |  |  | IPP | N/A | Real □
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | IPP | N/A | Real □
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | IPP | N/A | Real □
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | IPP | N/A | Real □
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | IPP | N/A | Real □
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | IPP | N/A | Real □
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | IPP | N/A | Real □
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | IPP | N/A | Real □
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | IPP | N/A | Real □
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | IPP | N/A | Real □
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | IPP | N/A | Real □
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | IPP | N/A | Real □
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | N/A | Real □
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | IPP | N/A | Real □
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | IPP | N/A | Real □
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | IPP | N/A | Real □
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | IPP | N/A | Real □
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | N/A | Real □
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | IPP | N/A | Real □
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | IPP | N/A | Real □
D7 | Transformer Tap Position | 0-10 | mA | 0-21 | Tap | IPP | N/A | Real □
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | IPP | N/A | Real □
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | IPP | N/A | Real □
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | IPP | N/A | Real □
Met 1 (if Registered Capacity >= 10 MW)
D11 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | IPP | N/A | Real □
D12 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | IPP | N/A | Real □
D13 | Air Temperature 1 | 0-10 | mA | -40-70 | C | IPP | N/A | Real □
D14 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Real □
Met N (if Registered Capacity >= 10 MW)
D15 | Wind Speed N | 0-10 | mA | 0-70 | m/s | IPP | N/A | Real □
D16 | Wind Direction N | 0-10 | mA | 0-360 | deg | IPP | N/A | Real □
D17 | Air Temperature N | 0-10 | mA | -40-70 | C | IPP | N/A | Real □
D18 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Real □
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | IPP | N/A | Real □
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Real □
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | IPP | N/A | Real □
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | IPP | N/A | Real □
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | IPP | N/A | Real □
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | IPP | N/A | Real □
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | IPP | N/A | Real □
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | IPP | N/A | Real □
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Real □
E8 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Real □
E9 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Real □
E10 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Real □
E11 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Real □
Single Command Outputs
E12 | Voltage Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Real □
E13 | Mvar (Q) Control Facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Real □
E14 | Power Factor (PF) Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Real □
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | IPP | N/A | Real □
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | IPP | N/A | Real □
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | IPP | N/A | Real □
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | IPP | N/A | Real □
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | IPP | N/A | Real □
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
How is NOIS implemented?
[6 empty] | IPP Name |  | 0
IPP Signature
EMS Name
EMS Signature
| NOTE: Non operable IPP signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  |  |  |  | ESB Telecoms Name / Position |  | ESBTS Team
| Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 |  |  |  |  | ESB Telecoms Signature
Date
Note on A5: EirGrid Telecoms Interface Enclosure

## ETIE
EirGrid Telecoms Interface Enclosure (ETIE)
Typical EirGrid RTU cabinet with integrated ETI and GPS clock 2.0m x 0.8m x 0.6m (rear access not required).
Note: This is for a typical installation and may vary from project to project. Any queries should be directed to generator_testing@eirgrid.com or esbts.scada.services@esb.ie
ETIE General Description
There will be four rows of terminals labelled Row 1, 2, 3, 4 as shown in the Layout drawing and Photograph above
Trunking shall be separated into IPP and EirGrid Telecoms trunking.
EirGrid Telecoms cabling to be in EirGrid Telecoms designated trunking only
IPP cabling to be in IPP designated trunking only
Access to terminals will be as follows:
Upper side to be used for EirGrid Telecoms use only
Lower side to be used for IPP use only
Isolating link to sever all connection between the IPP connection and EirGrid Telecoms connection
Command terminals to be covered with a Perspex cover and labelled "DO NOT ENERGISE"
Earthing of cabinet to be completed in accordance with 35 sq mm earth cable to EirGrid Telecoms earth bar

## ETIE Layout
Designation: Indications/Signals |  | ETIE Ref | ETIE ROW 1
POSITIVE 24V or 48V DC DOUBLE POINT INDICATION |  |  | +
WINDFARM T121 IPP 20 kV CB | open | A1 | 1
WINDFARM T121 IPP 20 kV CB | closed | A2 | 2
WINDFARM Feeder 1 20 kV CB | open | A3 | 3
WINDFARM Feeder 1 20 kV CB | closed | A4 | 4
WINDFARM Feeder 2 20 kV CB | open | A5 | 5
WINDFARM Feeder 2 20 kV CB | closed | A6 | 6
WINDFARM Feeder 3 20 kV CB | open | A7 | 7
WINDFARM Feeder 3 20 kV CB | closed | A8 | 8
WINDFARM Feeder 4 20 kV CB | open | A9 | 9
WINDFARM Feeder 4 20 kV CB | closed | A10 | 10
WINDFARM Feeder 5 20 kV CB | open | A11 | 11
WINDFARM Feeder 5 20 kV CB | closed | A12 | 12
EirGrid Sub-Remote Control | off | A13 | 13
EirGrid Sub-Remote Control | on | A14 | 14
Blackstart Shutdown | off | A15 | 15
Blackstart Shutdown | on | A16 | 16
Reactive Device >5 Mvar 1 | off | A17 | 17
Reactive Device >5 Mvar 1 | on | A18 | 18
Active Power Control facility status (feedback) | off | B1 | 19
Active Power Control facility status (feedback) | on | B2 | 20
Frequency Response System Mode Status (feedback) | off | B3 | 21
Frequency Response System Mode Status (feedback) | on | B4 | 22
Frequency Response Curve (feedback) | Curve 1 | B5 | 23
Frequency Response Curve (feedback) | Curve 2 | B6 | 24
AVR (kV) Control facility status (feedback) | off | B7 | 25
AVR (kV) Control facility status (feedback) | on | B8 | 26
Q (Mvar) Control facility status (feedback) | off | B9 | 27
Q (Mvar) Control facility status (feedback) | on | B10 | 28
Power Factor (PF) Control facility status (feedback) | off | B11 | 29
Power Factor (PF) Control facility status (feedback) | on | B12 | 30
31
32
33
34
35
36
37
38
39
40
POSITIVE 24V or 48V DC SINGLE POINT INDICATION |  |  | +
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
Designation: Measurands |  | ETIE Ref | ETIE ROW 2
Active Power Output at LV side of Grid Connected Transformer |  | C1 | 1
Active Power Output at LV side of Grid Connected Transformer |  | C1 | 2
Reactive Power at LV side of Grid Connected Transformer |  | C2 | 3
Reactive Power at LV side of Grid Connected Transformer |  | C2 | 4
Voltage at LV side of Grid Connected Transformer |  | C3 | 5
Voltage at LV side of Grid Connected Transformer |  | C3 | 6
Available Active Power |  | D1 | 7
Available Active Power |  | D1 | 8
Active Power Control Setpoint (feedback) |  | D2 | 9
Active Power Control Setpoint (feedback) |  | D2 | 10
Voltage Control Setpoint (feedback) |  | D3 | 11
Voltage Control Setpoint (feedback) |  | D3 | 12
Mvar (Q) Control Setpoint (feedback) |  | D4 | 13
Mvar (Q) Control Setpoint (feedback) |  | D4 | 14
Power Factor (PF) Control Setpoint (feedback) |  | D5 | 15
Power Factor (PF) Control Setpoint (feedback) |  | D5 | 16
Frequency Droop Setting (feedback) |  | D6 | 17
Frequency Droop Setting (feedback) |  | D6 | 18
Transformer Tap Position |  | D7 | 19
Transformer Tap Position |  | D7 | 20
%WTG not generating due to high wind |  | D8 | 21
%WTG not generating due to high wind |  | D8 | 22
%WTG not generating due to low wind |  | D9 | 23
%WTG not generating due to low wind |  | D9 | 24
Wind Farm Availability |  | D10 | 25
Wind Farm Availability |  | D10 | 26
Wind Speed 1 |  | D11 | 27
Wind Speed 1 |  | D11 | 28
Wind Direction 1 |  | D12 | 29
Wind Direction 1 |  | D12 | 30
Air Temperature 1 |  | D13 | 31
Air Temperature 1 |  | D13 | 32
Air Pressure 1 |  | D14 | 33
Air Pressure 1 |  | D14 | 34
Wind Speed N |  | D15 | 35
Wind Speed N |  | D15 | 36
Wind Direction N |  | D16 | 37
Wind Direction N |  | D16 | 38
Air Temperature N |  | D17 | 39
Air Temperature N |  | D17 | 40
Air Pressure N |  | D18 | 41
Air Pressure N |  | D18 | 42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
Designation: Commands |  | ETIE Ref | ETIE ROW 3
Analogue Output Active Power Control Setpoint |  | G1 | 1
Analogue Output Active Power Control Setpoint |  | G1 | 2
Analogue Voltage Control Setpoint |  | G2 | 3
Analogue Voltage Control Setpoint |  | G2 | 4
Analogue Mvar (Q) Control Setpoint |  | G3 | 5
Analogue Mvar (Q) Control Setpoint |  | G3 | 6
Analogue Power Factor (PF) Control Setpoint |  | G4 | 7
Analogue Power Factor (PF) Control Setpoint |  | G4 | 8
Frequency Droop Setting |  | G5 | 9
Frequency Droop Setting |  | G5 | 10
Designation: Controls |  | ETIE Ref | ETIE ROW 4
Active Power Control facility status | off | E1 | 1
Command Negative |  |  | 2
Active Power Control facility status | on | E2 | 3
Frequency Response System Mode Status | off | E3 | 4
Command Negative |  |  | 5
Frequency Response System Mode Status | on | E4 | 6
Frequency Response Curve Select | Curve 1 | E5 | 7
Command Negative |  |  | 8
Frequency Response Curve Select | Curve 2 | E6 | 9
Command Output |  |  | 10
Command Negative |  |  | 11
Single Command Outputs | 0 | 0 | 12
Command Output |  |  | 13
Command Negative |  |  | 14
Voltage Control facility status | on | E12 | 15
Command Output |  |  | 16
Command Negative |  |  | 17
Mvar (Q) Control Facility status | on | E13 | 18
Blackstart Shutdown | off | F1 | 19
Command Negative |  |  | 20
Blackstart Shutdown | on | F2 | 21
Command Output |  |  | 22
Command Negative |  |  | 23
Command Output |  |  | 24
Command Output |  |  | 25
Command Negative |  |  | 26
Command Output |  |  | 27
Command Output |  |  | 28
Command Negative |  |  | 29
Command Output |  |  | 30
Single Controls |  |  | +
31
32
33
34
35
36
37
38
39
40
41
42
Digital Output Frequency Droop Setting Enable |  | E11 | 43
|  | E11 | 44
Digital Output Active Power Control Setpoint Enable |  | E7 | 45
|  | E7 | 46
Digital Output Voltage Control (kV) Setpoint Enable |  | E8 | 47
|  | E8 | 48
Digital Output Mvar Control (Q) Setpoint Enable |  | E9 | 49
|  | E9 | 50
Digital Output Power Factor Control (PF) Setpoint Enable |  | E10 | 51
|  | E10 | 52
Note on D2: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4
Note on D68: Administrator: Administrator: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4
Note on D133: Administrator: There is a gap between the off / on commands for command negative
Note on D144: Administrator: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4

## Freq,Ramping,Voltage Settings
Frequency, Ramp Rate and Voltage Settings to be implemented in Wind Farm Control System
Definitions:
| AAP | Available Active Power
| DMOL | Designed Minimum Operating Level
| APC | Active Power Control
Frequency Response Mode On | [5 empty] | Frequency Response Diagrams
Curve 1: Wind Following Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 48 |  | 100% of AAP
|  | FA | 48 | PA | 100% of AAP
|  | Under Frequency Response | 48 < f < 49.8 |  | 100% of AAP
|  | FB | f = 49.8 | PB | 100% of AAP
|  | +/-0.2Hz Deadband | 49.8 < f < 50.2 |  | 100% of AAP
|  | FC | f = 50.2 | PC | 100% of AAP
|  | Over Frequency Response | 50.2 < f < 50.79 |  | AAP + ∆MW2
|  | FD | f = 50.79 | PD | Minimum of: AAP and DMOL
|  | FE | f = 50.8 | PE | 0%3
|  |  | f > 50.8 |  | 0%3
Curve 1: Active Power Control Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 48 |  | 100% of AAP
|  | FA | f = 48 | PA | 100% of AAP
|  | Under Frequency Response | 48 < f < 49.985 |  | Minimum of: APC Setpoint + ∆MW and AAP
|  | FB | f = 49.985 | PB | Minimum of: APC Setpoint and AAP
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | Minimum of: APC Setpoint and AAP
|  | FC | f = 50.015 | PC | Minimum of: APC Setpoint and AAP
|  | Over Frequency Response | 50.015 < f < 50.79 |  | Minimum of: APC Setpoint + ∆MW and AAP + ∆MW1, 2
|  | FD | f = 50.79 | PD | Minimum of: APC Setpoint and AAP and DMOL
|  | FE | f = 50.8 | PE | 0%3
|  |  | f > 50.8 |  | 0%3
Curve 2: Wind Following Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f <49.3 |  | 100% of AAP
|  | FA | f = 49.3 | PA | 100% of AAP
|  | Under Frequency Response | 49.3 < f < 49.985 |  | 95% of Available Active Power + ∆MW
|  | FB | f = 49.985 | PB | 95% of Available Active Power. This is = to 5% Reserve.
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | 95% of Available Active Power. This is = to 5% Reserve.
|  | FC | f = 50.015 | PC | 95% of Available Active Power. This is = to 5% Reserve.
|  | Over Frequency Response | 50.015 < f < 50.79 |  | 95% of AAP + ∆MW2
|  | FD | f = 50.79 | PD | Minimum of: AAP and DMOL
|  | FE | f = 50.8 | PE | 0%3
|  |  | f > 50.8 |  | 0%3
Curve 2: Active Power Control Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 49.3 |  | 100% of AAP
|  | FA | f = 49.3 | PA | 100% of AAP
|  | Under Frequency Response | 49.3 < f < 49.985 |  | Minimum of: AAP and APC Setpoint + ∆MW
|  | FB | f = 49.985 | PB | Minimum of: APC Setpoint and 95% of AAP
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | Minimum of: APC Setpoint and 95% of AAP
|  | FC | f = 50.015 | PC | Minimum of: APC Setpoint and 95% of AAP
|  | Over Frequency Response | 50.015 < f < 50.79 |  | Minimum of: APC Setpoint + ∆MW and 95% of AAP + ∆MW1, 2
|  | FD | f = 50.79 | PD | Minimum of: APC Setpoint and AAP and DMOL
|  | FE | f = 50.8 | PE | 0%3
|  |  | f > 50.8 |  | 0%3
Minimum reserve level in Curve 2 is 5% of Registered Capacity, not lower than DMOL (settable between DMOL and 100%)
Frequency Response Mode OFF
Curve 1 and Curve 2: Wind Following Mode
|  |  | Transmission System Frequency (Hz) |  | Required Active Power Output
|  |  | 47.5 ≤ f ≥ 52 | No governor action | 100% of AAP
Curve 1 and Curve 2: Active Power Control Mode
|  |  | Transmission System Frequency (Hz) |  | Required Active Power Output
|  |  | 47.5 ≤ f ≥ 52 | No governor action | Minimum of: AAP and APC Setpoint
1 APC Setpoint + ∆MW shall have a lower limit of the minimum of: APC Setpoint and DMOL.
2 (95% of) AAP + ∆MW shall have a lower limit of the minimum of AAP and DMOL
3 Any WTG which has disconnected due to high frequency shall be brought back on load as fast as technically feasible, provided the Frequency has fallen below 50.2Hz.
DMOL shall not be greater than 12% of Registered Capacity
If AAP < DMOL and f < FE, maximise output
Ramp Rates:
|  | Mode | Rate | Priority | Comment
|  | Frequency Response | As fast as technically possible. 60% of its expected Active Power response within 5 seconds 100% of its expected Active Power response within 15 seconds. | 1 | The WFPS shall latch its AAP when the frequency excursion occurs and calculate its expected response based on this value.
|  | Active Power Dispatch | 20% of Registered Capacity per Minute | 2 | Settable between: 1-100% Registered Capacity per Minute
|  | Wind Following | 20% of Registered Capacity per Minute | 3 | Settable between: 1-100% Registered Capacity per Minute
Frequency Droop:
|  | Frequency Droop | Droop Calculation | Comment
|  | 4% |  | Settable between: 2-10%, online
Rate of Change of Frequency:
If possible, ROCOF should be disabled on Transmission System-connected Windfarms. If this is not possible, ROCOF should be set to max that machine is capable of. Under no circumstances should ROCOF be set to less than 0.5 Hz/s
Proposed Modification to Grid Code. (Ref#MPID 229).
Voltage Regulation System Slope Setting
|  | Voltage System Slope | Voltage Calculation | Comment
|  | 4% |  | 90% of steady State Reactive Power response within 1 second including transition from maximum Mvar production to maximum Mvar absorption or vice-versa.
Note. Frequency Response settings have been updated to clarify expected performance below DMOL - per feedback from industry. Changes are highlighted in red.

## IPP Turbine Protection Settings
Recommended Wind Farm Power Station (WFPS) Turbine Protection Settings to be applied by IPP
| Underfrequency stage 1 Setpoint | f< | 47.5 Hz | If only two stages available for underfrequency on relay, use stage 2 and stage 3
| Underfrequency stage 1 time delay | t< | 3600 s
| Underfrequency stage 2 Setpoint | f<< | 47.4 Hz
| Underfrequency stage 2 time delay | t<< | 20 s
| Underfrequency stage 3 Setpoint | f<<< | 46.9 Hz
| Underfrequency stage 3 time delay | t<<< | 1 s
| Overfrequency stage 1 Setpoint | f> | 52Hz
| Overfrequency stage 1 time delay | t> | 3600 s
| Overfrequency stage 2 Setpoint | f>> | 52.1 Hz
| Overfrequency stage 2 time delay | t>> | 1 s
| Rate of Change of Frequency setpoint | df/dt | Max | If possible, ROCOF should be disabled on Transmission System-connected Windfarms. If this is not possible, ROCOF should be set to max that machine is capable of. Under no circumstances should ROCOF be set to less than 0.5 Hz/s
| Rate of Change of Frequency delay | t | Max
| Undervoltage stage 1 Setpoint | U< | 0.89 pu
| Undervoltage stage 1 time delay | t< | 3 s
| Undervoltage stage 2 Setpoint | U<< | 0.14 pu
| Undervoltage stage 2 time delay | t<< | 0.625 s
| Overvoltage stage 1 Setpoint | U> | 1.11 pu
| Overvoltage stage 1 time delay | t> | 60 s | This is the minimum time delay we would recommend. If the plant can operate at this voltage for longer periods, then a longer time delay (at the discretion of the IPP) should be implemented.
| Overvoltage stage 2 Setpoint | U>> | 1.2 pu
| Overvoltage stage 2 time delay | t>> | 15 s | This is the minimum time delay we would recommend. If the plant can operate at this voltage for longer periods, then a longer time delay (at the discretion of the IPP) should be implemented.

## Test Procedure Template
Grid Code Compliance Tests and Test Procedures
Test Template located at the following:
http://www.eirgrid.com/media/Grid%20Code%20Compliance%20Test%20Procedure%20for%20Wind%20Farms.pdf
SCHEDULE OF GRID CODE COMPLIANCE TESTS
Wind Farm: | [8 empty] | Date:
ID | Grid Code Compliance Test | Grid Code Clause (V3.2) | Test Procedure Reference | Mandatory Test in Presence of Witness on Site | Test Preferred in the Presence of Witness on Site | Preferred Test from TSO | Remote Control from TSO | Current Test Status | On Site Testing Date: | Remote Testing Date: | Sub-sequent Test Status | On Site Testing Date: | Remote Testing Date:
1 | Fault Ride Through | WFPS1.4
2 | Transmission System Frequency Ranges | WFPS1.5.1
| Active Power Management | WFPS1.5.2
3 | Active Power Control | WSPS1.5.2.1 |  | Yes |  |  | Yes
4 | Frequency Response | WFPS1.5.2.2 |  | Yes |  |  | Yes
5 | Ramp Rates and Start Up Test | WSPS1.5.3 |  | Yes
| Transmission System Voltage Requirements | WFPS1.6
6 | Transmission System Voltage Range | WFPS1.6.1 |  | Yes
7 | Automatic Voltage Regulation | WFPS1.6.2 |  | Yes |  |  | Yes
8 | Reactive Power Capability | WFPS1.6.3 |  | Yes |  |  | Yes
9 | Voltage Step Emissions | WFPS1.6.4 |  | Yes
| Signals, Communications and Control | WFPS1.7
10 | Signals, Communications and Control | WFPS1.7
10.1 to 10.5 | Signals from Controllable WFPS to the TSO | WFPS1.7.1
10.1 | Signal List #1 | WFPS1.7.1.1 |  | Yes |  |  | Yes
10.2 | Signal List #2 - Meteorological Data | WFPS1.7.1.2 |  | Yes |  |  | Yes
10.3 | Signal List #3 – Availability Data | WFPS1.7.1.3 |  | Yes |  |  | Yes
10.4 | Signal List #4 – Active Power Control Data | WFPS1.7.1.4 |  | Yes |  |  | Yes
10.5 | Signal List #5 – Frequency Response System Data | WFPS1.7.1.5 |  | Yes |  |  | Yes
10.6 to 10.9 | Control Signals from the TSO to the Controllable Wind Farm | WFPS1.7.2
10.6 | Active Power Control | WFPS1.7.2.2 |  | Yes |  |  | Yes
10.7 | Frequency Response | WFPS1.7.2.3 |  | Yes |  |  | Yes
10.8 | Voltage Regulation | WFPS1.7.2.4 |  | Yes |  |  | Yes
10.9 | Black Start Shutdown | WFPS1.7.2.5 |  | Yes |  |  | Yes
11 | Capacity |  |  |  | Yes |  | Yes
12 | Protection Test – Under / Over Frequency and Under / Over Voltage.
13 | Protection Test – Trip and Close selected HV line(s) in Wind Farm feeder station
14 | Disturbance Test – Trip of HV line feeding wind farm with Standby Diesel Generator |  |  | Yes |  |  | Yes
15 | Disturbance Test – Trip of HV line feeding wind farm without Standby Diesel Generator |  |  | Yes |  |  | Yes
16 | Disturbance Test – Trip of grid connected power transformer with Standby Diesel Generator |  |  | Yes |  |  | Yes
17 | Disturbance Test – Trip of grid connected power transformer without Standby Diesel Generator |  |  | Yes |  |  | Yes
18 | Black Start Shutdown Test – Trip of main wind farm CB in response to Black Start Shutdown signal |  |  | Yes |  |  | Yes
IPP to develop Test Procedure and agree with generator_testing@eirgrid.com via NDCC/SDCC at least 10 Business Days in advance of testing