## Cover Sheet
Signal List and Control System Parameter settings for WINDFARM NAME Type B XX MW v0.2
Disclaimer:
This Signal List contains information (and/or attachments) which may be privileged or confidential. All content is intended solely for the use of the individual or entity to whom it is addressed. If you are not the intended recipient please be aware that any disclosure, copying, distribution or use of the contents of this message is prohibited. If you suspect that you have received this Signal List in error please notify EirGrid immediately. Further information can be found at: http://www.eirgrid.com/aboutus/legal/

## Version Control
WINDFARM NAME Signal List Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by
0.1 |  |  |  |  | first draft
0.2 | 2015-03-23 |  |  |  | Frequency Response updated to clarify performance below DMOL per feedback from industry
Note on D3: Administrator: All signal lists circulated to EMS and ESBT for Review before issuance.

## Requirements, Process & Notes B
Requirements as per the Distribution Code DCC11.1.4
Type | B | Wind Farm Power Stations are classed as being Connection Type B when connected at a Distribution System Voltage (≤ 38 kV) to a dedicated Wind Farm Power Station(s) transmission station. There are no load customers connected to the DSO operated 38/20/10 kV busbar.
Wind Farm Size | <5 MW | >= 5 MW | >= 10 MW
TSO RTU requirement
| No TSO RTU installed | TSO RTU Installed | TSO RTU Installed
Station controls
|  | EirGrid Remote Control Switch | EirGrid Remote Control Switch
|  | Network Operator Initiated Shutdown | Network Operator Initiated Shutdown
Wind farm signals
|  | Available Active Power | Available Active Power
|  | Wind Farm Availability | Wind Farm Availability
|  | %WTG not generating due to high wind | %WTG not generating due to high wind
|  | %WTG not generating due to low wind | %WTG not generating due to low wind
Wind Speed
Wind Direction
Air Temperature
Air Pressure
Station controls |  |  |  | DCC11.1.4 Figure 5
|  | Remote Control Switch | Network Operator Remote Control Switch
|  | Network Operator Initiated Shutdown | Network Operator Initiated Shutdown
Station signals
|  | Active Power Measurement | Active Power Measurement
|  | Reactive Power Measurement | Reactive Power Measurement
|  | Voltage Measurement | Voltage Measurement
|  | DSO cable protection signals | DSO cable protection signals
|  | Connection and / or Transformer HV CB | Connection and / or Transformer HV CB
|  | Connection and / or Transformer MV CB | Connection and / or Transformer MV CB
|  | Feeder 20kV CB's | Feeder 20kV CB's
Detailed Process Overview
Additional Notes
A. Each Cert number 0, 1, 2, 3, 4, from the process flow map corresponds to the subsequent Tab within the .xcl file which needs to be sent to generator_testing@eirgrid.com by the responsible party (IPP, ESBT or EMS). B. The IPP via ESBN provides most up-to-date SLD and Connection Type (as per the Distribution code DCC 11.1.4). Any changes in the SLD will require a new Signal List developed by EirGrid. This may take from 2 to 4 weeks. This may subsequently postpone the Energisation Date by (2-4 weeks). The Signal list is reviewed by EirGrid and sent to IPP via ESBN for feedback. Once all feedback has been addressed the Signal List is Frozen by EirGrid. This should be done not less than 6 months prior to energisation and will be communicated to IPP via ESBN. C. The RTU / ETIE should be installed on site not less than 4 weeks prior to energisation. D. The IPP via ESBN submits the IPP Wiring Completion Cert and Wind Farm Contact Details in advance of Energisation. This is required before ESBT arrive on site to carry out Joint Signals Check. This may be carried out in accordance with ESBT timelines listed on Tab 1) Inst. Info & Contact Details. E. Joint Signals Check is carried out by IPP / ESBT / EMS EirGrid / DCC. As this is pre-energisation the IPP may provide simulated signals to the TSO RTU which will be verified by EMS / DCC. Any issues identified at Joint Signals Check must be addressed prior to energisation. F. The Energisation is as per Energisation Instruction issued by DCC as applicable. There is a 5MW export capacity limit applied to the Wind Farm Power Station. This remains in place until a Dispatch Test is carried out. The capacity limit allows for some of the Wind Turbines to be commissioned at this time. G. Joint Pre-Grid Code Check is carried out by carried out by IPP / ESBT / EMS EirGrid / DCC. As this is post-energisation the IPP must provide real signals via TSO RTU which will be verified by EMS / DCC. Any issues identified at Joint Pre Grid Code Check must be addressed prior to the Dispatch Test. H. The Dispatch Test reviews the Active Power Control System is working correctly and the Availability Signal is within the standard. The 5MW export capacity limit is applied locally at the WFPS until a Dispatch test is carried out by NCC. The IPP via ESBN must schedule this at least 10 days in advance of testing. Once complete the new capacity limit tested value + amount 'X' is applied. These tests continue until the MEC is reached where a final Dispatch Test is carried out. I. Once the Dispatch test is carried out for the MEC of the Wind Farm Power Station, the WFPS is confirmed 'Operationally Ready' and may register as a VPTG within the Market. The IPP must apply to SEMO and should allow ~25 days to change class. J. Test procedures must be submitted to EirGrid in Advance of Grid Code Compliance Testing (GCCT). These procedures must be agreed by no less than 10 days in advance of testing. K. IPP via ESBN must monitor the Wind Conditions and liaise with EirGrid to carry out Grid Code Compliance Testing. There is a minimum 75% requirement to carry out GCCT. Note: NCC one unit per day testing limit. 10 days in advance of testing. Confirmation required 10/5/3/1 days in advance of testing. L. Grid Code Compliance Testing is carried out with an EirGrid Witness on site. M. High resolution raw data from agreed measurements is submitted to EirGrid on the day of test or an agreed timeframe after the test. A Grid Code Compliance Testing report must be submitted to EirGrid for review. This is submitted within an agreed timeframe. Should any issues be identified a retest may be required as per K) above. N. Should there be no further issues after GCCT has been successfully carried out, an Operational Certificate will be issued Note that this is the general process notes and exceptions may apply depending on circumstance. ALL queries for clarification should be referred to generator_testing@eirgrid.com. |  |  |  |  | Reference Documents:
EirGrid Telecoms Interface Cabinet Connection Details (using ETI Ref)
Recommended ESBTS cabling standards advised on signal list
Network Operator Initiated Shutdown Specification
Remote Control Specification
[5 empty] | Grid Code | http://www.eirgrid.com/operations/gridcode/
[5 empty] | Distribution Code: | http://www.esb.ie/esbnetworks/en/about-us/our_networks/distribution_code.jsp
[5 empty] | Available Active Power Standard | http://www.eirgrid.com/media/Quality%20Standard%20for%20Windfarm%20Active%20Power.pdf
Abbreviations
[6 empty] | TSO | Transmission System Operator - EirGrid
[6 empty] | EMS | Energy Management System - EirGrid
[6 empty] | DSO | Distribution System Operator - ESBN
[6 empty] | ESBN | ESB Networks
[6 empty] | ESBTS | ESB Telecoms Services
[6 empty] | RTU | Remote Terminal Unit
[6 empty] | ETIE | EirGrid Terminal Interface Enclosure
[6 empty] | NOIS | Network Operator Initiated Shutdown
[6 empty] | WTG | Wind Turbine Generator
[6 empty] | CB | Circuit Breaker
[6 empty] | MEC | Maximum Export Capacity (In accordance with the User's Connection Agreement)
[6 empty] | WFPS | Wind Farm Power Station
[6 empty] | GCCT | Grid Code Compliance Testing
[6 empty] | MV | i.e. 20kV
[6 empty] | HV | i.e. 38kV / 110KV
[6 empty] | DCC | Distribution Control Centre
[6 empty] | SDCC | South Distribution Control Centre, ESBN
[6 empty] | NDCC | North Distribution Control Centre, ESBN
[6 empty] | NCC | National Control Centre, EirGrid

## Requirements, Process & Notes C
Requirements as per the Distribution Code DCC11.1.4
Type | C | Type C Wind Farm Power Station (WFPS) as per DCC11.1.4: A WFPS connected to the Distribution System via a dedicated feeder into an existing 110kV station.
Wind Farm Registered Capacity | <5 MW | >= 5 MW | >= 10 MW
EirGrid RTU requirement
| No TSO RTU installed | TSO RTU Installed | TSO RTU Installed
Wind farm controls
|  | Active Power Control system | Active Power Control system
|  | Frequency Response system | Frequency Response system
Wind farm signals
|  | Available Active Power | Available Active Power
|  | Wind Farm Availability | Wind Farm Availability
|  | %WTG not generating due to high wind | %WTG not generating due to high wind
|  | %WTG not generating due to low wind | %WTG not generating due to low wind
Wind Speed
Wind Direction
Air Temperature
Air Pressure
Station controls
|  | Remote Control Switch | Network Operator Remote Control Switch
|  | Network Operator Initiated Shutdown | Network Operator Initiated Shutdown
Station signals
|  | Active Power Measurement | Active Power Measurement
|  | Reactive Power Measurement | Reactive Power Measurement
|  | Voltage Measurement | Voltage Measurement
|  | DSO cable protection signals | DSO cable protection signals
|  | Connection and / or Transformer HV CB | Connection and / or Transformer HV CB | DCC11.1.4 Figure 6
|  | Connection and / or Transformer HV CB | Connection and / or Transformer MV CB
|  | Feeder 20kV CB's | Feeder 20kV CB's
Detailed Process Overview
Additional Notes
General Process Notes: |  |  | Reference Documents:
A. Each Cert number 0, 1, 2, 3, 4, 5 from the process flow map corresponds to the subsequent Tab within the .xcl file which needs to be sent to generator_testing@eirgrid.com by the responsible party (IPP, ESBT or EMS). B. The IPP via ESBN provides most up-to-date SLD and Connection Type (as per the Distribution code DCC 11.1.4). Any changes in the SLD will result in a new Signal List being issued which may affect the Energisation Date. The Signal list is reviewed by EirGrid and sent to IPP via ESBN for feedback. Once all feedback has been addressed the Signal List is Frozen by EirGrid. This should be done not less than 6 months prior to energisation and will be communicated to IPP via ESBN. C. The RTU / ETIE should be installed on site not less than 4 weeks prior to energisation. D. The IPP via ESBN submits the IPP Wiring Completion Cert and Wind Farm Contact Details in advance of Energisation. This is required before ESBT arrive on site to carry out Joint Signals Check. This may be carried out in accordance with ESBT timelines listed on Tab 1) Inst. Info & Contact Details. E. Joint Signals Check is carried out by IPP / ESBT / EMS EirGrid / DCC. As this is pre-energisation the IPP may provide simulated signals to the TSO RTU which will be verified by EMS / DCC. Any issues identified at Joint Signals Check must be addressed prior to energisation. F. The Energisation is as per Energisation Instruction issued by DCC as applicable. There is a 5MW export capacity limit applied to the Wind Farm Power Station. This remains in place until a Dispatch Test is carried out. The capacity limit allows for some of the Wind Turbines to be commissioned at this time. G. Joint Pre-Grid Code Check is carried out by carried out by IPP / ESBT / EMS EirGrid / DCC. As this is post-energisation the IPP must provide real signals via TSO RTU which will be verified by EMS / DCC. Any issues identified at Joint Pre Grid Code Check must be addressed prior to the Dispatch Test. H. The Dispatch Test reviews the Active Power Control System is working correctly and the Availability Signal is within the standard. The 5MW export capacity limit is applied locally at the WFPS until a Dispatch test is carried out by NCC. The IPP via ESBN must schedule this at least 10 days in advance of testing. Once complete the new capacity limit tested value + amount 'X' is applied. These tests continue until the MEC is reached where a final Dispatch Test is carried out. I. Once the Dispatch test is carried out for the MEC of the Wind Farm Power Station, the WFPS is confirmed 'Operationally Ready' and may register as a VPTG within the Market. The IPP must apply to SEMO and should allow ~25 days to change class. J. Test procedures must be submitted to EirGrid in Advance of Grid Code Compliance Testing (GCCT). These procedures must be agreed by no less than 10 days in advance of testing. K. IPP via ESBN must monitor the Wind Conditions and liaise with EirGrid to carry out Grid Code Compliance Testing. There is a minimum 75% requirement to carry out GCCT. Note: NCC one unit per day testing limit. 10 days in advance of testing. Confirmation required 10/5/3/1 days in advance of testing. L. Grid Code Compliance Testing is carried out with an EirGrid Witness on site. M. High resolution raw data from agreed measurements is submitted to EirGrid on the day of test or an agreed timeframe after the test. A Grid Code Compliance Testing report must be submitted to EirGrid for review. This is submitted within an agreed timeframe. Should any issues be identified a retest may be required as per K) above. N. Should there be no further issues after GCCT has been successfully carried out, an Operational Certificate will be issued Note that this is the general process notes and exceptions may apply depending on circumstance. ALL queries for clarification should be referred to generator_testing@eirgrid.com.
EirGrid Telecoms Interface Cabinet Connection Details (using ETI Ref)
Recommended ESBTS cabling standards advised on signal list
Network Operator Initiated Shutdown Specification
Remote Control Specification
|  |  | Grid Code | http://www.eirgrid.com/operations/gridcode/
|  |  | Distribution Code: | http://www.esb.ie/esbnetworks/en/about-us/our_networks/distribution_code.jsp
|  |  | Available Active Power Standard | http://www.eirgrid.com/media/Quality%20Standard%20for%20Windfarm%20Active%20Power.pdf
Abbreviations
|  |  |  | TSO | Transmission System Operator - EirGrid
|  |  |  | EMS | Energy Management System - EirGrid
|  |  |  | DSO | Distribution System Operator - ESBN
|  |  |  | ESBN | ESB Networks
|  |  |  | ESBTS | ESB Telecoms Services
|  |  |  | RTU | Remote Terminal Unit
|  |  |  | ETIE | EirGrid Terminal Interface Enclosure
|  |  |  | NOIS | Network Operator Initiated Shutdown
|  |  |  | WTG | Wind Turbine Generator
|  |  |  | CB | Circuit Breaker
|  |  |  | MEC | Maximum Export Capacity (In accordance with the User's Connection Agreement)
|  |  |  | WFPS | Wind Farm Power Station
|  |  |  | GCCT | Grid Code Compliance Testing
|  |  |  | MV | i.e. 20kV
|  |  |  | HV | i.e. 38kV / 110KV
|  |  |  | DCC | Distribution Control Centre
|  |  |  | SDCC | South Distribution Control Centre, ESBN
|  |  |  | NDCC | North Distribution Control Centre, ESBN
|  |  |  | NCC | National Control Centre, EirGrid

## Requirements, Process & Notes D
Requirements as per the Distribution Code DCC11.1.4
Type | D | Wind Farm Power Stations are classed as being Connection Type D when connected to the Distribution System via a dedicated 38kV, 20kV or 10kV feeder into an existing 38kV distribution station.
Wind Farm Size | <5 MW | >= 5 MW | >= 10 MW
TSO RTU requirement
| No TSO RTU installed | TSO RTU Installed | TSO RTU Installed
Station controls
|  | EirGrid Remote Control Switch | EirGrid Remote Control Switch
|  | Network Operator Initiated Shutdown | Network Operator Initiated Shutdown
Wind farm signals
|  | Available Active Power | Available Active Power
|  | Wind Farm Availability | Wind Farm Availability
|  | %WTG not generating due to high wind | %WTG not generating due to high wind
|  | %WTG not generating due to low wind | %WTG not generating due to low wind
Wind Speed
Wind Direction
Air Temperature
Air Pressure
Station controls |  |  |  | DCC11.1.4 Figure 7
|  | Remote Control Switch | Network Operator Remote Control Switch
|  | Network Operator Initiated Shutdown | Network Operator Initiated Shutdown
Station signals
|  | Active Power Measurement | Active Power Measurement
|  | Reactive Power Measurement | Reactive Power Measurement
|  | Voltage Measurement | Voltage Measurement
|  | DSO cable protection signals | DSO cable protection signals
|  | Connection and / or Transformer HV CB | Connection and / or Transformer HV CB
|  | Connection and / or Transformer MV CB | Connection and / or Transformer MV CB
|  | Feeder 20kV CB's | Feeder 20kV CB's
Detailed Process Overview
Additional Notes
A. Each Cert number 0, 1, 2, 3, 4, from the process flow map corresponds to the subsequent Tab within the .xcl file which needs to be sent to generator_testing@eirgrid.com by the responsible party (IPP, ESBT or EMS). B. The IPP via ESBN provides most up-to-date SLD and Connection Type (as per the Distribution code DCC 11.1.4). Any changes in the SLD will require a new Signal List developed by EirGrid. This may take from 2 to 4 weeks. This may subsequently postpone the Energisation Date by (2-4 weeks). The Signal list is reviewed by EirGrid and sent to IPP via ESBN for feedback. Once all feedback has been addressed the Signal List is Frozen by EirGrid. This should be done not less than 6 months prior to energisation and will be communicated to IPP via ESBN. C. The RTU / ETIE should be installed on site not less than 4 weeks prior to energisation. D. The IPP via ESBN submits the IPP Wiring Completion Cert and Wind Farm Contact Details in advance of Energisation. This is required before ESBT arrive on site to carry out Joint Signals Check. This may be carried out in accordance with ESBT timelines listed on Tab 1) Inst. Info & Contact Details. E. Joint Signals Check is carried out by IPP / ESBT / EMS EirGrid / DCC. As this is pre-energisation the IPP may provide simulated signals to the TSO RTU which will be verified by EMS / DCC. Any issues identified at Joint Signals Check must be addressed prior to energisation. F. The Energisation is as per Energisation Instruction issued by DCC as applicable. There is a 5MW export capacity limit applied to the Wind Farm Power Station. This remains in place until a Dispatch Test is carried out. The capacity limit allows for some of the Wind Turbines to be commissioned at this time. G. Joint Pre-Grid Code Check is carried out by carried out by IPP / ESBT / EMS EirGrid / DCC. As this is post-energisation the IPP must provide real signals via TSO RTU which will be verified by EMS / DCC. Any issues identified at Joint Pre Grid Code Check must be addressed prior to the Dispatch Test. H. The Dispatch Test reviews the Active Power Control System is working correctly and the Availability Signal is within the standard. The 5MW export capacity limit is applied locally at the WFPS until a Dispatch test is carried out by NCC. The IPP via ESBN must schedule this at least 10 days in advance of testing. Once complete the new capacity limit tested value + amount 'X' is applied. These tests continue until the MEC is reached where a final Dispatch Test is carried out. I. Once the Dispatch test is carried out for the MEC of the Wind Farm Power Station, the WFPS is confirmed 'Operationally Ready' and may register as a VPTG within the Market. The IPP must apply to SEMO and should allow ~25 days to change class. J. Test procedures must be submitted to EirGrid in Advance of Grid Code Compliance Testing (GCCT). These procedures must be agreed by no less than 10 days in advance of testing. K. IPP via ESBN must monitor the Wind Conditions and liaise with EirGrid to carry out Grid Code Compliance Testing. There is a minimum 75% requirement to carry out GCCT. Note: NCC one unit per day testing limit. 10 days in advance of testing. Confirmation required 10/5/3/1 days in advance of testing. L. Grid Code Compliance Testing is carried out with an EirGrid Witness on site. M. High resolution raw data from agreed measurements is submitted to EirGrid on the day of test or an agreed timeframe after the test. A Grid Code Compliance Testing report must be submitted to EirGrid for review. This is submitted within an agreed timeframe. Should any issues be identified a retest may be required as per K) above. N. Should there be no further issues after GCCT has been successfully carried out, an Operational Certificate will be issued Note that this is the general process notes and exceptions may apply depending on circumstance. ALL queries for clarification should be referred to generator_testing@eirgrid.com. |  |  |  |  | Reference Documents:
EirGrid Telecoms Interface Cabinet Connection Details (using ETI Ref)
Recommended ESBTS cabling standards advised on signal list
Network Operator Initiated Shutdown Specification
Remote Control Specification
[5 empty] | Grid Code | http://www.eirgrid.com/operations/gridcode/
[5 empty] | Distribution Code: | http://www.esb.ie/esbnetworks/en/about-us/our_networks/distribution_code.jsp
[5 empty] | Available Active Power Standard | http://www.eirgrid.com/media/Quality%20Standard%20for%20Windfarm%20Active%20Power.pdf
Abbreviations
[6 empty] | TSO | Transmission System Operator - EirGrid
[6 empty] | EMS | Energy Management System - EirGrid
[6 empty] | DSO | Distribution System Operator - ESBN
[6 empty] | ESBN | ESB Networks
[6 empty] | ESBTS | ESB Telecoms Services
[6 empty] | RTU | Remote Terminal Unit
[6 empty] | ETIE | EirGrid Terminal Interface Enclosure
[6 empty] | NOIS | Network Operator Initiated Shutdown
[6 empty] | WTG | Wind Turbine Generator
[6 empty] | CB | Circuit Breaker
[6 empty] | MEC | Maximum Export Capacity (In accordance with the User's Connection Agreement)
[6 empty] | WFPS | Wind Farm Power Station
[6 empty] | GCCT | Grid Code Compliance Testing
[6 empty] | MV | i.e. 20kV
[6 empty] | HV | i.e. 38kV / 110KV
[6 empty] | DCC | Distribution Control Centre
[6 empty] | SDCC | South Distribution Control Centre, ESBN
[6 empty] | NDCC | North Distribution Control Centre, ESBN
[6 empty] | NCC | National Control Centre, EirGrid

## Requirements, Process & Notes E
Requirements as per the Distribution Code DCC11.1.4
Type | E | Wind Farm Power Stations are classed as being Connection Type E when connected to an existing distribution line with load.
Wind Farm Size | <5 MW | >= 5 MW | >= 10 MW
TSO RTU requirement
| No TSO RTU installed | TSO RTU Installed | TSO RTU Installed
Station controls
|  | EirGrid Remote Control Switch | EirGrid Remote Control Switch
|  | Network Operator Initiated Shutdown | Network Operator Initiated Shutdown
Wind farm signals
|  | Available Active Power | Available Active Power
|  | Wind Farm Availability | Wind Farm Availability
|  | %WTG not generating due to high wind | %WTG not generating due to high wind
|  | %WTG not generating due to low wind | %WTG not generating due to low wind
Wind Speed
Wind Direction
Air Temperature
Air Pressure
Station controls |  |  |  | DCC11.1.4 Figure 8
|  | Remote Control Switch | Network Operator Remote Control Switch
|  | Network Operator Initiated Shutdown | Network Operator Initiated Shutdown
Station signals
|  | Active Power Measurement | Active Power Measurement
|  | Reactive Power Measurement | Reactive Power Measurement
|  | Voltage Measurement | Voltage Measurement
|  | DSO cable protection signals | DSO cable protection signals
|  | Connection and / or Transformer HV CB | Connection and / or Transformer HV CB
|  | Connection and / or Transformer MV CB | Connection and / or Transformer MV CB
|  | Feeder 20kV CB's | Feeder 20kV CB's
Detailed Process Overview
Additional Notes
A. Each Cert number 0, 1, 2, 3, 4, from the process flow map corresponds to the subsequent Tab within the .xcl file which needs to be sent to generator_testing@eirgrid.com by the responsible party (IPP, ESBT or EMS). B. The IPP via ESBN provides most up-to-date SLD and Connection Type (as per the Distribution code DCC 11.1.4). Any changes in the SLD will require a new Signal List developed by EirGrid. This may take from 2 to 4 weeks. This may subsequently postpone the Energisation Date by (2-4 weeks). The Signal list is reviewed by EirGrid and sent to IPP via ESBN for feedback. Once all feedback has been addressed the Signal List is Frozen by EirGrid. This should be done not less than 6 months prior to energisation and will be communicated to IPP via ESBN. C. The RTU / ETIE should be installed on site not less than 4 weeks prior to energisation. D. The IPP via ESBN submits the IPP Wiring Completion Cert and Wind Farm Contact Details in advance of Energisation. This is required before ESBT arrive on site to carry out Joint Signals Check. This may be carried out in accordance with ESBT timelines listed on Tab 1) Inst. Info & Contact Details. E. Joint Signals Check is carried out by IPP / ESBT / EMS EirGrid / DCC. As this is pre-energisation the IPP may provide simulated signals to the TSO RTU which will be verified by EMS / DCC. Any issues identified at Joint Signals Check must be addressed prior to energisation. F. The Energisation is as per Energisation Instruction issued by DCC as applicable. There is a 5MW export capacity limit applied to the Wind Farm Power Station. This remains in place until a Dispatch Test is carried out. The capacity limit allows for some of the Wind Turbines to be commissioned at this time. G. Joint Pre-Grid Code Check is carried out by carried out by IPP / ESBT / EMS EirGrid / DCC. As this is post-energisation the IPP must provide real signals via TSO RTU which will be verified by EMS / DCC. Any issues identified at Joint Pre Grid Code Check must be addressed prior to the Dispatch Test. H. The Dispatch Test reviews the Active Power Control System is working correctly and the Availability Signal is within the standard. The 5MW export capacity limit is applied locally at the WFPS until a Dispatch test is carried out by NCC. The IPP via ESBN must schedule this at least 10 days in advance of testing. Once complete the new capacity limit tested value + amount 'X' is applied. These tests continue until the MEC is reached where a final Dispatch Test is carried out. I. Once the Dispatch test is carried out for the MEC of the Wind Farm Power Station, the WFPS is confirmed 'Operationally Ready' and may register as a VPTG within the Market. The IPP must apply to SEMO and should allow ~25 days to change class. J. Test procedures must be submitted to EirGrid in Advance of Grid Code Compliance Testing (GCCT). These procedures must be agreed by no less than 10 days in advance of testing. K. IPP via ESBN must monitor the Wind Conditions and liaise with EirGrid to carry out Grid Code Compliance Testing. There is a minimum 75% requirement to carry out GCCT. Note: NCC one unit per day testing limit. 10 days in advance of testing. Confirmation required 10/5/3/1 days in advance of testing. L. Grid Code Compliance Testing is carried out with an EirGrid Witness on site. M. High resolution raw data from agreed measurements is submitted to EirGrid on the day of test or an agreed timeframe after the test. A Grid Code Compliance Testing report must be submitted to EirGrid for review. This is submitted within an agreed timeframe. Should any issues be identified a retest may be required as per K) above. N. Should there be no further issues after GCCT has been successfully carried out, an Operational Certificate will be issued Note that this is the general process notes and exceptions may apply depending on circumstance. ALL queries for clarification should be referred to generator_testing@eirgrid.com. |  |  |  |  | Reference Documents:
EirGrid Telecoms Interface Cabinet Connection Details (using ETI Ref)
Recommended ESBTS cabling standards advised on signal list
Network Operator Initiated Shutdown Specification
Remote Control Specification
[5 empty] | Grid Code | http://www.eirgrid.com/operations/gridcode/
[5 empty] | Distribution Code: | http://www.esb.ie/esbnetworks/en/about-us/our_networks/distribution_code.jsp
[5 empty] | Available Active Power Standard | http://www.eirgrid.com/media/Quality%20Standard%20for%20Windfarm%20Active%20Power.pdf
Abbreviations
[6 empty] | TSO | Transmission System Operator - EirGrid
[6 empty] | EMS | Energy Management System - EirGrid
[6 empty] | DSO | Distribution System Operator - ESBN
[6 empty] | ESBN | ESB Networks
[6 empty] | ESBTS | ESB Telecoms Services
[6 empty] | RTU | Remote Terminal Unit
[6 empty] | ETIE | EirGrid Terminal Interface Enclosure
[6 empty] | NOIS | Network Operator Initiated Shutdown
[6 empty] | WTG | Wind Turbine Generator
[6 empty] | CB | Circuit Breaker
[6 empty] | MEC | Maximum Export Capacity (In accordance with the User's Connection Agreement)
[6 empty] | WFPS | Wind Farm Power Station
[6 empty] | GCCT | Grid Code Compliance Testing
[6 empty] | MV | i.e. 20kV
[6 empty] | HV | i.e. 38kV / 110KV
[6 empty] | DCC | Distribution Control Centre
[6 empty] | SDCC | South Distribution Control Centre, ESBN
[6 empty] | NDCC | North Distribution Control Centre, ESBN
[6 empty] | NCC | National Control Centre, EirGrid

## DSO Required Inputs
IPP Inputs for Signal List Development
1 | Wind Farm Power Station (WFPS) Name (including alternative names) | Included in submission 
2 | WFPS Connection Type as per the Distribution Code DCC11.1.4 | Included in submission 
3 | WFPS Maximum Export Capacity | Included in submission 
4 | WFPS Installed Capacity (for Phase developments, i.e. MEC 20MW Phase 1 10MWQ1 2014, Phase 2 additional 10MW Q2 2015 ) | Included in submission 
5 | The number of Market Units at the WFPS (Phase 1 &2 is one market unit or two separate market units, noting that if the WFPS consists of two market units then additional signals will be required). | Included in submission 
6 | Energisation Date | Included in submission 
7 | Single Line Diagram (Note that for changes in SLD's, the Signal list requirements may change) | Included in submission 
| · Revision Number | Included in submission 
| · Ownership boundaries | Included in submission 
| · HV CB positions (IPP and ESBN as applicable) | Included in submission 
| · MV CB positions | Included in submission 
| · MV Feeders | Included in submission 
8 | Number of Met Masts on site - (if WFPS ≥10MW) | Included in submission 
9 | Nearest 110kV Station - normal feeding arrangements for WFPS | Included in submission 
10 | Confirmation of DSO RTU for the WFPS? | Included in submission 
11 | If there is no DSO RTU submission of DCC signals to be included within the DSO RTU (1-18). | Included in submission 
Information to be submitted to generator_testing@eirgrid.com via NDCC/SDCC

## 0) Signal List
WINDFARM NAME |  | Type | B | XX | MW | v0.2 |  | Signals List is based on this Single Line Diagram (SLD) as inserted.
EirGrid Signals, Command & Control Specification (Ref: DCC11.5)
Signals List |  | Registered Capacity: XX MW |  |  |  | Installed Plant: XXX MW
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
| Double Point Status Indications | (each individual input identified separately for clarity) | [5 empty] | Note: Signals treated as 2-bit binary
Digital Input Signals from Sub Station to EirGrid
A1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open |  |  | ESBN | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A2 | ESBN 20 kV interface switch (Nulec Recloser) |  | closed |  |  | ESBN | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A3 | WINDFARM NAME T421 IPP 20 kV CB |  | open |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A4 | WINDFARM NAME T421 IPP 20 kV CB |  | closed |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 | Typical SLD for a wind farm connecting to the system through a 38/20 kV transformer
A5 | WINDFARM NAME Feeder 1 20 kV CB |  | open |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A6 | WINDFARM NAME Feeder 1 20 kV CB |  | closed |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A7 | WINDFARM NAME Feeder 2 20 kV CB |  | open |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A8 | WINDFARM NAME Feeder 2 20 kV CB |  | closed |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A9 | WINDFARM NAME Feeder 3 20 kV CB |  | open |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A10 | WINDFARM NAME Feeder 3 20 kV CB |  | closed |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A11 | WINDFARM NAME Feeder 4 20 kV CB |  | open |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A12 | WINDFARM NAME Feeder 4 20 kV CB |  | closed |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | IPP | N/A | Distribution Code Signals List #1 DCC11.5.1.1 (Blocks all commands to IPP equipment, located on IPP side)
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | IPP | N/A | Distribution Code Signals List #1 DCC11.5.1.1 (Blocks all commands to IPP equipment, located on IPP side)
A15 | Dispatch Fail Market Command Lamp - IPP Panel |  | off |  |  | IPP | ESBN
A16 | Dispatch Fail Market Command Lamp - IPP Panel |  | on |  |  | IPP | ESBN
A17 | Blue Alert Lamp - IPP Panel |  | off |  |  | IPP | ESBN
A18 | Blue Alert Lamp - IPP Panel |  | on |  |  | IPP | ESBN
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A23 | Reactive Device >5 Mvar N |  | off |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A24 | Reactive Device >5 Mvar N |  | on |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4
B2 | Active Power Control facility status (feedback) |  | on |  |  | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (125% of Registered Cpapacity)
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (150% of Reactive Power at Registered Capacity)
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (125% of nominal conection voltage)
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (125% of Registered Capacity)
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4 (125% of Registered Capacity)
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | IPP | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Analogue WTG Availability
D4 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | IPP | ESBN | Distribution Code Signals List #3 DCC11.5.1.3
D5 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | IPP | ESBN | Distribution Code Signals List #3 DCC11.5.1.3
D6 | Wind Farm Availability | 0-10 | mA | 0-110 | % | IPP | N/A | Distribution Code Signals List #3 DCC11.5.1.3
Met 1 (if Registered Capacity >= 10 MW)
D7 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D8 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West), 10mA = 360deg (from the North)).
D9 | Air Temperature 1 | 0-10 | mA | -40-70 | C | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D10 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D11 | Met N (if Registered Capacity >= 10 MW)
D12 | Wind Speed N | 0-10 | mA | 0-70 | m/s | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D13 | Wind Direction N | 0-10 | mA | 0-360 | deg | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6 (0mA = 0deg (from the East), 2.5mA = 90deg (from the North), 5mA = 180deg (from the West), 10mA = 360deg (from the East))
D14 | Air Temperature N | 0-10 | mA | -40-70 | C | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D15 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
Digital Output Signals from EirGrid to Sub Station
F1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open | pulse | 0.5 seconds | ESBN | ESBN
F2 | ESBN 20 kV interface switch (Nulec Recloser) |  | close | pulse | 0.5 seconds | ESBN | ESBN
F3 | Dispatch Fail Market Command Lamp - IPP Panel |  | off | pulse | 0.5 seconds | IPP | ESBN
F4 | Dispatch Fail Market Command Lamp - IPP Panel |  | on | pulse | 0.5 seconds | IPP | ESBN
F5 | Blue Alert Lamp - IPP Panel |  | off | pulse | 0.5 seconds | IPP | ESBN
F6 | Blue Alert Lamp - IPP Panel |  | on | pulse | 0.5 seconds | IPP | ESBN
Strobe Enable Pulses
Digital Output Signals from EirGrid to WTG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4
E8 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | IPP | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | IPP | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | IPP | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | IPP | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | IPP | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
Recommended cable 15-pair cable, 15 x 2 x 0.6sqmm, TP, stranded, external sheath
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4 (125% of Registered Capacity)
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | IPP | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
Note on D1: Administrator: Insert the Type of the Wind Farm
Note on E1: Administrator: Insert the Registered Capacity of the WFPS
Note on A5: EirGrid Telecoms Interface Enclosure
Note on H5: No IPP involvement unless otherwise confirmed
Note on B9: Position indications required for all circuit breakers from connection point to wind farm feeders
Note on B13: Turbine Circuit Breakers are not Included. The number of Feeders is checked against the SLD attached above.
Note on B21: Described as TSO remote control enable switch in DSO code.
Note on D29: Typically reactive power device breaker. Open Closed maybe more correct.
Note on E47: +/-125%
Note on E49: 110kV: 0 to 132kV 38kV: 0 to 46.2kV 20kV: 0 to 24 kV
Note on E52: 0-125%
Note on E53: 0-125%
Note on I103: Administrator: ESBN to provide reference to this document.
Note on E127: 0 to 125%

## 1a) Inst.Info & Contact Details
WINDFARM NAME Information and Contact Details to be sent by IPP via ESB Networks to EirGrid (generator_testing@EirGrid.com)
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
DATE
| HV SUB STATION NAME |  |  |  |  | ESBTS Team |  | Liam Boland
[6 empty] | Nessan Heaslip | Karl O'Keeffe | Noel Cowhey
| EirGrid Contact Person | C&T Team | PHONE: |  | (+353) 1 2370583 | Robert Groarke | Oisín Goulding
| OSP Generic Email: Generator_testing@eirgrid.com |  |  |  |  | Frank Donnelly | Colm MacManus
| EMS Generic Email: ems.services@eirgrid.com |  |  |  |  | Liam Delany | C&T Team
[6 empty] | Niall Molloy | Ciarán Maguire
| ESBTS Project Manager | ESBTS Team | PHONE: |  | (+353) 1 7027835
| ESBTS Commissioner | ESBTS Team | PHONE: |  | (+353) 1 7027835
ESBTS Generic Email: esbts.scada.services@esb.ie
| ESB Networks (SPOC) |  | PHONE:
ESB Networks Build Generic Email: IPPdelivery@esb.ie
| ESB Networks (switchgear) |  | PHONE: |  | (+ )
| ESB Networks (metering) |  | PHONE: |  | (+ )
| IPP Project Manager |  | PHONE: |  | (+ )
| Electrical Contractor |  | PHONE: |  | (+ )
| Turbine Contractor |  | PHONE: |  | (+ )
| Work Programme / Schedule (.mpp format) |  |  | Insert File
| Single Line Diagram |  |  | Insert file
| Site Layout Drawing on OS Map |  |  | Insert file
| Substation & Control Building Layout Drawing on OS Map |  |  | Insert file
| IPP Energy Management System %error |  |  | %
| Directions including Map to the Wind Farm Power Station | Insert Map and brief description
| Safety & Site information | IPP to provide details
ESBTS Standard Requirements from IPP (may be customised for particular sites):
1) 90sq mm earth for Telecoms earth bar. 2) 35sq mm bonded from external earth grid to GPS clock antenna mounting bracket and if applicable Satellite antenna mounting bracket. 3) 48V DC Power System consisting of Switched Mode Power Supply (SMPS) with sealed cell battery. 4) If applicable - Fibre termination cabinet with fibre termination unit and fibre to distant station. 5) Satellite link consisting of Satellite transceiver and antenna if applicable. Satellite antenna preferably on a south facing wall with a clear view of the horizon. 6) Install and terminate process control and signal cables in ETI (the wiring schedule is available as a worksheet in the signal list excel file).
| ESB Telecom Services - Indicative Timelines for on site works | 1) 3 weeks notice required by ESBTS to schedule resources. 2) ~1 week to install the RTU cabinet with integrated ETI and GPS clock, GPS clock antenna. 3) ~1 week to pre commission the RTU referenced to frozen signal list with IPP electrical and WTG contractors. 4) ~1 week to install and commission the satellite link including antenna (if applicable). 5) ~2 days to commission the fibre link (if applicable). 6) ~1 week to commission the RTU with IPP electrical and WTG contractors.

## 1b) IPP Wiring Completion Cert
WINDFARM NAME |  | Type | B | XX | MW | v0.2 |  | Signals List is based on this Single Line Diagram (SLD) as inserted. | Wiring Completion Cert
EirGrid Signals, Command & Control Specification (Ref: DCC11.5) | [8 empty] | Continuity Check Complete
IPP Wiring Completion Certificate (to EirGrid ETIE/RTU) to be sent by IPP via ESBN to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open |  |  | ESBN | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A2 | ESBN 20 kV interface switch (Nulec Recloser) |  | closed |  |  | ESBN | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A3 | WINDFARM NAME T421 IPP 20 kV CB |  | open |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A4 | WINDFARM NAME T421 IPP 20 kV CB |  | closed |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A5 | WINDFARM NAME Feeder 1 20 kV CB |  | open |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A6 | WINDFARM NAME Feeder 1 20 kV CB |  | closed |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A7 | WINDFARM NAME Feeder 2 20 kV CB |  | open |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A8 | WINDFARM NAME Feeder 2 20 kV CB |  | closed |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A9 | WINDFARM NAME Feeder 3 20 kV CB |  | open |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A10 | WINDFARM NAME Feeder 3 20 kV CB |  | closed |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A11 | WINDFARM NAME Feeder 4 20 kV CB |  | open |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A12 | WINDFARM NAME Feeder 4 20 kV CB |  | closed |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | IPP | N/A | Distribution Code Signals List #1 DCC11.5.1.1 (Blocks all commands to IPP equipment, located on IPP side)
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | IPP | N/A | Distribution Code Signals List #1 DCC11.5.1.1 (Blocks all commands to IPP equipment, located on IPP side)
A15 | Dispatch Fail Market Command Lamp - IPP Panel |  | off |  |  | IPP | ESBN
A16 | Dispatch Fail Market Command Lamp - IPP Panel |  | on |  |  | IPP | ESBN
A17 | Blue Alert Lamp - IPP Panel |  | off |  |  | IPP | ESBN
A18 | Blue Alert Lamp - IPP Panel |  | on |  |  | IPP | ESBN
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A23 | Reactive Device >5 Mvar N |  | off |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
A24 | Reactive Device >5 Mvar N |  | on |  |  | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4
B2 | Active Power Control facility status (feedback) |  | on |  |  | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (125% of Registered Cpapacity)
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (150% of Reactive Power at Registered Capacity)
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (125% of nominal conection voltage)
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | IPP | ESBN | Distribution Code Signals List #1 DCC11.5.1.1 (125% of Registered Capacity)
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4 (125% of Registered Capacity)
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | IPP | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Analogue WTG Availability
D4 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | IPP | ESBN | Distribution Code Signals List #3 DCC11.5.1.3
D5 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | IPP | ESBN | Distribution Code Signals List #3 DCC11.5.1.3
D6 | Wind Farm Availability | 0-10 | mA | 0-110 | % | IPP | N/A | Distribution Code Signals List #3 DCC11.5.1.3
Met 1 (if Registered Capacity >= 10 MW)
D7 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D8 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | IPP | N/A | Grid Code Signals List #6 WFPS 1.7.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West), 10mA = 360deg (from the North)).
D9 | Air Temperature 1 | 0-10 | mA | -40-70 | C | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D10 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D11 | Met N (if Registered Capacity >= 10 MW)
D12 | Wind Speed N | 0-10 | mA | 0-70 | m/s | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D13 | Wind Direction N | 0-10 | mA | 0-360 | deg | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6 (0mA = 0deg (from the East), 2.5mA = 90deg (from the North), 5mA = 180deg (from the West), 10mA = 360deg (from the East))
D14 | Air Temperature N | 0-10 | mA | -40-70 | C | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6
D15 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Distribution Code Signals List #6 DCC11.5.1.6
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #5 DCC11.5.1.5
Digital Output Signals from EirGrid to Sub Station
F1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open | pulse | 0.5 seconds | ESBN | ESBN
F2 | ESBN 20 kV interface switch (Nulec Recloser) |  | close | pulse | 0.5 seconds | ESBN | ESBN
F3 | Dispatch Fail Market Command Lamp - IPP Panel |  | off | pulse | 0.5 seconds | IPP | ESBN
F4 | Dispatch Fail Market Command Lamp - IPP Panel |  | on | pulse | 0.5 seconds | IPP | ESBN
F5 | Blue Alert Lamp - IPP Panel |  | off | pulse | 0.5 seconds | IPP | ESBN
F6 | Blue Alert Lamp - IPP Panel |  | on | pulse | 0.5 seconds | IPP | ESBN
Strobe Enable Pulses
Digital Output Signals from EirGrid to WTG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4
E8 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | TSO Pass-through to | Distribution Code reference
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | IPP | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | IPP | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | IPP | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | IPP | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | IPP | ESBN | ESBN to specify Alarm type to IPP. (not required if DSO RTU is installed)
Recommended cable 15-pair cable, 15 x 2 x 0.6sqmm, TP, stranded, external sheath
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | IPP | N/A | Distribution Code Signals List #4 DCC11.5.1.4 (125% of Registered Capacity)
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | IPP | N/A | Distribution Code Modification #24 Approved by CER 08/10/2013
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet must be clearly marked with labels for identification. |  |  |  | Confirmed  |  |  |  | How is NOIS implemented?
All cables for interfacing at station interface cabinet or EirGrid telecoms interface cabinet must be terminated at connection terminals (i.e. stripped, crimped and marked at terminal connections). |  |  |  | Confirmed 
All cables for interfacing at station interface cabinet or EirGrid telecoms interface cabinet must use colour coding agreed by all parties i.e. ESBTS & IPP. |  |  |  | Confirmed 
All analogue and digital interface signals must be tested and simulated for compliance with the frozen signal list agreed by all parties. |  |  |  | Confirmed 
ESBTS Satellite Dish bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed 
ESBTS GPS clock antenna bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed 
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 | [6 empty] | IPP Name / Position | 0
IPP Signature
Date
Note on A3: Administrator: To be completed by the IPP and sent to EirGrid to schedule ESBTS site attendance to perform continuity check
Note on A5: EirGrid Telecoms Interface Enclosure

## 2) ESB Telecoms Completion Cert
WINDFARM NAME |  | Type | B | XX | MW | v0.2 |  | Completion Cert
EirGrid Signals, Command & Control Specification (Ref: DCC11.5) | [7 empty] | Local SCADA Checks/Tests
Pre Energisation Signals Testing Certificate to be sent by ESB Telecoms Services to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open |  |  | ESBN | ESBN
A2 | ESBN 20 kV interface switch (Nulec Recloser) |  | closed |  |  | ESBN | ESBN
A3 | WINDFARM NAME T421 IPP 20 kV CB |  | open |  |  | IPP | ESBN
A4 | WINDFARM NAME T421 IPP 20 kV CB |  | closed |  |  | IPP | ESBN
A5 | WINDFARM NAME Feeder 1 20 kV CB |  | open |  |  | IPP | ESBN
A6 | WINDFARM NAME Feeder 1 20 kV CB |  | closed |  |  | IPP | ESBN
A7 | WINDFARM NAME Feeder 2 20 kV CB |  | open |  |  | IPP | ESBN
A8 | WINDFARM NAME Feeder 2 20 kV CB |  | closed |  |  | IPP | ESBN
A9 | WINDFARM NAME Feeder 3 20 kV CB |  | open |  |  | IPP | ESBN
A10 | WINDFARM NAME Feeder 3 20 kV CB |  | closed |  |  | IPP | ESBN
A11 | WINDFARM NAME Feeder 4 20 kV CB |  | open |  |  | IPP | ESBN
A12 | WINDFARM NAME Feeder 4 20 kV CB |  | closed |  |  | IPP | ESBN
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | IPP | N/A
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | IPP | N/A
A15 | Dispatch Fail Market Command Lamp - IPP Panel |  | off |  |  | IPP | ESBN
A16 | Dispatch Fail Market Command Lamp - IPP Panel |  | on |  |  | IPP | ESBN
A17 | Blue Alert Lamp - IPP Panel |  | off |  |  | IPP | ESBN
A18 | Blue Alert Lamp - IPP Panel |  | on |  |  | IPP | ESBN
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | IPP | ESBN
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | IPP | ESBN
A23 | Reactive Device >5 Mvar N |  | off |  |  | IPP | ESBN
A24 | Reactive Device >5 Mvar N |  | on |  |  | IPP | ESBN
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | IPP | N/A
B2 | Active Power Control facility status (feedback) |  | on |  |  | IPP | N/A
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | IPP | N/A
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | IPP | N/A
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | IPP | N/A
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | IPP | N/A
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | IPP | ESBN
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | ESBN
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | IPP | ESBN
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | IPP | ESBN
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | IPP | N/A
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | IPP | N/A
Analogue WTG Availability
D4 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | IPP | ESBN
D5 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | IPP | ESBN
D6 | Wind Farm Availability | 0-10 | mA | 0-110 | % | IPP | N/A
Met 1 (if Registered Capacity >= 10 MW)
D7 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | IPP | N/A
D8 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | IPP | N/A
D9 | Air Temperature 1 | 0-10 | mA | -40-70 | C | IPP | N/A
D10 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | IPP | N/A
D11 | Met N (if Registered Capacity >= 10 MW)
D12 | Wind Speed N | 0-10 | mA | 0-70 | m/s | IPP | N/A
D13 | Wind Direction N | 0-10 | mA | 0-360 | deg | IPP | N/A
D14 | Air Temperature N | 0-10 | mA | -40-70 | C | IPP | N/A
D15 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | IPP | N/A
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | IPP | N/A
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | IPP | N/A
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | IPP | N/A
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | IPP | N/A
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | IPP | N/A
Digital Output Signals from EirGrid to Sub Station
F1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open | pulse | 0.5 seconds | ESBN | ESBN
F2 | ESBN 20 kV interface switch (Nulec Recloser) |  | close | pulse | 0.5 seconds | ESBN | ESBN
F3 | Dispatch Fail Market Command Lamp - IPP Panel |  | off | pulse | 0.5 seconds | IPP | ESBN
F4 | Dispatch Fail Market Command Lamp - IPP Panel |  | on | pulse | 0.5 seconds | IPP | ESBN
F5 | Blue Alert Lamp - IPP Panel |  | off | pulse | 0.5 seconds | IPP | ESBN
F6 | Blue Alert Lamp - IPP Panel |  | on | pulse | 0.5 seconds | IPP | ESBN
Strobe Enable Pulses
Digital Output Signals from EirGrid to WTG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A
E8 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | IPP | N/A
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | TSO Pass-through to
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | IPP | ESBN
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | IPP | ESBN
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | IPP | ESBN
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | IPP | ESBN
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | IPP | ESBN
Recommended cable 15-pair cable, 15 x 2 x 0.6sqmm, TP, stranded, external sheath
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | IPP | N/A
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | IPP | N/A
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
How is NOIS implemented?
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet are installed and correct. |  |  |  | Confirmed  |  |  | ESBTS Name / Position | ESBTS Team
ESBTS Signature
Date
| NOTE: Non operable IPP signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  | Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
Note on A5: EirGrid Telecoms Interface Enclosure

## 2 a) EMS Database Setup Cert
WINDFARM NAME |  | Type | B | XX | MW | v0.2
EirGrid Signals, Command & Control Specification (Ref: DCC11.5)
Energy Management System (EMS) Database setup Certificate
Completion Cert
Continuity Check Complete
Generator Modelled
Lines Modelled
Station Modelled
Calculations Updated
RTU Modelled
Display Work Completed:
WF SLD
Station SLD
Station List
Windfarm List
Embedded Wind
Windfarm Control
Station Wind MW
Wind Overview
Windfarm Availability Data
Blue Alert Page
Windfarm Weather Data
DCC signals provided via ICCP
EMS Name
EMS Signature
Date
EirGrid Internal Document - no IPP requirements. For Information only
Note on A3: Administrator: DCC to be Informed

## 3)Pre Energ. Sign&Con Test Cert
WINDFARM NAME |  | Type | B | XX | MW | v0.2 |  | Pre Energisation Signals and Controls Test
EirGrid Signals, Command & Control Specification (Ref: DCC11.5) | [7 empty] | Simulated □/Real □ value tested | mA Range | Value Range | Comment
Pre Energisation Signals & Controls Certificate to be sent by ESBT to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open |  |  | ESBN | ESBN | Real □
A2 | ESBN 20 kV interface switch (Nulec Recloser) |  | closed |  |  | ESBN | ESBN | Real □
A3 | WINDFARM NAME T421 IPP 20 kV CB |  | open |  |  | IPP | ESBN | Real □
A4 | WINDFARM NAME T421 IPP 20 kV CB |  | closed |  |  | IPP | ESBN | Real □
A5 | WINDFARM NAME Feeder 1 20 kV CB |  | open |  |  | IPP | ESBN | Real □
A6 | WINDFARM NAME Feeder 1 20 kV CB |  | closed |  |  | IPP | ESBN | Real □
A7 | WINDFARM NAME Feeder 2 20 kV CB |  | open |  |  | IPP | ESBN | Real □
A8 | WINDFARM NAME Feeder 2 20 kV CB |  | closed |  |  | IPP | ESBN | Real □
A9 | WINDFARM NAME Feeder 3 20 kV CB |  | open |  |  | IPP | ESBN | Real □
A10 | WINDFARM NAME Feeder 3 20 kV CB |  | closed |  |  | IPP | ESBN | Real □
A11 | WINDFARM NAME Feeder 4 20 kV CB |  | open |  |  | IPP | ESBN | Real □
A12 | WINDFARM NAME Feeder 4 20 kV CB |  | closed |  |  | IPP | ESBN | Real □
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | IPP | N/A | Real □
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | IPP | N/A | Real □
A15 | Dispatch Fail Market Command Lamp - IPP Panel |  | off |  |  | IPP | ESBN | Real □
A16 | Dispatch Fail Market Command Lamp - IPP Panel |  | on |  |  | IPP | ESBN | Real □
A17 | Blue Alert Lamp - IPP Panel |  | off |  |  | IPP | ESBN | Real □
A18 | Blue Alert Lamp - IPP Panel |  | on |  |  | IPP | ESBN | Real □
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN | Real □
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN | Real □
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | IPP | ESBN | Real □
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | IPP | ESBN | Real □
A23 | Reactive Device >5 Mvar N |  | off |  |  | IPP | ESBN | Real □
A24 | Reactive Device >5 Mvar N |  | on |  |  | IPP | ESBN | Real □
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | IPP | N/A | Simulated □
B2 | Active Power Control facility status (feedback) |  | on |  |  | IPP | N/A | Simulated □
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | IPP | N/A | Simulated □
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | IPP | N/A | Simulated □
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | IPP | N/A | Simulated □
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | IPP | N/A | Simulated □
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | IPP | ESBN | Real □
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | ESBN | Real □
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | IPP | ESBN | Real □
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | IPP | ESBN | Simulated □
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | IPP | N/A | Simulated □
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | IPP | N/A | Simulated □
Analogue WTG Availability
D4 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | IPP | ESBN | Simulated □
D5 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | IPP | ESBN | Simulated □
D6 | Wind Farm Availability | 0-10 | mA | 0-110 | % | IPP | N/A | Simulated □
Met 1 (if Registered Capacity >= 10 MW)
D7 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | IPP | N/A | Simulated □
D8 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | IPP | N/A | Simulated □
D9 | Air Temperature 1 | 0-10 | mA | -40-70 | C | IPP | N/A | Simulated □
D10 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Simulated □
D11 | Met N (if Registered Capacity >= 10 MW)
D12 | Wind Speed N | 0-10 | mA | 0-70 | m/s | IPP | N/A | Simulated □
D13 | Wind Direction N | 0-10 | mA | 0-360 | deg | IPP | N/A | Simulated □
D14 | Air Temperature N | 0-10 | mA | -40-70 | C | IPP | N/A | Simulated □
D15 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Simulated □
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | IPP | N/A | Simulated □
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Simulated □
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | IPP | N/A | Simulated □
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | IPP | N/A | Simulated □
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | IPP | N/A | Simulated □
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | IPP | N/A | Simulated □
Digital Output Signals from EirGrid to Sub Station
F1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open | pulse | 0.5 seconds | ESBN | ESBN | Simulated □
F2 | ESBN 20 kV interface switch (Nulec Recloser) |  | close | pulse | 0.5 seconds | ESBN | ESBN | Simulated □
F3 | Dispatch Fail Market Command Lamp - IPP Panel |  | off | pulse | 0.5 seconds | IPP | ESBN | Simulated □
F4 | Dispatch Fail Market Command Lamp - IPP Panel |  | on | pulse | 0.5 seconds | IPP | ESBN | Simulated □
F5 | Blue Alert Lamp - IPP Panel |  | off | pulse | 0.5 seconds | IPP | ESBN | Simulated □
F6 | Blue Alert Lamp - IPP Panel |  | on | pulse | 0.5 seconds | IPP | ESBN | Simulated □
Strobe Enable Pulses
Digital Output Signals from EirGrid to WTG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Simulated □
E8 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Simulated □
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | TSO Pass-through to
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN | Simulated □
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN | Simulated □
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN | Simulated □
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN | Simulated □
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN | Simulated □
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN | Simulated □
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN | Simulated □
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN | Simulated □
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN | Simulated □
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN | Simulated □
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN | Simulated □
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN | Simulated □
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN | Simulated □
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | IPP | ESBN | Simulated □
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | IPP | ESBN | Simulated □
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | IPP | ESBN | Simulated □
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | IPP | ESBN | Simulated □
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | IPP | ESBN | Simulated □
Recommended cable 15-pair cable, 15 x 2 x 0.6sqmm, TP, stranded, external sheath
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | IPP | N/A | Simulated □
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | IPP | N/A | Simulated □
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
Simulation Point
| How is NOIS implemented? |  |  |  |  | Simulation Method
[6 empty] | IPP Name / Position |  | 0
IPP Signature
EMS Name
EMS Signature
| NOTE: Non operable IPP signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  |  |  |  | ESB Telecoms Name / Position |  | ESBTS Team
| Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 |  |  |  |  | ESB Telecoms Signature
Date
Note on I1: Administrator: ESBTS Commission from NCC control desk to / via ETI to IPP plant.
Note on I2: Administrator: the electrical characteristics of IPP signals not tested due to plant unavailability must be simulated by IPP.
Note on A5: EirGrid Telecoms Interface Enclosure

## 4) Post Ener Pre Grid Code Cert
WINDFARM NAME |  | Type | B | XX | MW | v0.2 |  | Post Energisation Signals and Controls Test
EirGrid Signals, Command & Control Specification (Ref: DCC11.5) | [7 empty] | Simulated □/Real □ value tested | mA Range | Value Range | Comment
Post Energisation Pre Grid Code Cert to be provided by ESBT to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open |  |  | ESBN | ESBN | Real □
A2 | ESBN 20 kV interface switch (Nulec Recloser) |  | closed |  |  | ESBN | ESBN | Real □
A3 | WINDFARM NAME T421 IPP 20 kV CB |  | open |  |  | IPP | ESBN | Real □
A4 | WINDFARM NAME T421 IPP 20 kV CB |  | closed |  |  | IPP | ESBN | Real □
A5 | WINDFARM NAME Feeder 1 20 kV CB |  | open |  |  | IPP | ESBN | Real □
A6 | WINDFARM NAME Feeder 1 20 kV CB |  | closed |  |  | IPP | ESBN | Real □
A7 | WINDFARM NAME Feeder 2 20 kV CB |  | open |  |  | IPP | ESBN | Real □
A8 | WINDFARM NAME Feeder 2 20 kV CB |  | closed |  |  | IPP | ESBN | Real □
A9 | WINDFARM NAME Feeder 3 20 kV CB |  | open |  |  | IPP | ESBN | Real □
A10 | WINDFARM NAME Feeder 3 20 kV CB |  | closed |  |  | IPP | ESBN | Real □
A11 | WINDFARM NAME Feeder 4 20 kV CB |  | open |  |  | IPP | ESBN | Real □
A12 | WINDFARM NAME Feeder 4 20 kV CB |  | closed |  |  | IPP | ESBN | Real □
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | IPP | N/A | Real □
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | IPP | N/A | Real □
A15 | Dispatch Fail Market Command Lamp - IPP Panel |  | off |  |  | IPP | ESBN | Real □
A16 | Dispatch Fail Market Command Lamp - IPP Panel |  | on |  |  | IPP | ESBN | Real □
A17 | Blue Alert Lamp - IPP Panel |  | off |  |  | IPP | ESBN | Real □
A18 | Blue Alert Lamp - IPP Panel |  | on |  |  | IPP | ESBN | Real □
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN | Real □
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN | Real □
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | IPP | ESBN | Real □
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | IPP | ESBN | Real □
A23 | Reactive Device >5 Mvar N |  | off |  |  | IPP | ESBN | Real □
A24 | Reactive Device >5 Mvar N |  | on |  |  | IPP | ESBN | Real □
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | IPP | N/A | Real □
B2 | Active Power Control facility status (feedback) |  | on |  |  | IPP | N/A | Real □
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | IPP | N/A | Real □
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | IPP | N/A | Real □
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | IPP | N/A | Real □
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | IPP | N/A | Real □
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at Connection Point | -10 to 0 to 10 | mA | #VALUE! | MW | IPP | ESBN | Real □
C2 | Reactive Power at Connection Point | -10 to 0 to 10 | mA | #VALUE! | Mvar | IPP | ESBN | Real □
C3 | Voltage at Connection Point | 0-10 | mA | 0 to 24 | kV | IPP | ESBN | Real □
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | IPP | ESBN | Real □
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | IPP | N/A | Real □
D3 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | IPP | N/A
Analogue WTG Availability
D4 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | IPP | ESBN | Real □
D5 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | IPP | ESBN | Real □
D6 | Wind Farm Availability | 0-10 | mA | 0-110 | % | IPP | N/A | Real □
Met 1 (if Registered Capacity >= 10 MW)
D7 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | IPP | N/A | Real □
D8 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | IPP | N/A | Real □
D9 | Air Temperature 1 | 0-10 | mA | -40-70 | C | IPP | N/A | Real □
D10 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Real □
D11 | Met N (if Registered Capacity >= 10 MW)
D12 | Wind Speed N | 0-10 | mA | 0-70 | m/s | IPP | N/A | Real □
D13 | Wind Direction N | 0-10 | mA | 0-360 | deg | IPP | N/A | Real □
D14 | Air Temperature N | 0-10 | mA | -40-70 | C | IPP | N/A | Real □
D15 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | IPP | N/A | Real □
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | IPP | N/A | Real □
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | IPP | N/A | Real □
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | IPP | N/A | Real □
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | IPP | N/A | Real □
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | IPP | N/A | Real □
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | IPP | N/A | Real □
Digital Output Signals from EirGrid to Sub Station
F1 | ESBN 20 kV interface switch (Nulec Recloser) |  | open | pulse | 0.5 seconds | ESBN | ESBN | Real □
F2 | ESBN 20 kV interface switch (Nulec Recloser) |  | close | pulse | 0.5 seconds | ESBN | ESBN | Real □
F3 | Dispatch Fail Market Command Lamp - IPP Panel |  | off | pulse | 0.5 seconds | IPP | ESBN | Real □
F4 | Dispatch Fail Market Command Lamp - IPP Panel |  | on | pulse | 0.5 seconds | IPP | ESBN | Real □
F5 | Blue Alert Lamp - IPP Panel |  | off | pulse | 0.5 seconds | IPP | ESBN | Real □
F6 | Blue Alert Lamp - IPP Panel |  | on | pulse | 0.5 seconds | IPP | ESBN | Real □
Strobe Enable Pulses
Digital Output Signals from EirGrid to WTG System
E7 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Real □
E8 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | IPP | N/A | Real □
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Digital Alarms From Networks |  |  |  |  | Provided by | TSO Pass-through to
Single Bit Indications
Network Protection Signals
N1 | ESBN Alarm 1 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N2 | ESBN Alarm 2 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N3 | ESBN Alarm 3 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N4 | ESBN Alarm 4 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N5 | ESBN Alarm 5 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N6 | ESBN Alarm 6 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N7 | ESBN Alarm 7 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N8 | ESBN Alarm 8 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N9 | ESBN Alarm 9 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N10 | ESBN Alarm 10 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N11 | ESBN Alarm 11 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N12 | ESBN Alarm 12 |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N13 | ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  |  |  |  | ESBN | ESBN | Real / Point Tested □
N14 | ESBN Alarm 14 (AC FAIL) |  |  |  |  | IPP | ESBN | Real / Point Tested □
N15 | ESBN Alarm 15 (G10 protection trip) |  |  |  |  | IPP | ESBN | Real / Point Tested □
N16 | ESBN Alarm 16 (Customer traffo protection trip) |  |  |  |  | IPP | ESBN | Real / Point Tested □
N17 | ESBN Alarm 17 (Fire Alarm for ESB Room) |  |  |  |  | IPP | ESBN | Real / Point Tested □
N18 | ESBN Alarm 18 (Intruder Alarm for ESB Room) |  |  |  |  | IPP | ESBN | Real / Point Tested □
Recommended cable 15-pair cable, 15 x 2 x 0.6sqmm, TP, stranded, external sheath
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | IPP | N/A | Real □
G2 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | IPP | N/A | Real □
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by IPP.
How is NOIS implemented?
[6 empty] | IPP Name |  | 0
IPP Signature
EMS Name
EMS Signature
| NOTE: Non operable IPP signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  |  |  |  | ESB Telecoms Name / Position |  | ESBTS Team
| Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 |  |  |  |  | ESB Telecoms Signature
Date
Note on A5: EirGrid Telecoms Interface Enclosure

## ETIE ¦ RTU Location
EirGrid Telecoms Interface Enclosure (ETIE)
Typical EirGrid RTU cabinet with integrated ETI and GPS clock 2.0m x 0.8m x 0.6m (rear access not required).
Note: This is for a typical installation and may vary from project to project. Any queries should be directed to generator_testing@eirgrid.com or esbts.scada.services@esb.ie
ETIE General Description
There will be four rows of terminals labelled Row 1, 2, 3, 4 as shown in the Layout drawing and Photograph above
Trunking shall be separated into IPP and EirGrid Telecoms trunking.
EirGrid Telecoms cabling to be in EirGrid Telecoms designated trunking only
IPP cabling to be in IPP designated trunking only
Access to terminals will be as follows:
Upper side to be used for EirGrid Telecoms use only
Lower side to be used for IPP use only
Isolating link to sever all connection between the IPP connection and EirGrid Telecoms connection
Command terminals to be covered with a Perspex cover and labelled "DO NOT ENERGISE"
Earthing of cabinet to be completed in accordance with 35 sq mm earth cable to EirGrid Telecoms earth bar
RTU Location:
The TSO RTU will be located in the ESB Networks substation at the IPP site

## ETIE Layout
Designation: Indications/Signals |  | ETIE Ref | ETIE ROW 1
POSITIVE 24V or 48V DC DOUBLE POINT INDICATION |  |  | +
ESBN 20 kV interface switch (Nulec Recloser) | open | A1 | 1
ESBN 20 kV interface switch (Nulec Recloser) | closed | A2 | 2
WINDFARM NAME T421 IPP 20 kV CB | open | A3 | 3
WINDFARM NAME T421 IPP 20 kV CB | closed | A4 | 4
WINDFARM NAME Feeder 1 20 kV CB | open | A5 | 5
WINDFARM NAME Feeder 1 20 kV CB | closed | A6 | 6
WINDFARM NAME Feeder 2 20 kV CB | open | A7 | 7
WINDFARM NAME Feeder 2 20 kV CB | closed | A8 | 8
WINDFARM NAME Feeder 3 20 kV CB | open | A9 | 9
WINDFARM NAME Feeder 3 20 kV CB | closed | A10 | 10
WINDFARM NAME Feeder 4 20 kV CB | open | A11 | 11
WINDFARM NAME Feeder 4 20 kV CB | closed | A12 | 12
TSO Dispatch Control Enable Switch | off | A13 | 13
TSO Dispatch Control Enable Switch | on | A14 | 14
Dispatch Fail Market Command Lamp - IPP Panel | off | A15 | 15
Dispatch Fail Market Command Lamp - IPP Panel | on | A16 | 16
Blue Alert Lamp - IPP Panel | off | A17 | 17
Blue Alert Lamp - IPP Panel | on | A18 | 18
ESB SCADA Remote Control Switch | off | A19 | 19
ESB SCADA Remote Control Switch | on | A20 | 20
Reactive Device >5 Mvar 1 | off | A21 | 21
Reactive Device >5 Mvar 1 | on | A22 | 22
Reactive Device >5 Mvar N | off | A23 | 23
Reactive Device >5 Mvar N | on | A24 | 24
Active Power Control facility status (feedback) | off | B1 | 25
Active Power Control facility status (feedback) | on | B2 | 26
Frequency Response System Mode Status (feedback) | off | B3 | 27
Frequency Response System Mode Status (feedback) | on | B4 | 28
Frequency Response Curve (feedback) | Curve 1 | B5 | 29
Frequency Response Curve (feedback) | Curve 2 | B6 | 30
31
32
33
34
35
36
37
38
39
40
POSITIVE 24V or 48V DC SINGLE POINT INDICATION |  |  | +
ESBN Alarm 1 |  | N1 | 41
ESBN Alarm 2 |  | N2 | 42
ESBN Alarm 3 |  | N3 | 43
ESBN Alarm 4 |  | N4 | 44
ESBN Alarm 5 |  | N5 | 45
ESBN Alarm 6 |  | N6 | 46
ESBN Alarm 7 |  | N7 | 47
ESBN Alarm 8 |  | N8 | 48
ESBN Alarm 9 |  | N9 | 49
ESBN Alarm 10 |  | N10 | 50
ESBN Alarm 11 |  | N11 | 51
ESBN Alarm 12 |  | N12 | 52
ESBN Alarm 13 (24V Battery charge Fault/ Alarm) |  | N13 | 53
ESBN Alarm 14 (AC FAIL) |  | N14 | 54
ESBN Alarm 15 (G10 protection trip) |  | N15 | 55
ESBN Alarm 16 (Customer traffo protection trip) |  | N16 | 56
ESBN Alarm 17 (Fire Alarm for ESB Room) |  | N17 | 57
ESBN Alarm 18 (Intruder Alarm for ESB Room) |  | N18 | 58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
Designation: Measurands |  | ETIE Ref | ETIE ROW 2
Active Power Output at Connection Point |  | C1 | 1
Active Power Output at Connection Point |  | C1 | 2
Reactive Power at Connection Point |  | C2 | 3
Reactive Power at Connection Point |  | C2 | 4
Voltage at Connection Point |  | C3 | 5
Voltage at Connection Point |  | C3 | 6
Available Active Power |  | D1 | 7
Available Active Power |  | D1 | 8
Active Power Control Setpoint (feedback) |  | D2 | 9
Active Power Control Setpoint (feedback) |  | D2 | 10
Frequency Droop Setting (feedback) |  | D3 | 11
Frequency Droop Setting (feedback) |  | D3 | 12
%WTG not generating due to high wind |  | D4 | 13
%WTG not generating due to high wind |  | D4 | 14
%WTG not generating due to low wind |  | D5 | 15
%WTG not generating due to low wind |  | D5 | 16
Wind Farm Availability |  | D6 | 17
Wind Farm Availability |  | D6 | 18
Wind Speed 1 |  | D7 | 19
Wind Speed 1 |  | D7 | 20
Wind Direction 1 |  | D8 | 21
Wind Direction 1 |  | D8 | 22
Air Temperature 1 |  | D9 | 23
Air Temperature 1 |  | D9 | 24
Air Pressure 1 |  | D10 | 25
Air Pressure 1 |  | D10 | 26
Wind Speed N |  | D12 | 27
Wind Speed N |  | D12 | 28
Wind Direction N |  | D13 | 29
Wind Direction N |  | D13 | 30
Air Temperature N |  | D14 | 31
Air Temperature N |  | D14 | 32
Air Pressure N |  | D15 | TBC
Air Pressure N |  | D15 | TBC
Analogue Output MW |  |  | +
Analogue Output Active Power Control Setpoint |  | G1 | 33
Analogue Output Active Power Control Setpoint |  | G1 | 34
Frequency Droop Setting |  | G2 | 35
Frequency Droop Setting |  | G2 | 36
Analogue Output kV |  |  | +
37
38
39
40
Designation: Commands |  | ETIE Ref | ETIE ROW 3
Active Power Control facility status | off | E1 | 1
Command Negative |  |  | 2
Active Power Control facility status | on | E2 | 3
Frequency Response System Mode Status | off | E3 | 4
Command Negative |  |  | 5
Frequency Response System Mode Status | on | E4 | 6
Frequency Response Curve Select | Curve 1 | E5 | 7
Command Negative |  |  | 8
Frequency Response Curve Select | Curve 2 | E6 | 9
ESBN 20 kV interface switch (Nulec Recloser) | open | F1 | 10
Command Negative |  |  | 11
ESBN 20 kV interface switch (Nulec Recloser) | close | F2 | 12
Dispatch Fail Market Command Lamp - IPP Panel | off | F3 | 13
Command Negative |  |  | 14
Dispatch Fail Market Command Lamp - IPP Panel | on | F4 | 15
Blue Alert Lamp - IPP Panel | off | F5 | 16
Command Negative |  |  | 17
Blue Alert Lamp - IPP Panel | on | F6 | 18
Command Output |  |  | 19
Command Negative |  |  | 20
Command Output |  |  | 21
Command Output |  |  | 22
Command Negative |  |  | 23
Command Output |  |  | 24
Command Output |  |  | 25
Command Negative |  |  | 26
Command Output |  |  | 27
Command Output |  |  | 28
Command Negative |  |  | 29
Command Output |  |  | 30
Command Output |  |  | 31
Command Negative |  |  | 32
Command Output |  |  | 33
Command Output |  |  | 34
Command Negative |  |  | 35
Command Output |  |  | 36
Command Output |  |  | 37
Command Negative |  |  | 38
Command Output |  |  | 39
Command Output |  |  | 40
Command Negative |  |  | 41
Command Output |  |  | 42
Command Output |  |  | 43
Command Negative |  |  | 44
Command Output |  |  | 45
Command Output |  |  | 46
Command Negative |  |  | 47
Command Output |  |  | 48
Designation: Controls |  | ETIE Ref | ETIE ROW 4
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
Single Controls |  |  | +
37
38
39
40
41
42
43
44
45
46
47
48
Digital Output Active Power Control Setpoint Enable |  | E7 | 49
|  | E7 | 50
Digital Output Frequency Droop Setting Enable |  | E8 | 51
|  | E8 | 52
Note on D2: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4
Note on D76: Administrator: Administrator: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4
Note on D121: Administrator: There is a gap between the off / on commands for command negative
Note on D170: Administrator: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4

## Frequency and Ramping Settings
Frequency, Ramp Rate and Voltage Settings to be implemented in Wind Farm Control System
Definitions:
| AAP | Available Active Power
| DMOL | Designed Minimum Operating Level
| APC | Active Power Control
Frequency Response Mode On | [5 empty] | Frequency Response Diagrams
Curve 1: Wind Following Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 48 |  | 100% of AAP
|  | FA | 48 | PA | 100% of AAP
|  | Under Frequency Response | 48 < f < 49.8 |  | 100% of AAP
|  | FB | f = 49.8 | PB | 100% of AAP
|  | +/-0.2Hz Deadband | 49.8 < f < 50.2 |  | 100% of AAP
|  | FC | f = 50.2 | PC | 100% of AAP
|  | Over Frequency Response | 50.2 < f < 50.79 |  | AAP + ∆MW2
|  | FD | f = 50.79 | PD | Minimum of: AAP and DMOL
|  | FE | f = 50.8 | PE | 0%3
|  |  | f > 50.8 |  | 0%3
Curve 1: Active Power Control Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 48 |  | 100% of AAP
|  | FA | f = 48 | PA | 100% of AAP
|  | Under Frequency Response | 48 < f < 49.985 |  | Minimum of: APC Setpoint + ∆MW and AAP
|  | FB | f = 49.985 | PB | Minimum of: APC Setpoint and AAP
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | Minimum of: APC Setpoint and AAP
|  | FC | f = 50.015 | PC | Minimum of: APC Setpoint and AAP
|  | Over Frequency Response | 50.015 < f < 50.79 |  | Minimum of: APC Setpoint + ∆MW and AAP + ∆MW1, 2
|  | FD | f = 50.79 | PD | Minimum of: APC Setpoint and AAP and DMOL
|  | FE | f = 50.8 | PE | 0%3
|  |  | f > 50.8 |  | 0%3
Curve 2: Wind Following Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f <49.3 |  | 100% of AAP
|  | FA | f = 49.3 | PA | 100% of AAP
|  | Under Frequency Response | 49.3 < f < 49.985 |  | 95% of Available Active Power + ∆MW
|  | FB | f = 49.985 | PB | 95% of Available Active Power. This is = to 5% Reserve.
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | 95% of Available Active Power. This is = to 5% Reserve.
|  | FC | f = 50.015 | PC | 95% of Available Active Power. This is = to 5% Reserve.
|  | Over Frequency Response | 50.015 < f < 50.79 |  | 95% of AAP + ∆MW2
|  | FD | f = 50.79 | PD | Minimum of: AAP and DMOL
|  | FE | f = 50.8 | PE | 0%3
|  |  | f > 50.8 |  | 0%3
Curve 2: Active Power Control Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 49.3 |  | 100% of AAP
|  | FA | f = 49.3 | PA | 100% of AAP
|  | Under Frequency Response | 49.3 < f < 49.985 |  | Minimum of: AAP and APC Setpoint + ∆MW
|  | FB | f = 49.985 | PB | Minimum of: APC Setpoint and 95% of AAP
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | Minimum of: APC Setpoint and 95% of AAP
|  | FC | f = 50.015 | PC | Minimum of: APC Setpoint and 95% of AAP
|  | Over Frequency Response | 50.015 < f < 50.79 |  | Minimum of: APC Setpoint + ∆MW and 95% of AAP + ∆MW1, 2
|  | FD | f = 50.79 | PD | Minimum of: APC Setpoint and AAP and DMOL
|  | FE | f = 50.8 | PE | 0%3
|  |  | f > 50.8 |  | 0%3
Minimum reserve level in Curve 2 is 5% of Registered Capacity, not lower than DMOL (settable between DMOL and 100%)
Frequency Response Mode OFF
Curve 1 and Curve 2: Wind Following Mode
|  |  | Transmission System Frequency (Hz) |  | Required Active Power Output
|  |  | 47.5 ≤ f ≥ 52 | No governor action | 100% of AAP
Curve 1 and Curve 2: Active Power Control Mode
|  |  | Transmission System Frequency (Hz) |  | Required Active Power Output
|  |  | 47.5 ≤ f ≥ 52 | No governor action | Minimum of: AAP and APC Setpoint
1 APC Setpoint + ∆MW shall have a lower limit of the minimum of: APC Setpoint and DMOL.
2 (95% of) AAP + ∆MW shall have a lower limit of the minimum of AAP and DMOL
3 Any WTG which has disconnected due to high frequency shall be brought back on load as fast as technically feasible, provided the Frequency has fallen below 50.2Hz.
DMOL shall not be greater than 12% of Registered Capacity
If AAP < DMOL and f < FE, maximise output
Ramp Rates:
|  | Mode | Rate | Priority | Comment
|  | Frequency Response | As fast as technically possible. 60% of its expected Active Power response within 5 seconds 100% of its expected Active Power response within 15 seconds. | 1 | The WFPS shall latch its AAP when the frequency excursion occurs and calculate its expected response based on this value.
|  | Active Power Dispatch | 20% of Registered Capacity per Minute | 2 | Settable between: 1-100% Registered Capacity per Minute
|  | Wind Following | 20% of Registered Capacity per Minute | 3 | Settable between: 1-100% Registered Capacity per Minute
Frequency Droop:
|  | Frequency Droop | Droop Calculation | Comment
|  | 4% |  | Settable between: 2-10%, online
Rate of Change of Frequency:
If possible, ROCOF should be disabled on Transmission System-connected Windfarms. If this is not possible, ROCOF should be set to max that machine is capable of. Under no circumstances should ROCOF be set to less than 0.5 Hz/s
Proposed Modification to Grid Code. (Ref#MPID 229).
Note. Frequency Response settings have been updated to clarify expected performance below DMOL - per feedback from industry. Changes are highlighted in red.

## IPP Turbine Protection Settings
Recommended Wind Farm Power Station (WFPS) Turbine Protection Settings to be applied by IPP
| Underfrequency stage 1 Setpoint | f< | 47.5 Hz | If only two stages available for underfrequency on relay, use stage 2 and stage 3
| Underfrequency stage 1 time delay | t< | 3600 s
| Underfrequency stage 2 Setpoint | f<< | 47.4 Hz
| Underfrequency stage 2 time delay | t<< | 20 s
| Underfrequency stage 3 Setpoint | f<<< | 46.9 Hz
| Underfrequency stage 3 time delay | t<<< | 1 s
| Overfrequency stage 1 Setpoint | f> | 52Hz
| Overfrequency stage 1 time delay | t> | 3600 s
| Overfrequency stage 2 Setpoint | f>> | 52.1 Hz
| Overfrequency stage 2 time delay | t>> | 1 s
| Rate of Change of Frequency setpoint | df/dt | Max | If possible, ROCOF should be disabled on Transmission System-connected Windfarms. If this is not possible, ROCOF should be set to max that machine is capable of. Under no circumstances should ROCOF be set to less than 0.5 Hz/s
| Rate of Change of Frequency delay | t | Max
| Undervoltage stage 1 Setpoint | U< | 0.89 pu
| Undervoltage stage 1 time delay | t< | 3 s
| Undervoltage stage 2 Setpoint | U<< | 0.14 pu
| Undervoltage stage 2 time delay | t<< | 0.625 s
| Overvoltage stage 1 Setpoint | U> | 1.11 pu
| Overvoltage stage 1 time delay | t> | 60 s | This is the minimum time delay we would recommend. If the plant can operate at this voltage for longer periods, then a longer time delay (at the discretion of the IPP) should be implemented.
| Overvoltage stage 2 Setpoint | U>> | 1.2 pu
| Overvoltage stage 2 time delay | t>> | 15 s | This is the minimum time delay we would recommend. If the plant can operate at this voltage for longer periods, then a longer time delay (at the discretion of the IPP) should be implemented.

## Test Schedule and Templates
Compliance Test Schedule and Test Procedure templates
Test Template located at the following:
http://www.eirgrid.com/operations/gridcode/compliancetesting/wfpstestprocedures/#d.en.17698
SCHEDULE OF CODE COMPLIANCE TESTS
http://www.eirgrid.com/media/Schedule%20of%20Grid%20Code%20Compliance%20Tests.xls
Date:
Wind Farm:
| Compliance Test | Clause | Test Procedure Reference | Mandatory Test in Presence of Witness on Site | Test Preferred in the Presence of Witness on Site | Preferred Test from TSO | Remote Control from TSO | Current Test Status | On Site Testing Date: | Remote Testing Date: | Sub-sequent Test Status | On Site Testing Date: | Remote Testing Date:
ID
| Fault Ride Through | DCC11.2
| Active Power Control | DCC11.3.2.3 |  | Yes |  |  | Yes
| Frequency Response | DCC11.3.2.3 |  | Yes |  |  | Yes
| Ramp Rates and Start Up Test | DCC11.3.4 |  | Yes |  |  | Yes
| Power Factor Control | DCC11.4.3 |  | Yes
| Network Operator Iniated Shutdown | DCC11.5.2.4 |  | Yes |  |  | Yes via DCC.
IPP to develop Test Procedure and agree with generator_testing@eirgrid.com via DCC at least 10 Business Days in advance of testing