## 7-Year Summary
Renewable Electricity as % of Demand
| Northern Ireland | Ireland | All Island
2014 | 17.9% | 22.86% | 21.68%
2015 | 22.77% | 27.32% | 26.26%
2016 | 23.47% | 25.46% | 25.01%
2017 | 31.15% | 29.61% | 29.95%
2018 | 36.12% | 33.04% | 33.7%
2019 | 39.13% | 37.59% | 37.91%
2020 | 43.85% | 42.12% | 42.47%
Data Sources:
Ireland: SEAI - Updated April 2021
Northern Ireland: SONI metered data.
See "Fuel Mix & CO2" tab for more information.
Wind as % of Demand
| Northern Ireland | Ireland | All Island
2014 | 16.57% | 18.39% | 17.95%
2015 | 20.54% | 22.84% | 22.3%
2016 | 19.65% | 20.83% | 20.56%
2017 | 26.99% | 24.82% | 25.29%
2018 | 30.68% | 27.99% | 28.56%
2019 | 33.09% | 31.97% | 32.21%
2020 | 37.07% | 36.29% | 36.45%
Data Sources:
Ireland: SEAI - Updated April 2021
Northern Ireland: SONI metered data.
See "Fuel Mix & CO2" tab for more information.
Maximum Wind Penetration as % of Demand
| Northern Ireland | Ireland | All Island
2014 | 79.67% | 70.49% | 68.69%
2015 | 83.09% | 74.74% | 72.68%
2016 | 101.4% | 77.93% | 77.87%
2017 | 119.6% | 82.13% | 78.66%
2018 | 129% | 86.55% | 84.68%
2019 | 119.5% | 93.03% | 84.26%
2020 | 132.4% | 96.26% | 88.97%
Source: SCADA data - See "System Data Summary" tab.
Note: NI and IE max wind levels may not occur simultaneously.
Percentage of Year with Wind at 50% of Demand or Higher
| Northern Ireland | Ireland | All Island
2014 | 3.72% | 4.97% | 4.2%
2015 | 6.64% | 10.67% | 8.73%
2016 | 6.47% | 10.06% | 7.99%
2017 | 16.32% | 15.47% | 14.71%
2018 | 22.94% | 23.76% | 23.18%
2019 | 27.35% | 27.49% | 26.24%
2020 | 32.43% | 36.46% | 35.37%
Source: SCADA data - See "System Data Summary" tab.
Total Wind Generation GWh
| Northern Ireland | Ireland | All Island
2014 | 1342.83 | 5058.32 | 6401.15
2015 | 1696.17 | 6536.21 | 8232.38
2016 | 1498.95 | 6061.49 | 7560.43
2017 | 2033.89 | 7227.98 | 9261.87
2018 | 2384.6691 | 8683.5889 | 11068.258
2019 | 2461.707 | 9496.5132 | 11958.2202
2020 | 2629.0251 | 11070.3795 | 13699.4046
Source: SCADA data - See "System Data Summary" tab.
Maximum Wind Generation Level MW
| Northern Ireland | Ireland | All Island
2014 | 511.99 | 1825.51 | 2317.54
2015 | 583.24 | 2036.77 | 2606.89
2016 | 633.993 | 2230.84 | 2811.574
2017 | 831.185 | 2615.61 | 3280.794
2018 | 994.047 | 3051.98 | 3938.772
2019 | 1007.73 | 3135.76 | 3995.966
2020 | 1005.334 | 3358.57 | 4231.946
Source: SCADA data - See "System Data Summary" tab.
Note: NI and IE max wind levels may not occur simultaneously.
Installed Wind Capacity MW
| Northern Ireland | Ireland | All Island
2014 | 729.135 | 2266.417 | 2995.552
2015 | 751.025 | 2447.267 | 3198.292
2016 | 942.623 | 2794.756 | 3737.379
2017 | 1153.718 | 3312.264 | 4465.982
2018 | 1276.254 | 3667.038 | 4943.292
2019 | 1276.254 | 4119.643 | 5395.897
2020 | 1276.254 | 4299.841 | 5576.095
Data Sources:
Ireland TSO wind: EirGrid.
Ireland DSO wind: ESB Networks.
Northern Ireland Wind: SONI and NIE.
See "Wind Installed Capacities" and
"Connected Windfarm Lists" tabs for more information.
Wind Installed During Year MW
| Northern Ireland | Ireland | All Island
2014 | 89.181 | 343.14 | 432.321
2015 | 21.89 | 180.85 | 202.74
2016 | 191.598 | 347.489 | 539.087
2017 | 211.095 | 517.508 | 728.603
2018 | 122.536 | 354.774 | 477.31
2019 | 0 | 452.605 | 452.605
2020 | 0 | 180.198 | 180.198
Data Sources:
Ireland TSO wind: EirGrid.
Ireland DSO wind: ESB Networks.
Northern Ireland Wind: SONI and NIE.
See "Wind Installed Capacities" and
"Connected Windfarm Lists" tabs for more information.
Percentage of Year with SNSP at 50% or Higher
All Island
2014 |  |  | 0.71%
2015 |  |  | 2.63%
2016 |  |  | 3.98%
2017 |  |  | 9.8%
2018 |  |  | 20.92%
2019 |  |  | 22.91%
2020 |  |  | 32.19%
Source: SCADA data - See "System Data Summary" tab.
Total System Demand GWh
| Northern Ireland | Ireland | All Island
2014 | 8587.891 | 25770.691 | 34358.582
2015 | 8524.897 | 26575.624 | 35100.52
2016 | 8314.402 | 27155.16 | 35469.562
2017 | 8119.954 | 27742.043 | 35861.998
2018 | 8100.4786 | 28900.084 | 37000.5626
2019 | 7895.4443 | 29082.8817 | 36978.326
2020 | 7504.8552 | 29330.5234 | 36835.3785
Source: SCADA data - See "System Data Summary" tab.
System Peak Demand Level MW
| Northern Ireland | Ireland | All Island
2014 | 1683.64 | 4613.27 | 6269.63
2015 | 1709.22 | 4703.96 | 6396.95
2016 | 1649.16 | 4760.51 | 6375.021
2017 | 1627.525 | 4939.61 | 6531.683
2018 | 1651.98 | 4913.69 | 6504.008
2019 | 1590.214 | 5014.05 | 6547.514
2020 | 1550.681 | 5348.48 | 6894.431
Source: SCADA data - See "System Data Summary" tab.
Note: NI and IE peak demand levels may not occur simultaneously

## System Data Summary
|  |  | 2014 | [11 empty] | 2014 Total | 2015 | [11 empty] | 2015 Total | 2016 | [11 empty] | 2016 Total | 2017 | [11 empty] | 2017 Total | 2018 | [11 empty] | 2018 Total | 2019 | [11 empty] | 2019 Total | 2020 | [11 empty] | 2020 Total | 2021 | [11 empty] | 2021 Total |  | 2022 Total
|  |  | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 |  | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 |  | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 |  | 2017-01-01 | 2017-02-01 | 2017-03-01 | 2017-04-01 | 2017-05-01 | 2017-06-01 | 2017-07-01 | 2017-08-01 | 2017-09-01 | 2017-10-01 | 2017-11-01 | 2017-12-01 |  | 2018-01-01 | 2018-02-01 | 2018-03-01 | 2018-04-01 | 2018-05-01 | 2018-06-01 | 2018-07-01 | 2018-08-01 | 2018-09-01 | 2018-10-01 | 2018-11-01 | 2018-12-01 |  | 2019-01-01 | 2019-02-01 | 2019-03-01 | 2019-04-01 | 2019-05-01 | 2019-06-01 | 2019-07-01 | 2019-08-01 | 2019-09-01 | 2019-10-01 | 2019-11-01 | 2019-12-01 |  | 2020-01-01 | 2020-02-01 | 2020-03-01 | 2020-04-01 | 2020-05-01 | 2020-06-01 | 2020-07-01 | 2020-08-01 | 2020-09-01 | 2020-10-01 | 2020-11-01 | 2020-12-01 |  | 2021-01-01 | 2021-02-01 | 2021-03-01 | 2021-04-01 | 2021-05-01 | 2021-06-01 | 2021-07-01 | 2021-08-01 | 2021-09-01 | 2021-10-01 | 2021-11-01 | 2021-12-01 |  | 2022-01-01 |  | Data prior to 2014 is not available.
Northern Ireland | System Generation | Min (MW) | 375.91 | 538.29 | 460.44 | 414.73 | 452.98 | 435.71 | 417.27 | 511.89 | 413.13 | 438.58 | 483.43 | 421.88 | 375.91 | 543.1 | 545.15 | 435.87 | 515.6 | 523.4 | 489.99 | 485.52 | 600.99 | 496.59 | 608.33 | 530.5 | 488.04 | 435.87 | 564.4 | 660.57 | 528.67 | 527.99 | 574.01 | 387.95 | 475.052 | 465.504 | 407.402 | 333.883 | 564.273 | 564.11 | 333.883 | 523.33 | 615.84 | 618.565 | 632.44 | 635.703 | 484.194 | 628.351 | 573.514 | 561.77 | 505.787 | 532.885 | 375.942 | 375.942 | 491.007 | 541.845 | 570.848 | 340.288 | 395.137 | 429.576 | 485.43 | 453.436 | 473.713 | 308.305 | 333.44 | 327.271 | 308.305 | 363.066 | 364.735 | 356.835 | 359.58 | 320.196 | 482.459 | 317.4 | 308.057 | 304.907 | 325.931 | 304.751 | 356.094 | 304.751 | 425.114 | 382.441 | 383.513 | 299.863 | 325.497 | 369.443 | 311.758 | 349.35 | 338.35 | 397.452 | 437.669 | 422.417 | 299.863 | 305.486 | 326.516 | 361.429 | 349.661 | 305.189 | 326.977 | 364.625 | 374.832 | 280.921 | 321.833 | 365.04 | 390.382 | 280.921 | 455.407 | 455.407 | Notes: The system data in this report is is based on average 15-minute SCADA readings (MW). All figures represent net exported electricity. Maximum/Minimum figures in the different jurisdictions do not necessarily occur at the same time. SNSP (System Non-Synchronous Penetration) is the sum of non-synchronous generation (such as wind, solar and HVDC imports) as a percentage of "total demand + exports". The current maximum SNSP limit allowed on the system is currently 75%. SNSP may exceed this maximum limit due to wind variations. When the SNSP limit is raised, a trial period takes place before it becomes permanent. During the trial period, the system is operated at this increased SNSP limit except in times of extreme system events or during system testing.
|  | Avg (MW) | 945.9271 | 984.7476 | 829.3432 | 759.7631 | 798.5429 | 712.212 | 775.9477 | 830.6425 | 720.2799 | 857.0096 | 882.813 | 921.0552 | 834.3524 | 989.0065 | 961.8693 | 912.6707 | 839.5081 | 846.4799 | 832.4625 | 810.0141 | 883.6047 | 882.3109 | 926.8417 | 977.9203 | 1008.3049 | 905.7085 | 1044.9561 | 1033.7539 | 921.2557 | 963.6711 | 873.9915 | 813.4588 | 769.7032 | 806.8543 | 819.8945 | 872.7268 | 1049.1451 | 1012.435 | 914.5397 | 986.7262 | 1000.3472 | 940.0091 | 925.5046 | 922.8383 | 913.6653 | 936.4568 | 938.741 | 928.3051 | 928.9946 | 960.8068 | 932.8448 | 942.5826 | 1036.7168 | 1020.9426 | 984.1442 | 804.7389 | 812.2051 | 715.2599 | 723.2111 | 801.627 | 778.3159 | 850.5842 | 1006.847 | 880.0169 | 867.0667 | 924.0399 | 972.7745 | 915.8392 | 883.6016 | 800.8978 | 812.7469 | 671.4317 | 724.4459 | 768.8298 | 892.5199 | 925.5835 | 927.0156 | 850.6889 | 956.5753 | 999.7967 | 902.3504 | 674.4113 | 794.276 | 809.5153 | 865.5585 | 782.0343 | 877.9606 | 860.787 | 922.433 | 1028.2441 | 872.6955 | 1014.5363 | 1040.4014 | 874.2734 | 772.9283 | 789.2853 | 796.798 | 707.7712 | 780.2769 | 858.1353 | 827.5051 | 918.9077 | 1058.4592 | 868.8978 | 1055.603 | 1055.603
|  | Max (MW) | 1606.63 | 1580.57 | 1242.45 | 1227.65 | 1234.1 | 1053.93 | 1231.46 | 1211.07 | 1142.15 | 1320.03 | 1526 | 1483.75 | 1606.63 | 1600.45 | 1494.63 | 1444.1 | 1268.71 | 1221.76 | 1379.66 | 1185.07 | 1281.07 | 1326.79 | 1458.92 | 1521.85 | 1570.79 | 1600.45 | 1523.88 | 1506.53 | 1351.24 | 1441.58 | 1373.23 | 1228.55 | 1219.801 | 1256.449 | 1336.647 | 1524.064 | 1723.248 | 1804.633 | 1804.633 | 1457.657 | 1416.091 | 1359.88 | 1301.4 | 1410.321 | 1347.781 | 1335.784 | 1487.829 | 1381.091 | 1521.792 | 1538.461 | 1391.287 | 1538.461 | 1509.123 | 1571.516 | 1464.648 | 1206.483 | 1188.03 | 1156.02 | 1122.074 | 1294.168 | 1220.501 | 1455.226 | 1514.339 | 1626.36 | 1626.36 | 1615.588 | 1494.851 | 1670.489 | 1634.513 | 1420.708 | 1252.418 | 1247.57 | 1325.709 | 1485 | 1525.145 | 1739.735 | 1543.858 | 1739.735 | 1486.645 | 1532.841 | 1559.66 | 1347.077 | 1252.973 | 1339.185 | 1404.051 | 1338.209 | 1450.116 | 1482.997 | 1608.604 | 1961.206 | 1961.206 | 1667.872 | 1730.504 | 1629.625 | 1427.895 | 1422.782 | 1492.19 | 1146.532 | 1285.449 | 1474.025 | 1478.414 | 1748.587 | 1765.271 | 1765.271 | 1659.776 | 1659.776
|  | Total (GWh) | 703.7697 | 661.7504 | 616.202 | 547.0294 | 594.1159 | 512.7927 | 577.3051 | 617.998 | 518.6015 | 638.4722 | 635.6254 | 685.265 | 7308.9273 | 735.8208 | 646.3762 | 678.1143 | 604.4459 | 629.7811 | 599.373 | 602.6505 | 657.4019 | 635.2639 | 690.4971 | 704.1026 | 750.1789 | 7934.0061 | 777.4473 | 719.4927 | 684.493 | 693.8432 | 650.2496 | 585.6903 | 572.6592 | 600.2996 | 590.3241 | 650.1815 | 755.3844 | 753.2517 | 8033.3166 | 734.1243 | 672.2333 | 698.4267 | 666.3633 | 686.5917 | 657.839 | 696.7238 | 698.4233 | 668.3797 | 692.1009 | 691.7809 | 694.0365 | 8257.0235 | 771.3173 | 686.0734 | 731.2191 | 579.412 | 604.2806 | 514.9871 | 538.0691 | 596.4105 | 560.3874 | 633.6852 | 724.9299 | 654.7326 | 7595.5042 | 687.4857 | 653.7044 | 680.4685 | 636.1931 | 595.8679 | 585.1778 | 499.5452 | 538.9878 | 553.5575 | 664.9273 | 666.4201 | 689.6996 | 7452.035 | 711.692 | 695.8585 | 670.4463 | 485.5761 | 590.9413 | 582.851 | 643.9755 | 581.8335 | 632.1316 | 641.2863 | 664.1518 | 765.0136 | 7665.7577 | 754.815 | 699.1497 | 649.5851 | 556.5084 | 587.2282 | 573.6946 | 526.5818 | 580.526 | 617.8574 | 616.4913 | 661.6135 | 787.4937 | 7611.5448 | 785.3687 | 785.3687
| System Demand | Min (MW) | 655.55 | 674.68 | 643.68 | 561.49 | 544.76 | 507.84 | 488.97 | 522.93 | 545.94 | 561.85 | 572.89 | 604.9 | 488.97 | 589.05 | 673.76 | 641.53 | 586.61 | 540.32 | 510.19 | 486.45 | 506.58 | 543.64 | 567.61 | 557.39 | 565.67 | 486.45 | 578.55 | 634.63 | 586.81 | 584.03 | 494.56 | 477.23 | 494.49 | 491.411 | 521.391 | 563.906 | 602.124 | 552.35 | 477.23 | 580.579 | 501.68 | 543.781 | 463.177 | 495.106 | 473.233 | 488.323 | 500.869 | 473.936 | 456.682 | 521.283 | 502.709 | 456.682 | 537.633 | 615.312 | 584.372 | 500.317 | 435.833 | 449.76 | 478.117 | 476.052 | 460.141 | 508.101 | 543.997 | 489.968 | 435.833 | 532.447 | 511.602 | 528.053 | 504.03 | 473.416 | 434.964 | 456.749 | 431.345 | 472.451 | 446.374 | 549.563 | 450.761 | 431.345 | 500.384 | 501.194 | 498.061 | 444.623 | 377.615 | 369.559 | 385.466 | 463.063 | 431.598 | 440.979 | 454.941 | 474.578 | 369.559 | 535.912 | 504.691 | 479.519 | 476.932 | 473.934 | 485.637 | 490.435 | 495.249 | 494.44 | 443.103 | 464.166 | 460.175 | 443.103 | 428.281 | 428.281
|  | Avg (MW) | 1114.7913 | 1103.6994 | 1040.2284 | 948.2662 | 928.7113 | 888.3959 | 859.0329 | 879.1455 | 920.9104 | 971.2524 | 1038.5807 | 1079.2087 | 980.3528 | 1123.4407 | 1114.2362 | 1045.7741 | 942.8233 | 921.7341 | 888.3937 | 847.0546 | 855.5238 | 909.3112 | 959.6655 | 1031.7737 | 1048.096 | 973.1617 | 1067.7759 | 1065.7363 | 976.4543 | 934.938 | 852.2211 | 840.9634 | 827.1242 | 855.3218 | 897.1336 | 951.282 | 1057.0334 | 1038.4031 | 946.5394 | 1058.8627 | 1053.7137 | 978.3585 | 878.1499 | 851.1435 | 848.23 | 803.1537 | 852.6436 | 883.5342 | 904.5254 | 1007.372 | 1012.9886 | 926.9354 | 1054.8245 | 1053.2708 | 1019.697 | 905.2182 | 853.276 | 825.2998 | 795.4928 | 833.8677 | 858.4406 | 928.3597 | 992.5235 | 985.0535 | 924.7122 | 1027.3129 | 984.1636 | 948.0274 | 886.0416 | 862.6287 | 821.5582 | 789.2004 | 799.7657 | 842.3962 | 913.868 | 992.5654 | 954.1921 | 901.3064 | 975.1325 | 959.6281 | 908.0437 | 739.209 | 734.9937 | 761.3816 | 777.4845 | 798.3909 | 837.8107 | 872.3488 | 931.0667 | 959.1068 | 854.3779 | 977.4443 | 926.0538 | 889.904 | 842.8089 | 829.2293 | 810.5758 | 810.2393 | 823.1982 | 858.789 | 869.9121 | 932.9081 | 949.7001 | 876.492 | 962.1081 | 962.1081
|  | Max (MW) | 1683.64 | 1609.25 | 1508.17 | 1363.12 | 1295.55 | 1241.52 | 1190.74 | 1203.77 | 1272.07 | 1483.6 | 1630.95 | 1672.72 | 1683.64 | 1709.22 | 1679.31 | 1541.56 | 1386.61 | 1302.56 | 1307.32 | 1206.62 | 1179.99 | 1241.26 | 1485.37 | 1662.76 | 1623.76 | 1709.22 | 1649.16 | 1581.7 | 1478.75 | 1333.72 | 1224.39 | 1161.85 | 1205.271 | 1184.484 | 1281.241 | 1416.583 | 1644.258 | 1627.282 | 1649.16 | 1627.525 | 1574.404 | 1493.512 | 1237.88 | 1182.463 | 1233.655 | 1175.342 | 1231.929 | 1313.342 | 1407.714 | 1600.752 | 1611.901 | 1627.525 | 1651.98 | 1590.11 | 1499.979 | 1319.979 | 1227.293 | 1204.182 | 1138.435 | 1159.266 | 1241.292 | 1471.075 | 1553.429 | 1601.288 | 1651.98 | 1590.214 | 1504.5 | 1400.348 | 1325.164 | 1224.97 | 1207.077 | 1094.636 | 1115.271 | 1274.36 | 1411.62 | 1556.997 | 1542.783 | 1590.214 | 1523.559 | 1489.285 | 1377.694 | 1126.639 | 1101.953 | 1139.776 | 1158.865 | 1184.511 | 1214.051 | 1358.845 | 1488.995 | 1550.681 | 1550.681 | 1561.846 | 1467.557 | 1351.878 | 1200.562 | 1172.218 | 1168.639 | 1151.909 | 1134.905 | 1217.951 | 1246.381 | 1468.684 | 1504.238 | 1561.846 | 1523.794 | 1523.794
|  | Total (GWh) | 829.4047 | 741.686 | 772.8897 | 682.7516 | 690.9612 | 639.6451 | 639.1204 | 654.0842 | 663.0555 | 723.583 | 747.7781 | 802.9312 | 8587.8909 | 835.8399 | 748.7667 | 777.0101 | 678.8328 | 685.7702 | 639.6434 | 630.2086 | 636.5097 | 654.7041 | 714.9508 | 742.877 | 779.7834 | 8524.8968 | 794.4253 | 741.7525 | 725.5056 | 673.1553 | 634.0525 | 605.4936 | 615.3804 | 636.3594 | 645.9362 | 708.7051 | 761.0641 | 772.5719 | 8314.4019 | 787.7938 | 708.0956 | 726.9204 | 632.2679 | 633.2508 | 610.7256 | 597.5463 | 634.3668 | 636.1446 | 673.8714 | 725.3078 | 753.6635 | 8119.9545 | 784.7894 | 707.798 | 757.6349 | 651.7571 | 634.8373 | 594.2159 | 591.8466 | 620.3976 | 618.0772 | 691.628 | 714.6169 | 732.8798 | 8100.4786 | 764.3208 | 661.358 | 704.3843 | 637.9499 | 641.7958 | 591.5219 | 587.1651 | 595.0257 | 606.5252 | 680.8316 | 714.6471 | 709.9189 | 7895.4443 | 725.4986 | 667.9012 | 674.6765 | 532.2305 | 546.8353 | 548.1948 | 578.4485 | 594.0028 | 603.2237 | 649.8999 | 670.368 | 713.5755 | 7504.8552 | 727.2185 | 622.3082 | 661.1986 | 606.8224 | 616.9466 | 583.6146 | 602.8181 | 612.4595 | 618.3281 | 648.0845 | 671.6939 | 706.5769 | 7678.0699 | 715.8084 | 715.8084
| Wind Generation | Min (MW) | 0.32 | 6.5 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0 | 0 | 0 | 0.42 | 0 | 0 | 0 | 0.71 | 0 | 0 | 0.08 | 0 | 0.42 | 0 | 0.31 | 0 | 0.04 | 0.03 | 0.33 | 0 | 0 | 0 | 0 | 0.294 | 0 | 0 | 0 | 0.046 | 0 | 1.707 | 3.885 | 0.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.388 | 0 | 3.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.312 | 0.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Avg (MW) | 206.4332 | 265.7241 | 204.9375 | 149.0801 | 106.5474 | 63.4478 | 84.6536 | 143.9763 | 56.6602 | 201.1264 | 140.477 | 220.7497 | 153.291 | 290.3347 | 193.47 | 233.331 | 124.1486 | 213.5762 | 156.787 | 139.9828 | 132.6466 | 132.9398 | 137.4531 | 254.0216 | 311.5081 | 193.6271 | 253.7013 | 227.8343 | 155.6999 | 144.7333 | 131.3299 | 86.7735 | 106.7865 | 161.6244 | 193.8352 | 154.7454 | 153.5776 | 277.4459 | 170.645 | 237.8418 | 303.5395 | 221.8813 | 193.5092 | 169.615 | 226.5528 | 171.0185 | 188.0014 | 257.4372 | 308.5766 | 239.3428 | 275.2439 | 232.1795 | 396.2295 | 316.0683 | 296.4793 | 226.6723 | 192.1142 | 111.9267 | 117.5292 | 207.8976 | 289.2051 | 325.023 | 441.0688 | 350.0152 | 272.2225 | 283.1145 | 454.5026 | 381.532 | 300.114 | 168.9771 | 188.837 | 175.9592 | 250.5484 | 246.4039 | 318.185 | 246.6495 | 369.6698 | 281.0168 | 455.2483 | 515.4532 | 359.2914 | 186.0457 | 194.9426 | 202.0257 | 211.38 | 168.8775 | 266.4964 | 333.4572 | 339.6943 | 366.0865 | 299.297 | 271.3909 | 476.3416 | 329.8327 | 178.3885 | 210.4598 | 194.3949 | 55.3609 | 129.6352 | 167.5056 | 296.9694 | 321.355 | 351.5743 | 247.0889 | 380.3276 | 380.3276
|  | Max (MW) | 494.49 | 501.22 | 507.33 | 501.46 | 461.37 | 309.84 | 427.27 | 487.06 | 400.7 | 508.8 | 504.52 | 511.99 | 511.99 | 554.78 | 571.34 | 576.26 | 508.33 | 562.74 | 583.24 | 560.59 | 516 | 472.56 | 555.43 | 557.57 | 581.96 | 583.24 | 575.7 | 586.81 | 580.35 | 509.39 | 569.78 | 471.9 | 516.344 | 548.072 | 594.976 | 543.623 | 566.545 | 633.993 | 633.993 | 668.69 | 664.481 | 650.15 | 649.161 | 672.137 | 716.087 | 640.911 | 699.338 | 823.079 | 831.185 | 736.514 | 811.301 | 831.185 | 858.537 | 777.8 | 847.781 | 736.486 | 824.162 | 607.027 | 647.119 | 704.834 | 759.278 | 846.334 | 994.047 | 951.284 | 994.047 | 951.878 | 980.433 | 1007.73 | 986.228 | 821.392 | 722.584 | 759.851 | 822.435 | 893.445 | 829.964 | 849.28 | 957.496 | 1007.73 | 1005.334 | 969.718 | 974.649 | 733.525 | 701.816 | 823.374 | 685.753 | 784.818 | 791.008 | 926.156 | 935.364 | 976.655 | 1005.334 | 986.958 | 973.005 | 927.885 | 834.652 | 970.252 | 795.821 | 540.213 | 748.105 | 719 | 795.549 | 925.277 | 997.233 | 997.233 | 1043.006 | 1043.006
|  | Total (GWh) | 153.5863 | 178.5666 | 152.2685 | 107.3376 | 79.2713 | 45.6824 | 62.9823 | 107.1184 | 40.7953 | 149.8391 | 101.1435 | 164.2377 | 1342.8291 | 216.009 | 130.0118 | 173.365 | 89.387 | 158.9007 | 112.8867 | 104.1472 | 98.689 | 95.7167 | 102.4026 | 182.8956 | 231.762 | 1696.1733 | 188.7538 | 158.5727 | 115.685 | 104.208 | 97.7095 | 62.4769 | 79.4491 | 120.2485 | 139.5614 | 115.2853 | 110.5759 | 206.4197 | 1498.9459 | 176.9543 | 203.9786 | 164.8578 | 139.3266 | 126.1936 | 163.118 | 127.2378 | 139.873 | 185.3548 | 229.8896 | 172.3268 | 204.7815 | 2033.8923 | 294.7947 | 212.3979 | 220.2841 | 163.2041 | 142.933 | 80.5872 | 87.4417 | 154.6758 | 208.2277 | 242.1421 | 317.5695 | 260.4113 | 2384.6691 | 210.6372 | 305.4257 | 283.4782 | 216.0821 | 125.719 | 135.9626 | 130.9136 | 186.408 | 177.4108 | 237.0479 | 177.5876 | 275.0343 | 2461.707 | 338.7047 | 358.7554 | 266.9535 | 133.9529 | 145.0373 | 145.4585 | 157.2667 | 125.6449 | 191.8774 | 248.4256 | 244.5799 | 272.3683 | 2629.0251 | 201.9149 | 320.1016 | 245.0657 | 128.4397 | 156.5821 | 139.9643 | 41.1885 | 96.4486 | 120.604 | 221.2422 | 231.3756 | 261.5713 | 2164.4984 | 282.9637 | 282.9637
| Wind Penetration (% of Demand) | Min (%) | 0.02204% | 0.6132% | 0% | 0.00508% | 0% | 0% | 0% | 0% | 0% | 0.02575% | 0% | 0% | 0% | 0.04181% | 0% | 0% | 0% | 0.06386% | 0% | 0% | 0.01063% | 0% | 0.03767% | 0% | 0.02704% | 0% | 0.003131% | 0.002394% | 0.02571% | 0% | 0% | 0% | 0% | 0.04731% | 0% | 0% | 0% | 0.003033% | 0% | 0.1303% | 0.5031% | 0.004342% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.2289% | 0% | 0.4938% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.1161% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.2184% | 0.05132% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Disclaimer: Please note that the data contained herein is indicative as it is based on raw 15-minute SCADA readings which are produced in real time and have yet to be quality controlled. EirGrid as the Transmission System Operator (TSO) for Ireland and SONI as the TSO for Northern Ireland make no warranties or representations of any kind with respect of this document, including, without limitation, its quality, accuracy and completeness. While every effort has been made in the compilation of this report to ensure that the information herein is correct, the TSOs do not accept liability for any loss or damage arising from the use of this document or any reliance on the information it contains. Use of this document and the information it contains is at the user’s sole risk. In addition, the TSOs strongly recommend that any party wishing to make a decision based on the content of this document should consult the TSOs in advance.
|  | Avg (%) | 18.52% | 24.08% | 19.7% | 15.72% | 11.47% | 7.142% | 9.855% | 16.38% | 6.153% | 20.71% | 13.53% | 20.45% | 15.64% | 25.84% | 17.36% | 22.31% | 13.17% | 23.17% | 17.65% | 16.53% | 15.5% | 14.62% | 14.32% | 24.62% | 29.72% | 19.9% | 23.76% | 21.38% | 15.95% | 15.48% | 15.41% | 10.32% | 12.91% | 18.9% | 21.61% | 16.27% | 14.53% | 26.72% | 18.03% | 22.46% | 28.81% | 22.68% | 22.04% | 19.93% | 26.71% | 21.29% | 22.05% | 29.14% | 34.11% | 23.76% | 27.17% | 25.05% | 37.56% | 30.01% | 29.08% | 25.04% | 22.51% | 13.56% | 14.77% | 24.93% | 33.69% | 35.01% | 44.44% | 35.53% | 29.44% | 27.56% | 46.18% | 40.24% | 33.87% | 19.59% | 22.99% | 22.3% | 31.33% | 29.25% | 34.82% | 24.85% | 38.74% | 31.18% | 46.69% | 53.71% | 39.57% | 25.17% | 26.52% | 26.53% | 27.19% | 21.15% | 31.81% | 38.23% | 36.48% | 38.17% | 35.03% | 27.77% | 51.44% | 37.06% | 21.17% | 25.38% | 23.98% | 6.833% | 15.75% | 19.5% | 34.14% | 34.45% | 37.02% | 28.19% | 39.53% | 39.53%
|  | Max (%) | 63.75% | 68.92% | 68.98% | 62.72% | 60.56% | 36.46% | 61.93% | 60.77% | 52.22% | 79.67% | 75.01% | 70.81% | 79.67% | 77.06% | 67.34% | 70.23% | 59.72% | 75.47% | 76.08% | 81.19% | 78.76% | 69.17% | 80.22% | 83.09% | 73.61% | 83.09% | 77.48% | 80.6% | 80.87% | 71.85% | 79.21% | 58.51% | 59.46% | 71.39% | 88.05% | 77.3% | 77.3% | 101.4% | 101.4% | 90.65% | 86.32% | 86.07% | 81.63% | 81.75% | 110.3% | 86.75% | 90.5% | 102.2% | 113.1% | 100.1% | 119.7% | 119.7% | 102.5% | 102% | 113.4% | 94.11% | 90.58% | 107.9% | 80.1% | 114.6% | 129% | 119.6% | 114.4% | 114.5% | 129% | 114.1% | 119.3% | 111.1% | 110.2% | 100.9% | 100.7% | 114.5% | 105.5% | 119.5% | 102.2% | 89.83% | 111.2% | 119.5% | 111.3% | 104.1% | 98.1% | 89.65% | 105.2% | 102.8% | 104.9% | 101.5% | 113.3% | 119.3% | 105% | 132.4% | 132.4% | 127.1% | 139.7% | 129.7% | 137.5% | 147% | 121.4% | 94.76% | 110.1% | 122.4% | 121.5% | 133.2% | 147.4% | 147.4% | 139.6% | 139.6%
| Wind Penetration (% of Demand) | % of Month with Wind Less than 25% | 64.78% | 48.55% | 61.74% | 72.43% | 85.35% | 96.91% | 89.18% | 73.76% | 96.56% | 59.06% | 80.59% | 60.42% | 74.18% | 45.77% | 68.08% | 54% | 79.2% | 54.07% | 71.15% | 73.99% | 73.15% | 78.3% | 74.8% | 47.88% | 35.15% | 62.85% | 53.73% | 59.88% | 75.03% | 77.78% | 77.15% | 89.97% | 85.75% | 65.32% | 59.58% | 72.42% | 76.49% | 44.56% | 69.79% | 61.63% | 46.35% | 59.08% | 62.6% | 64.92% | 54.9% | 60.22% | 62.16% | 46.11% | 38.26% | 55.42% | 52.65% | 55.44% | 30.31% | 42.3% | 50.37% | 55.1% | 60.52% | 77.01% | 78.7% | 55.91% | 40.31% | 37.15% | 29.31% | 38.17% | 49.65% | 60.42% | 25.67% | 37.15% | 49.06% | 69.02% | 62.71% | 65.69% | 49.03% | 51.46% | 38.52% | 58.82% | 36.02% | 50.44% | 24.03% | 15.27% | 36.27% | 56.01% | 56.01% | 56.18% | 52.18% | 67.74% | 46.7% | 38.56% | 39.41% | 33.84% | 43.6% | 57.76% | 19.53% | 43.54% | 63.92% | 63.31% | 63.37% | 96.4% | 75.91% | 69.51% | 42.01% | 44.06% | 42.78% | 57.11% | 35.05% | 35.05%
|  | % of Month with Wind Between 25% and 50% | 29.91% | 43.23% | 33.41% | 26.15% | 14.01% | 3.09% | 9.677% | 24.33% | 3.264% | 30.81% | 16.63% | 31.49% | 22.1% | 44.83% | 26.75% | 38.66% | 19.62% | 38.27% | 20.9% | 20.26% | 21.91% | 20.9% | 20.2% | 42.36% | 50.44% | 30.5% | 35.18% | 26.11% | 19.78% | 19.69% | 17.88% | 9.792% | 13.84% | 29.74% | 29.9% | 23.36% | 19.83% | 39.35% | 23.73% | 25.03% | 35.42% | 27.96% | 23.85% | 24.63% | 23.99% | 30.11% | 29.6% | 30.83% | 29.73% | 32.5% | 25.94% | 28.25% | 34.41% | 37.31% | 24.39% | 27.29% | 29.84% | 14.41% | 13.31% | 28.6% | 29.72% | 30.84% | 25.52% | 33.87% | 27.41% | 14.75% | 20.76% | 25.84% | 23.44% | 20.4% | 22.57% | 19.46% | 25.2% | 23.44% | 28.52% | 18.96% | 22.98% | 22.21% | 25.57% | 21.12% | 23.35% | 26.77% | 27.08% | 19.79% | 27.79% | 14.72% | 25.76% | 23.89% | 23.68% | 27.89% | 23.97% | 21.47% | 27.6% | 21.23% | 24.62% | 16.16% | 23.68% | 2.688% | 12.47% | 17.08% | 26.11% | 26.04% | 22.28% | 20.03% | 29.07% | 29.07%
|  | % of Month with Wind Higher than 50% | 5.309% | 8.222% | 4.845% | 1.424% | 0.6384% | 0% | 1.142% | 1.915% | 0.1736% | 10.13% | 2.778% | 8.098% | 3.716% | 9.409% | 5.171% | 7.335% | 1.181% | 7.661% | 7.951% | 5.746% | 4.94% | 0.7986% | 5% | 9.757% | 14.42% | 6.644% | 11.09% | 14.01% | 5.182% | 2.535% | 4.973% | 0.2431% | 0.4032% | 4.94% | 10.52% | 4.228% | 3.681% | 16.1% | 6.475% | 13.34% | 18.23% | 12.95% | 13.54% | 10.45% | 21.11% | 9.677% | 8.233% | 23.06% | 32.01% | 12.08% | 21.4% | 16.32% | 35.28% | 20.39% | 25.24% | 17.6% | 9.644% | 8.576% | 7.997% | 15.49% | 29.97% | 32.01% | 45.17% | 27.96% | 22.94% | 24.83% | 53.57% | 37.01% | 27.5% | 10.58% | 14.72% | 14.85% | 25.77% | 25.1% | 32.95% | 22.22% | 40.99% | 27.35% | 50.4% | 63.61% | 40.38% | 17.22% | 16.9% | 24.03% | 20.03% | 17.54% | 27.53% | 37.55% | 36.91% | 38.27% | 32.43% | 20.77% | 52.86% | 35.23% | 11.46% | 20.53% | 12.95% | 0.9073% | 11.63% | 13.4% | 31.88% | 29.9% | 34.95% | 22.86% | 35.89% | 35.89%
Ireland | System Generation | Min (MW) | 1876.88 | 1984.8 | 1884.41 | 1673.7 | 1690.58 | 1543.37 | 1528.06 | 1539.03 | 1695 | 1763.09 | 1934.46 | 1753.34 | 1528.06 | 1993.91 | 2090.05 | 2123.88 | 2163.46 | 1784.97 | 1597.06 | 1915.47 | 2033.73 | 2104.16 | 2183.21 | 2308 | 1767.28 | 1597.06 | 1922.72 | 2357.49 | 2207.9 | 2367.47 | 1893.71 | 1872.13 | 2236.34 | 1956.55 | 2094.14 | 2118.98 | 2283.67 | 2072.27 | 1872.13 | 2666.25 | 2740.92 | 2416.84 | 2214.97 | 2033.65 | 2137.94 | 1860.09 | 2199.86 | 2076.57 | 2174.24 | 2288.14 | 1926.48 | 1860.09 | 2574.66 | 2777.48 | 2486.96 | 2238.95 | 2331.54 | 2231.32 | 1975.22 | 2068.2 | 1843.04 | 1707.35 | 2077.91 | 1663.46 | 1663.46 | 1639.57 | 2158.43 | 1828.19 | 2076.21 | 1949.05 | 1986.84 | 1673.57 | 1555.42 | 1576.19 | 1876.39 | 2125.11 | 1846.81 | 1555.42 | 2098.41 | 2330.42 | 1969.4 | 1496.57 | 1576.12 | 1736.43 | 1945.05 | 1841.63 | 1725.27 | 1700.97 | 1915.63 | 2273.51 | 1496.57 | 2436.82 | 2162.79 | 1993.47 | 2220.61 | 1892.48 | 2091.73 | 1703.35 | 1927.54 | 2176.79 | 1935.91 | 2028.47 | 2267.43 | 1703.35 | 2318.71 | 2318.71
|  | Avg (MW) | 2918.0395 | 2957.2249 | 2880.5528 | 2653.9353 | 2560.2081 | 2483.9114 | 2516.7957 | 2518.3397 | 2668.4316 | 2764.2612 | 2969.4941 | 3125.0865 | 2750.2806 | 3259.5883 | 3214.3108 | 3114.6381 | 2872.3318 | 2862.2981 | 2713.9796 | 2831.7325 | 2790.4362 | 2967.388 | 3026.4628 | 3263.5964 | 3294.465 | 3016.6689 | 3392.9611 | 3478.8805 | 3301.1799 | 3166.5775 | 2943.6763 | 2958.2294 | 3100.9007 | 3123.4979 | 3188.4947 | 3224.4849 | 3504.8355 | 3422.4196 | 3232.8174 | 3618.7834 | 3605.9972 | 3394.3955 | 3128.6461 | 2992.7977 | 3081.9401 | 3073.4553 | 3024.4675 | 3257.3757 | 3149.4414 | 3419.6263 | 3540.8495 | 3271.7952 | 3665.0244 | 3628.9386 | 3509.7231 | 3357.7923 | 3192.0006 | 3193.1058 | 3170.3063 | 3120.2187 | 3081.1397 | 3204.9556 | 3600.2013 | 3341.3681 | 3336.6473 | 3363.1309 | 3607.5081 | 3436.5854 | 3313.2935 | 3128.2787 | 3133.8506 | 2884.4336 | 2940.6325 | 3048.3453 | 3357.2692 | 3647.1624 | 3520.9657 | 3279.0593 | 3576.9654 | 3941.3285 | 3514.5749 | 2860.359 | 3047.3339 | 3157.4165 | 3218.2366 | 3214.8447 | 3328.7351 | 3451.6036 | 3640.6081 | 3824.9836 | 3396.7603 | 3766.2672 | 3801.6235 | 3419.7808 | 3189.1528 | 2981.7778 | 3037.9698 | 2770.8527 | 3091.6847 | 3219.1284 | 3417.587 | 3789.1268 | 4022.2551 | 3372.8303 | 3962.9993 | 3962.9993
|  | Max (MW) | 3911.19 | 4268.41 | 3948.54 | 3492.06 | 3472.91 | 3319.17 | 3273.48 | 3659.14 | 3696.92 | 3804.06 | 4166.31 | 4296.4 | 4296.4 | 4660.5 | 4235.54 | 4419.29 | 3659.96 | 3605.8 | 3483.09 | 3580.54 | 3628 | 3870.46 | 4051.79 | 4418.62 | 4341.18 | 4660.5 | 4487.4 | 4487.24 | 4328.27 | 4155.94 | 3750.05 | 3688.69 | 3998.51 | 4008.51 | 4212.48 | 4406.3 | 4887.63 | 4853.94 | 4887.63 | 4766.04 | 4714.66 | 4712.29 | 3910.75 | 3805.19 | 4061.25 | 4160.14 | 3867.04 | 4425.15 | 4375.87 | 4593.53 | 4772.37 | 4772.37 | 4815.25 | 4759.61 | 4698.69 | 4512.93 | 4080.41 | 4078.54 | 3912.63 | 4013.51 | 4174.85 | 4778.78 | 5326.44 | 5358.27 | 5358.27 | 5134.29 | 5147.02 | 5132.41 | 4851.8 | 4439.93 | 4216.99 | 4341.71 | 4333.97 | 4455.95 | 5074.18 | 5134.36 | 5267.27 | 5267.27 | 5151.9 | 5560.68 | 5293.26 | 4415.6 | 4306.09 | 4320.68 | 4393.61 | 4489.26 | 4577.52 | 5130.84 | 5344.58 | 5600.53 | 5600.53 | 5526.09 | 5773.39 | 5232.85 | 4446.08 | 4601.51 | 4533.7 | 4124.37 | 4618.93 | 4823.04 | 4978.56 | 5927.27 | 5965.7 | 5965.7 | 5866 | 5866
|  | Total (GWh) | 2171.0214 | 1987.2551 | 2140.2507 | 1910.8334 | 1904.7948 | 1788.4162 | 1872.496 | 1873.6447 | 1921.2707 | 2059.3746 | 2138.0357 | 2325.0644 | 24092.4579 | 2425.1337 | 2160.0168 | 2314.1761 | 2068.0789 | 2129.5498 | 1954.0653 | 2106.809 | 2076.0845 | 2136.5194 | 2254.7148 | 2349.7894 | 2451.082 | 26426.0199 | 2524.3631 | 2421.3009 | 2452.7767 | 2279.9358 | 2190.0951 | 2129.9252 | 2307.0701 | 2323.8825 | 2295.7162 | 2402.2412 | 2523.4816 | 2546.2802 | 28397.0685 | 2692.3749 | 2423.2301 | 2522.0358 | 2252.6252 | 2226.6415 | 2218.9968 | 2286.6507 | 2250.2038 | 2345.3105 | 2346.3339 | 2462.1309 | 2634.392 | 28660.9262 | 2726.7781 | 2438.6467 | 2607.7243 | 2417.6105 | 2374.8485 | 2299.0362 | 2358.7079 | 2321.4427 | 2218.4206 | 2387.6919 | 2592.1449 | 2485.9779 | 29229.0301 | 2502.1694 | 2424.2455 | 2553.3829 | 2385.5713 | 2327.4393 | 2256.3725 | 2146.0186 | 2187.8306 | 2194.8086 | 2501.1656 | 2625.9569 | 2619.5985 | 28724.5596 | 2661.2622 | 2743.1646 | 2611.3292 | 2059.4585 | 2267.2165 | 2273.3398 | 2394.368 | 2391.8445 | 2396.6893 | 2571.4447 | 2621.2378 | 2845.7878 | 29837.1428 | 2802.1028 | 2554.691 | 2540.8971 | 2296.19 | 2218.4427 | 2187.3383 | 2061.5144 | 2300.2134 | 2317.7725 | 2546.1023 | 2728.1713 | 2992.5578 | 29545.9936 | 2948.4715 | 2948.4715
| System Demand | Min (MW) | 2058.55 | 2209.78 | 2095.24 | 1859.09 | 1794.58 | 1722.73 | 1663.69 | 1694.29 | 1822.26 | 1889.47 | 1975.09 | 1957.71 | 1663.69 | 2109.77 | 2277.53 | 2182.08 | 2045.09 | 1910.89 | 1808.26 | 1758.84 | 1844.09 | 1948.22 | 1994.99 | 2057.93 | 1972.89 | 1758.84 | 2109.77 | 2319.56 | 2155.57 | 2132.67 | 1917.55 | 1878.19 | 1889.03 | 1895.05 | 1933.46 | 2002.59 | 2123.04 | 2117.65 | 1878.19 | 2166.33 | 2333.52 | 2258.4 | 2180.31 | 1948.93 | 1942.69 | 1935.35 | 1931.98 | 2060.11 | 1965.51 | 2278.43 | 2108.38 | 1931.98 | 2303.73 | 2536.27 | 2545.38 | 2230.64 | 2084.42 | 2066.33 | 2039.13 | 2072.63 | 2106.73 | 2217.93 | 2378.97 | 2137.57 | 2039.13 | 2336.4 | 2446.94 | 2436.23 | 2252.77 | 2155.51 | 2103.41 | 2088.35 | 2059.33 | 2120.17 | 2302.16 | 2486.21 | 2240.84 | 2059.33 | 2337.89 | 2621.24 | 2441.52 | 2162.61 | 2006.1 | 2033.57 | 2095.52 | 2123.49 | 2233.15 | 2383.52 | 2422.2 | 2333.59 | 2006.1 | 2582.39 | 2683.65 | 2622.87 | 2524.03 | 2360.35 | 2317.13 | 2353.45 | 2277.3 | 2393.76 | 2452.64 | 2599.85 | 2468.38 | 2277.3 | 2478.31 | 2478.31 | Differences: The data contained in this tab is indicative as it is based on raw 15-minute average SCADA readings which are produced in real time and have yet to be quality controlled. The data contained in the "Fuel Mix and CO2" tab however represents "metered data" which is more accurate than the real-time SCADA data and used for official purposes. This metered data will have been put through a quality control process and therefore may not be available until a few months after the event.
|  | Avg (MW) | 3226.1446 | 3247.282 | 3094.0429 | 2843.9994 | 2766.9746 | 2694.6679 | 2694.4508 | 2679.9139 | 2805.8437 | 2920.6497 | 3129.6939 | 3218.9842 | 2941.8597 | 3323.0879 | 3352.8142 | 3184.1145 | 2957.7475 | 2898.4485 | 2806.4485 | 2781.2369 | 2769.9424 | 2896.2105 | 3007.329 | 3220.299 | 3230.1973 | 3033.747 | 3328.052 | 3386.3306 | 3213.9232 | 3109.8192 | 2903.8072 | 2823.9496 | 2833.0419 | 2879.537 | 2940.703 | 3048.3796 | 3340.1425 | 3303.9006 | 3091.4344 | 3375.3821 | 3419.4111 | 3296.8341 | 3100.8677 | 2964.3698 | 2938.4635 | 2893.1212 | 2931.8397 | 3059.5125 | 3154.6353 | 3423.0688 | 3465.2215 | 3166.8999 | 3570.0812 | 3621.1535 | 3539.2871 | 3303.978 | 3096.4401 | 3025.2069 | 3017.0201 | 3029.4781 | 3125.3247 | 3291.2973 | 3536.7241 | 3458.0475 | 3299.0963 | 3569.8074 | 3558.1852 | 3467.7987 | 3339.57 | 3154.3064 | 3043.6769 | 3058.0745 | 3054.7962 | 3137.5835 | 3341.7186 | 3614.972 | 3517.6509 | 3319.9637 | 3632.6073 | 3746.0688 | 3529.1502 | 3011.867 | 2927.0468 | 3021.2052 | 3097.9185 | 3114.3334 | 3245.2533 | 3430.167 | 3589.0802 | 3734.9413 | 3339.0851 | 3751.3161 | 3770.2581 | 3614.0777 | 3450.6026 | 3359.763 | 3272.3102 | 3301.9808 | 3276.8848 | 3417.5943 | 3517.3579 | 3801.7336 | 3840.8473 | 3529.752 | 3873.023 | 3873.023
|  | Max (MW) | 4461.36 | 4448.27 | 4211.97 | 3786.21 | 3540.48 | 3494.45 | 3503.53 | 3630.56 | 3622.57 | 4090.95 | 4480.05 | 4613.27 | 4613.27 | 4703.96 | 4553.93 | 4387.07 | 3818.84 | 3675.31 | 3588.82 | 3591.11 | 3654.11 | 3754.42 | 4193.75 | 4545.27 | 4542.99 | 4703.96 | 4668.29 | 4592.17 | 4432.01 | 3959.82 | 3684.19 | 3592.61 | 3627.62 | 3726.52 | 3827.3 | 4202.46 | 4760.51 | 4712.58 | 4760.51 | 4663.35 | 4605.98 | 4516.33 | 3953.18 | 3729.63 | 3750.35 | 3718.72 | 3778.58 | 3991.64 | 4306.88 | 4776.03 | 4939.61 | 4939.61 | 4883.87 | 4811.56 | 4734.1 | 4243.09 | 3997.71 | 3819.22 | 3768.94 | 3831.74 | 4081.07 | 4633.85 | 4820.78 | 4913.69 | 4913.69 | 4904.49 | 4719.52 | 4621.62 | 4388.39 | 3981.13 | 3894.51 | 3894.65 | 3937.14 | 4049.47 | 4589.68 | 4943.11 | 5014.05 | 5014.05 | 4943.69 | 5026.57 | 4744.7 | 3879.04 | 3691.42 | 4219.24 | 4026.26 | 4046.62 | 4155.32 | 4769.61 | 4947.98 | 5348.48 | 5348.48 | 5231.53 | 5325.45 | 4795.04 | 4314.81 | 4285.72 | 4142.28 | 4134.39 | 4081.63 | 4320.3 | 4616.54 | 5192.85 | 5366.84 | 5366.84 | 5250.75 | 5250.75
|  | Total (GWh) | 2400.2516 | 2182.1735 | 2298.8739 | 2047.6796 | 2058.6291 | 1940.1609 | 2004.6714 | 1993.8559 | 2020.2075 | 2175.884 | 2253.3796 | 2394.9242 | 25770.6911 | 2472.3774 | 2253.0912 | 2365.7971 | 2129.5782 | 2156.4457 | 2020.6429 | 2069.2403 | 2060.8371 | 2085.2715 | 2240.4601 | 2318.6153 | 2403.2668 | 26575.6235 | 2476.0707 | 2356.8861 | 2387.945 | 2239.0698 | 2160.4325 | 2033.2437 | 2107.7832 | 2142.3755 | 2117.3062 | 2271.0428 | 2404.9026 | 2458.1021 | 27155.1602 | 2511.2842 | 2297.8443 | 2449.5477 | 2232.6248 | 2205.4911 | 2115.6937 | 2152.4821 | 2181.2887 | 2202.849 | 2350.2033 | 2464.6095 | 2578.1248 | 27742.0433 | 2656.1404 | 2433.4151 | 2629.6903 | 2378.8642 | 2303.7514 | 2178.1489 | 2244.663 | 2253.9317 | 2250.2338 | 2452.0165 | 2546.4413 | 2572.7873 | 28900.084 | 2655.9367 | 2391.1005 | 2576.5744 | 2404.4904 | 2346.804 | 2191.4474 | 2275.2074 | 2272.7684 | 2259.0601 | 2489.5804 | 2602.7798 | 2617.1322 | 29082.8817 | 2702.6599 | 2607.2639 | 2622.1586 | 2168.5443 | 2177.7228 | 2175.2678 | 2304.8514 | 2317.064 | 2336.5823 | 2555.4744 | 2584.1378 | 2778.7963 | 29330.5234 | 2790.9792 | 2533.6135 | 2685.2597 | 2484.4339 | 2499.6636 | 2356.0634 | 2456.6737 | 2438.0023 | 2460.6679 | 2620.4316 | 2737.2482 | 2857.5904 | 30920.6273 | 2881.5291 | 2881.5291
| Wind Generation | Min (MW) | 53.73 | 96.64 | 1.67 | 7.05 | 3.43 | 6.63 | 7.81 | 6.94 | 2.07 | 0 | 10.23 | 22.94 | 0 | 16.02 | 3.62 | 2.7 | 5.22 | 14.39 | 5.87 | 3.15 | 1.47 | 0.55 | 0.64 | 10.82 | 19.73 | 0.55 | 17.8 | 0 | 9.79 | 2.98 | 0 | 0.07 | 5.63 | 0 | 10.83 | 0 | 9.17 | 42.22 | 0 | 13.87 | 51.77 | 20.49 | 1.33 | 1.81 | 8.62 | 0 | 6.54 | 2.71 | 9.49 | 0 | 48.14 | 0 | 25.68 | 47.59 | 0 | 0 | 0 | 0 | 0 | 0 | 32.82 | 18.66 | 57.41 | 74.47 | 0 | 21.23 | 56.12 | 30.48 | 9.31 | 4.47 | 10.51 | 1.11 | 0.37 | 0 | 14.09 | 4.95 | 12.45 | 0 | 16.82 | 86.37 | 40.52 | 0 | 3.52 | 1.86 | 8.76 | 0 | 0 | 28.17 | 17.43 | 4.66 | 0 | 66.01 | 43.16 | 17.94 | 9.43 | 0 | 10.91 | 0 | 0 | 15.32 | 36.93 | 31.27 | 107.1 | 0 | 17.48 | 17.48
|  | Avg (MW) | 774.6899 | 925.4199 | 647.4185 | 493.9 | 461.0184 | 272.9953 | 306.1386 | 536.5834 | 249.1044 | 751.9599 | 584.6423 | 936.0032 | 577.4344 | 1062.7635 | 726.1736 | 807.6646 | 527.0047 | 788.5261 | 547.7528 | 655.5449 | 501.3057 | 526.4248 | 512.2648 | 1047.7038 | 1238.2191 | 746.1427 | 1050.5942 | 919.494 | 681.3988 | 630.2303 | 470.8869 | 418.585 | 469.8594 | 670.1821 | 743.6255 | 604.6314 | 695.659 | 931.7018 | 690.0601 | 881.6435 | 1218.5214 | 1002.0956 | 601.6436 | 597.5489 | 796.3655 | 545.8002 | 594.1574 | 825.0392 | 962.5715 | 829.8224 | 1076.2694 | 825.1117 | 1515.3306 | 1241.2026 | 1036.1121 | 1000.5533 | 684.4915 | 458.5368 | 459.9824 | 756.0488 | 922.5438 | 1020.7364 | 1473.1929 | 1347.2454 | 991.2773 | 1033.4358 | 1670.8572 | 1258.8091 | 1060.7691 | 704.7397 | 814.5363 | 633.1362 | 1024.7821 | 1027.0575 | 1203.4079 | 1171.5428 | 1454.2437 | 1084.0768 | 1502.1584 | 2110.0869 | 1514.971 | 755.4952 | 977.336 | 960.8001 | 967.171 | 798.9693 | 994.7049 | 1495.9281 | 1436.9323 | 1634.9536 | 1260.2891 | 1241.5327 | 1971.5923 | 1270.7467 | 879.8317 | 973.3057 | 804.1629 | 394.3308 | 715.9652 | 706.7048 | 1243.6373 | 1264.8991 | 1619.8639 | 1085.2391 | 1301.4202 | 1301.4202
|  | Max (MW) | 1624.31 | 1718 | 1680.19 | 1431.03 | 1417.06 | 1360.38 | 1250.3 | 1676.96 | 1048.02 | 1783.69 | 1645.71 | 1825.51 | 1825.51 | 1966.87 | 1969.05 | 1939.81 | 1775.9 | 1811.53 | 1805.49 | 1752.06 | 1785.37 | 1488.79 | 1856.61 | 2034.83 | 2036.77 | 2036.77 | 2131.91 | 2087.7 | 2028.75 | 1900.95 | 1858.08 | 1632.38 | 1665.56 | 1859.6 | 2094.23 | 1871.43 | 2038.76 | 2230.84 | 2230.84 | 2408.02 | 2410.07 | 2449.1 | 2118.55 | 2219.33 | 2059.9 | 1888.94 | 1938.93 | 2297.05 | 2276.46 | 2289.29 | 2615.61 | 2615.61 | 2811.21 | 2807.96 | 2912.88 | 2946.1 | 2390.67 | 2273.42 | 2239.81 | 2288.28 | 2529.51 | 2689.23 | 2878.93 | 3051.98 | 3051.98 | 2914.53 | 2952.49 | 2851.86 | 2919.63 | 2162.64 | 2292.21 | 2470.3 | 2402.93 | 2434.58 | 2764.16 | 2774.81 | 3135.76 | 3135.76 | 3191.34 | 3329.81 | 3199.86 | 2740.79 | 2764.51 | 2659.24 | 2500.47 | 2851.68 | 2582.14 | 2875.04 | 3188.39 | 3358.57 | 3358.57 | 3198.95 | 3571.3 | 3215.94 | 2467.73 | 3050.15 | 2444.05 | 2255.52 | 2718.86 | 2689.55 | 3251.15 | 3536.8 | 3484.12 | 3571.3 | 3466.27 | 3466.27
|  | Total (GWh) | 576.3693 | 621.8822 | 481.0319 | 355.608 | 342.9977 | 196.5566 | 227.7671 | 399.2181 | 179.3552 | 560.2101 | 420.9425 | 696.3864 | 5058.325 | 790.6961 | 487.9887 | 600.0948 | 379.4434 | 586.6634 | 394.382 | 487.7254 | 372.9715 | 379.0259 | 381.6373 | 754.3467 | 921.235 | 6536.21 | 781.6421 | 639.9678 | 506.2793 | 453.7658 | 350.3399 | 301.3812 | 349.5754 | 498.6155 | 535.4104 | 450.4504 | 500.8745 | 693.1862 | 6061.4883 | 655.9427 | 818.8464 | 744.557 | 433.1834 | 444.5763 | 573.3832 | 406.0754 | 442.0531 | 594.0282 | 717.1158 | 597.4721 | 800.7445 | 7227.9782 | 1127.406 | 834.0881 | 769.8313 | 720.3984 | 509.2617 | 330.1465 | 342.2269 | 562.5003 | 664.2315 | 760.4486 | 1060.6989 | 1002.3506 | 8683.5889 | 768.8763 | 1122.816 | 935.2951 | 763.7537 | 524.3263 | 586.4661 | 471.0533 | 762.4378 | 739.4814 | 896.5389 | 843.5108 | 1081.9573 | 9496.5132 | 1117.6058 | 1468.6205 | 1125.6234 | 543.9566 | 727.138 | 691.7761 | 719.5752 | 594.4332 | 716.1876 | 1114.4664 | 1034.5913 | 1216.4055 | 11070.3795 | 923.7003 | 1324.91 | 944.1648 | 633.4788 | 724.1394 | 578.9973 | 293.3821 | 532.6781 | 508.8275 | 926.5098 | 910.7274 | 1205.1787 | 9506.6942 | 968.2567 | 968.2567
| Wind Penetration (% of Demand) | Min (%) | 1.441% | 2.609% | 0.04619% | 0.2488% | 0.1062% | 0.2017% | 0.2522% | 0.2146% | 0.06349% | 0% | 0.2899% | 0.5214% | 0% | 0.5716% | 0.1376% | 0.07432% | 0.1511% | 0.4685% | 0.1782% | 0.097% | 0.04312% | 0.01632% | 0.02032% | 0.3977% | 0.5324% | 0.01632% | 0.6568% | 0% | 0.3532% | 0.1225% | 0% | 0.002076% | 0.1882% | 0% | 0.3706% | 0% | 0.2526% | 0.9305% | 0% | 0.3516% | 1.707% | 0.5479% | 0.0513% | 0.0517% | 0.2582% | 0% | 0.2844% | 0.07982% | 0.2517% | 0% | 1.248% | 0% | 0.6281% | 1.322% | 0% | 0% | 0% | 0% | 0% | 0% | 0.9633% | 0.5749% | 2.061% | 2.475% | 0% | 0.6305% | 1.346% | 0.8672% | 0.2758% | 0.1202% | 0.3712% | 0.04069% | 0.01078% | 0% | 0.3775% | 0.1613% | 0.3248% | 0% | 0.3517% | 2.124% | 0.9724% | 0% | 0.1047% | 0.06198% | 0.2603% | 0% | 0% | 0.7921% | 0.4898% | 0.1156% | 0% | 1.774% | 1.342% | 0.6197% | 0.2271% | 0% | 0.3316% | 0% | 0% | 0.3782% | 1.01% | 0.9457% | 2.228% | 0% | 0.4767% | 0.4767%
|  | Avg (%) | 24.01% | 28.5% | 20.92% | 17.37% | 16.66% | 10.13% | 11.36% | 20.02% | 8.878% | 25.75% | 18.68% | 29.08% | 19.63% | 31.98% | 21.66% | 25.37% | 17.82% | 27.21% | 19.52% | 23.57% | 18.1% | 18.18% | 17.03% | 32.53% | 38.33% | 24.59% | 31.57% | 27.15% | 21.2% | 20.27% | 16.22% | 14.82% | 16.58% | 23.27% | 25.29% | 19.83% | 20.83% | 28.2% | 22.32% | 26.12% | 35.64% | 30.4% | 19.4% | 20.16% | 27.1% | 18.87% | 20.27% | 26.97% | 30.51% | 24.24% | 31.06% | 26.05% | 42.45% | 34.28% | 29.27% | 30.28% | 22.11% | 15.16% | 15.25% | 24.96% | 29.52% | 31.01% | 41.65% | 38.96% | 30.05% | 28.95% | 46.96% | 36.3% | 31.76% | 22.34% | 26.76% | 20.7% | 33.55% | 32.73% | 36.01% | 32.41% | 41.34% | 32.65% | 41.35% | 56.33% | 42.93% | 25.08% | 33.39% | 31.8% | 31.22% | 25.65% | 30.65% | 43.61% | 40.04% | 43.77% | 37.74% | 33.1% | 52.29% | 35.16% | 25.5% | 28.97% | 24.57% | 11.94% | 21.85% | 20.68% | 35.36% | 33.27% | 42.17% | 30.75% | 33.6% | 33.6%
|  | Max (%) | 62.1% | 65.71% | 64.72% | 62.13% | 64.71% | 50.46% | 57.08% | 65.36% | 47.08% | 68.21% | 67.59% | 70.49% | 70.49% | 69.2% | 67.9% | 69.2% | 69.32% | 72.72% | 68.85% | 71.6% | 68.88% | 55.54% | 73.01% | 74.74% | 71.77% | 74.74% | 70.72% | 75.78% | 70.4% | 68.92% | 68.83% | 55.5% | 59.64% | 73.08% | 69.89% | 67.9% | 67.38% | 77.93% | 77.93% | 80.39% | 82.13% | 68.61% | 76.19% | 71.74% | 79.77% | 68.97% | 62.53% | 76.93% | 72.21% | 72.22% | 79.44% | 82.13% | 84% | 82.21% | 79.3% | 85.94% | 70.08% | 78.2% | 73.81% | 80.6% | 82.75% | 80.61% | 82.09% | 86.55% | 86.55% | 79.33% | 87.78% | 88.04% | 82.19% | 72.23% | 82.21% | 83.96% | 78.71% | 93.03% | 88.87% | 85.36% | 87.54% | 93.03% | 82.8% | 85.43% | 82.37% | 84.13% | 96.26% | 92.19% | 85.96% | 85.22% | 81.97% | 87.72% | 81.71% | 93.85% | 96.26% | 89.94% | 93.26% | 90.83% | 78.68% | 89.2% | 72.04% | 61.19% | 84.51% | 84.5% | 93.36% | 92.79% | 93.86% | 93.86% | 93.24% | 93.24%
| Wind Penetration (% of Demand) | % of Month with Wind Less than 25% | 52.18% | 37.54% | 61.37% | 72.81% | 71.81% | 89.58% | 89.18% | 66.2% | 95.49% | 49.8% | 68.06% | 39.82% | 66.22% | 35.18% | 61.87% | 51.75% | 70.24% | 46.94% | 68.61% | 52.89% | 72.41% | 68.54% | 70.44% | 36.35% | 19.66% | 54.45% | 40.99% | 51.47% | 68.37% | 71.15% | 75.87% | 81.25% | 78.29% | 56.79% | 53.4% | 64.56% | 62.99% | 46.1% | 62.61% | 56.12% | 36.2% | 37.82% | 70.17% | 66.53% | 55.76% | 67.1% | 67.61% | 49.06% | 39.53% | 54.51% | 44.22% | 53.82% | 25.6% | 37.35% | 50.87% | 52.29% | 60.89% | 77.57% | 80.81% | 58.67% | 47.01% | 44.97% | 25.69% | 32.22% | 49.58% | 48.99% | 20.16% | 39.6% | 46.08% | 62.16% | 53.68% | 70.97% | 38.14% | 37.12% | 36.38% | 41.88% | 30.14% | 43.96% | 27.35% | 11.57% | 26.18% | 57.95% | 44.02% | 52.47% | 40.99% | 60.28% | 41.91% | 21.48% | 32.92% | 26.48% | 37% | 43.75% | 16.74% | 49.97% | 51.08% | 58.5% | 57.12% | 86.32% | 66.5% | 68.72% | 41.21% | 41.39% | 21.91% | 50.49% | 46.03% | 46.03%
|  | % of Month with Wind Between 25% and 50% | 39.35% | 54.17% | 34.52% | 25.24% | 25.07% | 10.35% | 10.32% | 32.12% | 4.514% | 36.21% | 28.54% | 46.24% | 28.81% | 46.88% | 30.39% | 35.43% | 27.78% | 42.74% | 24.13% | 41.43% | 21.34% | 30.24% | 22.72% | 41.63% | 52.99% | 34.89% | 35.08% | 27.33% | 21.5% | 21.88% | 19.56% | 17.95% | 18.51% | 32.06% | 34.76% | 29.43% | 32.36% | 37.43% | 27.33% | 25.5% | 32.96% | 45.42% | 19.9% | 21.98% | 25.56% | 29.27% | 28.39% | 33.61% | 39.7% | 33.3% | 32.73% | 30.7% | 29.13% | 34.38% | 25.03% | 18.37% | 29.13% | 14.06% | 13.44% | 26.85% | 33.37% | 34.13% | 31.39% | 31.01% | 26.66% | 29.3% | 23.81% | 28.2% | 29.17% | 23.69% | 29.48% | 16.57% | 34.81% | 39.34% | 30.17% | 32.29% | 25.84% | 28.55% | 27.52% | 14.55% | 27.22% | 28.06% | 25.74% | 15.9% | 40.12% | 16.13% | 39.2% | 32.32% | 23.54% | 27.45% | 26.54% | 30.88% | 24.78% | 12.55% | 36.94% | 15.56% | 33.23% | 12.63% | 16.13% | 21.88% | 24.87% | 36.15% | 39.21% | 25.33% | 21.77% | 21.77%
|  | % of Month with Wind Higher than 50% | 8.468% | 8.296% | 4.105% | 1.944% | 3.125% | 0.06944% | 0.504% | 1.68% | 0% | 13.99% | 3.403% | 13.94% | 4.974% | 17.94% | 7.738% | 12.82% | 1.979% | 10.32% | 7.257% | 5.679% | 6.25% | 1.215% | 6.846% | 22.01% | 27.35% | 10.67% | 23.92% | 21.19% | 10.13% | 6.979% | 4.57% | 0.7986% | 3.192% | 11.16% | 11.84% | 6.007% | 4.653% | 16.47% | 10.06% | 18.38% | 30.84% | 16.76% | 9.931% | 11.49% | 18.68% | 3.629% | 3.999% | 17.33% | 20.77% | 12.19% | 23.05% | 15.47% | 45.26% | 28.27% | 24.09% | 29.34% | 9.98% | 8.368% | 5.746% | 14.48% | 19.62% | 20.91% | 42.92% | 36.76% | 23.76% | 21.71% | 56.03% | 32.2% | 24.76% | 14.15% | 16.84% | 12.47% | 27.05% | 23.54% | 33.46% | 25.83% | 44.02% | 27.49% | 45.13% | 73.89% | 46.6% | 13.99% | 30.24% | 31.63% | 18.88% | 23.59% | 18.89% | 46.21% | 43.54% | 46.07% | 36.46% | 25.37% | 58.48% | 37.48% | 11.98% | 25.94% | 9.653% | 1.042% | 17.37% | 9.41% | 33.93% | 22.47% | 38.88% | 24.17% | 32.19% | 32.19%
All Island | System Generation | Min (MW) | 2429.31 | 2655.21 | 2518.13 | 2269.06 | 2205.67 | 2143.77 | 2062.78 | 2144.23 | 2159.1 | 2337.79 | 2495.99 | 2314.49 | 2062.78 | 2603.92 | 2887.64 | 2692.25 | 2697.45 | 2454.01 | 2160.9 | 2508.61 | 2765.21 | 2704.18 | 2926.78 | 3067.14 | 2342.99 | 2160.9 | 2674.46 | 3077.01 | 2797.87 | 3110.08 | 2572.62 | 2518.11 | 2784.034 | 2540.061 | 2663.104 | 2572.349 | 2946.335 | 2915.276 | 2518.11 | 3278.237 | 3594.143 | 3099.374 | 3075.02 | 2777.216 | 2750.936 | 2680.272 | 2831.388 | 2780.005 | 2900.078 | 3285.339 | 2345.083 | 2345.083 | 3286.303 | 3451.192 | 3363.668 | 3070.181 | 3004.2 | 2923.426 | 2592.829 | 2737.994 | 2336.561 | 2262.693 | 2422.043 | 2042.472 | 2042.472 | 2113.724 | 2636.105 | 2348.946 | 2622.789 | 2276.77 | 2650.555 | 2146.463 | 1930.969 | 1943.136 | 2221.571 | 2456.922 | 2383.913 | 1930.969 | 2535.781 | 2930.993 | 2445.612 | 1891.851 | 1961.465 | 2204.15 | 2260.625 | 2454.037 | 2169.361 | 2225.874 | 2419.323 | 2789.773 | 1891.851 | 2947.812 | 2492.482 | 2553.632 | 2789.014 | 2340.438 | 2600.395 | 2110.86 | 2427.268 | 2661.029 | 2423.185 | 2487.48 | 2890.228 | 2110.86 | 2873.782 | 2873.782
|  | Avg (MW) | 3863.9666 | 3941.9725 | 3709.896 | 3413.6984 | 3358.751 | 3196.1234 | 3292.7434 | 3348.9821 | 3388.7114 | 3621.2708 | 3852.3071 | 4046.1417 | 3584.633 | 4248.5948 | 4176.1801 | 4027.3088 | 3711.84 | 3708.7781 | 3546.4422 | 3641.7466 | 3674.0409 | 3849.6989 | 3953.3045 | 4241.5167 | 4302.77 | 3922.3774 | 4437.9172 | 4512.6344 | 4222.4356 | 4130.2485 | 3817.6677 | 3771.6882 | 3870.6039 | 3930.3523 | 4008.3892 | 4097.2117 | 4553.9806 | 4434.8546 | 4147.3571 | 4605.5096 | 4606.3444 | 4334.4045 | 4054.1507 | 3915.6359 | 3995.6054 | 4009.9121 | 3963.2085 | 4185.6808 | 4078.436 | 4380.4331 | 4473.6943 | 4214.3778 | 4701.7412 | 4649.8811 | 4493.8673 | 4162.5312 | 4004.2058 | 3908.3657 | 3893.5174 | 3921.8457 | 3859.4556 | 4055.5398 | 4607.0483 | 4221.385 | 4203.714 | 4287.1708 | 4580.2826 | 4352.4245 | 4196.8951 | 3929.1764 | 3946.5975 | 3555.8653 | 3665.0784 | 3817.1752 | 4249.7891 | 4572.7459 | 4447.9812 | 4129.7482 | 4533.5407 | 4941.1252 | 4416.9253 | 3534.7703 | 3841.6099 | 3966.9317 | 4083.7951 | 3996.879 | 4206.6957 | 4312.3906 | 4563.0411 | 4853.2276 | 4269.4559 | 4780.8034 | 4842.0249 | 4294.0542 | 3962.0811 | 3771.0631 | 3834.7678 | 3478.6239 | 3871.9616 | 4077.2637 | 4245.0922 | 4708.0345 | 5080.7143 | 4241.7281 | 5018.6024 | 5018.6024
|  | Max (MW) | 5339.84 | 5451.45 | 5020.11 | 4688.11 | 4269.52 | 4091.84 | 4321.66 | 4823.81 | 4682.34 | 4966.11 | 5429.75 | 5620.22 | 5620.22 | 5899.03 | 5556.08 | 5447.76 | 4771.56 | 4647.28 | 4754.54 | 4668.3 | 4729.77 | 4946.62 | 5266.53 | 5885.82 | 5741.74 | 5899.03 | 5970.76 | 5771.6 | 5499.19 | 5237.53 | 5061.18 | 4816.03 | 4981.373 | 5046.842 | 5346.076 | 5468.65 | 6437.489 | 6459.258 | 6459.258 | 6067.254 | 5993.736 | 6027.434 | 5090.612 | 5085.903 | 5333.904 | 5317.277 | 5229.469 | 5697.171 | 5868.736 | 5874.289 | 5978.773 | 6067.254 | 6131.42 | 5931.501 | 5949.151 | 5655.863 | 5124.359 | 5101.212 | 4822.964 | 5086.621 | 5312.604 | 6011.583 | 6767.015 | 6869.911 | 6869.911 | 6552.155 | 6608.828 | 6467.476 | 6143.368 | 5617.969 | 5313.56 | 5413.431 | 5414.181 | 5792.482 | 6549.772 | 6640.753 | 6800.366 | 6800.366 | 6429.741 | 6995.586 | 6623.544 | 5449.501 | 5501.843 | 5509.53 | 5654.171 | 5606.047 | 5937.293 | 6594.659 | 6860.047 | 7413.628 | 7413.628 | 7153.403 | 7454.927 | 6694.601 | 5652.433 | 5762.17 | 5722.334 | 5040.484 | 5686.436 | 6145.672 | 6234.12 | 7342.406 | 7472.246 | 7472.246 | 7330.381 | 7330.381
|  | Total (GWh) | 2874.7912 | 2649.0056 | 2756.4527 | 2457.8629 | 2498.9107 | 2301.2089 | 2449.8011 | 2491.6427 | 2439.8722 | 2697.8468 | 2773.6611 | 3010.3294 | 31401.3852 | 3160.9546 | 2806.393 | 2992.2904 | 2672.5248 | 2759.3309 | 2553.4384 | 2709.4595 | 2733.4864 | 2771.7832 | 2945.2119 | 3053.892 | 3201.2609 | 34360.0259 | 3301.8104 | 3140.7936 | 3137.2697 | 2973.7789 | 2840.3448 | 2715.6155 | 2879.7293 | 2924.1821 | 2886.0402 | 3052.4228 | 3278.866 | 3299.5318 | 36430.3851 | 3426.4991 | 3095.4634 | 3220.4626 | 2918.9885 | 2913.2331 | 2876.8359 | 2983.3746 | 2948.6272 | 3013.6901 | 3038.4348 | 3153.9118 | 3328.4285 | 36917.9497 | 3498.0954 | 3124.7201 | 3338.9434 | 2997.0225 | 2979.1291 | 2814.0233 | 2896.777 | 2917.8532 | 2778.808 | 3021.3771 | 3317.0748 | 3140.7104 | 36824.5343 | 3189.6551 | 3077.9499 | 3233.8514 | 3021.7644 | 2923.3073 | 2841.5502 | 2645.5638 | 2726.8184 | 2748.3661 | 3166.0929 | 3292.3771 | 3309.298 | 36176.5946 | 3372.9543 | 3439.0231 | 3281.7755 | 2545.0346 | 2858.1578 | 2856.1908 | 3038.3436 | 2973.678 | 3028.8209 | 3212.731 | 3285.3896 | 3610.8013 | 37502.9005 | 3556.9177 | 3253.8407 | 3190.4823 | 2852.6984 | 2805.6709 | 2761.0328 | 2588.0962 | 2880.7394 | 2935.6299 | 3162.5937 | 3389.7848 | 3780.0515 | 37157.5384 | 3733.8402 | 3733.8402
| System Demand | Min (MW) | 2714.56 | 2896.71 | 2746.83 | 2429.67 | 2339.34 | 2234.74 | 2176.18 | 2228.35 | 2386.69 | 2458.62 | 2572.4 | 2578.68 | 2176.18 | 2701.58 | 2955.61 | 2825.88 | 2638.32 | 2456.68 | 2318.45 | 2263.44 | 2370.04 | 2493.96 | 2569.77 | 2640.21 | 2567.02 | 2263.44 | 2688.32 | 2955.91 | 2742.73 | 2728.7 | 2427.82 | 2369.56 | 2403.634 | 2403.211 | 2478.808 | 2577.142 | 2763.526 | 2671.16 | 2369.56 | 2746.909 | 2958.405 | 2813.349 | 2674.287 | 2457.262 | 2438.741 | 2424.306 | 2438.899 | 2582.331 | 2462.893 | 2838.052 | 2657.416 | 2424.306 | 2908.873 | 3203.658 | 3161.981 | 2791.787 | 2520.253 | 2569.548 | 2528.781 | 2597.637 | 2655.929 | 2798.149 | 2941.735 | 2677.095 | 2520.253 | 2893.284 | 3021.73 | 3037.921 | 2757.589 | 2641.042 | 2548.084 | 2563.409 | 2561.698 | 2641.467 | 2749.15 | 3083.909 | 2691.601 | 2548.084 | 2846.823 | 3133.334 | 2974.546 | 2648.809 | 2444.046 | 2405.211 | 2553.964 | 2606.814 | 2741.741 | 2878.892 | 2951.059 | 2838.369 | 2405.211 | 3165.863 | 3257.213 | 3139.187 | 3024.035 | 2870.697 | 2816.951 | 2863.092 | 2775.218 | 2940.28 | 2960.718 | 3066.03 | 2935.233 | 2775.218 | 2947.051 | 2947.051
|  | Avg (MW) | 4340.9359 | 4350.9814 | 4134.2713 | 3792.2656 | 3695.6859 | 3583.0638 | 3553.4836 | 3559.0594 | 3726.7541 | 3891.902 | 4168.2746 | 4298.1928 | 3922.2126 | 4446.5285 | 4467.0505 | 4229.8886 | 3900.5708 | 3820.1826 | 3694.8422 | 3628.2915 | 3625.4662 | 3805.5217 | 3966.9944 | 4252.0727 | 4278.2933 | 4006.9087 | 4395.828 | 4452.0669 | 4190.3776 | 4044.7572 | 3756.0283 | 3664.913 | 3660.1661 | 3734.8588 | 3837.8366 | 3999.6616 | 4397.1759 | 4342.3037 | 4037.9738 | 4434.2447 | 4473.1248 | 4275.1926 | 3979.0176 | 3815.5133 | 3786.6934 | 3696.2748 | 3784.4833 | 3943.0467 | 4059.1607 | 4430.4407 | 4478.21 | 4093.8354 | 4624.9056 | 4674.4243 | 4558.9841 | 4209.1962 | 3949.7161 | 3850.5067 | 3812.5129 | 3863.3458 | 3983.7653 | 4219.657 | 4529.2476 | 4443.1009 | 4223.8085 | 4597.1202 | 4542.3488 | 4415.8261 | 4225.6116 | 4016.9352 | 3865.2351 | 3847.2749 | 3854.5619 | 3979.9797 | 4255.5865 | 4607.5374 | 4471.843 | 4221.2701 | 4607.7399 | 4705.6969 | 4437.1939 | 3751.0761 | 3662.0404 | 3782.5868 | 3875.4031 | 3912.7242 | 4083.0639 | 4302.5158 | 4520.1469 | 4694.0481 | 4193.4629 | 4728.7604 | 4696.3119 | 4503.9816 | 4293.4116 | 4188.9922 | 4082.8861 | 4112.2201 | 4100.083 | 4276.3833 | 4387.27 | 4734.6417 | 4790.5474 | 4406.244 | 4835.1312 | 4835.1312
|  | Max (MW) | 6114.3 | 6056.82 | 5716.98 | 5140.14 | 4791.18 | 4731.38 | 4606.35 | 4826.88 | 4838.52 | 5558.21 | 6101.03 | 6269.63 | 6269.63 | 6396.95 | 6202.05 | 5852.25 | 5192.87 | 4905.48 | 4725.12 | 4776.51 | 4790.77 | 4982.09 | 5622.94 | 6178.06 | 6132.2 | 6396.95 | 6310.06 | 6113.1 | 5880.88 | 5236.07 | 4881 | 4719.57 | 4784.241 | 4896.487 | 5043.613 | 5598.362 | 6375.021 | 6309.102 | 6375.021 | 6268.202 | 6125.811 | 6009.394 | 5147.22 | 4901.995 | 4901.676 | 4860.113 | 5008.675 | 5224.987 | 5614.012 | 6372.992 | 6531.683 | 6531.683 | 6471.886 | 6393.744 | 6219.884 | 5502.181 | 5210.481 | 4995.172 | 4880.954 | 4981.147 | 5269.662 | 6090.057 | 6310.804 | 6504.008 | 6504.008 | 6475.681 | 6210.23 | 5982.078 | 5640.418 | 5182.261 | 5085.657 | 4905.159 | 5033.292 | 5308.394 | 5985.817 | 6428.404 | 6547.514 | 6547.514 | 6422.621 | 6450.315 | 6097.798 | 4996.055 | 4774.075 | 5122.546 | 5179.744 | 5184.441 | 5361.997 | 6107.225 | 6422.885 | 6894.431 | 6894.431 | 6785.877 | 6715.426 | 6108.579 | 5501.978 | 5431.592 | 5286.619 | 5280.667 | 5198.741 | 5473.128 | 5855.312 | 6630.084 | 6804.378 | 6804.378 | 6762.899 | 6762.899
|  | Total (GWh) | 3229.6563 | 2923.8595 | 3071.7636 | 2730.4312 | 2749.5903 | 2579.8059 | 2643.7918 | 2647.9402 | 2683.263 | 2899.467 | 3001.1577 | 3197.8555 | 34358.582 | 3308.2172 | 3001.8579 | 3142.8072 | 2808.411 | 2842.2159 | 2660.2864 | 2699.4489 | 2697.3469 | 2739.9756 | 2955.4109 | 3061.4923 | 3183.0502 | 35100.5203 | 3270.496 | 3098.6386 | 3113.4505 | 2912.2252 | 2794.485 | 2638.7373 | 2723.1636 | 2778.735 | 2763.2424 | 2979.7479 | 3165.9667 | 3230.674 | 35469.5621 | 3299.0781 | 3005.9399 | 3176.4681 | 2864.8927 | 2838.7419 | 2726.4193 | 2750.0285 | 2815.6556 | 2838.9936 | 3024.0747 | 3189.9173 | 3331.7883 | 35861.9978 | 3440.9298 | 3141.2131 | 3387.3252 | 3030.6213 | 2938.5888 | 2772.3648 | 2836.5096 | 2874.3293 | 2868.311 | 3143.6445 | 3261.0582 | 3305.6671 | 37000.5626 | 3420.2575 | 3052.4584 | 3280.9588 | 3042.4403 | 2988.5998 | 2782.9693 | 2862.3725 | 2867.7941 | 2865.5854 | 3170.412 | 3317.4269 | 3327.0512 | 36978.326 | 3428.1585 | 3275.1651 | 3296.8351 | 2700.7748 | 2724.5581 | 2723.4625 | 2883.2999 | 2911.0668 | 2939.806 | 3205.3742 | 3254.5058 | 3492.3718 | 36835.3785 | 3518.1977 | 3155.9216 | 3346.4584 | 3091.2563 | 3116.6102 | 2939.678 | 3059.4918 | 3050.4618 | 3078.996 | 3268.5161 | 3408.942 | 3564.1673 | 38598.6972 | 3597.3376 | 3597.3376
| Wind Generation | Min (MW) | 66.7 | 149.89 | 2.92 | 7.74 | 3.45 | 9.31 | 14.85 | 14.42 | 2.31 | 0.86 | 10.58 | 24.02 | 0.86 | 22.09 | 7.18 | 2.96 | 12.61 | 28.27 | 7.76 | 4.47 | 1.93 | 0.55 | 1.58 | 12.03 | 21.76 | 0.55 | 28.62 | 0.38 | 12.11 | 4.52 | 0 | 3.23 | 8.247 | 3.081 | 18.319 | 0 | 14.613 | 51.444 | 0 | 28.076 | 57.575 | 29.232 | 1.33 | 2.056 | 11.65 | 0.698 | 12.387 | 4.52 | 17.756 | 0 | 74.608 | 0 | 28.816 | 58.337 | 32.559 | 21.599 | 1.73 | 0 | 0.477 | 0 | 48.751 | 22.437 | 99.464 | 128.115 | 0 | 33.078 | 129.63 | 75.148 | 9.31 | 8.093 | 13.154 | 5.723 | 2.312 | 3.214 | 23.573 | 4.95 | 12.45 | 2.312 | 24.453 | 161.411 | 47.851 | 0 | 3.52 | 4.716 | 14.027 | 0 | 6.539 | 41.444 | 43.14 | 4.66 | 0 | 66.01 | 83.28 | 24.15 | 12.469 | 10.8 | 19.09 | 0.78 | 0 | 27.179 | 40.06 | 62.039 | 110.276 | 0 | 40.235 | 40.235
|  | Avg (MW) | 981.1231 | 1191.144 | 852.3559 | 642.9801 | 567.5658 | 336.4431 | 390.7922 | 680.5598 | 305.7646 | 953.0862 | 725.1194 | 1156.7528 | 730.7254 | 1353.0982 | 919.6436 | 1040.9956 | 651.1533 | 1002.1023 | 704.5398 | 795.5276 | 633.9523 | 659.3647 | 649.7179 | 1301.7254 | 1549.7272 | 939.7698 | 1304.2955 | 1147.3282 | 837.0987 | 774.9636 | 602.2168 | 505.3585 | 576.6459 | 831.8065 | 937.4608 | 759.3768 | 849.2366 | 1209.1477 | 860.7052 | 1119.4853 | 1522.0609 | 1223.9769 | 795.1528 | 767.1639 | 1022.9183 | 716.8188 | 782.1587 | 1082.4764 | 1271.1482 | 1069.1652 | 1351.5133 | 1057.2911 | 1911.5601 | 1557.2708 | 1332.5915 | 1227.2256 | 876.6057 | 570.4635 | 577.5116 | 963.9464 | 1211.7489 | 1345.7594 | 1914.2617 | 1697.2606 | 1263.4998 | 1316.5503 | 2125.3597 | 1640.341 | 1360.8831 | 873.7168 | 1003.3732 | 809.0953 | 1275.3304 | 1273.4614 | 1521.5929 | 1418.1923 | 1823.9135 | 1365.0936 | 1957.4066 | 2625.5401 | 1874.2624 | 941.5409 | 1172.2785 | 1162.8258 | 1178.551 | 967.8468 | 1261.2013 | 1829.3853 | 1776.6266 | 2001.04 | 1559.5861 | 1512.9236 | 2447.9339 | 1600.5795 | 1058.2202 | 1183.7654 | 998.5578 | 449.6916 | 845.6005 | 874.2104 | 1540.6067 | 1586.2541 | 1971.4382 | 1332.3279 | 1681.7478 | 1681.7478
|  | Max (MW) | 2105.69 | 2145.25 | 2139.04 | 1797.62 | 1772.7 | 1657.9 | 1573.5 | 2129.7 | 1423.13 | 2269.16 | 2120.74 | 2317.54 | 2317.54 | 2513.65 | 2401.94 | 2459.21 | 2233.97 | 2140.51 | 2328.82 | 2220.63 | 2249.22 | 1878.77 | 2379.4 | 2508.79 | 2606.89 | 2606.89 | 2682.58 | 2661.99 | 2569.01 | 2351.12 | 2375.62 | 2008.09 | 2151.523 | 2301.487 | 2620.629 | 2394.933 | 2583.232 | 2811.574 | 2811.574 | 3071.696 | 3062.517 | 3004.626 | 2723.652 | 2716.216 | 2681.9 | 2452.271 | 2585.922 | 2941.959 | 3070.703 | 3016.104 | 3280.794 | 3280.794 | 3612.641 | 3499.219 | 3654.784 | 3562.948 | 2934.228 | 2845.213 | 2850.223 | 2847.576 | 3261.665 | 3419.32 | 3790.636 | 3938.772 | 3938.772 | 3826.527 | 3864.493 | 3780.61 | 3872.444 | 2909.682 | 2965.367 | 3154.419 | 3012.522 | 3196.89 | 3500.448 | 3495.21 | 3995.966 | 3995.966 | 4128.152 | 4231.946 | 4042.465 | 3355.441 | 3180.25 | 3301.069 | 3017.343 | 3464.963 | 3354.37 | 3754.96 | 4012.027 | 4215.036 | 4231.946 | 4154.158 | 4472.228 | 4124.26 | 3241.855 | 3707.228 | 3147.221 | 2493.434 | 3300.219 | 3308.684 | 3937.845 | 4425.29 | 4353.79 | 4472.228 | 4483.725 | 4483.725
|  | Total (GWh) | 729.9556 | 800.4488 | 633.3005 | 462.9457 | 422.2689 | 242.239 | 290.7494 | 506.3365 | 220.1505 | 710.0493 | 522.0859 | 860.6241 | 6401.1541 | 1006.7051 | 618.0005 | 773.4597 | 468.8304 | 745.5641 | 507.2687 | 591.8726 | 471.6605 | 474.7426 | 484.0398 | 937.2423 | 1152.997 | 8232.3833 | 970.3959 | 798.5404 | 621.9643 | 557.9738 | 448.0493 | 363.8581 | 429.0245 | 618.864 | 674.9718 | 565.7357 | 611.4504 | 899.6059 | 7560.4342 | 832.897 | 1022.825 | 909.4149 | 572.51 | 570.7699 | 736.5012 | 533.3132 | 581.9261 | 779.383 | 947.0054 | 769.7989 | 1005.5259 | 9261.8705 | 1422.2007 | 1046.486 | 990.1154 | 883.6025 | 652.1946 | 410.7337 | 429.6686 | 717.1761 | 872.4592 | 1002.5907 | 1378.2685 | 1262.7619 | 11068.258 | 979.5134 | 1428.2418 | 1218.7734 | 979.8358 | 650.0453 | 722.4287 | 601.9669 | 948.8458 | 916.8922 | 1133.5867 | 1021.0985 | 1356.9916 | 11958.2202 | 1456.3105 | 1827.3759 | 1392.577 | 677.9095 | 872.1752 | 837.2346 | 876.842 | 720.078 | 908.065 | 1362.892 | 1279.1712 | 1488.7738 | 13699.4046 | 1125.6152 | 1645.0116 | 1189.2305 | 761.9185 | 880.7215 | 718.9616 | 334.5706 | 629.1267 | 629.4315 | 1147.752 | 1142.103 | 1466.75 | 11671.1927 | 1251.2204 | 1251.2204
| Wind Penetration (% of Demand) | Min (%) | 1.417% | 2.914% | 0.0599% | 0.1909% | 0.08106% | 0.2306% | 0.3756% | 0.3314% | 0.05262% | 0.02072% | 0.2232% | 0.5539% | 0.02072% | 0.6105% | 0.1586% | 0.0603% | 0.2826% | 0.6693% | 0.1776% | 0.09641% | 0.04321% | 0.01233% | 0.03754% | 0.3046% | 0.5891% | 0.01233% | 0.6705% | 0.007596% | 0.277% | 0.143% | 0% | 0.07467% | 0.2158% | 0.0834% | 0.3952% | 0% | 0.3045% | 0.8411% | 0% | 0.5179% | 1.661% | 0.5336% | 0.04368% | 0.04506% | 0.3206% | 0.01613% | 0.2681% | 0.1599% | 0.3572% | 0% | 1.424% | 0% | 0.5268% | 1.194% | 0.5899% | 0.4239% | 0.03712% | 0% | 0.01127% | 0% | 1.129% | 0.4742% | 2.913% | 2.426% | 0% | 0.6118% | 2.652% | 1.678% | 0.217% | 0.1702% | 0.4262% | 0.1658% | 0.05005% | 0.06864% | 0.4649% | 0.1313% | 0.2519% | 0.05005% | 0.3921% | 2.944% | 0.8952% | 0% | 0.08433% | 0.103% | 0.3304% | 0% | 0.2168% | 0.9098% | 0.8315% | 0.09089% | 0% | 1.401% | 2.176% | 0.4874% | 0.2364% | 0.2408% | 0.4645% | 0.01619% | 0% | 0.5298% | 0.8049% | 1.116% | 2.069% | 0% | 0.9053% | 0.9053%
|  | Avg (%) | 22.6% | 27.38% | 20.62% | 16.96% | 15.36% | 9.39% | 11% | 19.12% | 8.205% | 24.49% | 17.4% | 26.91% | 18.63% | 30.43% | 20.59% | 24.61% | 16.69% | 26.23% | 19.07% | 21.93% | 17.49% | 17.33% | 16.38% | 30.61% | 36.22% | 23.45% | 29.67% | 25.77% | 19.98% | 19.16% | 16.03% | 13.79% | 15.75% | 22.27% | 24.43% | 18.99% | 19.31% | 27.85% | 21.32% | 25.25% | 34.03% | 28.63% | 19.98% | 20.11% | 27.01% | 19.39% | 20.67% | 27.45% | 31.32% | 24.13% | 30.18% | 25.83% | 41.33% | 33.31% | 29.23% | 29.16% | 22.19% | 14.82% | 15.15% | 24.95% | 30.42% | 31.89% | 42.26% | 38.2% | 29.91% | 28.64% | 46.79% | 37.15% | 32.21% | 21.75% | 25.96% | 21.03% | 33.09% | 32% | 35.76% | 30.78% | 40.79% | 32.34% | 42.48% | 55.79% | 42.24% | 25.1% | 32.01% | 30.74% | 30.41% | 24.74% | 30.89% | 42.52% | 39.3% | 42.63% | 37.19% | 31.99% | 52.12% | 35.54% | 24.65% | 28.26% | 24.46% | 10.94% | 20.62% | 20.44% | 35.12% | 33.5% | 41.15% | 30.24% | 34.78% | 34.78%
|  | Max (%) | 61.15% | 62.38% | 61.55% | 59.52% | 62.72% | 45.97% | 57% | 63.66% | 46.78% | 68.69% | 64.35% | 66.85% | 68.69% | 65.51% | 65.47% | 63.9% | 63.71% | 67.07% | 68.94% | 67.07% | 67.49% | 57.22% | 69.08% | 72.68% | 69.93% | 72.68% | 70.59% | 73.31% | 69.33% | 65.54% | 70.77% | 52.42% | 54.29% | 63.92% | 67.15% | 66.38% | 67.12% | 77.87% | 77.87% | 78.41% | 77.4% | 68.7% | 75.01% | 71.88% | 78.66% | 71.12% | 64.42% | 72.87% | 73.58% | 71.56% | 77.95% | 78.66% | 81.15% | 82.24% | 73.71% | 83.06% | 69.68% | 79.9% | 73.15% | 83.05% | 84.68% | 83.16% | 83.82% | 82.49% | 84.68% | 82.67% | 84.26% | 83.29% | 82.52% | 76.52% | 83.93% | 79.83% | 78.72% | 83.66% | 82.84% | 81.71% | 83.78% | 84.26% | 83.29% | 81% | 80.05% | 80.71% | 88.26% | 88.97% | 88.65% | 86.79% | 85.5% | 86.61% | 81.85% | 88.93% | 88.97% | 95.37% | 92.86% | 90.01% | 82.12% | 93.53% | 78.64% | 56.72% | 84.45% | 90.68% | 94.19% | 96.48% | 93.97% | 96.48% | 97.18% | 97.18%
| Wind Penetration (% of Demand) | % of Month with Wind Less than 25% | 55.07% | 41.29% | 61.68% | 73.12% | 73.66% | 91.63% | 90.05% | 67.24% | 96.56% | 52.28% | 71.7% | 43.51% | 68.2% | 37.7% | 62.69% | 51.45% | 71.25% | 48.25% | 69.55% | 56.15% | 72.51% | 70.69% | 73.12% | 38.82% | 23.99% | 56.23% | 42.88% | 52.48% | 69.68% | 72.6% | 76.71% | 87.22% | 80.28% | 58.33% | 55.03% | 66.21% | 68.12% | 45.5% | 64.59% | 56.99% | 37.54% | 42.06% | 68.72% | 67.61% | 55.17% | 66.5% | 66.36% | 47.95% | 38.52% | 54.24% | 45.53% | 54.04% | 25.44% | 37.76% | 51.31% | 52.88% | 60.32% | 77.74% | 80.75% | 57.29% | 43.09% | 42.35% | 27.22% | 31.62% | 49.06% | 49.53% | 20.8% | 38.73% | 44.03% | 64.38% | 55.42% | 71.74% | 39.45% | 39.83% | 34.77% | 44.38% | 27.62% | 44.39% | 26.41% | 11.96% | 26.38% | 57.57% | 44.76% | 52.74% | 44.02% | 62.13% | 42.85% | 23.19% | 34.31% | 27.52% | 37.86% | 45.13% | 17.41% | 49.87% | 54.72% | 58.67% | 57.95% | 89.38% | 67.31% | 68.85% | 40.23% | 42.67% | 25.94% | 51.74% | 44.42% | 44.42%
|  | % of Month with Wind Between 25% and 50% | 37.94% | 51.12% | 34.59% | 25.1% | 24.7% | 8.368% | 9.442% | 31.52% | 3.438% | 35.47% | 25.31% | 44.86% | 27.59% | 47.85% | 30.51% | 37.89% | 27.95% | 44.39% | 23.44% | 38.47% | 22.41% | 28.61% | 20.5% | 43.58% | 53.93% | 35.04% | 41.03% | 29.6% | 22.61% | 22.78% | 18.75% | 12.5% | 19.15% | 33.06% | 34.24% | 28.93% | 28.12% | 38.07% | 27.42% | 25.97% | 35.16% | 45.19% | 21.11% | 21.4% | 26.32% | 30.17% | 30.07% | 33.78% | 38.19% | 34.9% | 32.8% | 31.25% | 32.59% | 37.05% | 23.45% | 20.59% | 30.34% | 14.27% | 13.44% | 28.56% | 34.93% | 34.36% | 29.24% | 34.85% | 27.77% | 29.97% | 23.44% | 27.56% | 32.6% | 23.79% | 29.69% | 15.59% | 35.25% | 37.29% | 32.62% | 34.44% | 30.07% | 29.36% | 26.85% | 15.41% | 30.28% | 28.23% | 28.36% | 16.35% | 37.8% | 15.42% | 36.63% | 33.36% | 24.41% | 27.39% | 26.77% | 31.65% | 25.89% | 12.79% | 33.96% | 17.04% | 32.85% | 9.946% | 18.25% | 21.49% | 28.12% | 34.1% | 36.22% | 25.13% | 22.78% | 22.78%
|  | % of Month with Wind Higher than 50% | 6.989% | 7.589% | 3.735% | 1.771% | 1.647% | 0% | 0.504% | 1.243% | 0% | 12.25% | 2.986% | 11.63% | 4.201% | 14.45% | 6.808% | 10.67% | 0.7986% | 7.359% | 7.014% | 5.376% | 5.074% | 0.6944% | 6.376% | 17.6% | 22.08% | 8.73% | 16.1% | 17.92% | 7.705% | 4.618% | 4.536% | 0.2778% | 0.5712% | 8.602% | 10.73% | 4.866% | 3.75% | 16.43% | 7.989% | 17.04% | 27.31% | 12.75% | 10.17% | 10.99% | 18.51% | 3.327% | 3.562% | 18.26% | 23.29% | 10.87% | 21.67% | 14.71% | 41.97% | 25.19% | 25.24% | 26.53% | 9.341% | 7.986% | 5.813% | 14.15% | 21.98% | 23.29% | 43.54% | 33.53% | 23.18% | 20.5% | 55.77% | 33.71% | 23.37% | 11.83% | 14.9% | 12.67% | 25.3% | 22.88% | 32.62% | 21.18% | 42.31% | 26.24% | 46.74% | 72.63% | 43.34% | 14.2% | 26.88% | 30.9% | 18.18% | 22.45% | 20.52% | 43.46% | 41.28% | 45.09% | 35.37% | 23.22% | 56.7% | 37.35% | 11.32% | 24.29% | 9.201% | 0.672% | 14.45% | 9.653% | 31.64% | 23.23% | 37.84% | 23.13% | 32.8% | 32.8%
SNSP |  | % of Month with SNSP Less than 25% | 31.22% | 18.27% | 36.44% | 47.15% | 60.48% | 80.97% | 81.05% | 54.97% | 89.06% | 37.82% | 55.45% | 29.23% | 51.94% | 24.19% | 50.97% | 43.94% | 65.66% | 39.58% | 61.7% | 56.45% | 73.05% | 71.32% | 70.34% | 32.5% | 18.21% | 50.58% | 39.78% | 51.01% | 66.12% | 70.21% | 76.38% | 85.94% | 81.82% | 61.46% | 58.54% | 69.09% | 71.15% | 44.52% | 64.67% | 59.07% | 32.25% | 37.52% | 67.43% | 67.24% | 56.6% | 71.2% | 68.95% | 48.12% | 29.16% | 42.57% | 38.1% | 51.65% | 18.08% | 28.76% | 41.59% | 45.73% | 53.83% | 72.92% | 76.68% | 53.9% | 29.55% | 22.11% | 14.03% | 7.124% | 38.75% | 24.87% | 7.068% | 21.4% | 26.81% | 55.91% | 49.17% | 38.71% | 14.68% | 18.51% | 18.36% | 30.03% | 16.03% | 26.91% | 12.63% | 3.807% | 12.48% | 37.15% | 42.2% | 51.84% | 40.12% | 61.46% | 35.56% | 5.772% | 22.81% | 17.51% | 28.66% | 35.79% | 7.589% | 25.3% | 31.15% | 21.2% | 35.9% | 50.77% | 55.24% | 57.19% | 22.89% | 29.55% | 25.97% | 33.36% | 41.1% | 41.1%
|  | % of Month with SNSP Between 25% and 50% | 67.71% | 80.21% | 61.68% | 52.43% | 39.31% | 18.96% | 18.95% | 43.88% | 10.94% | 60.94% | 44.44% | 69.93% | 47.35% | 74.13% | 48.03% | 55.08% | 34.1% | 59.48% | 37.33% | 43.25% | 26.31% | 28.68% | 25.67% | 58.92% | 69.72% | 46.79% | 52.76% | 42.71% | 27.25% | 29.24% | 21.27% | 14.06% | 17.91% | 36.19% | 35.38% | 28.66% | 27.5% | 43.41% | 31.35% | 28.49% | 47.66% | 55.65% | 25.52% | 23.56% | 30.17% | 26.81% | 29.54% | 42.95% | 56.85% | 51.77% | 44.32% | 38.54% | 41.1% | 48.74% | 36.1% | 29.24% | 39.15% | 21.28% | 18.88% | 31.75% | 51.22% | 56.14% | 48.37% | 62.43% | 40.33% | 55.04% | 40.59% | 46.16% | 52.67% | 35.82% | 43.09% | 51.48% | 61.32% | 60.87% | 56.95% | 54.41% | 43.18% | 50.18% | 40.36% | 23.85% | 44.89% | 44.1% | 36.09% | 21.98% | 47.61% | 18.95% | 52.85% | 56.01% | 37.6% | 44.52% | 39.15% | 44.29% | 33.63% | 39.37% | 60.56% | 53.43% | 57.67% | 47.01% | 30.61% | 33.58% | 45.13% | 48.99% | 42.98% | 44.8% | 28.6% | 28.6%
|  | % of Month with SNSP Higher than 50% | 1.075% | 1.525% | 1.884% | 0.4167% | 0.2016% | 0.06944% | 0% | 1.142% | 0% | 1.242% | 0.1042% | 0.8401% | 0.7078% | 1.68% | 1.004% | 0.9758% | 0.2431% | 0.9409% | 0.9722% | 0.3024% | 0.6384% | 0% | 3.993% | 8.576% | 12.06% | 2.631% | 7.46% | 6.286% | 6.629% | 0.5556% | 2.352% | 0% | 0.2688% | 2.352% | 6.076% | 2.248% | 1.354% | 12.06% | 3.979% | 12.43% | 20.09% | 6.83% | 7.049% | 9.207% | 13.23% | 1.983% | 1.512% | 8.924% | 13.99% | 5.66% | 17.57% | 9.803% | 40.83% | 22.51% | 22.31% | 25.03% | 7.023% | 5.799% | 4.435% | 14.35% | 19.24% | 21.74% | 37.6% | 30.44% | 20.92% | 20.09% | 52.34% | 32.44% | 20.52% | 8.266% | 7.743% | 9.812% | 23.99% | 20.62% | 24.7% | 15.56% | 40.79% | 22.91% | 47.01% | 72.34% | 42.63% | 18.75% | 21.71% | 26.18% | 12.26% | 19.59% | 11.6% | 38.22% | 39.58% | 37.97% | 32.19% | 19.93% | 58.78% | 35.33% | 8.299% | 25.37% | 6.424% | 2.218% | 14.15% | 9.236% | 31.98% | 21.46% | 31.05% | 21.83% | 30.31% | 30.31%
|  | SNSP Limit | 2014-01-01: 50% | [10 empty] | 55% Trial | [5 empty] | 55% | [7 empty] | 60% Trial |  |  |  |  | 60% | [7 empty] | 65% Trial | [5 empty] | 65% | [35 empty] | 70% Trial |  |  | 75% Trial

## Fuel Mix & CO2
Electricity Fuel Mix as Percentage of Demand - Latest Available 12-Month Average (Oct 2020 to Sep 2021):
Oct 2020 to Sep 2021 | Ireland |  | Northern Ireland |  | All Island
Fuel | GWh | % | GWh | % | GWh | %
Coal | 2488.6479 | 7.966% | 896.315 | 11.03% | 3384.9629 | 8.599%
Oil | 400.1235 | 1.281% | 14.5746 | 0.1794% | 414.6981 | 1.053%
NR Peat | 749.9574 | 2.401% |  | 0% | 749.9574 | 1.905%
Gas | 14205.6233 | 45.47% | 4418.4365 | 54.38% | 18624.0598 | 47.31%
Wind | 10049.4151 | 32.17% | 2492.0568 | 30.67% | 12541.4719 | 31.86%
Solar | 0 | 0% | 163.4519 | 2.012% | 163.4519 | 0.4152%
Hydro | 859.9967 | 2.753% | 16.3312 | 0.201% | 876.3279 | 2.226%
Other Renewable | 647.2282 | 2.072% | 361.929 | 4.455% | 1009.1572 | 2.564%
Other Non-Renewable | 297.8978 | 0.9536% | 2.891 | 0.03558% | 300.7888 | 0.7641%
Net Imports | 1540.586 | 4.932% | -241.1479 | -2.968% | 1299.438 | 3.301%
Total Demand | 31239.4757 | 100% | 8124.8381 | 100% | 39364.3138 | 100%
Total Renewables | 11556.6399 | 36.99% | 3033.769 | 37.34% | 14590.4089 | 37.07%
Note: Ireland's renewable percentage does not include small scale/micro generation. These final figures will be published by SEAI after the end of the calendar year.
Data Sources: EirGrid and SONI metered data. See additional notes below.
Electricity Fuel Mix as Percentage of Demand - Calendar Year Charts:
Electricity Fuel Mix as Percentage of Demand - Calendar Year Figures:
| Ireland | [13 empty] | Northern Ireland | [13 empty] | All Island
| 2014 |  | 2015 |  | 2016 |  | 2017 |  | 2018 |  | 2019 |  | 2020 |  | 2014 |  | 2015 |  | 2016 |  | 2017 |  | 2018 |  | 2019 |  | 2020 |  | 2014 |  | 2015 |  | 2016 |  | 2017 |  | 2018 |  | 2019 |  | 2020
Fuel Type | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | % | GWh | %
Coal | 3956.7479 | 14.15% | 4874.4338 | 16.94% | 4695.6563 | 15.91% | 3644.5618 | 12.15% | 2151.6739 | 6.97% | 507.902 | 1.621% | 669.1903 | 2.103% | 2064.427 | 23.55% | 2018.7503 | 23% | 2034.1318 | 23.31% | 1300.3244 | 15.46% | 1272.4779 | 15.14% | 866.2515 | 10.38% | 994.2734 | 12.45% | 6021.1749 | 16.4% | 6893.184 | 18.36% | 6729.7881 | 17.6% | 4944.8862 | 12.88% | 3424.1518 | 8.719% | 1374.1534 | 3.462% | 1663.4637 | 4.178%
Oil | 258.3765 | 0.9242% | 406.8328 | 1.414% | 292.8228 | 0.9923% | 141.8704 | 0.473% | 139.4216 | 0.4517% | 280.2434 | 0.8942% | 393.4696 | 1.236% | 5.98 | 0.06822% | 9.8066 | 0.1117% | 26.6166 | 0.305% | 12.9916 | 0.1544% | 28.1961 | 0.3355% | 14.9754 | 0.1794% | 15.1437 | 0.1896% | 264.3565 | 0.7199% | 416.6394 | 1.109% | 319.4394 | 0.8355% | 154.862 | 0.4032% | 167.6177 | 0.4268% | 295.2188 | 0.7439% | 408.6134 | 1.026%
NR Peat | 2496.0858 | 8.928% | 2518.2205 | 8.751% | 2317.8851 | 7.855% | 2164.3795 | 7.216% | 2090.7165 | 6.773% | 1927.1063 | 6.149% | 960.4285 | 3.018% |  | 0% |  | 0% |  | 0% |  | 0% |  | 0% |  | 0% |  | 0% | 2496.0858 | 6.797% | 2518.2205 | 6.706% | 2317.8851 | 6.062% | 2164.3795 | 5.635% | 2090.7165 | 5.324% | 1927.1063 | 4.856% | 960.4285 | 2.412%
Gas | 12635.047 | 45.19% | 12367.4914 | 42.98% | 15328.4023 | 51.94% | 15679.8551 | 52.28% | 16013.963 | 51.88% | 15906.1845 | 50.75% | 16250.1098 | 51.06% | 3835.612 | 43.76% | 4150.0875 | 47.28% | 4440.3785 | 50.89% | 4788.8546 | 56.92% | 3828.3686 | 45.56% | 4047.5025 | 48.49% | 3935.9651 | 49.28% | 16470.659 | 44.85% | 16517.5789 | 43.98% | 19768.7808 | 51.7% | 20468.7097 | 53.3% | 19842.3316 | 50.53% | 19953.687 | 50.28% | 20186.0749 | 50.7%
Wind | 5140.0611 | 18.39% | 6572.9976 | 22.84% | 6147.0427 | 20.83% | 7444.0365 | 24.82% | 8639.7665 | 27.99% | 10019.4844 | 31.97% | 11549.42 | 36.29% | 1452.624 | 16.57% | 1802.7341 | 20.54% | 1714.8779 | 19.65% | 2270.3946 | 26.99% | 2577.853 | 30.68% | 2762.5644 | 33.09% | 2960.9452 | 37.07% | 6592.6851 | 17.95% | 8375.7317 | 22.3% | 7861.9206 | 20.56% | 9714.4312 | 25.29% | 11217.6195 | 28.56% | 12782.0488 | 32.21% | 14510.3652 | 36.45%
Solar | 2.4574 | 0.00879% | 3.4082 | 0.01184% | 6.16 | 0.02087% | 10.8014 | 0.03601% | 16.6558 | 0.05396% | 21.4197 | 0.06835% | 27.7265 | 0.08712% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 149.2118 | 1.788% | 165.5596 | 2.073% | 2.4574 | 0.006692% | 3.4082 | 0.009076% | 6.16 | 0.01611% | 10.8014 | 0.02812% | 16.6558 | 0.04241% | 170.6315 | 0.4299% | 193.2862 | 0.4855%
Hydro | 708.6539 | 2.535% | 806.4902 | 2.803% | 681.0255 | 2.308% | 691.6029 | 2.306% | 694.0896 | 2.249% | 886.5839 | 2.829% | 932.6554 | 2.931% | 12.678 | 0.1446% | 11.9615 | 0.1363% | 9.5852 | 0.1099% | 11.0798 | 0.1317% | 15.0839 | 0.1795% | 18.0923 | 0.2167% | 18.6881 | 0.234% | 721.3319 | 1.964% | 818.4517 | 2.179% | 690.6107 | 1.806% | 702.6827 | 1.83% | 709.1735 | 1.806% | 904.6762 | 2.279% | 951.3435 | 2.39%
Other Renewables | 540.9747 | 1.935% | 478.5868 | 1.663% | 679.2152 | 2.302% | 735.2478 | 2.451% | 848.3409 | 2.748% | 852.3075 | 2.72% | 894.8816 | 2.812% | 104.0141 | 1.187% | 183.599 | 2.092% | 323.1626 | 3.704% | 338.9711 | 4.029% | 441.937 | 5.259% | 336.5316 | 4.032% | 356.6551 | 4.466% | 644.9888 | 1.756% | 662.1859 | 1.763% | 1002.3778 | 2.622% | 1074.2189 | 2.797% | 1290.2779 | 3.286% | 1188.8391 | 2.995% | 1251.5367 | 3.144%
Other Non-Renewables | 69.5934 | 0.2489% | 74.0614 | 0.2574% | 72.8002 | 0.2467% | 159.3015 | 0.5311% | 301.5882 | 0.977% | 294.6709 | 0.9402% | 299.0442 | 0.9396% | 5.952 | 0.0679% | 4.6396 | 0.05286% | 4.3769 | 0.05016% | 4.4004 | 0.0523% | 9.3791 | 0.1116% | 3.0804 | 0.0369% | 3.5548 | 0.04451% | 75.5454 | 0.2057% | 78.701 | 0.2096% | 77.1771 | 0.2019% | 163.7019 | 0.4262% | 310.9673 | 0.7918% | 297.7513 | 0.7502% | 302.5989 | 0.7601%
Net Imports | 2149.057 | 7.687% | 673.37 | 2.34% | -711.7486 | -2.412% | -678.5025 | -2.262% | -27.7299 | -0.08983% | 644.5404 | 2.057% | -151.8538 | -0.4772% | 1284.6765 | 14.66% | 595.3532 | 6.783% | 172.3441 | 1.975% | -313.7773 | -3.73% | 229.7499 | 2.734% | 149.2876 | 1.788% | -463.9716 | -5.809% | 3433.7335 | 9.35% | 1268.7232 | 3.379% | -539.4045 | -1.411% | -992.2798 | -2.584% | 202.02 | 0.5144% | 793.828 | 2% | -615.8254 | -1.547%
Total Demand | 27957.0548 | 100% | 28775.8927 | 100% | 29509.2615 | 100% | 29993.1545 | 100% | 30868.4861 | 100% | 31340.4429 | 100% | 31825.0721 | 100% | 8765.9637 | 100% | 8776.9317 | 100% | 8725.4735 | 100% | 8413.2393 | 100% | 8403.0455 | 100% | 8347.4974 | 100% | 7986.8134 | 100% | 36723.0185 | 100% | 37552.8244 | 100% | 38234.735 | 100% | 38406.3937 | 100% | 39271.5316 | 100% | 39687.9403 | 100% | 39811.8855 | 100%
Renewables | 6392.1471 | 22.86% | 7861.4828 | 27.32% | 7513.4434 | 25.46% | 8881.6887 | 29.61% | 10198.8528 | 33.04% | 11779.7955 | 37.59% | 13404.6835 | 42.12% | 1569.3161 | 17.9% | 1998.2946 | 22.77% | 2047.6257 | 23.47% | 2620.4456 | 31.15% | 3034.8739 | 36.12% | 3266.4001 | 39.13% | 3501.848 | 43.85% | 7961.4632 | 21.68% | 9859.7775 | 26.26% | 9561.0691 | 25.01% | 11502.1342 | 29.95% | 13233.7267 | 33.7% | 15046.1956 | 37.91% | 16906.5315 | 42.47%
Notes:
All figures represent net exported energy.
Negative net imports indicate net exported energy.
Data Sources:
Ireland: Sustainable Energy Authority of Ireland (SEAI) - Latest update Apr 2021.
SEAI's figures are comprised of EirGrid's provisional figures plus other small scale and micro generation data compiled by SEAI.
EirGrid provisional figures consist of: EirGrid/SEMO metered data + ESBN/MRSO metered data for distribution-connected generation.
EirGrid and SEAI may publish future updates to fuel mix figures as more data is collected throughout the year.
Other Non-Renewables include: non-renewable waste energy, non-renewable CHP and Diesel.
Other Renewables include: renewable CHP, bio energy (biomass, biogas, LFG) and ocean energy (tidal and wave).
Pumped hydro is not included. It is considered storage or delayed output rather than primary production.
Northern Ireland: Fuel mix figures are based on latest metered data provided by SONI.
Other Non-Renewables include: DSO CHP and Diesel.
Other Renewables include: Biomass, Biogas, LFG, Renewable CHP and Hydro.
Differences:
The data contained in the "System Summary" tab is indicative as it is based on raw 15-minute average SCADA readings which are produced in real time and have yet to be quality controlled.
The data contained in this tab however represents "metered data" which is more accurate than the real-time SCADA data and used for official purposes.
This metered data will have been put through a quality control process and therefore may not be available until a few months after the event.
Metered data may also be updated in the future if more information is received from the various data sources.
Electricity Fuel Mix as Percentage of Demand (Ireland only) - Source: SEAI - Apr 2021
Percentages (%)
Ireland Electricity Fuel Mix | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020
Coal | 41.64% | 39.24% | 42.24% | 41.02% | 39.77% | 39.95% | 37.26% | 34.49% | 32.16% | 26.5% | 28.68% | 28.96% | 26.91% | 23.83% | 23.25% | 23.09% | 20.36% | 18.31% | 16.93% | 13.94% | 12.41% | 14.26% | 18.23% | 15.39% | 14.15% | 16.94% | 15.91% | 12.15% | 6.97% | 1.621% | 2.103%
Peat | 15.8% | 14.39% | 13.83% | 11.62% | 11.38% | 11.48% | 11.65% | 10.46% | 8.083% | 7.643% | 7.446% | 8.994% | 8.214% | 7.792% | 5.551% | 8.854% | 7.4% | 7.283% | 9.071% | 9.151% | 7.606% | 7.701% | 8.846% | 8.202% | 8.928% | 8.751% | 7.855% | 7.216% | 6.773% | 6.149% | 3.018%
Oil: | 9.928% | 16.21% | 15.57% | 14.41% | 16.75% | 15.14% | 14.19% | 17.61% | 23.14% | 28.03% | 19.51% | 21.34% | 14.71% | 9.429% | 11.99% | 12.07% | 9.808% | 6.396% | 5.625% | 3.195% | 2.106% | 0.845% | 0.8557% | 0.6788% | 0.9242% | 1.414% | 0.9923% | 0.473% | 0.4517% | 0.8942% | 1.236%
Gas Oil | 0.1337% | 0.114% | 0.1332% | 0.08059% | 0.2915% | 0.2334% | 0.1332% | 0.1474% | 0.1718% | 0.2908% | 0.2903% | 0.242% | 0.1341% | 0.4303% | 0.2352% | 0.8204% | 0.8618% | 0.2388% | 0.1775% | 0.1445% | 0.4901% | 0.134% | 0.1314% | 0.07462% | 0.1343% | 0.381% | 0.1781% | 0.1151% | 0.1186% | 0.1848% | 0.1504%
Fuel Oil | 9.752% | 16.04% | 15.35% | 14.25% | 16.37% | 14.79% | 13.97% | 17.26% | 22.77% | 27.53% | 19.01% | 20.89% | 14.41% | 8.837% | 11.59% | 11.09% | 8.808% | 6.006% | 5.341% | 2.947% | 1.45% | 0.5734% | 0.5695% | 0.4911% | 0.6837% | 0.8414% | 0.7323% | 0.3395% | 0.3216% | 0.6983% | 1.079%
Refinery Gas | 0.04222% | 0.04693% | 0.08882% | 0.07439% | 0.08925% | 0.1195% | 0.07993% | 0.2033% | 0.1956% | 0.2136% | 0.2145% | 0.2092% | 0.1618% | 0.1575% | 0.1568% | 0.1518% | 0.135% | 0.1455% | 0.102% | 0.09815% | 0.1569% | 0.1288% | 0.1452% | 0.1014% | 0.09624% | 0.1793% | 0.07129% | 0.006512% | 0% | 0% | 0%
LPG | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.003945% | 0.003842% | 0.003733% | 0.003614% | 0.003461% | 0.004771% | 0.00461% | 0.004954% | 0.008808% | 0.008821% | 0.009635% | 0.01178% | 0.01% | 0.01205% | 0.01068% | 0.01194% | 0.01142% | 0.01111% | 0.007345%
Natural Gas | 27.73% | 25.16% | 23.14% | 28.11% | 26.51% | 29.37% | 33.52% | 33.38% | 30.66% | 31.62% | 38.97% | 37.52% | 42.72% | 50.09% | 48.13% | 41.83% | 47.71% | 54.09% | 55.05% | 56.73% | 63.22% | 55.8% | 51.31% | 47.2% | 45.19% | 42.98% | 51.94% | 52.28% | 51.88% | 50.75% | 51.06%
Renewables: | 4.904% | 5.002% | 5.215% | 4.835% | 5.587% | 4.149% | 4.066% | 4.111% | 5.583% | 5.112% | 4.989% | 4.212% | 5.453% | 4.372% | 5.204% | 6.77% | 8.565% | 9.438% | 11.84% | 14.33% | 13.02% | 19.61% | 19.07% | 20.23% | 22.86% | 27.32% | 25.46% | 29.61% | 33.04% | 37.59% | 42.12%
Hydro | 4.904% | 5.002% | 5.183% | 4.742% | 5.474% | 4.058% | 3.847% | 3.446% | 4.371% | 3.849% | 3.563% | 2.444% | 3.598% | 2.298% | 2.352% | 2.281% | 2.507% | 2.245% | 3.189% | 3.139% | 2.092% | 2.555% | 2.912% | 2.155% | 2.535% | 2.803% | 2.308% | 2.306% | 2.249% | 2.829% | 2.931%
Wind | 0% | 0% | 0.03172% | 0.09298% | 0.113% | 0.09107% | 0.0746% | 0.2541% | 0.8064% | 0.8497% | 1.026% | 1.37% | 1.531% | 1.744% | 2.445% | 4.018% | 5.614% | 6.597% | 7.937% | 10.29% | 9.825% | 15.84% | 14.55% | 16.33% | 18.39% | 22.84% | 20.83% | 24.82% | 27.99% | 31.97% | 36.29%
Solar PV | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.001476% | 0.001662% | 0.00196% | 0.002344% | 0.002514% | 0.00879% | 0.01184% | 0.02087% | 0.03601% | 0.05396% | 0.06835% | 0.08712%
Other Renewables | 0% | 0% | 0% | 0% | 0% | 0% | 0.1439% | 0.4116% | 0.4056% | 0.4135% | 0.3996% | 0.3978% | 0.3235% | 0.3304% | 0.4069% | 0.4708% | 0.4445% | 0.5966% | 0.7146% | 0.9057% | 1.098% | 1.215% | 1.607% | 1.747% | 1.935% | 1.663% | 2.302% | 2.451% | 2.748% | 2.72% | 2.812%
Non-Renewable Waste | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.1805% | 0.2354% | 0.2489% | 0.2574% | 0.2467% | 0.5311% | 0.977% | 0.9402% | 0.9396%
Net Imports | 0% | 0% | 0% | 0% | 0% | -0.08538% | -0.6874% | -0.06098% | 0.377% | 1.095% | 0.4122% | -1.025% | 1.985% | 4.48% | 5.876% | 7.387% | 6.153% | 4.481% | 1.483% | 2.658% | 1.642% | 1.772% | 1.5% | 8.06% | 7.687% | 2.34% | -2.412% | -2.262% | -0.08983% | 2.057% | -0.4772%
Total | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Volumes (GWh)
Ireland Electricity Fuel Mix | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020
Coal | 5918 | 5853 | 6658 | 6618 | 6684 | 7018 | 6992 | 6787 | 6740 | 5832 | 6817 | 7062 | 6821 | 6203 | 6229 | 6389 | 5884 | 5436.9602 | 5141.863 | 4004.3138 | 3554.7158 | 3944.7722 | 5024.3589 | 4282.5514 | 3956.7479 | 4874.4338 | 4695.6563 | 3644.5618 | 2151.6739 | 507.902 | 669.1903
Peat | 2245 | 2147 | 2180 | 1875 | 1913 | 2017 | 2187 | 2059 | 1694 | 1682 | 1770 | 2193 | 2082 | 2028 | 1487 | 2450 | 2138 | 2162.1861 | 2754.3551 | 2629.0841 | 2178.9521 | 2129.7783 | 2437.786 | 2281.4842 | 2496.0858 | 2518.2205 | 2317.8851 | 2164.3795 | 2090.7165 | 1927.1063 | 960.4285
Oil: | 1411 | 2417 | 2455 | 2324 | 2815 | 2660 | 2662 | 3465 | 4849 | 6169 | 4638 | 5203 | 3729 | 2454 | 3211 | 3340 | 2834 | 1898.7124 | 1708.056 | 917.8437 | 603.1902 | 233.685 | 235.8109 | 188.8358 | 258.3765 | 406.8328 | 292.8228 | 141.8704 | 139.4216 | 280.2434 | 393.4696
Gas Oil | 19 | 17 | 21 | 13 | 49 | 41 | 25 | 29 | 36 | 64 | 69 | 59 | 34 | 112 | 63 | 227 | 249 | 70.897 | 53.9135 | 41.5022 | 140.3991 | 37.0667 | 36.2224 | 20.7586 | 37.5411 | 109.6424 | 52.5483 | 34.5155 | 36.6156 | 57.9047 | 47.8644
Fuel Oil | 1386 | 2393 | 2420 | 2299 | 2751 | 2598 | 2622 | 3396 | 4772 | 6058 | 4518 | 5093 | 3653 | 2300 | 3105 | 3070 | 2545 | 1783.1946 | 1621.7715 | 846.7182 | 415.3119 | 158.5698 | 156.9225 | 136.6009 | 191.1336 | 242.1286 | 216.0862 | 101.8211 | 99.2803 | 218.8556 | 343.2677
Refinery Gas | 6 | 7 | 14 | 12 | 15 | 21 | 15 | 40 | 41 | 47 | 51 | 51 | 41 | 41 | 42 | 42 | 39 | 43.2045 | 30.971 | 28.2 | 44.956 | 35.609 | 40.011 | 28.2 | 26.9058 | 51.5932 | 21.036 | 1.9531 | 0 | 0 | 0
LPG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1.4164 | 1.4 | 1.4234 | 2.5231 | 2.4394 | 2.655 | 3.2762 | 2.7959 | 3.4686 | 3.1524 | 3.5807 | 3.5256 | 3.4832 | 2.3375
Natural Gas | 3941 | 3752 | 3648 | 4535 | 4456 | 5160 | 6291 | 6569 | 6425 | 6958 | 9263 | 9147 | 10829 | 13038 | 12894 | 11574 | 13785 | 16057.6603 | 16716.1176 | 16298.1184 | 18110.7547 | 15432.1985 | 14139.2898 | 13129.7506 | 12635.047 | 12367.4914 | 15328.4023 | 15679.8551 | 16013.963 | 15906.1845 | 16250.1098
Renewables: | 697 | 746 | 822 | 780 | 939 | 729 | 763 | 809 | 1170 | 1125 | 1186 | 1027 | 1382 | 1138 | 1394 | 1873.432 | 2474.7469 | 2802.0599 | 3595.3461 | 4117.5987 | 3728.7813 | 5423.5931 | 5256.2689 | 5627.5907 | 6392.1471 | 7861.4828 | 7513.4434 | 8881.6887 | 10198.8528 | 11779.7955 | 13404.6835
Hydro | 697 | 746 | 817 | 765 | 920 | 713 | 722 | 678 | 916 | 847 | 847 | 596 | 912 | 598 | 630 | 631.26 | 724.273 | 666.5756 | 968.3232 | 901.7344 | 599.2311 | 706.687 | 802.3487 | 599.4974 | 708.6539 | 806.4902 | 681.0255 | 691.6029 | 694.0896 | 886.5839 | 932.6554
Wind | 0 | 0 | 5 | 15 | 19 | 16 | 14 | 50 | 169 | 187 | 244 | 334 | 388 | 454 | 655 | 1111.91 | 1622.0412 | 1958.3706 | 2410.013 | 2955.2173 | 2814.659 | 4380.3147 | 4010.4782 | 4541.5145 | 5140.0611 | 6572.9976 | 6147.0427 | 7444.0365 | 8639.7665 | 10019.4844 | 11549.42
Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42416 | 0.47602 | 0.54198 | 0.64581 | 0.69934 | 2.4574 | 3.4082 | 6.16 | 10.8014 | 16.6558 | 21.4197 | 27.7265
Other Renewables | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 81 | 85 | 91 | 95 | 97 | 82 | 86 | 109 | 130.262 | 128.4327 | 177.1138 | 217.0099 | 260.2228 | 314.4151 | 336.0494 | 442.7962 | 485.8796 | 540.9747 | 478.5868 | 679.2152 | 735.2478 | 848.3409 | 852.3075 | 894.8816
Non-Renewable Waste | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.7481 | 65.47 | 69.5934 | 74.0614 | 72.8002 | 159.3015 | 301.5882 | 294.6709 | 299.0442
Net Imports | 0 | 0 | 0 | 0 | 0 | -15 | -129 | -12 | 79 | 241 | 98 | -250 | 503 | 1166 | 1574 | 2044.15 | 1777.8778 | 1330.35 | 450.2164 | 763.7532 | 470.326 | 490.0951 | 413.4748 | 2242.1926 | 2149.057 | 673.37 | -711.7486 | -678.5025 | -27.7299 | 644.5404 | -151.8538
Total Demand | 14212 | 14915 | 15763 | 16132 | 16807 | 17569 | 18766 | 19677 | 20957 | 22007 | 23772 | 24382 | 25346 | 26027 | 26789 | 27670.582 | 28893.6247 | 29687.929 | 30365.9543 | 28730.7119 | 28646.7201 | 27654.1221 | 27556.7374 | 27817.8753 | 27957.0548 | 28775.8927 | 29509.2615 | 29993.1545 | 30868.4861 | 31340.4429 | 31825.0721
Notes:
Data source for Ireland's electricity fuel mix figures: Sustainable Energy Authority of Ireland (SEAI).
These figures are comprised of EirGrid's centrally dispatched generation figures plus small scale generation data compiled by SEAI.
SEAI may publish future updates to fuel mix figures as more data is collected throughout the year.
The "Oil" and "Renewable" rows are subtotals of the relevant categories below them.
"Other Renewable" energy source include renewable CHP, bio energy, solar and ocean energy.
Pumped hydro is not included in the hydro figures. It is considered storage and delayed output rather than primary production.
Negative net imports indicate net exported energy.
CO2 Intensity from Electricity Generation in Ireland (gCO2/kWh)
Year | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020
Intensity gCO2/kWh | 896.3079 | 884.9171 | 887.3383 | 862.3077 | 855.1494 | 860.7763 | 854.3175 | 838.7814 | 823.1023 | 814.8659 | 770.6335 | 806.6769 | 742.9137 | 675.0731 | 638.2081 | 635.6464 | 596.1805 | 560.9941 | 547.9139 | 522.9669 | 529.7696 | 488.8886 | 529.0011 | 465.5487 | 456.102 | 467.3236 | 483.9902 | 440.9203 | 375.4298 | 324.5521 | 296.2108
Source: SEAI - Apr 2021

## Wind Installed Capacities
| Wind Installed Capacities (MW) | [11 empty] | Wind Installed Capacities (MW) Monthly from 1992 to Date
| Ireland |  |  | Northern Ireland |  |  | All Island | [5 empty] | Ireland |  |  | Northern Ireland |  |  | All Island
Year End | TSO | DSO | Total | TSO | DSO | Total | TSO | DSO | Total | YYYY | Mon | Month | TSO | DSO | Total | TSO | DSO | Total | Total
1990 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1992 | Jan | 1992-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1992 | Feb | 1992-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1992 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 0 | 6.45 | 6.45 | 1992 | Mar | 1992-03-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1993 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 0 | 6.45 | 6.45 | 1992 | Apr | 1992-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1994 | 0 | 6.45 | 6.45 | 0 | 5.791 | 5.791 | 0 | 12.241 | 12.241 | 1992 | May | 1992-05-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1995 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 0 | 29.614 | 29.614 | 1992 | Jun | 1992-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1996 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 0 | 29.614 | 29.614 | 1992 | Jul | 1992-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1997 | 15 | 42.23 | 57.23 | 0 | 29.534 | 29.534 | 15 | 71.764 | 86.764 | 1992 | Aug | 1992-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1998 | 15 | 47.23 | 62.23 | 0 | 29.534 | 29.534 | 15 | 76.764 | 91.764 | 1992 | Sep | 1992-09-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1999 | 15 | 55.18 | 70.18 | 0 | 30.576 | 30.576 | 15 | 85.756 | 100.756 | 1992 | Oct | 1992-10-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2000 | 15 | 101.53 | 116.53 | 0 | 30.576 | 30.576 | 15 | 132.106 | 147.106 | 1992 | Nov | 1992-11-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2001 | 15 | 107.93 | 122.93 | 0 | 30.576 | 30.576 | 15 | 138.506 | 153.506 | 1992 | Dec | 1992-12-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2002 | 15 | 119.83 | 134.83 | 0 | 30.576 | 30.576 | 15 | 150.406 | 165.406 | 1993 | Jan | 1993-01-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2003 | 40 | 170.34 | 210.34 | 0 | 75.977 | 75.977 | 40 | 246.317 | 286.317 | 1993 | Feb | 1993-02-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2004 | 112.4 | 224.02 | 336.42 | 0 | 91.613 | 91.613 | 112.4 | 315.633 | 428.033 | 1993 | Mar | 1993-03-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2005 | 222.9 | 270.37 | 493.27 | 0 | 124.621 | 124.621 | 222.9 | 394.991 | 617.891 | 1993 | Apr | 1993-04-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2006 | 267.9 | 408.57 | 676.47 | 0 | 144.194 | 144.194 | 267.9 | 552.764 | 820.664 | 1993 | May | 1993-05-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2007 | 310.85 | 429.61 | 740.46 | 0 | 251.327 | 251.327 | 310.85 | 680.937 | 991.787 | 1993 | Jun | 1993-06-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2008 | 417.75 | 524.507 | 942.257 | 0 | 267.658 | 267.658 | 417.75 | 792.165 | 1209.915 | 1993 | Jul | 1993-07-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2009 | 668.75 | 582.557 | 1251.307 | 0 | 348.731 | 348.731 | 668.75 | 931.288 | 1600.038 | 1993 | Aug | 1993-08-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2010 | 727.8 | 662.638 | 1390.438 | 0 | 392.163 | 392.163 | 727.8 | 1054.801 | 1782.601 | 1993 | Sep | 1993-09-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2011 | 769.2 | 815.398 | 1584.598 | 73.6 | 438.838 | 512.438 | 842.8 | 1254.236 | 2097.036 | 1993 | Oct | 1993-10-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2012 | 769.2 | 934.28 | 1703.48 | 73.6 | 526.049 | 599.649 | 842.8 | 1460.329 | 2303.129 | 1993 | Nov | 1993-11-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2013 | 845.2 | 1078.077 | 1923.277 | 73.6 | 566.354 | 639.954 | 918.8 | 1644.431 | 2563.231 | 1993 | Dec | 1993-12-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2014 | 1046.55 | 1219.867 | 2266.417 | 73.6 | 655.535 | 729.135 | 1120.15 | 1875.402 | 2995.552 | 1994 | Jan | 1994-01-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2015 | 1152.55 | 1294.717 | 2447.267 | 73.6 | 677.425 | 751.025 | 1226.15 | 1972.142 | 3198.292 | 1994 | Feb | 1994-02-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2016 | 1371.25 | 1423.506 | 2794.756 | 73.6 | 869.023 | 942.623 | 1444.85 | 2292.529 | 3737.379 | 1994 | Mar | 1994-03-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2017 | 1591.5 | 1720.764 | 3312.264 | 121.1 | 1032.618 | 1153.718 | 1712.6 | 2753.382 | 4465.982 | 1994 | Apr | 1994-04-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2018 | 1774.45 | 1892.588 | 3667.038 | 121.1 | 1155.154 | 1276.254 | 1895.55 | 3047.742 | 4943.292 | 1994 | May | 1994-05-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2019 | 1932.45 | 2187.193 | 4119.643 | 121.1 | 1155.154 | 1276.254 | 2053.55 | 3342.347 | 5395.897 | 1994 | Jun | 1994-06-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2020 | 2064.75 | 2235.091 | 4299.841 | 121.1 | 1155.154 | 1276.254 | 2185.85 | 3390.245 | 5576.095 | 1994 | Jul | 1994-07-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
2021 Sep | 2074.05 |  |  | 121.1 | 1155.154 | 1276.254 | 2195.15 |  |  | 1994 | Aug | 1994-08-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
Data Sources: | [9 empty] | 1994 | Sep | 1994-09-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
Ireland TSO (Transmission-Connected) Wind: EirGrid. Updated 01-Oct-2021. | [9 empty] | 1994 | Oct | 1994-10-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
Ireland DSO (Distribution-Connected/Energised) Wind: ESB Networks. Updated 15-Jan-2021. | [9 empty] | 1994 | Nov | 1994-11-01 | 0 | 6.45 | 6.45 | 0 | 0 | 0 | 6.45
Northern Ireland TSO & DSO (Transmission & Distribution-Connected) Wind: SONI & NIE. Updated 17-May-2019. | [9 empty] | 1994 | Dec | 1994-12-01 | 0 | 6.45 | 6.45 | 0 | 5.791 | 5.791 | 12.241
Notes: | [9 empty] | 1995 | Jan | 1995-01-01 | 0 | 6.45 | 6.45 | 0 | 5.791 | 5.791 | 12.241
1. The figures are updated with the best information available at the time of publication. | [9 empty] | 1995 | Feb | 1995-02-01 | 0 | 6.45 | 6.45 | 0 | 11.582 | 11.582 | 18.032
These Figures may be revised in the future based on the latest updates from our various data sources. | [9 empty] | 1995 | Mar | 1995-03-01 | 0 | 6.45 | 6.45 | 0 | 11.582 | 11.582 | 18.032
2. Ireland's DSO-connected wind installed capacities are currently unavailable. MEC values used instead. | [9 empty] | 1995 | Apr | 1995-04-01 | 0 | 6.45 | 6.45 | 0 | 11.582 | 11.582 | 18.032
3. Knockacummer windfarm (100 MW) has switched from a DSO to a TSO connection. Figures amended accordingly. | [9 empty] | 1995 | May | 1995-05-01 | 0 | 6.45 | 6.45 | 0 | 11.582 | 11.582 | 18.032
4. Northern Ireland small scale wind connection dates are unavailable - best estimates are used instead. | [9 empty] | 1995 | Jun | 1995-06-01 | 0 | 6.45 | 6.45 | 0 | 11.582 | 11.582 | 18.032
More detailed information on connected and contracted generators in Ireland is available on our website: | [9 empty] | 1995 | Jul | 1995-07-01 | 0 | 6.45 | 6.45 | 0 | 11.582 | 11.582 | 18.032
http://www.eirgridgroup.com/customer-and-industry/general-customer-information/connected-and-contracted-generators/ | [9 empty] | 1995 | Aug | 1995-08-01 | 0 | 6.45 | 6.45 | 0 | 11.582 | 11.582 | 18.032
[10 empty] | 1995 | Sep | 1995-09-01 | 0 | 6.45 | 6.45 | 0 | 11.582 | 11.582 | 18.032
[10 empty] | 1995 | Oct | 1995-10-01 | 0 | 6.45 | 6.45 | 0 | 17.373 | 17.373 | 23.823
[10 empty] | 1995 | Nov | 1995-11-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1995 | Dec | 1995-12-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1996 | Jan | 1996-01-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1996 | Feb | 1996-02-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1996 | Mar | 1996-03-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1996 | Apr | 1996-04-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1996 | May | 1996-05-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1996 | Jun | 1996-06-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1996 | Jul | 1996-07-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1996 | Aug | 1996-08-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1996 | Sep | 1996-09-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1996 | Oct | 1996-10-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1996 | Nov | 1996-11-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1996 | Dec | 1996-12-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1997 | Jan | 1997-01-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1997 | Feb | 1997-02-01 | 0 | 6.45 | 6.45 | 0 | 23.164 | 23.164 | 29.614
[10 empty] | 1997 | Mar | 1997-03-01 | 0 | 11.25 | 11.25 | 0 | 29.534 | 29.534 | 40.784
[10 empty] | 1997 | Apr | 1997-04-01 | 0 | 11.25 | 11.25 | 0 | 29.534 | 29.534 | 40.784
[10 empty] | 1997 | May | 1997-05-01 | 0 | 11.25 | 11.25 | 0 | 29.534 | 29.534 | 40.784
[10 empty] | 1997 | Jun | 1997-06-01 | 0 | 11.25 | 11.25 | 0 | 29.534 | 29.534 | 40.784
[10 empty] | 1997 | Jul | 1997-07-01 | 15 | 16.23 | 31.23 | 0 | 29.534 | 29.534 | 60.764
[10 empty] | 1997 | Aug | 1997-08-01 | 15 | 21.03 | 36.03 | 0 | 29.534 | 29.534 | 65.564
[10 empty] | 1997 | Sep | 1997-09-01 | 15 | 21.03 | 36.03 | 0 | 29.534 | 29.534 | 65.564
[10 empty] | 1997 | Oct | 1997-10-01 | 15 | 21.03 | 36.03 | 0 | 29.534 | 29.534 | 65.564
[10 empty] | 1997 | Nov | 1997-11-01 | 15 | 21.03 | 36.03 | 0 | 29.534 | 29.534 | 65.564
[10 empty] | 1997 | Dec | 1997-12-01 | 15 | 42.23 | 57.23 | 0 | 29.534 | 29.534 | 86.764
[10 empty] | 1998 | Jan | 1998-01-01 | 15 | 42.23 | 57.23 | 0 | 29.534 | 29.534 | 86.764
[10 empty] | 1998 | Feb | 1998-02-01 | 15 | 42.23 | 57.23 | 0 | 29.534 | 29.534 | 86.764
[10 empty] | 1998 | Mar | 1998-03-01 | 15 | 42.23 | 57.23 | 0 | 29.534 | 29.534 | 86.764
[10 empty] | 1998 | Apr | 1998-04-01 | 15 | 47.23 | 62.23 | 0 | 29.534 | 29.534 | 91.764
[10 empty] | 1998 | May | 1998-05-01 | 15 | 47.23 | 62.23 | 0 | 29.534 | 29.534 | 91.764
[10 empty] | 1998 | Jun | 1998-06-01 | 15 | 47.23 | 62.23 | 0 | 29.534 | 29.534 | 91.764
[10 empty] | 1998 | Jul | 1998-07-01 | 15 | 47.23 | 62.23 | 0 | 29.534 | 29.534 | 91.764
[10 empty] | 1998 | Aug | 1998-08-01 | 15 | 47.23 | 62.23 | 0 | 29.534 | 29.534 | 91.764
[10 empty] | 1998 | Sep | 1998-09-01 | 15 | 47.23 | 62.23 | 0 | 29.534 | 29.534 | 91.764
[10 empty] | 1998 | Oct | 1998-10-01 | 15 | 47.23 | 62.23 | 0 | 29.534 | 29.534 | 91.764
[10 empty] | 1998 | Nov | 1998-11-01 | 15 | 47.23 | 62.23 | 0 | 29.534 | 29.534 | 91.764
[10 empty] | 1998 | Dec | 1998-12-01 | 15 | 47.23 | 62.23 | 0 | 29.534 | 29.534 | 91.764
[10 empty] | 1999 | Jan | 1999-01-01 | 15 | 49.87 | 64.87 | 0 | 30.576 | 30.576 | 95.446
[10 empty] | 1999 | Feb | 1999-02-01 | 15 | 50.56 | 65.56 | 0 | 30.576 | 30.576 | 96.136
[10 empty] | 1999 | Mar | 1999-03-01 | 15 | 50.56 | 65.56 | 0 | 30.576 | 30.576 | 96.136
[10 empty] | 1999 | Apr | 1999-04-01 | 15 | 50.56 | 65.56 | 0 | 30.576 | 30.576 | 96.136
[10 empty] | 1999 | May | 1999-05-01 | 15 | 50.56 | 65.56 | 0 | 30.576 | 30.576 | 96.136
[10 empty] | 1999 | Jun | 1999-06-01 | 15 | 50.56 | 65.56 | 0 | 30.576 | 30.576 | 96.136
[10 empty] | 1999 | Jul | 1999-07-01 | 15 | 50.56 | 65.56 | 0 | 30.576 | 30.576 | 96.136
[10 empty] | 1999 | Aug | 1999-08-01 | 15 | 50.56 | 65.56 | 0 | 30.576 | 30.576 | 96.136
[10 empty] | 1999 | Sep | 1999-09-01 | 15 | 50.56 | 65.56 | 0 | 30.576 | 30.576 | 96.136
[10 empty] | 1999 | Oct | 1999-10-01 | 15 | 50.56 | 65.56 | 0 | 30.576 | 30.576 | 96.136
[10 empty] | 1999 | Nov | 1999-11-01 | 15 | 55.18 | 70.18 | 0 | 30.576 | 30.576 | 100.756
[10 empty] | 1999 | Dec | 1999-12-01 | 15 | 55.18 | 70.18 | 0 | 30.576 | 30.576 | 100.756
[10 empty] | 2000 | Jan | 2000-01-01 | 15 | 55.18 | 70.18 | 0 | 30.576 | 30.576 | 100.756
[10 empty] | 2000 | Feb | 2000-02-01 | 15 | 55.18 | 70.18 | 0 | 30.576 | 30.576 | 100.756
[10 empty] | 2000 | Mar | 2000-03-01 | 15 | 55.18 | 70.18 | 0 | 30.576 | 30.576 | 100.756
[10 empty] | 2000 | Apr | 2000-04-01 | 15 | 55.18 | 70.18 | 0 | 30.576 | 30.576 | 100.756
[10 empty] | 2000 | May | 2000-05-01 | 15 | 55.18 | 70.18 | 0 | 30.576 | 30.576 | 100.756
[10 empty] | 2000 | Jun | 2000-06-01 | 15 | 55.18 | 70.18 | 0 | 30.576 | 30.576 | 100.756
[10 empty] | 2000 | Jul | 2000-07-01 | 15 | 55.18 | 70.18 | 0 | 30.576 | 30.576 | 100.756
[10 empty] | 2000 | Aug | 2000-08-01 | 15 | 55.18 | 70.18 | 0 | 30.576 | 30.576 | 100.756
[10 empty] | 2000 | Sep | 2000-09-01 | 15 | 63.1 | 78.1 | 0 | 30.576 | 30.576 | 108.676
[10 empty] | 2000 | Oct | 2000-10-01 | 15 | 67.06 | 82.06 | 0 | 30.576 | 30.576 | 112.636
[10 empty] | 2000 | Nov | 2000-11-01 | 15 | 89.65 | 104.65 | 0 | 30.576 | 30.576 | 135.226
[10 empty] | 2000 | Dec | 2000-12-01 | 15 | 101.53 | 116.53 | 0 | 30.576 | 30.576 | 147.106
[10 empty] | 2001 | Jan | 2001-01-01 | 15 | 101.53 | 116.53 | 0 | 30.576 | 30.576 | 147.106
[10 empty] | 2001 | Feb | 2001-02-01 | 15 | 101.53 | 116.53 | 0 | 30.576 | 30.576 | 147.106
[10 empty] | 2001 | Mar | 2001-03-01 | 15 | 101.53 | 116.53 | 0 | 30.576 | 30.576 | 147.106
[10 empty] | 2001 | Apr | 2001-04-01 | 15 | 101.53 | 116.53 | 0 | 30.576 | 30.576 | 147.106
[10 empty] | 2001 | May | 2001-05-01 | 15 | 101.53 | 116.53 | 0 | 30.576 | 30.576 | 147.106
[10 empty] | 2001 | Jun | 2001-06-01 | 15 | 101.53 | 116.53 | 0 | 30.576 | 30.576 | 147.106
[10 empty] | 2001 | Jul | 2001-07-01 | 15 | 101.53 | 116.53 | 0 | 30.576 | 30.576 | 147.106
[10 empty] | 2001 | Aug | 2001-08-01 | 15 | 104.53 | 119.53 | 0 | 30.576 | 30.576 | 150.106
[10 empty] | 2001 | Sep | 2001-09-01 | 15 | 107.93 | 122.93 | 0 | 30.576 | 30.576 | 153.506
[10 empty] | 2001 | Oct | 2001-10-01 | 15 | 107.93 | 122.93 | 0 | 30.576 | 30.576 | 153.506
[10 empty] | 2001 | Nov | 2001-11-01 | 15 | 107.93 | 122.93 | 0 | 30.576 | 30.576 | 153.506
[10 empty] | 2001 | Dec | 2001-12-01 | 15 | 107.93 | 122.93 | 0 | 30.576 | 30.576 | 153.506
[10 empty] | 2002 | Jan | 2002-01-01 | 15 | 107.93 | 122.93 | 0 | 30.576 | 30.576 | 153.506
[10 empty] | 2002 | Feb | 2002-02-01 | 15 | 107.93 | 122.93 | 0 | 30.576 | 30.576 | 153.506
[10 empty] | 2002 | Mar | 2002-03-01 | 15 | 107.93 | 122.93 | 0 | 30.576 | 30.576 | 153.506
[10 empty] | 2002 | Apr | 2002-04-01 | 15 | 107.93 | 122.93 | 0 | 30.576 | 30.576 | 153.506
[10 empty] | 2002 | May | 2002-05-01 | 15 | 107.93 | 122.93 | 0 | 30.576 | 30.576 | 153.506
[10 empty] | 2002 | Jun | 2002-06-01 | 15 | 107.93 | 122.93 | 0 | 30.576 | 30.576 | 153.506
[10 empty] | 2002 | Jul | 2002-07-01 | 15 | 107.93 | 122.93 | 0 | 30.576 | 30.576 | 153.506
[10 empty] | 2002 | Aug | 2002-08-01 | 15 | 119.83 | 134.83 | 0 | 30.576 | 30.576 | 165.406
[10 empty] | 2002 | Sep | 2002-09-01 | 15 | 119.83 | 134.83 | 0 | 30.576 | 30.576 | 165.406
[10 empty] | 2002 | Oct | 2002-10-01 | 15 | 119.83 | 134.83 | 0 | 30.576 | 30.576 | 165.406
[10 empty] | 2002 | Nov | 2002-11-01 | 15 | 119.83 | 134.83 | 0 | 30.576 | 30.576 | 165.406
[10 empty] | 2002 | Dec | 2002-12-01 | 15 | 119.83 | 134.83 | 0 | 30.576 | 30.576 | 165.406
[10 empty] | 2003 | Jan | 2003-01-01 | 15 | 119.83 | 134.83 | 0 | 30.576 | 30.576 | 165.406
[10 empty] | 2003 | Feb | 2003-02-01 | 15 | 119.83 | 134.83 | 0 | 30.576 | 30.576 | 165.406
[10 empty] | 2003 | Mar | 2003-03-01 | 15 | 119.83 | 134.83 | 0 | 30.576 | 30.576 | 165.406
[10 empty] | 2003 | Apr | 2003-04-01 | 15 | 119.83 | 134.83 | 0 | 75.977 | 75.977 | 210.807
[10 empty] | 2003 | May | 2003-05-01 | 40 | 123.23 | 163.23 | 0 | 75.977 | 75.977 | 239.207
[10 empty] | 2003 | Jun | 2003-06-01 | 40 | 123.23 | 163.23 | 0 | 75.977 | 75.977 | 239.207
[10 empty] | 2003 | Jul | 2003-07-01 | 40 | 123.89 | 163.89 | 0 | 75.977 | 75.977 | 239.867
[10 empty] | 2003 | Aug | 2003-08-01 | 40 | 126.44 | 166.44 | 0 | 75.977 | 75.977 | 242.417
[10 empty] | 2003 | Sep | 2003-09-01 | 40 | 126.44 | 166.44 | 0 | 75.977 | 75.977 | 242.417
[10 empty] | 2003 | Oct | 2003-10-01 | 40 | 126.44 | 166.44 | 0 | 75.977 | 75.977 | 242.417
[10 empty] | 2003 | Nov | 2003-11-01 | 40 | 170.34 | 210.34 | 0 | 75.977 | 75.977 | 286.317
[10 empty] | 2003 | Dec | 2003-12-01 | 40 | 170.34 | 210.34 | 0 | 75.977 | 75.977 | 286.317
[10 empty] | 2004 | Jan | 2004-01-01 | 40 | 172.89 | 212.89 | 0 | 91.613 | 91.613 | 304.503
[10 empty] | 2004 | Feb | 2004-02-01 | 40 | 172.89 | 212.89 | 0 | 91.613 | 91.613 | 304.503
[10 empty] | 2004 | Mar | 2004-03-01 | 40 | 175.44 | 215.44 | 0 | 91.613 | 91.613 | 307.053
[10 empty] | 2004 | Apr | 2004-04-01 | 40 | 178.84 | 218.84 | 0 | 91.613 | 91.613 | 310.453
[10 empty] | 2004 | May | 2004-05-01 | 40 | 187.15 | 227.15 | 0 | 91.613 | 91.613 | 318.763
[10 empty] | 2004 | Jun | 2004-06-01 | 40 | 187.15 | 227.15 | 0 | 91.613 | 91.613 | 318.763
[10 empty] | 2004 | Jul | 2004-07-01 | 40 | 187.15 | 227.15 | 0 | 91.613 | 91.613 | 318.763
[10 empty] | 2004 | Aug | 2004-08-01 | 40 | 187.15 | 227.15 | 0 | 91.613 | 91.613 | 318.763
[10 empty] | 2004 | Sep | 2004-09-01 | 40 | 196.4 | 236.4 | 0 | 91.613 | 91.613 | 328.013
[10 empty] | 2004 | Oct | 2004-10-01 | 112.4 | 196.4 | 308.8 | 0 | 91.613 | 91.613 | 400.413
[10 empty] | 2004 | Nov | 2004-11-01 | 112.4 | 211.4 | 323.8 | 0 | 91.613 | 91.613 | 415.413
[10 empty] | 2004 | Dec | 2004-12-01 | 112.4 | 224.02 | 336.42 | 0 | 91.613 | 91.613 | 428.033
[10 empty] | 2005 | Jan | 2005-01-01 | 112.4 | 229.97 | 342.37 | 0 | 91.613 | 91.613 | 433.983
[10 empty] | 2005 | Feb | 2005-02-01 | 112.4 | 229.97 | 342.37 | 0 | 91.613 | 91.613 | 433.983
[10 empty] | 2005 | Mar | 2005-03-01 | 112.4 | 235.07 | 347.47 | 0 | 91.613 | 91.613 | 439.083
[10 empty] | 2005 | Apr | 2005-04-01 | 112.4 | 240.06 | 352.46 | 0 | 124.621 | 124.621 | 477.081
[10 empty] | 2005 | May | 2005-05-01 | 143.9 | 240.06 | 383.96 | 0 | 124.621 | 124.621 | 508.581
[10 empty] | 2005 | Jun | 2005-06-01 | 143.9 | 240.06 | 383.96 | 0 | 124.621 | 124.621 | 508.581
[10 empty] | 2005 | Jul | 2005-07-01 | 143.9 | 242.61 | 386.51 | 0 | 124.621 | 124.621 | 511.131
[10 empty] | 2005 | Aug | 2005-08-01 | 163.4 | 242.61 | 406.01 | 0 | 124.621 | 124.621 | 530.631
[10 empty] | 2005 | Sep | 2005-09-01 | 163.4 | 261.02 | 424.42 | 0 | 124.621 | 124.621 | 549.041
[10 empty] | 2005 | Oct | 2005-10-01 | 222.9 | 270.37 | 493.27 | 0 | 124.621 | 124.621 | 617.891
[10 empty] | 2005 | Nov | 2005-11-01 | 222.9 | 270.37 | 493.27 | 0 | 124.621 | 124.621 | 617.891
[10 empty] | 2005 | Dec | 2005-12-01 | 222.9 | 270.37 | 493.27 | 0 | 124.621 | 124.621 | 617.891
[10 empty] | 2006 | Jan | 2006-01-01 | 222.9 | 275.97 | 498.87 | 0 | 144.194 | 144.194 | 643.064
[10 empty] | 2006 | Feb | 2006-02-01 | 222.9 | 280.92 | 503.82 | 0 | 144.194 | 144.194 | 648.014
[10 empty] | 2006 | Mar | 2006-03-01 | 267.9 | 306.92 | 574.82 | 0 | 144.194 | 144.194 | 719.014
[10 empty] | 2006 | Apr | 2006-04-01 | 267.9 | 306.92 | 574.82 | 0 | 144.194 | 144.194 | 719.014
[10 empty] | 2006 | May | 2006-05-01 | 267.9 | 313.72 | 581.62 | 0 | 144.194 | 144.194 | 725.814
[10 empty] | 2006 | Jun | 2006-06-01 | 267.9 | 317.97 | 585.87 | 0 | 144.194 | 144.194 | 730.064
[10 empty] | 2006 | Jul | 2006-07-01 | 267.9 | 351.17 | 619.07 | 0 | 144.194 | 144.194 | 763.264
[10 empty] | 2006 | Aug | 2006-08-01 | 267.9 | 405.17 | 673.07 | 0 | 144.194 | 144.194 | 817.264
[10 empty] | 2006 | Sep | 2006-09-01 | 267.9 | 405.17 | 673.07 | 0 | 144.194 | 144.194 | 817.264
[10 empty] | 2006 | Oct | 2006-10-01 | 267.9 | 405.17 | 673.07 | 0 | 144.194 | 144.194 | 817.264
[10 empty] | 2006 | Nov | 2006-11-01 | 267.9 | 408.57 | 676.47 | 0 | 144.194 | 144.194 | 820.664
[10 empty] | 2006 | Dec | 2006-12-01 | 267.9 | 408.57 | 676.47 | 0 | 144.194 | 144.194 | 820.664
[10 empty] | 2007 | Jan | 2007-01-01 | 267.9 | 416.07 | 683.97 | 0 | 144.194 | 144.194 | 828.164
[10 empty] | 2007 | Feb | 2007-02-01 | 267.9 | 416.07 | 683.97 | 0 | 144.194 | 144.194 | 828.164
[10 empty] | 2007 | Mar | 2007-03-01 | 267.9 | 416.07 | 683.97 | 0 | 144.194 | 144.194 | 828.164
[10 empty] | 2007 | Apr | 2007-04-01 | 267.9 | 416.07 | 683.97 | 0 | 154.618 | 154.618 | 838.588
[10 empty] | 2007 | May | 2007-05-01 | 267.9 | 427.06 | 694.96 | 0 | 163.652 | 163.652 | 858.612
[10 empty] | 2007 | Jun | 2007-06-01 | 267.9 | 427.06 | 694.96 | 0 | 163.652 | 163.652 | 858.612
[10 empty] | 2007 | Jul | 2007-07-01 | 300.35 | 427.06 | 727.41 | 0 | 163.652 | 163.652 | 891.062
[10 empty] | 2007 | Aug | 2007-08-01 | 310.85 | 427.06 | 737.91 | 0 | 163.652 | 163.652 | 901.562
[10 empty] | 2007 | Sep | 2007-09-01 | 310.85 | 427.06 | 737.91 | 0 | 177.203 | 177.203 | 915.113
[10 empty] | 2007 | Oct | 2007-10-01 | 310.85 | 427.06 | 737.91 | 0 | 239.745 | 239.745 | 977.655
[10 empty] | 2007 | Nov | 2007-11-01 | 310.85 | 427.06 | 737.91 | 0 | 251.327 | 251.327 | 989.237
[10 empty] | 2007 | Dec | 2007-12-01 | 310.85 | 429.61 | 740.46 | 0 | 251.327 | 251.327 | 991.787
[10 empty] | 2008 | Jan | 2008-01-01 | 310.85 | 437.11 | 747.96 | 0 | 251.327 | 251.327 | 999.287
[10 empty] | 2008 | Feb | 2008-02-01 | 310.85 | 437.11 | 747.96 | 0 | 251.327 | 251.327 | 999.287
[10 empty] | 2008 | Mar | 2008-03-01 | 310.85 | 454.31 | 765.16 | 0 | 251.327 | 251.327 | 1016.487
[10 empty] | 2008 | Apr | 2008-04-01 | 336.35 | 454.5 | 790.85 | 0 | 261.751 | 261.751 | 1052.601
[10 empty] | 2008 | May | 2008-05-01 | 336.35 | 454.5 | 790.85 | 0 | 261.751 | 261.751 | 1052.601
[10 empty] | 2008 | Jun | 2008-06-01 | 417.75 | 471.39 | 889.14 | 0 | 261.751 | 261.751 | 1150.891
[10 empty] | 2008 | Jul | 2008-07-01 | 417.75 | 513.44 | 931.19 | 0 | 261.751 | 261.751 | 1192.941
[10 empty] | 2008 | Aug | 2008-08-01 | 417.75 | 513.44 | 931.19 | 0 | 267.658 | 267.658 | 1198.848
[10 empty] | 2008 | Sep | 2008-09-01 | 417.75 | 513.44 | 931.19 | 0 | 267.658 | 267.658 | 1198.848
[10 empty] | 2008 | Oct | 2008-10-01 | 417.75 | 521.107 | 938.857 | 0 | 267.658 | 267.658 | 1206.515
[10 empty] | 2008 | Nov | 2008-11-01 | 417.75 | 524.507 | 942.257 | 0 | 267.658 | 267.658 | 1209.915
[10 empty] | 2008 | Dec | 2008-12-01 | 417.75 | 524.507 | 942.257 | 0 | 267.658 | 267.658 | 1209.915
[10 empty] | 2009 | Jan | 2009-01-01 | 417.75 | 527.507 | 945.257 | 0 | 348.731 | 348.731 | 1293.988
[10 empty] | 2009 | Feb | 2009-02-01 | 417.75 | 527.507 | 945.257 | 0 | 348.731 | 348.731 | 1293.988
[10 empty] | 2009 | Mar | 2009-03-01 | 432.25 | 527.507 | 959.757 | 0 | 348.731 | 348.731 | 1308.488
[10 empty] | 2009 | Apr | 2009-04-01 | 432.25 | 542.407 | 974.657 | 0 | 348.731 | 348.731 | 1323.388
[10 empty] | 2009 | May | 2009-05-01 | 432.25 | 544.207 | 976.457 | 0 | 348.731 | 348.731 | 1325.188
[10 empty] | 2009 | Jun | 2009-06-01 | 464.75 | 551.607 | 1016.357 | 0 | 348.731 | 348.731 | 1365.088
[10 empty] | 2009 | Jul | 2009-07-01 | 519.15 | 551.607 | 1070.757 | 0 | 348.731 | 348.731 | 1419.488
[10 empty] | 2009 | Aug | 2009-08-01 | 519.15 | 551.607 | 1070.757 | 0 | 348.731 | 348.731 | 1419.488
[10 empty] | 2009 | Sep | 2009-09-01 | 519.15 | 551.607 | 1070.757 | 0 | 348.731 | 348.731 | 1419.488
[10 empty] | 2009 | Oct | 2009-10-01 | 583.25 | 563.357 | 1146.607 | 0 | 348.731 | 348.731 | 1495.338
[10 empty] | 2009 | Nov | 2009-11-01 | 583.25 | 576.357 | 1159.607 | 0 | 348.731 | 348.731 | 1508.338
[10 empty] | 2009 | Dec | 2009-12-01 | 668.75 | 582.557 | 1251.307 | 0 | 348.731 | 348.731 | 1600.038
[10 empty] | 2010 | Jan | 2010-01-01 | 668.75 | 585.107 | 1253.857 | 0 | 348.731 | 348.731 | 1602.588
[10 empty] | 2010 | Feb | 2010-02-01 | 668.75 | 604.907 | 1273.657 | 0 | 348.731 | 348.731 | 1622.388
[10 empty] | 2010 | Mar | 2010-03-01 | 668.75 | 622.907 | 1291.657 | 0 | 348.731 | 348.731 | 1640.388
[10 empty] | 2010 | Apr | 2010-04-01 | 668.75 | 622.907 | 1291.657 | 0 | 348.731 | 348.731 | 1640.388
[10 empty] | 2010 | May | 2010-05-01 | 668.75 | 622.907 | 1291.657 | 0 | 371.895 | 371.895 | 1663.552
[10 empty] | 2010 | Jun | 2010-06-01 | 727.8 | 622.907 | 1350.707 | 0 | 371.895 | 371.895 | 1722.602
[10 empty] | 2010 | Jul | 2010-07-01 | 727.8 | 634.657 | 1362.457 | 0 | 371.895 | 371.895 | 1734.352
[10 empty] | 2010 | Aug | 2010-08-01 | 727.8 | 655.657 | 1383.457 | 0 | 371.895 | 371.895 | 1755.352
[10 empty] | 2010 | Sep | 2010-09-01 | 727.8 | 657.247 | 1385.047 | 0 | 392.163 | 392.163 | 1777.21
[10 empty] | 2010 | Oct | 2010-10-01 | 727.8 | 657.497 | 1385.297 | 0 | 392.163 | 392.163 | 1777.46
[10 empty] | 2010 | Nov | 2010-11-01 | 727.8 | 662.62 | 1390.42 | 0 | 392.163 | 392.163 | 1782.583
[10 empty] | 2010 | Dec | 2010-12-01 | 727.8 | 662.638 | 1390.438 | 0 | 392.163 | 392.163 | 1782.601
[10 empty] | 2011 | Jan | 2011-01-01 | 769.2 | 662.638 | 1431.838 | 0 | 415.327 | 415.327 | 1847.165
[10 empty] | 2011 | Feb | 2011-02-01 | 769.2 | 667.288 | 1436.488 | 0 | 415.327 | 415.327 | 1851.815
[10 empty] | 2011 | Mar | 2011-03-01 | 769.2 | 667.788 | 1436.988 | 0 | 415.327 | 415.327 | 1852.315
[10 empty] | 2011 | Apr | 2011-04-01 | 769.2 | 679.478 | 1448.678 | 0 | 415.327 | 415.327 | 1864.005
[10 empty] | 2011 | May | 2011-05-01 | 769.2 | 679.478 | 1448.678 | 0 | 415.327 | 415.327 | 1864.005
[10 empty] | 2011 | Jun | 2011-06-01 | 769.2 | 691.978 | 1461.178 | 0 | 417.991 | 417.991 | 1879.169
[10 empty] | 2011 | Jul | 2011-07-01 | 769.2 | 691.978 | 1461.178 | 0 | 417.991 | 417.991 | 1879.169
[10 empty] | 2011 | Aug | 2011-08-01 | 769.2 | 727.468 | 1496.668 | 0 | 438.838 | 438.838 | 1935.506
[10 empty] | 2011 | Sep | 2011-09-01 | 769.2 | 753.468 | 1522.668 | 73.6 | 438.838 | 512.438 | 2035.106
[10 empty] | 2011 | Oct | 2011-10-01 | 769.2 | 780.198 | 1549.398 | 73.6 | 438.838 | 512.438 | 2061.836
[10 empty] | 2011 | Nov | 2011-11-01 | 769.2 | 798.898 | 1568.098 | 73.6 | 438.838 | 512.438 | 2080.536
[10 empty] | 2011 | Dec | 2011-12-01 | 769.2 | 815.398 | 1584.598 | 73.6 | 438.838 | 512.438 | 2097.036
[10 empty] | 2012 | Jan | 2012-01-01 | 769.2 | 815.398 | 1584.598 | 73.6 | 438.838 | 512.438 | 2097.036
[10 empty] | 2012 | Feb | 2012-02-01 | 769.2 | 818.798 | 1587.998 | 73.6 | 438.838 | 512.438 | 2100.436
[10 empty] | 2012 | Mar | 2012-03-01 | 769.2 | 818.798 | 1587.998 | 73.6 | 438.838 | 512.438 | 2100.436
[10 empty] | 2012 | Apr | 2012-04-01 | 769.2 | 818.798 | 1587.998 | 73.6 | 497.442 | 571.042 | 2159.04
[10 empty] | 2012 | May | 2012-05-01 | 769.2 | 851.798 | 1620.998 | 73.6 | 497.442 | 571.042 | 2192.04
[10 empty] | 2012 | Jun | 2012-06-01 | 769.2 | 851.928 | 1621.128 | 73.6 | 497.442 | 571.042 | 2192.17
[10 empty] | 2012 | Jul | 2012-07-01 | 769.2 | 886.078 | 1655.278 | 73.6 | 497.442 | 571.042 | 2226.32
[10 empty] | 2012 | Aug | 2012-08-01 | 769.2 | 896.078 | 1665.278 | 73.6 | 497.442 | 571.042 | 2236.32
[10 empty] | 2012 | Sep | 2012-09-01 | 769.2 | 905.078 | 1674.278 | 73.6 | 497.442 | 571.042 | 2245.32
[10 empty] | 2012 | Oct | 2012-10-01 | 769.2 | 934.28 | 1703.48 | 73.6 | 497.442 | 571.042 | 2274.522
[10 empty] | 2012 | Nov | 2012-11-01 | 769.2 | 934.28 | 1703.48 | 73.6 | 497.442 | 571.042 | 2274.522
[10 empty] | 2012 | Dec | 2012-12-01 | 769.2 | 934.28 | 1703.48 | 73.6 | 526.049 | 599.649 | 2303.129
[10 empty] | 2013 | Jan | 2013-01-01 | 769.2 | 941.78 | 1710.98 | 73.6 | 550.371 | 623.971 | 2334.951
[10 empty] | 2013 | Feb | 2013-02-01 | 769.2 | 941.797 | 1710.997 | 73.6 | 550.371 | 623.971 | 2334.968
[10 empty] | 2013 | Mar | 2013-03-01 | 769.2 | 1001.777 | 1770.977 | 73.6 | 566.354 | 639.954 | 2410.931
[10 empty] | 2013 | Apr | 2013-04-01 | 774.2 | 1010.927 | 1785.127 | 73.6 | 566.354 | 639.954 | 2425.081
[10 empty] | 2013 | May | 2013-05-01 | 793.2 | 1010.927 | 1804.127 | 73.6 | 566.354 | 639.954 | 2444.081
[10 empty] | 2013 | Jun | 2013-06-01 | 793.2 | 1019.877 | 1813.077 | 73.6 | 566.354 | 639.954 | 2453.031
[10 empty] | 2013 | Jul | 2013-07-01 | 793.2 | 1023.877 | 1817.077 | 73.6 | 566.354 | 639.954 | 2457.031
[10 empty] | 2013 | Aug | 2013-08-01 | 793.2 | 1023.877 | 1817.077 | 73.6 | 566.354 | 639.954 | 2457.031
[10 empty] | 2013 | Sep | 2013-09-01 | 805.2 | 1069.077 | 1874.277 | 73.6 | 566.354 | 639.954 | 2514.231
[10 empty] | 2013 | Oct | 2013-10-01 | 810.2 | 1069.077 | 1879.277 | 73.6 | 566.354 | 639.954 | 2519.231
[10 empty] | 2013 | Nov | 2013-11-01 | 815.2 | 1069.077 | 1884.277 | 73.6 | 566.354 | 639.954 | 2524.231
[10 empty] | 2013 | Dec | 2013-12-01 | 845.2 | 1078.077 | 1923.277 | 73.6 | 566.354 | 639.954 | 2563.231
[10 empty] | 2014 | Jan | 2014-01-01 | 855.2 | 1154.927 | 2010.127 | 73.6 | 566.354 | 639.954 | 2650.081
[10 empty] | 2014 | Feb | 2014-02-01 | 864.55 | 1167.567 | 2032.117 | 73.6 | 566.354 | 639.954 | 2672.071
[10 empty] | 2014 | Mar | 2014-03-01 | 874.55 | 1167.567 | 2042.117 | 73.6 | 566.354 | 639.954 | 2682.071
[10 empty] | 2014 | Apr | 2014-04-01 | 874.55 | 1167.567 | 2042.117 | 73.6 | 566.354 | 639.954 | 2682.071
[10 empty] | 2014 | May | 2014-05-01 | 912.55 | 1167.567 | 2080.117 | 73.6 | 566.354 | 639.954 | 2720.071
[10 empty] | 2014 | Jun | 2014-06-01 | 912.55 | 1167.867 | 2080.417 | 73.6 | 566.354 | 639.954 | 2720.371
[10 empty] | 2014 | Jul | 2014-07-01 | 939.55 | 1211.967 | 2151.517 | 73.6 | 566.354 | 639.954 | 2791.471
[10 empty] | 2014 | Aug | 2014-08-01 | 951.55 | 1211.967 | 2163.517 | 73.6 | 614.998 | 688.598 | 2852.115
[10 empty] | 2014 | Sep | 2014-09-01 | 963.55 | 1211.967 | 2175.517 | 73.6 | 638.162 | 711.762 | 2887.279
[10 empty] | 2014 | Oct | 2014-10-01 | 1000.55 | 1212.267 | 2212.817 | 73.6 | 638.162 | 711.762 | 2924.579
[10 empty] | 2014 | Nov | 2014-11-01 | 1015.55 | 1212.267 | 2227.817 | 73.6 | 655.535 | 729.135 | 2956.952
[10 empty] | 2014 | Dec | 2014-12-01 | 1046.55 | 1219.867 | 2266.417 | 73.6 | 655.535 | 729.135 | 2995.552
[10 empty] | 2015 | Jan | 2015-01-01 | 1046.55 | 1231.367 | 2277.917 | 73.6 | 655.535 | 729.135 | 3007.052
[10 empty] | 2015 | Feb | 2015-02-01 | 1046.55 | 1232.367 | 2278.917 | 73.6 | 655.535 | 729.135 | 3008.052
[10 empty] | 2015 | Mar | 2015-03-01 | 1046.55 | 1232.367 | 2278.917 | 73.6 | 658.199 | 731.799 | 3010.716
[10 empty] | 2015 | Apr | 2015-04-01 | 1046.55 | 1232.367 | 2278.917 | 73.6 | 658.199 | 731.799 | 3010.716
[10 empty] | 2015 | May | 2015-05-01 | 1051.55 | 1282.267 | 2333.817 | 73.6 | 658.199 | 731.799 | 3065.616
[10 empty] | 2015 | Jun | 2015-06-01 | 1066.55 | 1286.867 | 2353.417 | 73.6 | 658.199 | 731.799 | 3085.216
[10 empty] | 2015 | Jul | 2015-07-01 | 1084.55 | 1286.867 | 2371.417 | 73.6 | 658.199 | 731.799 | 3103.216
[10 empty] | 2015 | Aug | 2015-08-01 | 1084.55 | 1286.867 | 2371.417 | 73.6 | 658.199 | 731.799 | 3103.216
[10 empty] | 2015 | Sep | 2015-09-01 | 1103.55 | 1291.117 | 2394.667 | 73.6 | 658.199 | 731.799 | 3126.466
[10 empty] | 2015 | Oct | 2015-10-01 | 1127.55 | 1291.117 | 2418.667 | 73.6 | 658.199 | 731.799 | 3150.466
[10 empty] | 2015 | Nov | 2015-11-01 | 1132.55 | 1294.717 | 2427.267 | 73.6 | 658.199 | 731.799 | 3159.066
[10 empty] | 2015 | Dec | 2015-12-01 | 1152.55 | 1294.717 | 2447.267 | 73.6 | 677.425 | 751.025 | 3198.292
[10 empty] | 2016 | Jan | 2016-01-01 | 1162.55 | 1294.717 | 2457.267 | 73.6 | 677.425 | 751.025 | 3208.292
[10 empty] | 2016 | Feb | 2016-02-01 | 1172.55 | 1294.717 | 2467.267 | 73.6 | 677.425 | 751.025 | 3218.292
[10 empty] | 2016 | Mar | 2016-03-01 | 1172.55 | 1294.717 | 2467.267 | 73.6 | 677.425 | 751.025 | 3218.292
[10 empty] | 2016 | Apr | 2016-04-01 | 1182.55 | 1297.717 | 2480.267 | 73.6 | 693.755 | 767.355 | 3247.622
[10 empty] | 2016 | May | 2016-05-01 | 1182.55 | 1297.717 | 2480.267 | 73.6 | 693.755 | 767.355 | 3247.622
[10 empty] | 2016 | Jun | 2016-06-01 | 1193.25 | 1297.717 | 2490.967 | 73.6 | 704.41 | 778.01 | 3268.977
[10 empty] | 2016 | Jul | 2016-07-01 | 1193.25 | 1297.717 | 2490.967 | 73.6 | 704.41 | 778.01 | 3268.977
[10 empty] | 2016 | Aug | 2016-08-01 | 1193.25 | 1332.917 | 2526.167 | 73.6 | 704.41 | 778.01 | 3304.177
[10 empty] | 2016 | Sep | 2016-09-01 | 1198.25 | 1350.016 | 2548.266 | 73.6 | 750.135 | 823.735 | 3372.001
[10 empty] | 2016 | Oct | 2016-10-01 | 1228.25 | 1392.216 | 2620.466 | 73.6 | 750.135 | 823.735 | 3444.201
[10 empty] | 2016 | Nov | 2016-11-01 | 1265.65 | 1393.516 | 2659.166 | 73.6 | 767.508 | 841.108 | 3500.274
[10 empty] | 2016 | Dec | 2016-12-01 | 1371.25 | 1423.506 | 2794.756 | 73.6 | 869.023 | 942.623 | 3737.379
[10 empty] | 2017 | Jan | 2017-01-01 | 1371.25 | 1434.106 | 2805.356 | 73.6 | 869.023 | 942.623 | 3747.979
[10 empty] | 2017 | Feb | 2017-02-01 | 1416.25 | 1434.605 | 2850.855 | 73.6 | 933.187 | 1006.787 | 3857.642
[10 empty] | 2017 | Mar | 2017-03-01 | 1416.25 | 1443.404 | 2859.654 | 73.6 | 967.817 | 1041.417 | 3901.071
[10 empty] | 2017 | Apr | 2017-04-01 | 1421.25 | 1443.404 | 2864.654 | 73.6 | 992.313 | 1065.913 | 3930.567
[10 empty] | 2017 | May | 2017-05-01 | 1469.25 | 1457.204 | 2926.454 | 73.6 | 992.313 | 1065.913 | 3992.367
[10 empty] | 2017 | Jun | 2017-06-01 | 1505.5 | 1463.204 | 2968.704 | 73.6 | 1006.79 | 1080.39 | 4049.094
[10 empty] | 2017 | Jul | 2017-07-01 | 1529.5 | 1486.604 | 3016.104 | 73.6 | 1006.79 | 1080.39 | 4096.494
[10 empty] | 2017 | Aug | 2017-08-01 | 1541.5 | 1543.404 | 3084.904 | 121.1 | 1006.79 | 1127.89 | 4212.794
[10 empty] | 2017 | Sep | 2017-09-01 | 1541.5 | 1568.482 | 3109.982 | 121.1 | 1006.79 | 1127.89 | 4237.872
[10 empty] | 2017 | Oct | 2017-10-01 | 1541.5 | 1568.482 | 3109.982 | 121.1 | 1006.79 | 1127.89 | 4237.872
[10 empty] | 2017 | Nov | 2017-11-01 | 1541.5 | 1630.107 | 3171.607 | 121.1 | 1006.79 | 1127.89 | 4299.497
[10 empty] | 2017 | Dec | 2017-12-01 | 1591.5 | 1720.764 | 3312.264 | 121.1 | 1032.618 | 1153.718 | 4465.982
[10 empty] | 2018 | Jan | 2018-01-01 | 1591.5 | 1752.514 | 3344.014 | 121.1 | 1032.618 | 1153.718 | 4497.732
[10 empty] | 2018 | Feb | 2018-02-01 | 1591.5 | 1784.514 | 3376.014 | 121.1 | 1059.256 | 1180.356 | 4556.37
[10 empty] | 2018 | Mar | 2018-03-01 | 1631.1 | 1784.514 | 3415.614 | 121.1 | 1059.256 | 1180.356 | 4595.97
[10 empty] | 2018 | Apr | 2018-04-01 | 1631.1 | 1797.064 | 3428.164 | 121.1 | 1059.256 | 1180.356 | 4608.52
[10 empty] | 2018 | May | 2018-05-01 | 1631.1 | 1797.064 | 3428.164 | 121.1 | 1059.256 | 1180.356 | 4608.52
[10 empty] | 2018 | Jun | 2018-06-01 | 1636.1 | 1810.244 | 3446.344 | 121.1 | 1059.256 | 1180.356 | 4626.7
[10 empty] | 2018 | Jul | 2018-07-01 | 1641.1 | 1814.694 | 3455.794 | 121.1 | 1155.154 | 1276.254 | 4732.048
[10 empty] | 2018 | Aug | 2018-08-01 | 1679.9 | 1814.694 | 3494.594 | 121.1 | 1155.154 | 1276.254 | 4770.848
[10 empty] | 2018 | Sep | 2018-09-01 | 1691.95 | 1846.693 | 3538.643 | 121.1 | 1155.154 | 1276.254 | 4814.897
[10 empty] | 2018 | Oct | 2018-10-01 | 1754.45 | 1849.193 | 3603.643 | 121.1 | 1155.154 | 1276.254 | 4879.897
[10 empty] | 2018 | Nov | 2018-11-01 | 1759.45 | 1849.193 | 3608.643 | 121.1 | 1155.154 | 1276.254 | 4884.897
[10 empty] | 2018 | Dec | 2018-12-01 | 1774.45 | 1892.588 | 3667.038 | 121.1 | 1155.154 | 1276.254 | 4943.292
[10 empty] | 2019 | Jan | 2019-01-01 | 1789.65 | 1893.088 | 3682.738 | 121.1 | 1155.154 | 1276.254 | 4958.992
[10 empty] | 2019 | Feb | 2019-02-01 | 1789.65 | 1893.088 | 3682.738 | 121.1 | 1155.154 | 1276.254 | 4958.992
[10 empty] | 2019 | Mar | 2019-03-01 | 1789.65 | 1911.088 | 3700.738 | 121.1 | 1155.154 | 1276.254 | 4976.992
[10 empty] | 2019 | Apr | 2019-04-01 | 1789.65 | 1913.726 | 3703.376 | 121.1 | 1155.154 | 1276.254 | 4979.63
[10 empty] | 2019 | May | 2019-05-01 | 1789.65 | 1940.176 | 3729.826 | 121.1 | 1155.154 | 1276.254 | 5006.08
[10 empty] | 2019 | Jun | 2019-06-01 | 1794.65 | 1943.675 | 3738.325 | 121.1 | 1155.154 | 1276.254 | 5014.579
[10 empty] | 2019 | Jul | 2019-07-01 | 1794.65 | 1943.675 | 3738.325 | 121.1 | 1155.154 | 1276.254 | 5014.579
[10 empty] | 2019 | Aug | 2019-08-01 | 1814.65 | 1961.635 | 3776.285 | 121.1 | 1155.154 | 1276.254 | 5052.539
[10 empty] | 2019 | Sep | 2019-09-01 | 1878.65 | 2022.615 | 3901.265 | 121.1 | 1155.154 | 1276.254 | 5177.519
[10 empty] | 2019 | Oct | 2019-10-01 | 1882.45 | 2078.654 | 3961.104 | 121.1 | 1155.154 | 1276.254 | 5237.358
[10 empty] | 2019 | Nov | 2019-11-01 | 1887.45 | 2124.154 | 4011.604 | 121.1 | 1155.154 | 1276.254 | 5287.858
[10 empty] | 2019 | Dec | 2019-12-01 | 1932.45 | 2187.193 | 4119.643 | 121.1 | 1155.154 | 1276.254 | 5395.897
[10 empty] | 2020 | Jan | 2020-01-01 | 1962.45 | 2193.692 | 4156.142 | 121.1 | 1155.154 | 1276.254 | 5432.396
[10 empty] | 2020 | Feb | 2020-02-01 | 1999.95 | 2200.292 | 4200.242 | 121.1 | 1155.154 | 1276.254 | 5476.496
[10 empty] | 2020 | Mar | 2020-03-01 | 1999.95 | 2213.291 | 4213.241 | 121.1 | 1155.154 | 1276.254 | 5489.495
[10 empty] | 2020 | Apr | 2020-04-01 | 2019.75 | 2227.091 | 4246.841 | 121.1 | 1155.154 | 1276.254 | 5523.095
[10 empty] | 2020 | May | 2020-05-01 | 2019.75 | 2227.091 | 4246.841 | 121.1 | 1155.154 | 1276.254 | 5523.095
[10 empty] | 2020 | Jun | 2020-06-01 | 2019.75 | 2227.091 | 4246.841 | 121.1 | 1155.154 | 1276.254 | 5523.095
[10 empty] | 2020 | Jul | 2020-07-01 | 2019.75 | 2227.091 | 4246.841 | 121.1 | 1155.154 | 1276.254 | 5523.095
[10 empty] | 2020 | Aug | 2020-08-01 | 2019.75 | 2227.091 | 4246.841 | 121.1 | 1155.154 | 1276.254 | 5523.095
[10 empty] | 2020 | Sep | 2020-09-01 | 2019.75 | 2227.091 | 4246.841 | 121.1 | 1155.154 | 1276.254 | 5523.095
[10 empty] | 2020 | Oct | 2020-10-01 | 2019.75 | 2235.091 | 4254.841 | 121.1 | 1155.154 | 1276.254 | 5531.095
[10 empty] | 2020 | Nov | 2020-11-01 | 2019.75 | 2235.091 | 4254.841 | 121.1 | 1155.154 | 1276.254 | 5531.095
[10 empty] | 2020 | Dec | 2020-12-01 | 2064.75 | 2235.091 | 4299.841 | 121.1 | 1155.154 | 1276.254 | 5576.095
[10 empty] | 2021 | Jan | 2021-01-01 | 2074.05 |  |  | 121.1 | 1155.154 | 1276.254
[10 empty] | 2021 | Feb | 2021-02-01 | 2074.05 |  |  | 121.1 | 1155.154 | 1276.254
[10 empty] | 2021 | Mar | 2021-03-01 | 2074.05 |  |  | 121.1 | 1155.154 | 1276.254
[10 empty] | 2021 | Apr | 2021-04-01 | 2074.05 |  |  | 121.1 | 1155.154 | 1276.254
[10 empty] | 2021 | May | 2021-05-01 | 2074.05 |  |  | 121.1 | 1155.154 | 1276.254
[10 empty] | 2021 | Jun | 2021-06-01 | 2074.05 |  |  | 121.1 | 1155.154 | 1276.254

## Connected Windfarm Lists
Transmission Connected Windfarms in Ireland | [14 empty] | Distribution Connected Windfarms in Ireland | [10 empty] | Connected Windfarms in Northern Ireland
Source: EirGrid - Last updated 01-Oct-2021 | [14 empty] | Source: ESBN - Last updated 15-Jan-2021 | [10 empty] | Sources: SONI and NIE - Last updated 17-May-2019
More information on connected generators in Ireland can be found online: | [14 empty] | More information on connected generators in Ireland can be found online:
http://www.eirgridgroup.com/customer-and-industry/general-customer-information/connected-and-contracted-generators/ | [14 empty] | http://www.eirgridgroup.com/customer-and-industry/general-customer-information/connected-and-contracted-generators/
No | Type | Category | Gate | Ref. Code | Generator | Phase | Connection Full / Partial | Maximum Export Capacity (MW) | Installed Capacity (MW) | Full / Latest Connection Date | Notes | County | No of Turbines | Controllable | Reference | DSO Windfarm | Type | MEC (MW) | 110kV Station | Connection Voltage | No of Turbines | Offer Type | Status | Estimated Connection Date | Higlighted dates are best estimates | Project Name | Total Installed Capacity (MW) | MEC (MW) | FAQ (MW) | Status | Estimated Connection Dates | TSO / DNO Connection | Generation Technology(s) | Controllable/ Uncontrollable
1 | Wind | Onshore | PG | P25 | Golagh | 1 | Full | 15 | 15 | 1997-07-01 |  | Donegal | 25 | N | DG405a | Cappawhite A Wind Farm (Gate 3) | Wind | 49.08 | Cauteen | 38 kV | 17 | Gate 3 | Energised | 2017-08-11 |  | Altahullion 1 | 26 | 26 | 26 | Connected | 2003-04-04 | Distribution | Wind | Uncontrollable
2 | Wind | Onshore | PG | P38A | Kingsmountain | 1 | Full | 23.75 | 25 | 2003-05-01 |  | Sligo | 10 | N | DG290 | Cleanrath Wind Farm | Wind | 42.64 | Coomataggart | 38 kV | 15 | Gate 3 | Energised | 2019-10-30 |  | Altahullion 2 | 11.7 | 11.7 | 11.7 | Connected | 2007-09-27 | Distribution | Wind | Controllable
3 | Wind | Onshore | PG | P38BDF | Meentycat | 1 | Full | 70.96 | 72.4 | 2004-10-01 |  | Donegal | 38 | Y | DG82 | Knocknagoum (1) | Wind | 42.55 | Reamore | 38 kV | 11, 5, 5, 4 | Gate 2 | Energised | 2013-09-01 |  | Altamuskin | 14.1 | 14.1 | 0 | Connected | 2017-02-08 | Distribution | Wind | Controllable
4 | Wind | Onshore | PG | TG13 | Ballywater | 1 | Full | 31.5 | 31.5 | 2005-05-01 |  | Wexford | 16 | Y | DG94 | Leitir Guingaid Wind Farm | Wind | 40.9 | Salthill | 38 kV | 4, 6, 7 | Gate 3 | Energised | 2014-01-31 |  | Altaveedan | 21.15 | 18 | 0 | Connected | 2017-04-07 | Distribution | Wind | Controllable
5 | Wind | Onshore | PG | TG07 | Booltiagh | 1 | Full | 19.45 | 19.5 | 2005-08-01 |  | Clare | 13 | Y | DG291 | Magheramore and Cloontooa Wind Farm | Wind | 40.8 | Dalton | 38 kV | 18 | Gate 3 | Energised | 2018-12-12 |  | Bessy Bell | 5 | 5 | 5 | Connected | 1995-10-01 | Distribution | Wind | Uncontrollable
6 | Wind | Onshore | PG | P33 | Derrybrien | 1 | Full | 59.5 | 59.5 | 2005-10-01 | Gort | Galway | 70 | Y | TG84 | Bruckana | Wind | 39.6 | Lisheen | 38 kV | 14 | Gate 3 | Energised | 2014-07-16 |  | Bessy Bell 2 | 9 | 9 | 9 | Connected | 2008-04-22 | Distribution | Wind | Controllable
7 | Wind | Onshore | PG | TG11 | Coomagearlahy | 1 | Full | 42.5 | 45 | 2006-03-01 |  | Kerry | 15 | Y | TG30 | Boolynagleragh (1) | Wind | 36.98 | Booltiagh | 38 kV | 16 | Gate 3 | Energised | 2019-09-03 |  | Bin Mountain | 9 | 9 | 9 | Connected | 2007-04-13 | Distribution | Wind | Controllable
8 | Wind | Onshore | 1 | TG47 | Midas | 1 | Full | 29.8 | 32.45 | 2007-07-01 | Glanlee 1 | Kerry | 23 | Y | DG90 | Garracummer Wind Farm | Wind | 36.9 | Cauteen | 38 kV | 17 | Gate 2 | Connected | 2013-03-05 |  | Brackagh Quarry | 4.98 | 4.98 | N/A | Connected | 2016-09-20 | Distribution | Wind | Uncontrollable
9 | Wind | Onshore | 2 | TG35 | Ballywater | 2 | Full | 10.5 | 10.5 | 2007-08-01 |  | Wexford | 5 | Y | DG71 | Scartaglen Wind Farm | Wind | 35.45 | Cordal | 38 kV | 10+5 | Gate 2 | Energised | 2017-12-12 |  | Brett Martin | 2.3 | 0 | N/A | Connected | 2011-06-30 | Distribution | Wind | Uncontrollable
10 | Wind | Onshore | PG | TG06 | Mountain Lodge | 1 | Full | 24.8 | 25.5 | 2008-04-01 |  | Cavan | 17 | Y | TG45 | Raheenleagh (1) | Wind | 35.2 | Arklow | 38 kV | 11 | Gate 3 | Energised | 2016-08-04 |  | Brockaghboy | 47.5 | 47.5 | 0 | Connected | 2017-08-29 | Transmission | Wind | Controllable
11 | Wind | Onshore | 1 | TG12 | Pallas | 1 | Full | 37.8 | 40 | 2008-06-01 | Clahane 1 | Kerry | 20 | Y | DG159 | Carrowleagh Wind Farm (1) | Wind | 34.15 | Glenree | 38 kV | 16 | Gate 2 | Connected | 2012-07-30 |  | Callagheen | 16.9 | 16.9 | 16.9 | Connected | 2006-01-16 | Distribution | Wind | Controllable
12 | Wind | Onshore | 1 | TG18 | Coomacheo | 1 | Full | 41.225 | 41.4 | 2008-06-01 |  | Cork | 18 | Y | DG420 | Derrysallagh Wind Farm (Formerly Kilronan 2) | Wind | 34 | GARVAGH | 38 kV |  | Gate 3 | Energised | 2019-11-30 |  | Carn Hill | 13.8 | 13.8 | 13.8 | Connected | 2013-03-20 | Distribution | Wind | Controllable
13 | Wind | Onshore | 2 | TG50 | Coomagearlahy | 2 | Full | 8.5 | 8.5 | 2009-03-01 |  | Kerry | 10 | Y | TG31 | Castlepook (1) | Wind | 33.1 | Charleville | 38 kV | 14 | Gate 3 | Energised | 2017-11-28 |  | Carrickatane | 24.7 | 20.7 | 20.7 | Connected | 2012-12-12 | Distribution | Wind | Controllable
14 | Wind | Onshore | 2 | TG52 | Mountain Lodge | 3 | Full | 5.82 | 6 | 2009-03-01 |  | Cavan | 4 | Y | DG181 | Glencarbry Wind Farm | Wind | 33 | Cauteen | 38 kV | 12 | Gate 3 | Energised | 2016-10-01 |  | Castlecraig | 25 | 25 | 4.125 | Connected | 2018-07-01 | Distribution | Wind | TBC
15 | Wind | Onshore | 2 | TG54 | Coomagearlahy | 3 | Full | 30 | 32.5 | 2009-06-01 |  | Kerry | 13 | Y | DG68 | Glenough Wind Farm | Wind | 33 | Cauteen | 38 kV | 10 + 4 | Gate 2 | Connected | 2012-05-23 |  | Church Hill | 18.4 | 18.4 | 18.4 | Connected | 2012-04-05 | Distribution | Wind | Controllable
16 | Wind | Onshore | 2 | DG187 | Coomacheo | 2 | Full | 18 | 18.4 | 2009-07-01 |  | Cork | 8 | Y | DG136b | Monaincha Bog Wind Farm (Gate 3) | Wind | 32.55 | Ikerrin | 38 kV | 15 | Gate 3 | Energised | 2014-01-31 |  | Cloonty | 9.2 | 9.2 | 0 | Connected | 2016-06-09 | Distribution | Wind | Controllable
17 | Wind | Onshore | 2 | TG55 | Lisheen | 1 | Full | 36 | 36 | 2009-07-01 |  | Tipperary | 18 | Y | DG134 | Barranafaddock Wind Farm | Wind | 32.4 | Barrymore | 38 kV | 12 | Gate 3 | Energised | 2015-05-01 |  | Corkey | 5 | 5 | 5 | Connected | 1994-12-20 | Distribution | Wind | Uncontrollable
18 | Wind | Onshore | 1 | TG65 | Meentycat | 2 | Full | 14 | 16.1 | 2009-10-01 |  | Donegal | 7 | Y | DG909 | Sorne Hill Wind Farm | Wind | 31.5 | SORNE HILL | 110 kV | 16 | Pre-Gate | Connected | 2006-07-01 |  | Cornavarrow | 38.4 | 36 | 0 | Connected | 2018-07-01 | Distribution | Wind | TBC
19 | Wind | Onshore | PG | P38-1 | Bindoo | 1a | Full | 48 | 48 | 2009-10-01 | Ratrussan | Cavan | 32 | Y | DG160 | Bunnyconnellan Wind Farm | Wind | 28 | Glenree | 38 kV | 12 | Gate 2 | Energised | 2019-12-04 |  | Cregganconroe | 13.8 | 13.8 | 0 | Connected | 2016-12-15 | Distribution | Wind | Controllable
20 | Wind | Onshore | 2 | TG29 | Boggeragh | 1 | Full | 57 | 57 | 2009-12-01 |  | Cork | 19 | Y | DG26 | Taurbeg Wind Farm | Wind | 26 | Glenlara | 38 kV | 11 | PMOD | Connected | 2006-03-01 |  | Crigshane | 32.2 | 32.2 | 32.2 | Connected | 2012-04-12 | Distribution | Wind | Controllable
21 | Wind | Onshore | 2 | DG141 | Dromada | 1 | Full | 28.5 | 28.5 | 2009-12-01 |  | Limerick | 19 | Y | DG934 | Arklow Bank Wind Farm (1) | Wind (Offshore) | 25.2 | Arklow | 38 kV | 7 | Pre-Gate | Connected | 2003-11-01 |  | Crockagarran | 17.5 | 17.5 | 17.5 | Connected | 2010-09-02 | Distribution | Wind | Controllable
22 | Wind | Onshore | 2 | TG23a | Garvagh | 1a | Full | 26 | 26 | 2010-06-01 | Glebe | Leitrim | 13 | Y | TG73 | Sorrell Island (Prev Glenmore) | Wind | 24 | BOOLTIAGH | 38 kV | 9 | Gate 3 | Energised | 2019-09-03 |  | Crockandun | 15 | 15 | 0 | Connected | 2017-02-27 | Distribution | Wind | Controllable
23 | Wind | Onshore | 2 | TG23c | Garvagh | 1c | Full | 22 | 22 | 2010-06-01 | Tullynahaw | Roscommon | 11 | Y | DG58 | Bawnmore (Burren/Carraignimma) | Wind | 24 | Macroom | 38 kV | 6+5 | Gate 2 | Connected | 2011-10-14 |  | Crockbaravally | 7.5 | 7.5 | 0 | Connected | 2017-02-17 | Distribution | Wind | Uncontrollable
24 | Wind | Onshore | 2 | TG40 | Kingsmountain | 2 | Full | 11.05 | 11.05 | 2010-06-01 |  | Sligo | 13 | Y | DG35 | Knockawarriga Wind Farm | Wind | 22.5 | Trien | 38 kV | 9 | Gate 1 | Connected | 2008-07-15 |  | Crockdun | 12.5 | 12.5 | 0 | Connected | 2017-06-26 | Distribution | Wind | Capped
25 | Wind | Onshore | 2 | DG88 | Castledockrell | 1 | Full | 20 | 20.7 | 2011-01-01 |  | Wexford | 9 | Y | DG1049 | Carrickallen Wind Farm | Wind | 22 | Shankill | 38 kV | 10 | Pre-Gate | Energised | 2018-09-10 |  | Curryfree | 18 | 15 | 15 | Connected | 2011-08-01 | Distribution | Wind | Controllable
26 | Wind | Onshore | 2 | DG172 | Castledockrell | 2 | Full | 2 | 2.3 | 2011-01-01 |  | Wexford | 1 | Y | DG69 | Gortahile Wind Farm | Wind | 21 | Carlow | 38 kV | 8 | Gate 2 | Connected | 2010-08-24 |  | Dunbeg | 42 | 42 | 0 | Connected | 2014-08-25 | Distribution | Wind | Controllable
27 | Wind | Onshore | 2 | DG189 | Castledockrell | 3 | Full | 3.3 | 2.3 | 2011-01-01 |  | Wexford | 1 | Y | DG08 | Richfield Wind Farm | Wind | 20.25 | Wexford | 38 kV | 14 | Pre-Gate | Connected | 2006-08-01 |  | Dunmore | 21 | 21 | 0 | Connected | 2013-01-17 | Distribution | Wind | Controllable
28 | Wind | Onshore | 2 | DG201 | Castledockrell | 4 | Full | 16.1 | 16.1 | 2011-01-01 |  | Wexford | 7 | Y | DG152 | Glanaruddery 1 (formerly Dromadda More Wind Farm) | Wind | 20 | Cloghboola | 20 kV | 7 | Gate 2 | Energised | 2018-02-13 |  | Eglish | 15 | 15 | 0 | Connected | 2016-12-12 | Distribution | Wind | Controllable
29 | Wind | Onshore | 2 | TG55a | Lisheen | 2 | Full | 23 | 24 | 2013-05-01 |  | Tipperary | 12 | Y | DG19 | Carraigcannon Wind Farm | Wind | 20 | BOGGERAGH | 38 kV | 10 | PMOD | Connected | 2011-09-01 |  | Elginny Hill | 23 | 23 | 23 | Connected | 2018-02-16 | Distribution | Wind | TBC
30 | Wind | Onshore | 2 | TG38 | Booltiagh | 2 | Full | 12 | 12 | 2013-09-01 | Booltiagh 2 & 3 (TG38 & TG39) | Clare | 6 | Y | DG14 | Ballybane (Glanta Commons) Wind Farm | Wind | 19.55 | Ballylickey | 38 kV | 9 | Pre-Gate | Connected | 2008-07-14 |  | Elliots Hill | 5 | 5 | 5 | Connected | 1995-02-13 | Distribution | Wind | Uncontrollable
31 | Wind | Onshore | 1 | TG22a | Athea | 1a | Full | 34.35 | 34.35 | 2014-02-01 |  | Limerick | 16 | Y | TG59A | Killala Wind Farm (Phase 1) | Wind | 19.2 | TAWNAGHMORE | 38 kV | Phase 1 (6) Phase 2 (TBC) | Gate 3 | Energised | 2019-05-30 |  | Eshmore | 7.05 | 7.05 | 0 | Connected | 2016-12-15 | Distribution | Wind | Uncontrollable
32 | Wind | Onshore | 2 | TG24 | Knockacummer | 1 | Full | 100 | 100 | 2015-07-01 | Glentanemacelligot 1 Switched connection from DSO to TSO in Nov-2018 | Cork | 40 | Y | DG927 | Raheen Barr Wind Farm | Wind | 18.7 | Castlebar | 38 kV | 22 | Pre-Gate | Connected | 2003-11-01 |  | Garves | 15 | 15 | 15 | Connected | 2009-01-27 | Distribution | Wind | Controllable
33 | Wind | Onshore | 3 | TG66 | Mountlucas | 1 | Full | 79.2 | 84 | 2014-11-01 |  | Offaly | 28 | Y | DG122 | Coollegrean Wind Farm | Wind | 18.5 | Cordal | 38 kV | 7 | Gate 2 | Energised | 2018-01-30 |  | Glenbuck | 9.2 | 9.2 | 0 | Connected | 2016-12-13 | Distribution | Wind | Uncontrollable
34 | Wind | Onshore | 3 | TG69 | Kill Hill | 1 | Full | 36 | 36 | 2014-12-01 |  | Tipperary | 16 | Y | DG224 | Knocknatallig Wind Farm (formerly Buttevant Wind Farm) | Wind | 18.3 | Charleville | 38 kV | 6 | Gate 3 | Energised | 2017-11-28 |  | Gortfinbar | 15 | 15 | 0 | Connected | 2016-12-15 | Distribution | Wind | Controllable
35 | Wind | Onshore | 3 | DG135 | Woodhouse | 1 | Full | 20 | 20 | 2015-06-01 |  | Waterford | 8 | Y | DG209 | Ballycumber Wind Farm | Wind | 18 | Arklow | 38 kV | 6 | Gate 3 | Energised | 2019-03-20 |  | Gruig | 25 | 25 | 25 | Connected | 2009-01-27 | Distribution | Wind | Controllable
36 | Wind | Onshore | 2 | DG50 | Cloghboola | 1 | Full | 46 | 48 | 2015-10-01 | Knocknagashel | Kerry | 16 | Y | DG165 | Leanamore Wind Farm (Tarbert Wind Farm) | Wind | 18 | Kilpaddoge | 20 kV | 9 | Gate 3 | Energised | 2017-12-18 |  | Hunters Hill | 20 | 20 | 20 | Connected | 2010-05-13 | Distribution | Wind | Controllable
37 | Wind | Onshore | 3 | TG102 | Boggeragh | 2 | Full | 65.7 | 65.7 | 2016-06-01 | Knockduff + Killavoy 1 (DG200) | Cork | 26 | Y | DG260 | Cronalaght Wind Farm 2 | Wind | 17.96 | Ardnagappary | 38 kV | 5 | Gate 3 | Energised | 2019-08-28 |  | Inishative | 13.8 | 13.8 | 0 | Connected | 2017-03-03 | Distribution | Wind | Controllable
38 | Wind | Onshore | 3 | DG308 | Mulreavy | 2 | Full | 5.4 | 5 | 2016-10-01 | Meenadreen South 2 | Donegal | 2 | Y | TG197 | Acres Wind Farm | Wind | 17.5 | Cathaleens Fall | 38 kV | 6+1(+1) | Gate 3 | Energised | 2015-05-23 |  | Lendrum's Bridge | 13.2 | 13.2 | 13.2 | Connected | 2003-04-01 | Distribution | Wind | Uncontrollable
39 | Wind | Onshore | 3 | TG94 | Sliabh Bawn | 1 | Full | 58 | 64 | 2016-12-01 |  | Roscommon | 20 | Y | DG03 | Tournafulla (2) Wind Farm | Wind | 17.2 | Trien | 38 kV | 17 | Gate 1 | Connected | 2008-03-07 |  | Lisglass | 2.3 | 2.3 | N/A | Connected | 2015-03-09 | Distribution | Wind | Uncontrollable
40 | Wind | Onshore | 2 | TG51 | Mulreavy | 1 | Full | 89.85 | 90 | 2017-02-01 | Mulreavy 1 (82MW)(TG51) + Croaghnameal 1 (4.25MW)(DG198) + Meenadreen South 1 (3.6MW)(DG65) | Donegal | 36 | Y | DG75 | Killaveenoge Windfarm (Derryvacorneen merge with Barrboy Windfarm) | Wind | 17 | Dunmanway | 38 kV | 6 off | Gate 2 | Energised | 2016-12-16 |  | Long Mountain | 27.6 | 27.6 | 24 | Connected | 2016-12-13 | Distribution | Wind | Controllable
41 | Wind | Onshore | 3 | DG92 | Uggool | 1 | Full | 64 | 64 | 2017-02-01 |  | Galway | 22 | Y | DG79 | Dromdeeveen Wind Farm (2) | Wind | 16.5 | Glenlara | 38 kV | DG911 | Gate 2 | Connected | 2011-12-07 |  | Lough Hill | 7.8 | 7.8 | 7.8 | Connected | 2007-05-25 | Distribution | Wind | Controllable
42 | Wind | Onshore | 1 | TG15 | Moneypoint | 1 | Full | 17.25 | 17.25 | 2017-06-01 |  | Clare | 5 | Y | DG404a | Grove Hill Windfarm (formerly Tullynageer WF) | Wind | 16.1 | Dundalk | 38 kV | 6 | Gate 3 | Energised | 2016-09-03 |  | Michelin | 4.6 | 4.6 | N/A | Connected | 2015-12-23 | Distribution | Wind | Uncontrollable
43 | Wind | Onshore | 3 | TG58 | Seecon | 1 | Full | 105 | 108 | 2017-08-01 |  | Galway | 36 | Y | DG25 | Muingnaminnane Wind Farm | Wind | 15.3 | Reamore | 38 kV | 14 + 4 | Gate 1 | Connected | 2010-02-09 |  | Molly Mountain | 15 | 15 | 0 | Connected | 2014-11-27 | Distribution | Wind | Controllable
44 | Wind | Onshore | 2 | DG49 | Cordal | 1 | Full | 35.85 | 35.2 | 2018-03-01 |  | Kerry | 11 | Y | DG78 | Grouse Lodge Wind Farm | Wind | 15 | Rathkeale | 38 kV | 6 | Gate 2 | Connected | 2011-08-31 |  | Monnaboy | 12 | 12 | 0 | Connected | 2015-12-10 | Distribution | Wind | Controllable
45 | Wind | Onshore | 3 | DG272 | Cordal | 2 | Full | 54 | 54.4 | 2018-03-01 | Merged with Cordal 3 | Kerry | 17 | Y | DG941 | Tursillagh Wind Farm | Wind | 15 | Tralee | 38 kV | 23 | Pre-Gate | Connected | 2000-11-01 |  | Ora More | 15 | 15 | 0 | Connected | 2016-11-03 | Distribution | Wind | Controllable
46 | Wind | Onshore | 3 | TG83 | Clahane | 2 | Full | 13.8 | 13.8 | 2018-08-01 |  | Kerry | 6 | Y | DG42a | Cark | Wind | 15 | Letterkenny | 38 kV | 25 | Pre-Gate | Connected | 1997-12-01 |  | Owenreagh 1 | 5.5 | 5.5 | 5.5 | Connected | 1997-03-10 | Distribution | Wind | Uncontrollable
47 | Wind | Onshore | N/A | TG256 | Kelwin | 1 | Full | 37.05 | 37.05 | 2018-09-01 | Hybrid: 37.05 MW Wind (including 2.6MW batteries) + 2 MW Diesel | Kerry | 13 | Y | DG984 | Ballincollig Hill Wind Farm (Lee Strand) | Wind | 15 | Tralee | 38 kV | 18 | Pre-Gate | Connected | 2010-03-04 |  | Owenreagh 2 | 5.1 | 5.1 | 5.1 | Connected | 2008-08-06 | Distribution | Wind | Controllable
48 | Wind | Onshore | 2 | TG49 | Knockalassa | 1 | Full | 26.875 | 27.5 | 2018-10-01 |  | Clare | 11 | Y | DG185 | Gibbet Hill Wind Farm | Wind | 14.8 | Crory | 20 kV | 6 | Gate 2 | Energised | 2013-03-29 |  | Rathsherry | 22.3 | 21.15 | 21.2 | Connected | 2017-12-01 | Distribution | Wind | Controllable
49 | Wind | Onshore | 2&3 | DG73 | Boolinrudda | 1 | Full | 44.515 | 45 | 2018-10-01 | 26.875 MW Gate 2 + 17.64 MW Gate 3 | Clare | 18 | Y | DG30A | Ballycadden Wind Farm (1) | Wind | 14.45 | Crory | 20 kV | 5 | Gate 1 | Connected | 2012-10-12 |  | Rigged Hill | 5 | 5 | 5 | Connected | 1995-11-22 | Distribution | Wind | Uncontrollable
50 | Wind | Onshore | 3 | DG191 | Knockalough | 1 | Full | 33.6 | 35.2 | 2019-01-01 |  | Galway | 11 | Y | DG907 | Beam Hill Wind Farm | Wind | 14 | Trillick | 38 kV | 8 | Pre-Gate | Connected | 2006-08-01 |  | Screggagh | 20 | 20 | 20 | Connected | 2011-01-13 | Distribution | Wind | Controllable
51 | Wind | Onshore | 3 | TG25 | Oweninny | 1 | Full | 89 | 92.8 | 2019-10-01 |  | Mayo | 29 | Y | DG311 | Tullabrack Wind Farm | Wind | 13.8 | Tullabrack | 38 kV | 6 | Gate 3 | Connected | 2017-05-19 |  | Seegronan | 14.1 | 14.1 | 0 | Connected | 2016-04-15 | Distribution | Wind | Controllable
52 | Wind | Onshore | 3 | TG34 | Grousemount | 1 | Full | 114.2 | 114.2 | 2020-04-01 |  | Kerry | 38 | Y | DG234a | Mauricetown (Glenduff) Wind Farm | Wind | 13.8 | Glenlara | 38 kV | 6 | Gate 2 | Energised | 2020-04-16 |  | Shantavny Scotch | 16.1 | 16.1 | 0 | Connected | 2017-03-03 | Distribution | Wind | Controllable
53 | Wind | Onshore | 2 | DG141a | Beenanaspuck & Tobertoreen | 1 | Full | 23.15 | 23.1 | 2020-04-01 | 23.15 MW Wind + 11 MW Battery | Kerry | 7 | Y | DG131 | Ballybay Wind Farm (Tullaroan) | Wind | 13.8 | Thurles | 38 kV | 6 | Gate 3 | Energised | 2017-07-07 |  | Slieve Divena 1 | 30 | 30 | 30 | Connected | 2009-01-07 | Distribution | Wind | Controllable
54 | Wind | Onshore | 3 | TG44 | Carrigdangan | 1 | Full | 54.3 | 54.3 | 2021-01-01 |  | Cork |  | Y | DG120 | Lissycasey Wind Farm | Wind | 13.399 | BOOLTIAGH | 38 kV |  | Gate 3 | Energised | 2019-10-31 |  | Slieve Divena 2 | 18.8 | 18.8 | 20 | Connected | 2017-02-08 | Distribution | Wind | Controllable
[15 empty] | TG41 | Cappawhite B Wind Farm (Cappagh White) | Wind | 13.18 | Cauteen | 38 kV | 4 | Gate 2 | Connected | 2018-06-19 |  | Slieve Kirk | 73.6 | 73.6 | 27.6 | Connected | 2011-09-01 | Transmission | Wind | Controllable
Note: The Full/latest connection dates for TSO-connected windfarms listed in the above table do not reflect the gradual growth of installed capacity | [14 empty] | DG940 | Moanmore Wind Farm | Wind | 12.6 | Tullabrack | 38 kV | 7 | Pre-Gate | Connected | 2004-12-21 |  | Slieve Rushen (Mantlin) | 54 | 54 | 54 | Connected | 2007-10-31 | Distribution | Wind | Controllable
during the months/years preceding that date. This progression is reflected more accurately in the tables listed in the "Wind Installed Capacities" tab. | [14 empty] | DG151 | Cloghaneleskirt Wind Farm | Wind | 12.55 | Cloghboola | 20 kV | 5 | Gate 2 | Energised | 2018-04-27 |  | Slieveglass | 6.9 | 6.9 | 0 | Connected | 2018-07-01 | Distribution | Wind | TBC
[15 empty] | DG17 | Rathcahill West Wind Farm | Wind | 12.5 | Rathkeale | 38 kV | 5 | PMOD | Connected | 2011-06-15 |  | Slievehanaghan | 0.9 | 0.9 | N/A | Connected | 1999-01-01 | Distribution | Wind | Uncontrollable
[15 empty] | DG312 | Black Lough Wind farm | Wind | 12.5 | Glenree | 20 kV | 6 | ECP-1 | Energised | 2020-03-13 |  | Snugborough | 13.5 | 13.5 | 13.5 | Connected | 2004-01-01 | Distribution | Wind | Uncontrollable
[15 empty] | DG321 | Glanaruddery 2 (formerly Dromadda More 2) | Wind | 12 | Cloghboola | 20 kV | 4 | Gate 3 | Energised | 2018-02-13 |  | Tappaghan | 28.5 | 28.5 | 28.5 | Connected | 2005-04-01 | Distribution | Wind | Controllable
[15 empty] | DG406 | Tullynamoyle Wind Farm 3 (Formerly Geevagh 2) | Wind | 11.98 | Corderry | 20 kV | 4 | Gate 3 | Energised | 2017-09-18 |  | Teiges | 12.5 | 11 | 0 | Connected | 2018-07-01 | Distribution | Wind | TBC
[15 empty] | DG38 | Meenachullalan Wind Farm | Wind | 11.9 | Binbane | 38 kV | 5 | Gate 1 | Connected | 2008-06-19 |  | Thornog | 20 | 20 | 10 | Connected | 2014-09-16 | Distribution | Wind | Controllable
[15 empty] | DG919 | Carnsore Wind Farm | Wind | 11.9 | Wexford | 38 kV | 14 | Pre-Gate | Connected | 2002-08-30 |  | Tievenameenta | 34.5 | 34.5 | 0 | Connected | 2016-09-20 | Distribution | Wind | Controllable
[15 empty] | DG963 | Culliagh Wind Farm (Meenbog) | Wind | 11.88 | Letterkenny | 38 kV | 18 | Pre-Gate | Connected | 2000-12-05 |  | Wolf Bog | 10 | 10 | 10 | Connected | 2007-11-23 | Distribution | Wind | Controllable
[15 empty] | DG222 | Ballybane 2A (Glanta Commons) Wind Farm | Wind | 11.5 | Ballylickey | 38 kV | 6 | Gate 3 | Energised | 2015-01-30 |  | Aggregated Small Scale Wind Generation | 157.774 | 155.684 |  | Connected |  | Distribution | Wind | Uncontrollable
[15 empty] | DG294 | Raragh 2 Wind Farm | Wind | 11.5 | Meath Hill | 20 kV | 5 | Gate 3 | Energised | 2019-11-28
[15 empty] | DG213 | An Cnoc | Wind | 11.5 | Thurles | 20 kV | 5 | Gate 3 | Energised | 2017-09-19
[15 empty] | DG938 | Gartnaneane (1) Wind Farm | Wind | 10.5 | Meath Hill | 38 kV | 7 | Pre-Gate | Connected | 2004-11-13
[15 empty] | DG911 | Dromdeeveen Wind Farm (1) | Wind | 10.5 | Glenlara | 38 kV | 14 | PMOD | Connected | 2011-08-24
[15 empty] | DG1076 | Tullynamoyle 2 Wind Farm | Wind | 10.225 | CORDERRY | 20 kV | 5 | Gate 3 | Energised | 2017-11-17
[15 empty] | DG85 | Caherdowney Wind Farm | Wind | 10 | Garrow | 20 kV | 4 | Gate 2 | Energised | 2012-08-27
[15 empty] | DG217 | Glantaunyalkeen Windfarm | Wind | 9.999 | Cloghboola | 20 kV | 3 | Gate 3 | Energised | 2018-09-08
[15 empty] | TG93B | Meenwaun Wind Farm | Wind | 9.99 | Dallow | 20 kV | 4 | Gate 3 | Energised | 2017-12-21
[15 empty] | DG43 | Corkermore Wind Farm Phase 1 | Wind | 9.99 | Binbane | 38 kV | 5 | Gate 1 | Connected | 2011-08-17
[15 empty] | DG173 | Drumlough Hill (2) (Lough Doo) | Wind | 9.99 | Trillick | 38 kV | 12 | Pre-Gate | Connected | 2011-04-30
[15 empty] | DG306 | Ballycadden Wind Farm (2) | Wind | 9.762 | Crory | 20 kV | 4 | Gate 3 | Energised | 2012-10-12
[15 empty] | DG157 | Foyle Wind Farm (prev Holmes Hill) | Wind | 9.6 | Thurles | 20 kV | 4 | Gate 3 | Energised | 2017-07-07
[15 empty] | DG947 | Gneeves Wind Farm | Wind | 9.35 | Knockearagh | 38 kV | 11 | Pre-Gate | Connected | 2005-10-04
[15 empty] | DG269A | Clogheravaddy Wind Farm (Phase 1) | Wind | 9.2 | Binbane | 38 kV |  | Gate 3 | Energised | 2019-12-03
[15 empty] | DG60 | Flughland | Wind | 9.2 | SORNE HILL | 20 kV | 4 | Gate 2 | Connected | 2010-07-08
[15 empty] | DG285 | Lisdowney Wind Farm | Wind | 9.2 | PORTLAOISE 110KV | 20 kV | 4 | Gate 3 | Energised | 2016-10-14
[15 empty] | DG194 | Hollyford(Holyford) Wind Farm | Wind | 9 | Cauteen | 20 kV | 3 | Gate 2 | Energised | 2013-12-13
[15 empty] | DG118 | Knockaneden Wind Farm | Wind | 9 | Oughtragh | 38 kV | 3+1 | Gate 2 | Connected | 2012-09-14
[15 empty] | DG265 | Teevurcher Wind Farm | Wind | 9 | Meath Hill | 20 kV | 5 | Gate 3 | Energised | 2017-12-18
[15 empty] | DG214 | Tullynamoyle | Wind | 9 | Corderry | 20 kV | 4 | Gate 2 | Connected | 2011-11-17
[15 empty] | DG133 | Garranereagh Wind Farm | Wind | 8.75 | Bandon | 20 kV | 4 | Gate 2 | Connected | 2013-04-30
[15 empty] | DG05 | Kealkil Wind Farm | Wind | 8.5 | Ballylickey | 38 kV | 10 | Pre-Gate | Connected | 2006-08-22
[15 empty] | DG47 | Derrynadivva Wind Farm (prev. Raheen Bar 2) | Wind | 8.5 | Castlebar | 38 kV | 10 | Gate 2 | Connected | 2009-11-12
[15 empty] | DG48 | Ballybane 2 (Glanta Commons) Wind Farm | Wind | 8.4 | Ballylickey | 38 kV | 4 | Gate 2 | Connected | 2009-04-01
[15 empty] | DG408 | Ballymartin (2) - Smithstown | Wind | 8.28 | Waterford | 20 kV | 4 | Gate 3 | Energised | 2013-03-29
[15 empty] | DG1817 | Sorrell Island (Glenmore) WF Ext | Wind | 8 | BOOLTIAGH | 38 kV | 3 | ECP-1 | Energised | 2020-10-30
[15 empty] | DG121 | Killaveenoge Windfarm - (Derryvacorneen merge with Barrboy) | Wind | 7.8 | Dunmanway | 38 kV | 10 | Gate 3 | Energised | 2016-12-16
[15 empty] | DG933 | Sonnagh Old Phase 1 | Wind | 7.65 | Somerset | 38 kV | 9 | Pre-Gate | Connected | 2004-05-27
[15 empty] | DG945 | Altagowlan Wind Farm | Wind | 7.65 | Corderry | 20 kV | 9 | Pre-Gate | Connected | 2005-09-23
[15 empty] | DG46 | Loughderryduff Wind Farm | Wind | 7.65 | Binbane | 38 kV | 9 | Gate 1 | Connected | 2008-10-07
[15 empty] | DG87 | Carrickeeny Wind Farm | Wind | 7.65 | Sligo | 20 kV | 4 | Gate 3 | Energised | 2014-02-28
[15 empty] | DG912 | Knockastanna Wind Farm | Wind | 7.5 | Ardnacrusha | 20 kV | 5 | PMOD | Connected | 2009-10-28
[15 empty] | DG36 | Mullananalt Wind Farm | Wind | 7.5 | Meath Hill | 38 kV | 5 | Gate 1 | Connected | 2008-01-01
[15 empty] | DG18 | Tournafulla Wind Farm (1) | Wind | 7.5 | Trien | 38 kV | 5 | Pre-Gate | Connected | 2007-01-26
[15 empty] | DG59 | Sorne Hill (2) | Wind | 7.4 | SORNE HILL | 110 kV | 3 | Gate 2 | Connected | 2009-06-01
[15 empty] | DG284 | Meenaward Wind Farm (Formerly Beam Hill 2) | Wind | 6.9 | Trillick | 38 kV | 3 | Gate 3 | Energised | 2017-12-15
[15 empty] | DG163 | Derrynadivva Extension | Wind | 6.8 | Castlebar | 38 kV | 3 | Gate 2 | Energised | 2019-12-18
[15 empty] | DG921 | Black Banks (2) | Wind | 6.8 | Corderry | 20 kV | 8 | Pre-Gate | Connected | 2005-09-08
[15 empty] | DG941a | Tursillagh (2) Wind Farm | Wind | 6.8 | Tralee | 38 kV | 8 | Pre-Gate | Connected | 2004-09-16
[15 empty] | DG34 | Richfield Wind Farm (2) | Wind | 6.75 | Wexford | 38 kV | 4 | Gate 1 | Connected | 2006-08-01
[15 empty] | DG35a | Knockawarriga Extension (Knockacummer & Caherlevoy) Wind Farm | Wind | 6.6 | Trien | 38 kV | 3 | Gate 2 | Energised | 2020-02-12
[15 empty] | DG955 | Bellacorrick Wind Farm | Wind | 6.45 | Bellacorick | 20 kV | 21 | Pre-Gate | Connected | 1992-10-01
[15 empty] | DG101 | Faughary Wind Farm | Wind | 6 | Sligo | 20 kV | 3 | Gate 3 | Energised | 2014-12-12
[15 empty] | DG52 | Lackan Wind Farm | Wind | 6 | Moy | 20 kV | 3 | Gate 1 | Connected | 2007-05-01
[15 empty] | DG148 | Cahermurphy Wind Farm | Wind | 6 | BOOLTIAGH | 20 kV | 3 | Gate 3 | Energised | 2020-01-15
[15 empty] | DG44 | Killin Hill Wind Farm | Wind | 6 | Binbane | 38 kV | 3 | Gate 1 | Energised | 2017-06-23
[15 empty] | DG130 | Ballymartin (1) (Smithstown) | Wind | 6 | Waterford | 20 kV | 3 | Gate 2 | Connected | 2011-09-30
[15 empty] | DG939 | Coomatallin Wind Farm | Wind | 5.95 | Dunmanway | 20 kV | 7 | Pre-Gate | Connected | 2005-01-01
[15 empty] | DG971 | Largan Hill | Wind | 5.94 | Tonroe | 38 kV | 9 | Pre-Gate | Connected | 2000-11-01
[15 empty] | DG973 | Milane Hill Wind Farm | Wind | 5.94 | Dunmanway | 38 kV | 9 | Pre-Gate | Connected | 2000-09-01
[15 empty] | DG918 | Mount Eagle Wind Farm | Wind | 5.1 | Tralee | 20 kV | 6 | Pre-Gate | Connected | 2005-03-01
[15 empty] | DG970 | Kilronan | Wind | 5 | Arigna | 20 kV | 10 | Pre-Gate | Connected | 1997-12-01
[15 empty] | DG37 | Knocknalour Wind Farm (1) | Wind | 5 | Crory | 20 kV | 4 | Gate 1 | Energised | 2013-06-20
[15 empty] | DG962 | Crockahenny | Wind | 5 | Trillick | 38 kV | 10 | Pre-Gate | Connected | 1998-04-01
[15 empty] | DG190 | Ballycurreen Wind Farm | Wind | 4.99 | Dungarvan | 20 kV | 2 | Gate 3 | Energised | 2014-02-01
[15 empty] | DG39 | Lurganboy Wind Farm | Wind | 4.99 | Letterkenny | 20 kV | 6 | Gate 1 | Connected | 2008-06-20
[15 empty] | DG267 | Kiltumper Wind Farm | Wind | 4.99 | BOOLTIAGH | 20 kV | 2 | Gate 3 | Energised | 2019-12-18
[15 empty] | DG45 | Cronelea Wind Farm | Wind | 4.99 | Carlow | 20 kV | 2 | Gate 1 | Connected | 2007-05-21
[15 empty] | DG174 | Clydaghroe Wind Farm | Wind | 4.99 | Garrow | 20 kV | 2 | Gate 2 | Connected | 2012-10-31
[15 empty] | DG113 | Carrons (A&B) Wind Farm | Wind | 4.99 | Rathkeale | 38 kV | 2 + 1 | Gate 2 | Energised | 2010-11-26
[15 empty] | DG942 | Greenoge Wind Farm | Wind | 4.99 | Crane | 20 kV | 4 | Pre-Gate | Connected | 2005-04-01
[15 empty] | DG974 | Mount Cronalaght | Wind | 4.98 | Letterkenny | 38 kV | 8 | Pre-Gate | Connected | 1997-07-01
[15 empty] | DG40 | Geevagh Wind Farm | Wind | 4.95 | Corderry | 20 kV | 6 | Pre-Gate | Connected | 2006-02-16
[15 empty] | DG961 | Corrie Mt. | Wind | 4.8 | Arigna | 20 kV | 8 | Pre-Gate | Connected | 1997-03-01
[15 empty] | DG920 | Drumlough Hill Wind Farm | Wind | 4.8 | Trillick | 38 kV | 8 | Pre-Gate | Connected | 1997-08-01
[15 empty] | DG303 | Kilberehert Wind Farm | Wind | 4.799 | Charleville | 20 kV | 3 | Gate 3 | Connected | 2017-03-28
[15 empty] | DG93 | Kilmeedy Wind Farm | Wind | 4.7 | Charleville | 20 kV | 2 | Gate 3 | Energised | 2016-12-22
[15 empty] | DG162 | Lenanavea (Burren) Wind Farm | Wind | 4.65 | Castlebar | 20 kV | 6 | Gate 2 | Connected | 2011-02-07
[15 empty] | DG964 | Currabwee Wind Farm | Wind | 4.62 | Dunmanway | 38 kV | 7 | Pre-Gate | Connected | 1999-11-01
[15 empty] | DG53 | Seltanaveeny Wind Farm | Wind | 4.6 | Arigna | 20 kV | 3 | Gate 2 | Connected | 2011-11-16
[15 empty] | DG154 | Ballincurry Wind Farm Ltd (Glengoole) | Wind | 4.6 | Thurles | 10 kV | 2 | Gate 3 | Energised | 2019-05-31
[15 empty] | DG233 | Ballagh Wind Farm | Wind | 4.6 | Trien | 20 kV | 2 | Gate 3 | Energised | 2018-01-31
[15 empty] | DG128 | Carrownaweelaun Wind Farm | Wind | 4.6 | Tullabrack | 20 kV | 2 | Gate 3 | Energised | 2015-06-17
[15 empty] | DG102 | Skrine Wind Farm | Wind | 4.6 | Lanesborough | 20 kV | 2 | Gate 2 | Connected | 2011-11-17
[15 empty] | DG226 | WEDcross Wind Farm | Wind | 4.5 | Knockearagh | 38 kV | 2 | Gate 2 | Connected | 2009-11-01
[15 empty] | DG905 | Gartnaneane II Wind Farm | Wind | 4.5 | Meath Hill | 20 kV | 3 | Pre-Gate | Connected | 2004-11-13
[15 empty] | DG16 | Kilvinane Wind Farm | Wind | 4.5 | Bandon | 20 kV | 2 + 1 | Pre-Gate | Connected | 2006-08-02
[15 empty] | DG63 | Cronelea Wind Farm (2) | Wind | 4.5 | Carlow | 20 kV | 2 | Gate 2 | Connected | 2009-12-11
[15 empty] | DG54 | Reenascreena Wind Farm | Wind | 4.5 | Dunmanway | 10 kV | 5 | Gate 2 | Connected | 2010-02-10
[15 empty] | DG219 | Curraghderrig | Wind | 4.5 | Trien | 20 kV | 2 | Gate 3 | Energised | 2017-12-14
[15 empty] | DG119 | Boolard Wind Farm | Wind | 4.45 | Charleville | 20 kV | 2 | Gate 3 | Energised | 2019-12-05
[15 empty] | DG222A | Ballybane 3 (Glanta Commons) Wind Farm | Wind | 4.45 | Ballylickey | 38 kV | 2 | Gate 3 | Energised | 2017-01-29
[15 empty] | DG115 | Rathnacally Wind Farm | Wind | 4.45 | Charleville | 20 kV | 2 | Gate 3 | Connected | 2018-07-09
[15 empty] | DG1035 | Gortnacloghy Wind Farm | Wind | 4.4 | Trien | 20 kV | 2 | Gate 3 | Energised | 2018-01-31
[15 empty] | DG67 | Rahora Wind Farm | Wind | 4.25 | Waterford | 20 kV | 5 | Gate 2 | Connected | 2009-10-27
[15 empty] | DG98 | Three Trees | Wind | 4.25 | SORNE HILL | 20 kV | 2 | Gate 2 | Energised | 2019-12-18
[15 empty] | DG139 | Cloonlusk Wind Farm | Wind | 4.25 | Cloon | 20 kV | 2 | Gate 2 | Energised | 2018-01-26
[15 empty] | DG12a | Skehanagh Wind Farm | Wind | 4.25 | Dallow | 20 kV | 5 | PMOD | Connected | 2006-05-29
[15 empty] | DG21 | Lahanaght Hill Wind Farm | Wind | 4.25 | Dunmanway | 20 kV | 5 | PMOD | Connected | 2006-06-08
[15 empty] | DG66 | Leabeg Wind Farm | Wind | 4.25 | Dallow | 20 kV | 2 | Gate 2 | Energised | 2015-09-30
[15 empty] | DG99 | Meenkeeragh Wind Farm | Wind | 4.2 | SORNE HILL | 20 kV | 2 | Gate 2 | Connected | 2009-04-29
[15 empty] | DG195 | Cooly Wind Farm | Wind | 4 | Trillick | 20 kV | 2 | Gate 3 | Energised | 2017-03-15
[15 empty] | DG125 | Ballynancoran Wind Farm | Wind | 4 | Crory | 20 kV | 2 | Gate 2 | Energised | 2013-07-03
[15 empty] | DG106 | Ballyduff Wind Farm | Wind | 4 | Crory | 20 kV | 2 | Gate 2 | Energised | 2017-01-13
[15 empty] | DG954 | Beenageeha Wind Farm | Wind | 3.96 | Tralee | 10 kV | 4 | Pre-Gate | Connected | 2000-10-01
[15 empty] | DG946 | Moneenatieve Wind Farm (1) | Wind | 3.96 | Corderry | 20 kV | 5 | Pre-Gate | Connected | 2005-09-23
[15 empty] | DG307 | Knocknalour Wind Farm G3 | Wind | 3.95 | Crory | 20 kV | 2 | Gate 3 | Connected | 2013-06-20
[15 empty] | DG184 | Templederry Wind Farm | Wind | 3.9 | NENAGH | 20 kV | 2 | Gate 2 | Connected | 2013-01-15
[15 empty] | DG261 | Scartaglen 2 Wind Farm | Wind | 3.8 | Cordal | 38 kV |  | Gate 3 | Energised | 2017-12-12
[15 empty] | DG103 | Roosky Wind Farm | Wind | 3.6 | Tonroe | 10 kV | 2 | Gate 2 | Connected | 2015-11-10
[15 empty] | DG126 | Ballaman (Kennystown) Wind Farm | Wind | 3.6 | Crory | 20 kV | 2 | Gate 2 | Connected | 2013-01-15
[15 empty] | DG921X | Black Banks (1) | Wind | 3.4 | Corderry | 20 kV | 4 | Pre-Gate | Connected | 2001-09-01
[15 empty] | DG931 | Cuillalea Wind Farm | Wind | 3.4 | Castlebar | 10 kV | 4 | Pre-Gate | Connected | 2004-04-01
[15 empty] | DG136a | Monaincha Bog Wind Farm (Gate 2) | Wind | 3.4 | Ikerrin | 38 kV | 15 | Gate 2 | Energised | 2014-01-31
[15 empty] | DG924 | Meenadreen Wind Farm | Wind | 3.4 | Cathaleens Fall | 20 kV | 4 | Pre-Gate | Connected | 2003-05-07
[15 empty] | DG55 | Meenanilta (3) | Wind | 3.4 | Letterkenny | 20 kV | 4 | Gate 2 | Connected | 2012-02-22
[15 empty] | DG908 | Carrane Hill Wind Farm | Wind | 3.4 | Corderry | 20 kV | 4 | Pre-Gate | Connected | 2006-11-01
[15 empty] | DG981 | Mountain Lodge Wind Farm | Wind | 3 | Shankill | 20 kV | 2 | Pre-Gate | Connected | 2009-01-27
[15 empty] | DG257 | Rossaveel Wind Farm | Wind | 3 | Screeb | 10 kV | 1 | Gate 3 | Energised | 2019-06-28
[15 empty] | DG117 | Slievereagh Wind Farm (1) | Wind | 3 | Tipperary | 10 kV | 1 | Gate 2 | Connected | 2010-03-01
[15 empty] | DG960 | CORNEEN Wind Farm | Wind | 3 | Gortawee | 10 kV | 2 | Pre-Gate | Connected | 2001-08-01
[15 empty] | DG405b | Cappawhite A Wind Farm (Gate 2) | Wind | 2.92 | Cauteen | 38 kV | DG405a | Gate 2 | Energised | 2017-08-11
[15 empty] | DG254 | Carrowleagh Wind Farm Ext. (2) | Wind | 2.65 | Glenree | 38 kV | 1 | Gate 3 | Energised | 2019-05-24
[15 empty] | DG923 | Knock South Wind Farm (Inverin) | Wind | 2.64 | Screeb | 20 kV | 4 | Pre-Gate | Connected | 1999-01-01
[15 empty] | DG240 | Tullynamalra Wind Farm | Wind | 2.638 | Meath Hill | 10 kV | 1 | Gate 3 | Energised | 2019-04-15
[15 empty] | DG143 | Bunnahowen Wind Farm (Temp) | Wind | 2.55 | Bellacorick | 20 kV | 3 | Gate 3 | Energised | 2019-12-18
[15 empty] | DG206 | Mace Upper Wind Farm | Wind | 2.55 | Dalton | 20 kV | 3 | Gate 2 | Connected | 2010-01-02
[15 empty] | DG142 | Shannagh (Kilcar) | Wind | 2.55 | Binbane | 10 kV | 3 | Gate 2 | Connected | 2010-07-06
[15 empty] | DG928a | Meenanilta Wind Farm (1) | Wind | 2.55 | Letterkenny | 20 kV | 3 | Pre-Gate | Connected | 2004-03-29
[15 empty] | DG950 | Ballinveny Wind Farm | Wind | 2.55 | NENAGH | 10 kV | 3 | PMOD | Connected | 2006-01-12
[15 empty] | DG61 | Killybegs Wind Farm | Wind | 2.55 | Binbane | 10 kV | 3 | Gate 1 | Connected | 2007-12-19
[15 empty] | DG12 | Carrig Wind Farm | Wind | 2.55 | Dallow | 20 kV | 3 | PMOD | Connected | 2006-05-29
[15 empty] | DG936 | Curraghgraigue Wind Farm | Wind | 2.55 | NENAGH | 10 kV | 3 | Pre-Gate | Connected | 2004-01-01
[15 empty] | DG944 | Cronelea Upper Wind Farm | Wind | 2.55 | Carlow | 20 kV | 3 | Pre-Gate | Connected | 2005-07-01
[15 empty] | DG949 | Ballinlough Wind Farm | Wind | 2.55 | NENAGH | 10 kV | 3 | Pre-Gate | Connected | 2006-01-12
[15 empty] | DG925 | Beale Hill (2) | Wind | 2.55 | Trien | 20 kV | 4 | Pre-Gate | Connected | 2003-08-01
[15 empty] | DG1000 | DePuy 3MW Wind Turbine | Wind | 2.5 | Barnahely | 20 kV | 1 | Non GPA | Energised | 2014-07-21
[15 empty] | DG864 | Grady Joinery Wind Farm | Wind | 2.5 | Tonroe | 10 kV | 1 | Non GPA | Energised | 2017-08-05
[15 empty] | DG183 | Kilbranish Wind Farm | Wind | 2.5 | Crane | 20 kV | 1 | Gate 2 | Energised | 2018-10-11
[15 empty] | DG928 | Meenanilta Wind Farm (2) | Wind | 2.45 | Letterkenny | 20 kV | 3 | Pre-Gate | Connected | 2004-09-13
[15 empty] | DG100 | CURRAGHGRAIGUE (2) Wind Farm | Wind | 2.44 | NENAGH | 10 kV | 3 | Gate 2 | Connected | 2011-10-13
[15 empty] | DG241a | Collon Wind Power Limited (Gate 3) | Wind | 2.3 | Drybridge | 10 kV | 1 | Gate 3 | Energised | 2016-04-11
[15 empty] | DG158 | Gurteen Lower Wind Farm | Wind | 2.3 | Thurles | 10 kV | 1 | Gate 3 | Energised | 2017-08-22
[15 empty] | DG124 | Enros - Sorne Hill Single Turbine | Wind | 2.3 | SORNE HILL | 20 kV | 1 | Gate 2 | Energised | 2019-12-18
[15 empty] | DG235 | Corvin Wind Turbine | Wind | 2.1 | SORNE HILL | 20 kV | 1 | Gate 3 | Energised | 2018-12-20
[15 empty] | DG997 | Wind Energy Project (Janssen) | Wind | 2 | Barnahely | 20 kV | 1 | Non GPA | Energised | 2014-07-01
[15 empty] | ZG937 | Anarget Wind Farm (1) | Wind | 1.98 | Cathaleens Fall | 20 kV | 3 | Pre-Gate | Connected | 2000-09-01
[15 empty] | DG283 | Knocknagoum (2) | Wind | 1.8 | Reamore | 38 kV | 1 | Gate 3 | Energised | 2013-09-13
[15 empty] | DG246 | Dunmore 2 | Wind | 1.8 | Drybridge | 10 kV | 2 | Gate 2 | Energised | 2009-05-01
[15 empty] | DG180 | Cronelea Upper Wind Farm (2) | Wind | 1.7 | Carlow | 20 kV | 2 | Gate 2 | Connected | 2009-12-11
[15 empty] | DG910 | Beallough Wind Farm | Wind | 1.7 | Butlerstown | 10 kV | 2 | PMOD | Connected | 2008-11-01
[15 empty] | DG62 | Dunmore Wind Farm | Wind | 1.7 | Drybridge | 10 kV | 2 | Gate 1 | Connected | 2006-07-01
[15 empty] | DG116 | Mount Eagle Wind Farm (2) | Wind | 1.7 | Tralee | 20 kV | 2 | Gate 1 | Connected | 2008-11-04
[15 empty] | DG167 | Crocane Wind Farm | Wind | 1.7 | Midleton | 10 kV | 2 | Gate 2 | Connected | 2011-04-13
[15 empty] | DG409 | Beale Hill (1) | Wind | 1.65 | Trien | 20 kV | 1 | Pre-Gate | Connected | 2000-11-07
[15 empty] | DG117b | Slievereagh Wind Farm (2) | Wind | 1.6 | Tipperary | 10 kV | 1 | Gate 3 | Energised | 2014-12-01
[15 empty] | DG989 | Liffey Autoproduction Project | Wind | 1.6 | Shankill | 10 kV | 1 | Non GPA | Energised | 2017-12-15
[15 empty] | DG210 | Tullynamoyle Wind Farm 3 (Carrane Hill Merged Capacity) | Wind | 1.598 | Corderry | 20 kV | 2 | Gate 2 | Energised | 2017-09-18
[15 empty] | DG906 | Cuillalea Wind Farm (2) | Wind | 1.59 | Castlebar | 20 kV | 2 | Gate 2 | Connected | 2010-09-08
[15 empty] | DG222B | Ballybane 2A (Glanta Commons) Wind Farm Extension | Wind | 1.55 | Ballylickey | 38 kV | 0 | Gate 3 | Energised | 2017-01-29
[15 empty] | DG1192 | Liffey Autoproduction Project (extension) | Wind | 1.417 | Shankill | 10 kV | 0 | Non GPA | Energised | 2017-12-15
[15 empty] | DG225 | Glackmore Hill (2) | Wind | 1.4 | SORNE HILL | 20 kV | 0 | Gate 2 | Connected | 2009-04-28
[15 empty] | DG110 | Beale Hill (3) Wind Farm | Wind | 1.3 | Trien | 20 kV | 2 | Gate 2 | Energised | 2016-11-14
[15 empty] | DG978 | Spion Kop Wind Farm | Wind | 1.2 | Arigna | 20 kV | 2 | Pre-Gate | Connected | 1997-12-01
[15 empty] | DG324 | Garracummer (2) | Wind | 1 | Cauteen | 38 kV | 0 | Gate 3 | Energised | 2015-02-11
[15 empty] | DG166 | Pluckanes Wind Farm | Wind | 0.85 | Kilbarry | 20 kV | 1 | Gate 2 | Energised | 2013-09-27
[15 empty] | DG241b | Collon Wind Power Limited (Gate 2) | Wind | 0.7 | Drybridge | 10 kV | 0 | Gate 2 | Energised | 2016-04-11
[15 empty] | DG923x | Knock South Wind Farm (2) | Wind | 0.69 | Screeb | 20 kV |  | Pre-Gate | Connected | 1999-02-15
[15 empty] | DG957 | Burtonport Harbour Single Turbine | Wind | 0.66 | Binbane | 10 kV | 1 | Pre-Gate | Connected | 2003-07-25
[15 empty] | DG932 | Mounvaun (Mienvee) Wind Farm | Wind | 0.66 | Ardnacrusha | 20 kV | 1 | Pre-Gate | Connected | 2004-05-17
[15 empty] | DG51 | Glackmore Hill (1) | Wind | 0.6 | SORNE HILL | 20 kV | 1 | Gate 1 | Connected | 2009-04-28
[15 empty] | DG323 | Ballyduff Wind Farm | Wind | 0.6 | Crory | 20 kV | 2 | Gate 3 | Energised | 2017-01-13
[15 empty] | DG993 | Michael Aylward | Wind | 0.5 | Waterford | 20 kV | 1 | Non GPA | Energised | 2016-09-26
[15 empty] | DG223 | Anarget Wind Farm (3) | Wind | 0.5 | Cathaleens Fall | 20 kV | 1 | Gate 3 | Energised | 2011-11-04
[15 empty] | DG569 | Country Crest | Wind | 0.5 | Glasmore | 20 kV | 1 | Non GPA | Connected | 2011-03-16
[15 empty] | DG86 | Dundalk IT Wind Turbine | Wind | 0.5 | Dundalk | 10 kV | 1 | Non GPA | Connected | 2006-01-01
[15 empty] | DG1017 | Mossedge Wind Farm | Wind | 0.5 | SORNE HILL | 20 kV | 1 | Non GPA | Energised | 2019-01-17
[15 empty] | DG887 | Gortnahalla | Wind | 0.499 | Thurles | 10 kV | 1 | Non GPA | Energised | 2019-06-07
[15 empty] | DG1045 | Moyvane Wind | Wind | 0.499 | Trien | LV | 1 | Non GPA | Energised | 2019-12-10
[15 empty] | DG1047 | Kilpatrick Wind | Wind | 0.499 | Bandon | 10 kV | 1 | Non GPA | Energised | 2020-01-30
[15 empty] | DG1071 | Ballon Wind | Wind | 0.499 | Carlow | 10 kV | 1 | Non GPA | Energised | 2017-02-06
[15 empty] | DG1089 | Ballynultagh Wind Farm | Wind | 0.499 | Carlow | 20 kV | 1 | Non GPA | Energised | 2020-03-20
[15 empty] | DG1066 | Tesco Donabate | Wind | 0.499 | Glasmore | 20 kV | 1 | Non GPA | Energised | 2016-09-01
[15 empty] | DG1050 | Patrick Costello Wind Turbine | Wind | 0.495 | Cahir | 20 kV | 1 | Non GPA | Energised | 2018-12-21
[15 empty] | DG820 | KWT Energy Ltd | Wind | 0.49 | Dungarvan | 20 kV | 1 | Non GPA | Energised | 2016-12-20
[15 empty] | DG243 | Meenkeeragh Wind Farm (2) | Wind | 0.4 | Sorne Hill | 20 kV | 2 | Gate 3 | Connected | 2013-04-25
[15 empty] | DG228 | Glackmore Hill (3) | Wind | 0.3 | SORNE HILL | 20 kV | 0 | Gate 2 | Connected | 2009-04-28
[15 empty] | DG897 | Meade Potato Company | Wind | 0.3 | Drybridge | LV | 1 | Non GPA | Connected | 2014-06-03
[15 empty] | DG208 | Moneenatieve Wind Farm (2) | Wind | 0.29 | Corderry | 20 kV | 0 | Gate 2 | Connected | 2011-10-15
[15 empty] | DG481 | Donaghmede Fr Collins Park Wind Farm | Wind | 0.25 | Grange (DR) | LV | 5 | Non GPA | Connected | 2010-10-20
[15 empty] | DG270 | Mounvaun (Mienvee) Wind Farm (2) | Wind | 0.19 | Ardnacrusha | 20 kV | 1 | Non GPA | Connected | 2008-04-18
[15 empty] | DG870 | Burtonstown Autoproducer | Wind | 0.15 | Drybridge | LV | 1 | Non GPA | Energised | 2014-10-01
[15 empty] | DG845 | Burtonstown | Wind | 0.15 | Drybridge | LV | 1 | Non GPA | Energised | 2014-10-01
[15 empty] | DG780 | Tullow Mushroom Growers Ltd | Wind | 0.133 | Carlow | LV | 1 | Non GPA | Connected | 2010-11-01
[15 empty] | DG842 | St Patricks Missionary Society, Co. Wicklow | Wind | 0.13 | Stratford | LV | 1 | Non GPA | Energised | 2012-06-26
[15 empty] | DG937 | Anarget Wind Farm (2) | Wind | 0.02 | Cathaleens Fall | 20 kV | 2 | Pre-Gate | Connected | 2004-12-01
[15 empty] | DG739 | Owenstown | Wind | 0.018 | Griffinrath | LV | 1 | Non GPA | Connected | 2010-12-31
[15 empty] | DG683 | Shalvey Poultry WT | Wind | 0.017 | Shankill | LV | 1 | Non GPA | Energised | 2013-02-01
[15 empty] | DG634 | Lios na Carraige | Wind | 0.017 | Meath Hill | LV | 1 | Non GPA | Connected | 2008-10-01