## AVR Calculations
Dynamic Data |  |  |  | Table of data required for GCCT Report
Description | Value | Unit |  | Mvar Measured Pre-Event | Time of Set-point Change | New Set-point Received (kV) | System Voltage Post-Settling (kV) | Mvar Required Post-Settling | Mvar Measured Post-Settling | Mvar Required After 1 Second | Mvar Measured After 1 Second
Mvar Measured Pre Event | 4.2 | Mvar | Fill in this value | 4.2 | 12:43 | 116 | 115.1 | 13.5 | 13.51 | 12.57 | 12.89
Time of Set-point Change | 12:43 |  | Fill in this value
New Set-point Received (kV) | 116 | kV | Fill in this value
System Voltage Post-Settling (kV) | 115.1 | kV | Fill in this value
Mvar Measured Post-Settling | 13.51 | Mvar | Fill in this value
Mvar Measured After 1 Second | 12.89 | Mvar | Fill in this value
Static Data and Calculated Values
Description | Value | Unit
Installed Capacity | 105 | MW | Fill in this value
MEC | 99.7 | MW | Fill in this value
WFPS Registered Capacity | 100 | MW | Minimum of Installed MW & MEC
Mvar range required under Grid Code | 66 | Mvar | +/- 0.33 Q/Pmax
Nominal System Voltage | 110 | kV | Fill in this value
Droop Setting | 4 | % | Fill in this value
kV Set-point | 116 | kV | taken from table, above
System Voltage post settling | 115.1 | kV | taken from table, above
Required Mvar post settling | 13.5 | Mvar | calculated using equation, below
Measured Mvar prior to set-point change | 4.2 | Mvar | taken from table, above
Required Mvar change | 9.3 | ΔMvar | Required Mvar post settling - Measured Mvar prior to set-point change
Required Mvar 1 second after set-point change | 12.57 | Mvar | Measured Mvar prior to set-point change + (Required Mvar change*0.9)
∆𝑀𝑣𝑎𝑟= (∆𝑘𝑉 ∗〖𝑀𝑣𝑎𝑟〗_𝑟𝑎𝑛𝑔𝑒)/(〖𝑘𝑉〗_𝑛𝑜𝑚𝑖𝑛𝑎𝑙 ∗𝐷𝑟𝑜𝑜𝑝)